## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-09-2026 | during | 13-09-2026 | during | 13-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Titas gas restriction due to RMS maintenance
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 362 | 412 | 412 | 365 | 365 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 149 | 335 | 335 | 145 | 145 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 34 | 55 | 55 | 55 | 15 | 15 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 328 | 335 | 335 | 305 | 305 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 77 | 149.36 | 149.36 | 32 | 32 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 4.8 | 4.2 | 33 | 33 | 2.2 | 2.2 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 42 | 52.19 | 52.19 | 16 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 154 | 294 | 300 | 300 | 32 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 115 | 149 | 149 | 17 | 35 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 105 | 105 | 34 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 505 | 545 | 584 | 584 | 470 | 470 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 34 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 2091.22 | 2521.62 | 5400.16 | 5370.16 | 1678.2 | 2254.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 15 | 0 | 14 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 19 | 19 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 217 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 222 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 17 | 17 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 51 | 24 | 50 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 75 | 100 | 100 | 50 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 7 | 25 | 32 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 24 | 55 | 95.1 | 95.1 | 31 | 50 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.51 | 0 | 4.55 | 0 | 5.21 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 32 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 36 | 54.36 | 54.36 | 0 | 17 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 85 | 100 | 100 | 100 | 37 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 107 | 116 | 116 | 92 | 92 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 23 | 36 | 163 | 163 | 34 | 34 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1212 | 1224 | 1224 | 1224 | 1224 | 1224 | AGC+FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 8 | 4 | 0 | 15 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1020 | 722 | 1150 | 1150 | 1020 | 1020 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3012.51 | 2996.5 | 4102.51 | 4162.96 | 3092.21 | 3303.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 209 | 221.25 | 221.25 | 210 | 210 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 355 | 350.01 | 350.01 | 280 | 300 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 290 | 230 | 342.01 | 342.01 | 200 | 300 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 250 | 393 | 393 | 220 | 300 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 30 | 41.65 | 41.65 | 10 | 43 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 8 | 8 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 35 | 44 | 51 | 51 | 44 | 44 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 150 | 150 | 150 | 20 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 15 | 24 | 24 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 131 | 163 | 163 | 85 | 120 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 101 | 174 | 200 | 200 | 120 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 160 | 140 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 17.83 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 103 | 114 | 114 | 17 | 17 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 33 | 113 | 113 | 27 | 27 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 31 | 115 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 46 | 0 | 75 | 0 | 75 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1692 | 1983 | 2730.77 | 2671.44 | 1597 | 2069.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-09-2026 | during | 13-09-2026 | during | 13-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 8.2 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 154 | 120 | 170 | 120 | 170 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 95 | 60 | 90 | 60 | 90 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.5 | 0 | 50 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 1 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 214.9 | 262 | 538.6 | 546.5 | 263.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 30 | 0 | 0 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 40 | 40 | 39 | 39 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 0 | 0 | 128 | 128 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 0 | 0 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 392 | 380 | 350 | 390 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 400 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1527 | 1525 | 1390 | 1430 | 1489 | 1489
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 797 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 | 25 | 25 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 140 | 205 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 36 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 105 | 105 | 52 | 52 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 45 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 210 | 330 | 330 | 220 | 220 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1090 | 1040 | 1040 | 1040 | 1090 | 1090 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2214 | 2355 | 3375 | 3330 | 2752 | 2699
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 400 | 800 | 800 | 800 | 800 | machine problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 110 | 110 | 16 | 32 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 87 | 117 | 120 | 120 | 116 | 116 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 200 | 307 | 307 | 150 | 150 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.45 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1860.45 | 1609 | 2288 | 2287 | 1900 | 1915
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 61.81 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 24 | 24 | 24 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 146 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 366 | 270 | 413.79 | 413.79 | 390 | 390 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 20 | 26 | 26 | 26 | 26 | 26 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 113 | 113 | 35 | 70 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 50 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.66 | 0 | 0 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 757.45 | 762.16 | 748 | 748 | 748 | 748 | U#2 withdrawn
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 32.1 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1591.02 | 1488.36 | 2520.41 | 2307.99 | 1728.12 | 1610.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 47 | 47 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 155 | 158 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 0 | 35 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 63 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 178 | 0 | 186 | 0 | 182.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 470.3 | 515 | 690 | 469 | 576.56 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 14673.4 | 15255.48 | 23035.45 | 22575.05 | 15076.19 | 16023.52
Forecast Scenario (13-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14900 |  | 2798.15 |  | 17830
|  |  |  | 1:00 | 14220 |  | 2807.7 |  | 17160
|  |  |  | 2:00 | 14020 |  | 2702.65 |  | 16850
|  |  |  | 3:00 | 14080 |  | 2568.95 |  | 16770
|  |  |  | 4:00 | 13980 |  | 2425.7 |  | 16520
|  |  |  | 5:00 | 14030 |  | 1843.15 |  | 15960
|  |  |  | 6:00 | 13940 |  | 1442.05 |  | 15450
|  |  |  | 7:00 | 13890 |  | 1231.95 |  | 15180
|  |  |  | 8:00 | 13820 |  | 620.75 |  | 14470
|  |  |  | 9:00 | 14100 |  | 191 |  | 14300
|  |  |  | 10:00 | 14150 |  | 391.55 |  | 14560
|  |  |  | 11:00 | 14220 |  | 544.35 |  | 14790
|  |  |  | 12:00 | 14680 |  | 802.2 |  | 15520
|  |  |  | 13:00 | 14840 |  | 630.3 |  | 15500
|  |  |  | 14:00 | 14840 |  | 658.95 |  | 15530
|  |  |  | 15:00 | 14690 |  | 1126.9 |  | 15870
|  |  |  | 16:00 | 14460 |  | 955 |  | 15460
|  |  |  | 17:00 | 14390 |  | 802.2 |  | 15230
|  |  |  | 18:00 | 14700 |  | 162.35 |  | 14870
|  |  |  | 18:30 | 14800 |  | 845.175 |  | 15685
|  |  |  | 19:00 | 14900 |  | 1528 |  | 16500
|  |  |  | 19:30 | 14680 |  | 1948.2 |  | 16720
|  |  |  | 20:00 | 14850 |  | 1833.6 |  | 16770
|  |  |  | 21:00 | 15260 |  | 1585.3 |  | 16920
|  |  |  | 22:00 | 15370 |  | 1155.55 |  | 16580
|  |  |  | 23:00 | 15250 |  | 1327.45 |  | 16640
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15520.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1585
Probable Maximum Demand at Evening Peak: |  |  | 16920.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 20717.20 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 462.52882 MKWHr. |  | 400 | 115 | 170 | 250 | 100 | 200 | 80 | 150 | 120 | 1585
*** This report is generated digitally from Operation Information System (OIS) at 09:56 hrs on 13-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-09-2026 | [28 empty] | Date: | 12-09-2026 | [28 empty] | Date: | 12-09-2026 | [28 empty] | Date: | 12-09-2026 | [28 empty] | Date: | 12-09-2026 | [17 empty] | Date: | 12-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 54 | 35 | 149 | 30 | 294 | 55 | 55 | 162 | 0 | 141 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 2.5 | 22 | 0 | 410 | 107 | 16 | 48 | 0 | 7 | 51 | 54 | 17 | 100 | 100 | 0 | 222 | 17 | 42 | 1020 | 35 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 20 | 45 | 240 | 280 | 250 | 44 | 0 | 221 | 10 | 108 | 138 | 127 | 28 | 19 | 16 | 158 | 0 | 0 | 0 | 315 | 400 | 380 | 40 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 127 | 0 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9090.92 | 835 | 0 | 0 | 13 | 42 | 0 | 230 | 0 | 0 | 0 | 15 | 0 | 1090 | 17 | 0 | 0 | 752.48 | 0 | 24 | 0 | 35 | 35 | 0 | 69 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 154 | 49 | 114 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 6133.68 | 15224.6 | 105.66
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 54 | 17 | 149 | 30 | 146 | 55 | 35 | 72 | 0 | 136 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 3 | 22 | 0 | 440 | 109 | 16 | 31 | 0 | 22 | 51 | 23 | 0 | 75 | 100 | 0 | 221 | 17 | 42 | 1020 | 35 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 18 | 45 | 240 | 280 | 270 | 44 | 0 | 221 | 10 | 102 | 140 | 57 | 8 | 19 | 16 | 150 | 0 | 0 | 0 | 310 | 400 | 380 | 41 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 141 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8549.42 | 835 | 0 | 0 | 13 | 41 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 751.77 | 0 | 24 | 0 | 0 | 0 | 0 | 69 | 21 | 52.2 | 0 | 0 | 25 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 156 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5914.97 | 14464.39 | 105.66
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 54 | 17 | 149 | 30 | 146 | 55 | 35 | 72 | 0 | 141 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 3 | 22 | 0 | 470 | 107 | 16 | 24 | 0 | 17 | 51 | 23 | 0 | 75 | 100 | 0 | 219 | 17 | 42 | 1020 | 36 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1163 | 0 | 18 | 45 | 260 | 300 | 270 | 44 | 0 | 221 | 10 | 75 | 140 | 51 | 0 | 19 | 16 | 146 | 0 | 0 | 0 | 290 | 400 | 380 | 41 | 40 | 0 | 0 | 0 | 0 | 86 | 0 | 142 | 0 | 127 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8479.42 | 835 | 0 | 0 | 13 | 41 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 758.85 | 0 | 24 | 0 | 0 | 0 | 0 | 69 | 14 | 52.2 | 0 | 0 | 25 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 156 | 52 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5902.05 | 14381.47 | 105.67
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 54 | 17 | 149 | 30 | 146 | 55 | 35 | 72 | 0 | 141 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 3 | 14 | 0 | 440 | 109 | 16 | 24 | 0 | 9 | 51 | 23 | 0 | 75 | 100 | 0 | 218 | 17 | 42 | 1020 | 35 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 20 | 26 | 260 | 300 | 270 | 44 | 0 | 217 | 10 | 69 | 140 | 52 | 0 | 19 | 16 | 144 | 0 | 0 | 0 | 300 | 400 | 340 | 41 | 40 | 0 | 0 | 0 | 0 | 86 | 0 | 140 | 0 | 127 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8373.42 | 835 | 0 | 0 | 13 | 41 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 755.45 | 0 | 24 | 0 | 0 | 0 | 0 | 68 | 14 | 52.2 | 0 | 0 | 25 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 156 | 51 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5978.65 | 14352.07 | 105.37
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35 | 17 | 134 | 30 | 146 | 55 | 35 | 72 | 0 | 138 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 3 | 14 | 0 | 480 | 107 | 16 | 25 | 0 | 3 | 51 | 23 | 0 | 75 | 100 | 0 | 172 | 17 | 42 | 1020 | 35 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 20 | 26 | 260 | 300 | 270 | 35 | 0 | 217 | 10 | 69 | 141 | 52 | 0 | 19 | 16 | 144 | 0 | 0 | 0 | 300 | 400 | 319 | 41 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 142 | 0 | 127 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8381.42 | 835 | 0 | 0 | 13 | 30 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 758.84 | 0 | 24 | 0 | 0 | 0 | 0 | 68 | 14 | 52.2 | 0 | 0 | 25 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 154 | 51 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5935.04 | 14316.46 | 105.68
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35 | 17 | 134 | 30 | 146 | 55 | 35 | 72 | 0 | 143 | 0 | 0 | 35 | 293 | 0 | 0 | 0 | 143.42 | 3 | 14 | 0 | 520 | 107 | 16 | 24 | 0 | 10 | 51 | 23 | 0 | 75 | 100 | 0 | 173 | 17 | 42 | 1020 | 35 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1224 | 0 | 20 | 26 | 260 | 300 | 270 | 35 | 0 | 217 | 10 | 69 | 141 | 52 | 0 | 19 | 16 | 140 | 0 | 0 | 0 | 310 | 400 | 319 | 41 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 142 | 0 | 124 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8414.42 | 835 | 0 | 0 | 10 | 30 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 0 | 0 | 757.27 | 0 | 24 | 0 | 0 | 0 | 0 | 68 | 14 | 52.2 | 0 | 0 | 25 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 156 | 52 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5879.47 | 14293.89 | 105.68
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 17 | 133 | 30 | 146 | 55 | 17 | 72 | 0 | 149 | 0 | 0 | 35 | 307 | 0 | 0 | 0 | 143.42 | 3 | 14 | 0 | 480 | 107 | 16 | 18 | 0 | 4 | 0 | 23 | 0 | 75 | 100 | 0.03 | 174 | 17 | 42 | 1020 | 35 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 1160 | 1 | 20 | 26 | 230 | 300 | 240 | 35 | 0 | 206 | 10 | 69 | 141 | 52 | 0 | 19 | 16 | 142 | 0 | 2 | 0 | 305 | 400 | 220 | 41 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 140 | 0 | 125 | 0 | 59 | 0.02 | 67 | 0 | 0 | 0.09 | 12 | 8070.56 | 835 | 0 | 0 | 10 | 30 | 0 | 175 | 0 | 0 | 0 | 0 | 1 | 1090 | 17 | 0 | 0 | 760.16 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 0.24 | 0 | 25 | 0 | 0.35 | 156 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0.04 | 154 | 48 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5778 | 13848.56 | 105.69
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 17 | 133 | 30 | 146 | 55 | 17 | 72 | 0 | 144 | 0 | 0 | 35 | 300 | 0 | 0 | 3 | 143.42 | 3 | 14 | 0 | 480 | 100 | 16 | 18 | 0 | 7 | 0 | 23 | 0 | 50 | 100 | 0.23 | 175 | 17 | 38 | 1020 | 35 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 1160 | 5 | 18 | 26 | 230 | 300 | 240 | 35 | 0 | 198 | 10 | 68 | 141 | 52 | 0 | 19 | 16 | 136 | 0 | 9 | 0 | 310 | 400 | 220 | 40 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 142 | 0 | 124 | 0 | 59 | 2.33 | 67 | 0 | 0.4 | 4.48 | 8 | 8025.86 | 835 | 0 | 0 | 0 | 30 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 1090 | 17 | 0 | 0 | 759.32 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 5.7 | 13 | 25 | 0 | 6.23 | 158 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0.57 | 156 | 47 | 95 | 3 | 0 | 0 | 0 | 0 | 1.5 | 17 | 0.09 | 16 | 200 | 117 | 220 | 0 | 800 | 570 | 17 | 5755.61 | 13781.47 | 105.69
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 17 | 133 | 30 | 146 | 55 | 17 | 72 | 0 | 142 | 0 | 0 | 35 | 305 | 0 | 0 | 10 | 143.42 | 2.8 | 14 | 0 | 470 | 87 | 16 | 19 | 0 | 1 | 0 | 23 | 0 | 50 | 100 | 1.56 | 176 | 17 | 23 | 1020 | 35 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 1155 | 12 | 20 | 83 | 220 | 280 | 200 | 35 | 0 | 220 | 10 | 70 | 141 | 61 | 1 | 8 | 0 | 142 | 0 | 30 | 0 | 305 | 400 | 346 | 40 | 40 | 0 | 1 | 16 | 0 | 86 | 0 | 142 | 0 | 124 | 0 | 59 | 11 | 67 | 0 | 1.12 | 8.03 | 12 | 8140.93 | 835 | 0 | 0 | 0 | 30 | 0 | 120 | 0 | 0 | 0 | 0 | 48 | 1078 | 17 | 0 | 0 | 760.5 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 13.12 | 28 | 25 | 0 | 12.74 | 158 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.38 | 153 | 47 | 93 | 7 | 0 | 0 | 0 | 0 | 1.4 | 58 | 0.2 | 16 | 200 | 116 | 180 | 0 | 800 | 570 | 17 | 5775.54 | 13916.47 | 105.7
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 134 | 30 | 110 | 45 | 17 | 72 | 0 | 140 | 0 | 0 | 35 | 286 | 0 | 0 | 17 | 143.42 | 2.8 | 14 | 0 | 415 | 15 | 16 | 19 | 0 | 0 | 0 | 8 | 0 | 12 | 100 | 3.12 | 222 | 17 | 14 | 1020 | 17 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1155 | 10 | 20 | 108 | 220 | 280 | 200 | 35 | 0 | 188 | 10 | 34 | 141 | 102 | 9 | 8 | 0 | 144 | 0 | 34 | 0 | 300 | 400 | 354 | 40 | 40 | 0 | 1 | 8 | 0 | 84 | 0 | 141 | 0 | 124 | 0 | 59 | 7.6 | 70 | 0 | 1.08 | 15.81 | 12 | 7918.83 | 930 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 19 | 1043 | 17 | 0 | 0 | 752.27 | 0 | 24 | 0 | 0 | 1 | 0 | 0 | 0 | 8 | 36.35 | 59 | 25 | 0 | 16.94 | 158 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.16 | 157 | 47 | 50 | 25 | 0 | 0 | 0 | 0 | 5.7 | 92 | 0.19 | 16 | 200 | 87 | 220 | 0 | 800 | 570 | 17 | 5797.61 | 13716.44 | 105.7
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 133 | 30 | 110 | 30 | 35 | 72 | 0 | 150 | 0 | 0 | 35 | 302 | 0 | 0 | 25 | 105 | 4.8 | 14 | 0 | 505 | 15 | 16 | 21 | 0 | 0 | 0 | 7 | 0 | 12 | 12 | 3.38 | 221 | 17 | 4 | 1020 | 16 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1160 | 18 | 20 | 8 | 280 | 280 | 265 | 35 | 0 | 201 | 10 | 16 | 141 | 17 | 9 | 16 | 0 | 140 | 0 | 41 | 0 | 305 | 400 | 388 | 37 | 37 | 0 | 2 | 8 | 0 | 84 | 0 | 142 | 0 | 124 | 0 | 59 | 8.17 | 114 | 0 | 2.1 | 22.43 | 12 | 7973.88 | 930 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 22 | 1040 | 17 | 0 | 0 | 750.8 | 0 | 24 | 0 | 0 | 30 | 0 | 0 | 0 | 8 | 37.12 | 50 | 25 | 0 | 23.61 | 157 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 2.36 | 155 | 46 | 35 | 12 | 0 | 0 | 0 | 0 | 6.3 | 154 | 0.18 | 16 | 200 | 87 | 220 | 0 | 800 | 570 | 17 | 5915.37 | 13889.25 | 105.71
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 17 | 120 | 30 | 110 | 30 | 35 | 72 | 0 | 142 | 0 | 0 | 35 | 303 | 0 | 0 | 32 | 105 | 4.8 | 14 | 0 | 505 | 15 | 16 | 25 | 0 | 0 | 0 | 7 | 0 | 12 | 12 | 4.62 | 222 | 17 | 2 | 1000 | 16 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1180 | 17 | 20 | 8 | 350 | 354 | 290 | 35 | 0 | 197 | 10 | 16 | 140 | 17 | 8 | 19 | 0 | 152 | 0 | 69 | 0 | 305 | 400 | 392 | 29 | 37 | 0 | 4 | 8 | 0 | 86 | 0 | 142 | 0 | 126 | 0 | 59 | 9.3 | 114 | 0 | 0.7 | 23.47 | 12 | 8206.89 | 930 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 42 | 1045 | 17 | 0 | 0 | 759.03 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 41.1 | 82 | 20 | 0 | 14.6 | 158 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1.99 | 154 | 48 | 35 | 33 | 0 | 0 | 0 | 0 | 7.9 | 202 | 0.4 | 16 | 150 | 88 | 220 | 0 | 800 | 570 | 17 | 6012.02 | 14218.91 | 105.71
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 17 | 115 | 30 | 154 | 34 | 35 | 72 | 0 | 140 | 0 | 0 | 35 | 335 | 0 | 0 | 19 | 143.42 | 4.8 | 14 | 0 | 505 | 90 | 16 | 24 | 0 | 6 | 0 | 7 | 0 | 50 | 85 | 2.51 | 222 | 17 | 2 | 1020 | 23 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 1212 | 10 | 20 | 0 | 280 | 354 | 290 | 35 | 0 | 210 | 0 | 31 | 138 | 101 | 8 | 19 | 0 | 160 | 0 | 46 | 0 | 300 | 400 | 392 | 29 | 39 | 0 | 5 | 8 | 0 | 86 | 0 | 142 | 0 | 126 | 0 | 59 | 8.2 | 113 | 0 | 1.2 | 21.5 | 12 | 8537.63 | 930 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 37 | 1090 | 17 | 0 | 0 | 757.45 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 61.81 | 110 | 20 | 0 | 32.1 | 156 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 3.66 | 155 | 50 | 63 | 19 | 0 | 0 | 0 | 0 | 5.3 | 178 | 0.45 | 16 | 150 | 87 | 220 | 0 | 800 | 570 | 17 | 6135.77 | 14673.4 | 105.72
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 17 | 105 | 30 | 195 | 55 | 35 | 72 | 0 | 141 | 0 | 0 | 17 | 311 | 0 | 0 | 34 | 143.42 | 4.8 | 14 | 0 | 510 | 90 | 16 | 26 | 0 | 0 | 0 | 29 | 17 | 50 | 88 | 4.4 | 220 | 17 | 0 | 1020 | 34 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 1175 | 13 | 20 | 0 | 260 | 320 | 250 | 35 | 0 | 216 | 0 | 75 | 138 | 119 | 9 | 19 | 0 | 160 | 0 | 29 | 0 | 300 | 400 | 392 | 29 | 37 | 0 | 4 | 16 | 0 | 86 | 0 | 141 | 0 | 124 | 0 | 58 | 12.14 | 114 | 0 | 1.9 | 40.62 | 12 | 8552.28 | 930 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 95 | 1090 | 17 | 0 | 0 | 759.14 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 13.35 | 109 | 20 | 0 | 61.44 | 152 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 5.23 | 155 | 50 | 95 | 22 | 0 | 0 | 0 | 0 | 8 | 148 | 0.44 | 16 | 150 | 85 | 220 | 0 | 800 | 570 | 17 | 6283.8 | 14836.08 | 105.72
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 97 | 30 | 195 | 55 | 35 | 72 | 0 | 138 | 0 | 0 | 35 | 307 | 0 | 0 | 32 | 143.42 | 4.8 | 14 | 0 | 480 | 107 | 16 | 35 | 0 | 5 | 0 | 27 | 17 | 50 | 75 | 0.69 | 218 | 17 | 0 | 1020 | 36 | 0 | 2 | 8 | 0 | 210 | 0 | 0 | 0 | 1224 | 7 | 20 | 0 | 280 | 355 | 250 | 35 | 0 | 204 | 0 | 108 | 138 | 119 | 8 | 19 | 0 | 156 | 0 | 29 | 0 | 300 | 400 | 392 | 29 | 39 | 0 | 6 | 16 | 0 | 86 | 0 | 142 | 0 | 126 | 0 | 59 | 14.21 | 114 | 0 | 1.1 | 26.1 | 12 | 8641.32 | 930 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 65 | 1090 | 17 | 0 | 0 | 759.62 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 24.63 | 105 | 20 | 0 | 52.89 | 148 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 5.15 | 155 | 49 | 92 | 30 | 0 | 0 | 0 | 0 | 6.8 | 198 | 0.55 | 16 | 200 | 85 | 180 | 0 | 700 | 570 | 36 | 6192.84 | 14834.16 | 105.73
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 17 | 97 | 30 | 225 | 55 | 35 | 72 | 0 | 145 | 0 | 0 | 35 | 307 | 0 | 0 | 26 | 143.42 | 4.5 | 0 | 0 | 460 | 109 | 16 | 40 | 0 | 2 | 0 | 26 | 17 | 50 | 75 | 3.1 | 217 | 17 | 0 | 1020 | 35 | 0 | 18 | 8 | 0 | 223 | 0 | 0 | 0 | 1175 | 5 | 20 | 0 | 300 | 356 | 250 | 35 | 0 | 206 | 0 | 107 | 138 | 120 | 8 | 19 | 0 | 158 | 0 | 37 | 0 | 295 | 400 | 393 | 30 | 40 | 0 | 9 | 16 | 0 | 85 | 0 | 142 | 0 | 125 | 0 | 58 | 18.4 | 114 | 0 | 1.3 | 29.29 | 12 | 8643.01 | 930 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 71 | 1090 | 17 | 0 | 0 | 761.97 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 10.97 | 30 | 20 | 0 | 8.47 | 145 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 1.77 | 155 | 49 | 92 | 23 | 30 | 0 | 0 | 0 | 5.7 | 155 | 0.43 | 16 | 200 | 85 | 220 | 0 | 700 | 570 | 35 | 6047.51 | 14690.52 | 105.74
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17 | 17 | 72 | 30 | 195 | 55 | 35 | 162 | 0 | 141 | 0 | 0 | 35 | 308 | 0 | 0 | 17 | 143.42 | 0 | 14 | 0 | 500 | 107 | 16 | 45 | 0 | 11 | 0 | 26 | 17 | 50 | 75 | 2.07 | 218 | 17 | 0 | 830 | 36 | 0 | 19 | 8 | 0 | 223 | 0 | 0 | 0 | 1160 | 11 | 20 | 0 | 300 | 354 | 230 | 35 | 0 | 202 | 0 | 108 | 137 | 119 | 8 | 19 | 17 | 158 | 0 | 30 | 0 | 305 | 400 | 388 | 30 | 40 | 0 | 6 | 16 | 0 | 85 | 0 | 142 | 0 | 125 | 0 | 58 | 10.83 | 114 | 0 | 1 | 23.03 | 12 | 8517.35 | 929 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 40 | 1090 | 17 | 0 | 0 | 751.91 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 4.76 | 6 | 15 | 0 | 20.06 | 145 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 2.52 | 153 | 51 | 94 | 15 | 40 | 0 | 0 | 0 | 1.1 | 91 | 0.3 | 32 | 200 | 85 | 220 | 0 | 700 | 570 | 35 | 5937.85 | 14455.2 | 105.75
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 54 | 17 | 70 | 30 | 195 | 55 | 35 | 162 | 0 | 138 | 0 | 0 | 35 | 293 | 0 | 0 | 5 | 143.42 | 0 | 14 | 0 | 440 | 109 | 16 | 44 | 0 | 1 | 0 | 36 | 17 | 50 | 88 | 1.18 | 219 | 17 | 0 | 780 | 35 | 0 | 19 | 8 | 0 | 218 | 0 | 0 | 0 | 1160 | 1 | 33 | 0 | 300 | 354 | 230 | 35 | 0 | 196 | 15 | 108 | 138 | 123 | 10 | 19 | 70 | 150 | 0 | 4 | 0 | 310 | 400 | 380 | 30 | 40 | 0 | 3 | 16 | 0 | 85 | 0 | 142 | 0 | 126 | 0 | 57 | 4.3 | 114 | 0 | 0.1 | 7.64 | 12 | 8430.64 | 930 | 0 | 0 | 0 | 15 | 0 | 202 | 0 | 0 | 0 | 32 | 8 | 1090 | 17 | 0 | 0 | 751.5 | 0 | 24 | 0 | 35 | 40 | 0 | 0 | 0 | 52.2 | 2.79 | 4 | 15 | 0 | 9.79 | 145 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0.53 | 156 | 49 | 91 | 7 | 49 | 0 | 0 | 0 | 0.7 | 34 | 0.22 | 48 | 200 | 115 | 220 | 0 | 700 | 570 | 35 | 5956.73 | 14387.37 | 105.76
18:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 17 | 70 | 30 | 195 | 55 | 35 | 162 | 0 | 144 | 0 | 0 | 35 | 305 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 515 | 107 | 16 | 44 | 0 | 0 | 0 | 36 | 17 | 75 | 88 | 0 | 215 | 17 | 0 | 722 | 36 | 0 | 19 | 8 | 0 | 218 | 0 | 0 | 0 | 1192 | 0 | 82 | 0 | 275 | 354 | 230 | 44 | 0 | 205 | 15 | 108 | 138 | 154 | 27 | 19 | 103 | 150 | 0 | 0 | 0 | 310 | 400 | 381 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 140 | 0 | 126 | 0 | 58 | 0.05 | 113 | 0 | 0 | 0 | 12 | 8665.97 | 930 | 0 | 0 | 0 | 24 | 0 | 204 | 0 | 0 | 0 | 50 | 1 | 1090 | 17 | 0 | 0 | 751.09 | 0 | 24 | 0 | 35 | 50 | 0 | 100 | 5 | 52.2 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 158 | 49 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 2 | 0 | 48 | 200 | 115 | 220 | 0 | 700 | 570 | 35 | 6042.29 | 14708.26 | 105.77
19:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 17 | 124 | 30 | 200 | 55 | 55 | 162 | 0 | 144 | 0 | 0 | 35 | 285 | 0 | 0 | 0 | 143.42 | 4.2 | 14 | 0 | 460 | 107 | 16 | 46 | 0 | 0 | 51 | 45 | 17 | 75 | 100 | 0 | 216 | 17 | 4 | 722 | 35 | 0 | 19 | 17.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 107 | 0 | 275 | 355 | 230 | 44 | 0 | 183 | 30 | 103 | 131 | 156 | 27 | 19 | 103 | 148 | 0 | 0 | 0 | 315 | 400 | 355 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 126 | 0 | 94 | 0 | 150 | 0 | 0 | 0 | 12 | 8854.12 | 820 | 0 | 0 | 0 | 32 | 0 | 206 | 0 | 0 | 0 | 50 | 0 | 1090 | 17 | 0 | 0 | 751.67 | 0 | 24 | 0 | 35 | 50 | 0 | 92 | 24 | 52.2 | 0 | 0 | 26 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 157 | 49 | 93 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 800 | 570 | 35 | 6048.87 | 14902.99 | 105.78
19:30 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 17 | 130 | 30 | 245 | 55 | 55 | 162 | 0 | 137 | 0 | 0 | 35 | 301 | 0 | 0 | 0 | 143.42 | 4.2 | 14 | 0 | 490 | 107 | 16 | 50 | 0 | 4 | 51 | 51 | 17 | 75 | 100 | 0 | 216 | 17 | 6 | 722 | 35 | 0 | 19 | 17.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 275 | 353 | 230 | 44 | 0 | 200 | 30 | 115 | 131 | 175 | 27 | 19 | 104 | 146 | 0 | 0 | 0 | 315 | 400 | 355 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 126 | 0 | 95 | 0 | 152 | 0 | 0 | 0 | 12 | 9045.12 | 820 | 0 | 0 | 0 | 36 | 0 | 205 | 0 | 0 | 0 | 50 | 0 | 1090 | 17 | 0 | 0 | 752.2 | 0 | 24 | 0 | 35 | 50 | 0 | 92 | 22 | 52.2 | 0 | 0 | 26 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 158 | 49 | 94 | 0 | 49 | 0 | 100 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 284 | 570 | 35 | 5630.4 | 14675.52
20:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 54 | 17 | 122 | 30 | 294 | 55 | 55 | 162 | 0 | 137 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 4.2 | 14 | 0 | 490 | 109 | 16 | 53 | 0 | 6 | 51 | 51 | 36 | 75 | 100 | 0 | 217 | 17 | 7 | 722 | 36 | 0 | 19 | 17.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 270 | 354 | 230 | 44 | 0 | 196 | 30 | 115 | 131 | 170 | 29 | 19 | 103 | 132 | 0 | 0 | 0 | 320 | 400 | 380 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 126 | 0 | 95 | 0 | 153 | 0 | 0 | 0 | 12 | 9121.12 | 820 | 0 | 0 | 0 | 37 | 0 | 207 | 0 | 51 | 0 | 50 | 0 | 1070 | 17 | 0 | 0 | 754 | 0 | 24 | 0 | 35 | 50 | 0 | 100 | 23 | 52.2 | 0 | 0 | 26 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 157 | 49 | 95 | 0 | 49 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 288 | 570 | 17 | 5732.2 | 14853.32 | 105.78
21:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 115 | 77 | 294 | 55 | 55 | 162 | 0 | 149 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 143.42 | 4.2 | 14 | 0 | 545 | 107 | 32 | 55 | 0 | 8 | 51 | 51 | 36 | 75 | 100 | 0 | 217 | 17 | 7 | 722 | 36 | 0 | 19 | 17.5 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 250 | 355 | 230 | 44 | 0 | 209 | 30 | 115 | 131 | 174 | 33 | 19 | 103 | 140 | 0 | 0 | 0 | 305 | 400 | 380 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 142 | 0 | 126 | 1 | 95 | 0 | 154 | 0 | 0 | 0 | 12 | 9288.12 | 797 | 0 | 0 | 0 | 36 | 0 | 205 | 0 | 210 | 0 | 50 | 0 | 1040 | 17 | 0 | 0 | 762.16 | 0 | 24 | 0 | 35 | 50 | 0 | 100 | 23 | 52.2 | 0 | 0 | 26 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 158 | 49 | 94 | 0 | 49 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 400 | 570 | 54 | 5967.36 | 15255.48 | 105.79
22:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 17 | 115 | 78 | 294 | 55 | 55 | 162 | 0 | 141 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 143.42 | 4.2 | 22 | 0 | 510 | 107 | 32 | 57 | 0 | 0 | 51 | 51 | 36 | 75 | 100 | 0 | 222 | 17 | 6 | 770 | 35 | 0 | 19 | 17.5 | 0 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 250 | 355 | 230 | 44 | 0 | 205 | 30 | 101 | 139 | 173 | 46 | 19 | 103 | 148 | 0 | 0 | 0 | 315 | 400 | 380 | 30 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 126 | 17 | 95 | 0 | 153 | 0 | 0 | 0 | 12 | 9358.12 | 820 | 0 | 0 | 0 | 34 | 0 | 195 | 0 | 200 | 0 | 50 | 0 | 1040 | 17 | 0 | 0 | 765.03 | 0 | 24 | 0 | 35 | 50 | 0 | 100 | 30 | 52.2 | 0 | 0 | 26 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 155 | 49 | 105 | 0 | 49 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 400 | 570 | 54 | 6012.23 | 15370.35 | 105.79
23:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 54 | 17 | 115 | 78 | 294 | 55 | 55 | 162 | 0 | 147 | 0 | 0 | 35 | 309 | 0 | 0 | 0 | 143.42 | 4.2 | 22 | 0 | 460 | 107 | 32 | 52 | 0 | 6 | 51 | 51 | 17 | 75 | 100 | 0 | 221 | 17 | 5 | 850 | 36 | 0 | 19 | 17.5 | 0 | 222 | 0 | 0 | 0 | 1164 | 0 | 61 | 0 | 230 | 354 | 230 | 44 | 0 | 220 | 10 | 86 | 139 | 172 | 44 | 19 | 103 | 150 | 0 | 0 | 0 | 310 | 400 | 386 | 30 | 40 | 0 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 126 | 17 | 96 | 0 | 153 | 0 | 0 | 0 | 12 | 9122.12 | 915 | 0 | 0 | 23 | 40 | 0 | 184 | 0 | 200 | 0 | 50 | 0 | 1040 | 17 | 0 | 0 | 753.4 | 0 | 24 | 0 | 35 | 50 | 0 | 100 | 30 | 52.2 | 0 | 0 | 26 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 156 | 50 | 115 | 0 | 49 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 400 | 570 | 54 | 6124.6 | 15246.72 | 105.8
Total KWH | 0 | 694080 | 390240 | 0 | 0 | 0 | 0 | 0 | 9100800 | 0 | 0 | 861480 | 434520 | 2871648 | 888000 | 4521633 | 1260972 | 858696 | 2528640 | 0 | 3431767 | 0 | 0 | 856659 | 7481694 | 0 | 0 | 222681 | 3332400 | 79800 | 385920 | 0 | 11600909.09 | 2239364 | 459164 | 832320 | 0 | 124800 | 558832 | 678336 | 256746 | 1400640 | 2084160 | 19563 | 5055809 | 423200 | 426720 | 22443636.36 | 807927 | 0 | 300480 | 253211.4 | 0 | 5173963 | 0 | 0 | 0 | 28527270 | 116505 | 1083927 | 535273 | 6375500 | 8150600 | 5990000 | 928264 | 0 | 5128000 | 297504 | 1949760 | 3279946 | 2476320 | 348600 | 448840 | 802560 | 3532800 | 0 | 344373 | 0 | 7404000 | 9538200 | 10801000 | 825000 | 954960 | 0 | 37741 | 313200 | 0 | 2051520 | 0 | 3196000 | 0 | 2732050 | 39600 | 1604400 | 104760 | 2544000 | 0 | 12350 | 239500 | 293280 | 208349013.85 | 21297455 | 0 | 0 | 101280 | 529280 | 0 | 4452672 | 0 | 758331 | 0 | 338256 | 514080 | 25818180 | 418080 | 0 | 0 | 18227273 | 0 | 580339 | 0 | 278208 | 709632 | 0 | 988412 | 245844 | 1096877 | 301160 | 660280 | 520260 | 0 | 288000 | 3657000 | 0 | 0 | 0 | 0 | 0 | 7840073 | 0 | 26760 | 3833000 | 1164218 | 2267816 | 224421 | 541363 | 0 | 750015 | 0 | 45122.64 | 1287360 | 3573 | 700032 | 4712000 | 2569000 | 5399630 | 0 | 16770909 | 14043636.36 | 672000 | 144631828 | 352980841.85

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14673.4 | MW | 12:00 Hr. | Energy Generated |  |  | 352.9808 |  | MKWHr.
| Day Peak Demand |  |  | 14958.69 | MW | 12:00 Hr. | Energy Unserverd |  |  | 24.639 |  | MKWHr.
| Evening Peak Generation |  |  | 15255.48 | MW | 21:00 Hr. | Energy Demand |  |  | 377.6198 |  | MKWHr.
| Evening Peak Demand |  |  | 18178.48 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 13716.44 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 868.83 |  | MMCFD
| Maximum Generation of the Day |  |  | 15370.35 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.8669 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.0809 | 0 | 19.499 | 0 | 0 | 0.22268 | 0 | 0 | 51.8025 | Gas | 126.0971 | Gas | 435338437.4653
| Chattogram Zone |  |  | 5.6007 | 50.9709 | 10.2944 | 0 | 5.0558 | 0.13607 | 0 | 0.1248 | 72.1826 | Coal | 117.3128 | Coal | 834138497.2048
| Cumilla Zone |  |  | 31.1339 | 0 | 6.6612 | 0 | 0 | 0.34437 | 3.5328 | 0 | 41.6723 | HFO | 50.9235 | HFO | 1032161807.372
| Mymensingh Zone |  |  | 0 | 0 | 4.4813 | 0 | 0 | 0.35661 | 0 | 0 | 4.8379 | HSD | 5.961 | HSD | 143205594.84
| Sylhet Zone |  |  | 37.8159 | 0 | 0 | 0 | 0 | 0.037741 | 0 | 0 | 37.8537 | Hydro | 5.0558 | Hydro | 505580.9
| Khulna Zone |  |  | 0 | 25.8182 | 1.3869 | 5.211 | 0 | 0.51408 | 21.2975 | 0 | 54.2276 | Solar | 4.4482 | Solar | 72656299.0004
| Barishal Zone |  |  | 7.9686 | 35.5265 | 1.372 | 0 | 0 | 0.003573 | 0 | 0 | 44.8708 | Import | 43.0575 | Import | 257013268.63
| Rajshahi Zone |  |  | 11.4971 | 0 | 4.4196 | 0 | 0 | 1.2762 | 18.2273 | 0 | 35.4201 | Wind | 0.1248 | Wind | 1835808
| Rangpur Zone |  |  | 0 | 4.9972 | 2.8092 | 0.75001 | 0 | 1.5569 | 0 | 0 | 10.1133
| Total |  |  | 126.0971 | 117.3128 | 50.9235 | 5.961 | 5.0558 | 4.4482 | 43.0575 | 0.1248 | 352.9808
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 435338437.4653 |  | Hydro | 505580.9
|  |  |  | Coal | 834138497.2048 |  | Solar | 72656299.0004
|  |  |  | HFO | 1032161807.372 |  | Import | 257013268.63
|  |  |  | HSD | 143205594.84 |  | Wind | 1835808
[5 empty] | Total: | 277,68,55,293 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 2000 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2975 | Peak Hr Flow | 797.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36602545.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.2273 | Peak Hr Flow | 762.16 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1289 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5328 | Peak Hr Flow | 140.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2046 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.0575 | Peak Hr Flow | 1699.16 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 477 |  | 6228
|  |  |  | Chattogram |  | 195 |  | 1684
|  |  |  | Cumilla |  | 396 |  | 1722
|  |  |  | Mymensingh |  | 357 |  | 1565
|  |  |  | Sylhet |  | 165 |  | 756
|  |  |  | Khulna |  | 462 |  | 2086
|  |  |  | Barishal |  | 187 |  | 591
|  |  |  | Rajshahi |  | 308 |  | 1778
|  |  |  | Rangpur |  | 250 |  | 1226
|  |  |  | Total |  | 2797 |  | 17636
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 108.5
|  |  |  | Total Unavailable Capacity |  |  |  | 408.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:14 | Mirpur 132/33kV S/S Reserve Bus is restored.
|  | 08:15 | Mirpur 132/33kV S/S T1 HT is restored.
|  | 08:15 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
|  | 08:16 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
|  | 08:20 | Mirpur 132/33kV S/S T1 LT is restored.
| 08:34 | 16:06 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to cable change
| 08:35 | 16:07 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to cable change
|  | 08:55 | Fenchuganj-Sreemangal 132kV Ckt-2 is restored.
| 09:10 | 17:25 | Purbasadipur 230/132/33kV S/S ATR-2 HT Scheduled S/D Due to Silicon paint on facing
bricks
| 09:10 | 17:26 | Purbasadipur 230/132/33kV S/S ATR-2 LT Scheduled S/D Due to Silicon paint on facing
bricks
| 11:06 | 12:08 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D
| 11:06 | 12:09 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D | [7 empty] | 50.0MW load
interrup.
| 11:14 | 14:26 | Faridpur 132/33kV S/S ATR-2 LT Project Work S/D
| 11:14 | 14:26 | Faridpur 132/33kV S/S ATR-2 HT Project Work S/D
| 11:16 | 12:39 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Scheduled S/D Due to Pbs Porsha 33kv feeder | [7 empty] | 15.0MW load
|  |  | red hot maintenance. | [7 empty] | interrup.
| 11:16 | 12:38 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Scheduled S/D Due to Pbs Porsha 33kv feeder | [7 empty] | 15.0MW load
|  |  | red hot maintenance. | [7 empty] | interrup.
| 12:00 |  | Day peak generation is 14673 MW.
| 14:18 | 14:58 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to PDB Side 33kV bus DS maintenance
| 14:20 | 14:56 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to PDB Side 33kV bus DS maintenance
| 14:37 | 17:15 | Faridpur 132/33kV S/S ATR-1 LT Project Work S/D Due to Project work
| 14:38 | 16:47 | Faridpur 132/33kV S/S ATR-1 HT Project Work S/D Due to Project work
| 15:19 | 17:28 | BIPTC S/S 20DF22 Tripped showing 87.1 (Differential Relay) relays Due to Capacitor cell
bushing cable is disconnected.
| 16:22 | 16:37 | Khulna (C) S/S Tr-3 405T LT Forced S/D Due to 132 kv TR3 HT Side metering problem.
| 16:23 | 16:36 | Khulna (C) S/S Tr-3 405T HT Forced S/D Due to 132KV TR3 HT side metering Problem.
|  | 16:37 | Khulna (C) S/S Tr-3 405T LT is restored.
| 16:45 | 17:28 | BIPTC S/S 20DF22 Forced S/D Due to Already tripped due to a disconnected capacitor cell
bushing cable.
|  | 17:31 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
|  | 17:31 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
|  | 17:50 | Monakasha-Rahanpur 400kV Ckt-2 is restored.
|  | 19:18 | Khulna(S)-Rupsha 230kV Ckt-2 is restored.
|  | 20:42 | Gopalganj-Rooppur 400kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation: 15255 MW.
| 00:24 |  | Patuakhali 1320 MW (RNPL) Unit-1 was sync.
| 06:04 |  | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Maintanance work by BPDB S&D-5&1 | [7 empty] | 70.0MW load
interrup.
| 06:05 |  | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Maintanance work by BPDB S&D-5&1 | [7 empty] | 50.0MW load
interrup.
| 06:31 |  | Haripur 230/132kV S/S Auto TR-1 HT Tripped showing PRD,General trip relays.
| 06:51 |  | Haripur 230/132kV S/S Auto TR-1 LT Tripped showing PRD,General trip relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 9100800 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 149 | 3431767 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1260972 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7481694 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 861480 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 77 | 888000 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 858696 | Fuel Shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 856659 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 4.2 | 79800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 385920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 390240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 4521633 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 2871648 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 694080 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2528640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 222681 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 434520 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 545 | 11600909.09 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3332400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2521.62 | 51802539.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17.5 | 253211.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 116505 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 300480 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 217 | 5055809 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5173963 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 678336 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 558832 | ps availability is less
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 1400640 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 426720 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 55 | 832320 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19563 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 459164 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 36 | 256746 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 423200 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2084160 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2239364 | Engine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 36 | 807927 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28527270 | AGC+FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 124800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 722 | 22443636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 2996.5 | 72182646.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 209 | 5128000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8150600 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 5990000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 250 | 6375500 | Line Overload
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 297504 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 535273 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 928264 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1083927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | ps availability is less
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 131 | 3279946 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 174 | 2476320 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 140 | 3532800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 448840 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 802560 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 33 | 348600 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1949760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 344373 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1983 | 41672267
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 104760 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2544000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 95 | 1604400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 239500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293280 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 1 | 39600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 262 | 4837890
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 37741 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 825000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 954960 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3196000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2051520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2732050 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 313200 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7404000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 10801000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9538200 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1525 | 37853671
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 797 | 21297455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 101280 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 205 | 4452672 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 36 | 529280 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 418080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 338256 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 210 | 758331 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1040 | 25818180 | Coal Shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2355 | 54227614
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 400 | 16770909 | Coal Shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 700032 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2569000 | ps availability is less
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 14043636.36 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5399630 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 672000 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4712000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3573 | -
Barishal Area Total |  |  |  |  | 3326.69 | 1609 | 44870780.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 301160 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 580339 | Fuel Shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 245844 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 146 | 3657000 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 270 | 7840073 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 520260 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1096877 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 988412 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 709632 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 278208 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 26760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 762.16 | 18227273 | U-2 Under maint.
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 288000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 660280 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1488.36 | 35420118
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 750015 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3833000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 541363 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45122.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 2267816 | Machine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 224421 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1287360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 515 | 10113315.64
Eastern Grid Total |  |  |  |  | 17427.666 | 9288.12 | 208349013.85
Western Grid Total |  |  |  |  | 11731.125 | 5967.36 | 144631828
National Grid Total |  |  |  |  | 29158.791 | 15255.48 | 352980841.85
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10365.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4473.8 | MW
i) Dhaka area |  |  | 5751.25 |  | MW | i) Khulna area |  |  |  | 1624 | MW
ii) Chattogram area |  |  | 1488.8 |  | MW | ii) Barishal area |  |  |  | 403.8 | MW
iii) Cumilla area |  |  | 1326 |  | MW | iii) Rajshahi area |  |  |  | 1470 | MW
iv) Mymensingh area |  |  | 1208 |  | MW | iv) Rangpur area |  |  |  | 976 | MW
v) Sylhet area |  |  | 591 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14838.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 72 | Ishurdi | 81 | 14:00 | 143 | Palashbari | 136 | 03:00
2 | AKSML | 145 | 13:00 | 73 | Jaldhaka | 87 | 03:00 | 144 | Panchagarh | 74 | 19:00
3 | Aftabnagar | 46 | 13:00 | 74 | Jamalpur | 133 | 00:00 | 145 | Patiya | 33 | 18:30
4 | Agargaon | 121 | 13:00 | 75 | Jashore | 162 | 19:00 | 146 | Patnitala | 23 | 22:00
5 | Agrabad | 70 | 18:00 | 76 | Jhenaidah | 86 | 18:30 | 147 | Patuakhali | 71 | 18:30
6 | Amnura | 31 | 04:00 | 77 | Joydebpur | 170 | 08:00 | 148 | Payra | 38 | 18:30
7 | Araihazar | 81 | 21:00 | 78 | Joypurhat | 60 | 05:00 | 149 | Postogola | 64 | 12:00
8 | Ashuganj | 80 | 03:00 | 79 | Juldah | 18 | 12:00 | 150 | Pubail | 47 | 18:30
9 | BSRM | 199 | 21:00 | 80 | KSRM | 25 | 16:00 | 151 | Purbachal | 23 | 13:00
10 | Bagerhat | 76 | 05:00 | 81 | Kabirpur | 261 | 06:00 | 152 | Purbasadipur | 142 | 19:00
11 | Bajitpur | 101 | 21:00 | 82 | Kachua | 92 | 05:00 | 153 | Rahanpur | 37 | 05:00
12 | Bakerganj | 14.4 | 18:30 | 83 | Kaliganj | 40 | 18:30 | 154 | Rahim | 50 | 13:00
13 | Bakulia | 90 | 12:00 | 84 | Kallyanpur | 129 | 00:00 | 155 | Rajbari | 80 | 18:30
14 | Banani | 48 | 12:00 | 85 | Kalurghat | 42 | 18:30 | 156 | Rajendrapur | 119 | 18:00
15 | Bangabhaban | 7 | 12:00 | 86 | Kamrangirchar | 81 | 13:00 | 157 | Rajshahi | 98 | 02:00
16 | Barapukuria | 63 | 23:00 | 87 | Kaptai | N/A | N/A | 158 | Rajshahi-230 | 106 | 13:00
17 | Barguna | 22 | 00:00 | 88 | Kasba | 37 | 18:30 | 159 | Ramganj | 122 | 18:00
18 | Barishal | 103 | 12:00 | 89 | Kazla | 128 | 12:00 | 160 | Rampur | 45 | 18:30
19 | Barishal-230 | 92 | 00:00 | 90 | Keranigonj | 90 | 21:00 | 161 | Rangamati | 20 | 18:30
20 | Baroaulia | 56 | 11:00 | 91 | Khagrachori | 32 | 19:30 | 162 | Rangpur | 132 | 18:30
21 | Baroirhat | 60 | 22:00 | 92 | Khulna | 69 | 15:00 | 163 | Ruppur | 2.6 | 12:00
22 | Bashundhara | 236 | 13:00 | 93 | Khulshi | 184 | 19:30 | 164 | SSM | 0 | 00:00
23 | BashundharaCement | 0 | 00:00 | 94 | Kishoreganj | 132 | 01:00 | 165 | Saidpur | 113 | 18:30
24 | Beanibazar | 66 | 14:00 | 95 | Kodda | 317 | 08:00 | 166 | Santhia | 38 | 18:30
25 | Benapole | 71 | 22:00 | 96 | Kulaura | 53 | 16:00 | 167 | Satkhira | 121 | 22:00
26 | Bhaluka | 189 | 17:00 | 97 | Kurigram | 60 | 10:00 | 168 | Satmasjid | 109 | 13:00
27 | Bhandaria | 50 | 07:00 | 98 | Kushtia | 151 | 13:00 | 169 | Savar | 226 | 11:00
28 | Bhangura | 37 | 14:00 | 99 | Laksam | 39 | 22:00 | 170 | SevenRings | 10.64 | 12:00
29 | Bheramara(GK) | 71 | 18:30 | 100 | Lakshmipur | 52 | 18:30 | 171 | ShahCement | 21 | 00:00
30 | Bhulta | 207 | 11:00 | 101 | Lalbag | 79 | 13:00 | 172 | Shahjadpur | 77 | 18:30
31 | Bog-Sherpur | 66 | 05:00 | 102 | Lalmonirhat | 54 | 22:00 | 173 | Shahjibazar | 126 | 22:00
32 | Bogura | 208 | 22:00 | 103 | MI_Cement | 12 | 01:00 | 174 | Shahmirpur | 53 | 18:00
33 | Borhanuddin | 81 | 18:30 | 104 | Madanganj | 52 | 18:30 | 175 | Shariatpur | 88 | 06:00
34 | Brahmanbaria | 133 | 05:00 | 105 | Madaripur | 96 | 04:00 | 176 | Sherpur | 154 | 23:00
35 | Cantonment | 141 | 13:00 | 106 | Madartek | 90 | 23:00 | 177 | Shikalbaha | 41 | 11:00
36 | Chandina | 24 | 08:00 | 107 | Madunaghat | 51 | 13:00 | 178 | Shitalakhya | 83.9 | 16:00
37 | Chandpur | 84 | 03:00 | 108 | Magura | 69 | 18:30 | 179 | Sholosohor | 48 | 11:00
38 | Chandraghona | 32 | 20:00 | 109 | Mahasthangarh | 77 | 03:00 | 180 | Shomvuganj | 55 | 21:00
39 | Chapai | 72 | 21:00 | 110 | Maijdee | 49 | 18:30 | 181 | Shyampur | 180 | 12:00
40 | Charfasson | 33 | 18:30 | 111 | Manikganj | 158 | 21:00 | 182 | Siddhirganj | 139 | 12:00
41 | Charsaidpur | 30 | 10:00 | 112 | Maniknagar | 79 | 13:00 | 183 | Sirajganj | 126 | 19:30
42 | Chauddagram | 76 | 18:30 | 113 | Matarbari | 50 | 01:00 | 184 | Sitakunda | 31 | 02:00
43 | Chhatak | 37 | 18:00 | 114 | Matuail | 76 | 14:00 | 185 | Sonargaon | 137 | 18:00
44 | Chowmuhani | 156 | 03:00 | 115 | Metrorail_Motijheel | 38 | 12:00 | 186 | Sreemongol | 79 | 04:00
45 | Chuadanga | 108 | 04:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 187 | Sreepur | 137 | 18:00
46 | Coxsbazar | 146 | 12:00 | 117 | Millgate | 108 | 15:00 | 188 | Srinagar | 54.4 | 22:00
47 | Cumilla(N) | 152 | 00:00 | 118 | Mirpur | 162 | 18:30 | 189 | Sunamganj | 65 | 18:30
48 | Cumilla(S) | 166 | 18:30 | 119 | Mirsorai | 48 | 13:00 | 190 | Sylhet | 124 | 00:00
49 | Daganbhuiyan | 34 | 00:00 | 120 | Mirzapur | 47 | 00:00 | 191 | Sylhet_(South) | 64 | 21:00
50 | Daudkandi | 125 | 18:00 | 121 | Mithapukur | 74 | 03:00 | 192 | TK | 0 | 00:00
51 | DhakaUniversity | 90 | 13:00 | 122 | Modern | N/A | N/A | 193 | Tangail | 186 | 00:00
52 | Dhamrai | 100 | 04:00 | 123 | Mogbazar | 65.9 | 14:00 | 194 | Taraganj | 34 | 22:00
53 | Dhanmondi | 114 | 13:00 | 124 | Mongla | 38 | 19:30 | 195 | Tasnim | 47 | 22:00
54 | Dohazari | 124 | 19:30 | 125 | Motijheel | 51 | 12:00 | 196 | Thakurgaon | 118 | 00:00
55 | Faridpur | 176 | 01:00 | 126 | Muktagacha | 42 | 00:00 | 197 | Tongi | 164 | 11:00
56 | Fatullah | 116 | 15:00 | 127 | Munshiganj | 128 | 21:00 | 198 | Ullahpara | 43 | 18:30
57 | Fenchuganj | 40 | 23:00 | 128 | Muradnagar | 58 | 05:00 | 199 | Ullon | 51 | 00:00
58 | Feni | 114 | 22:00 | 129 | Mymensingh | 162 | 22:00 | 200 | Uttara | 105 | 13:00
59 | GPH | 1 | 00:00 | 130 | Nabinagar | 110 | 08:00 | 201 | UttaraNew | 57 | 00:00
60 | Ghatail | 88 | 21:00 | 131 | Naogaon | 115 | 00:00 | 202 | Zigatola | 102 | 13:00
61 | Ghorashal | 0 | 00:00 | 132 | Narail | 68 | 18:30
62 | Ghorashal-230 | 109 | 03:00 | 133 | Narinda | 75 | 13:00
63 | Goalpara | 36 | 02:00 | 134 | Narshingdi | 204 | 21:00
64 | Gollamari | 102 | 13:00 | 135 | Natore | 158 | 03:00
65 | Gopalganj | 113 | 18:30 | 136 | Nawabganj | 58.4 | 22:00
66 | Gulshan | 108 | 13:00 | 137 | Netrakona | 148 | 08:00
67 | Halishahar | 131 | 15:00 | 138 | New | 95.4 | 15:00
68 | HaripurSBU | 133 | 00:00 | 139 | Niamatpur | 71 | 21:00
69 | Hasnabad | 115 | 23:00 | 140 | Noapara | 48 | 18:30
70 | Hathazari | 85 | 23:00 | 141 | PHP | 10 | 06:00
71 | Hatirjheel | 78 | 15:00 | 142 | Pabna | 100 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15224.6 | 1882 |  | 17191.29
1:00 | 14464.39 | 2021 |  | 16576.34
2:00 | 14381.47 | 1591 |  | 16044.47
3:00 | 14352.07 | 1015 |  | 15413.07
4:00 | 14316.46 | 935 |  | 15293.46
5:00 | 14293.89 | 326 |  | 14634.89
6:00 | 13848.56 | 171 |  | 14027.56
7:00 | 13781.47 | 161 |  | 13949.47
8:00 | 13916.47 | 159 |  | 14082.63
9:00 | 13716.44 | 224 |  | 13950.44
10:00 | 13889.25 | 120 |  | 14014.25
11:00 | 14218.91 | 112 |  | 14335.95
12:00 | 14673.4 | 273 |  | 14958.69
13:00 | 14836.08 | 349 |  | 15201.08
14:00 | 14834.16 | 336 |  | 15185.16
15:00 | 14690.52 | 650 |  | 15369.52
16:00 | 14455.2 | 577 |  | 15058.2
17:00 | 14387.37 | 585 |  | 14998.37
18:00 | 14708.26 | 316 |  | 15038.26
19:00 | 14902.99 | 2518 |  | 17533.99
19:30 | 14675.52 | 2722 |  | 17519.52
20:00 | 14853.32 | 2813 |  | 17793.32
21:00 | 15255.48 | 2797 |  | 18178.48
22:00 | 15370.35 | 2344 |  | 17819.35
23:00 | 15246.72 | 2364 |  | 17716.72
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9090.92 | 6133.68 | 15224.6 | DAILY GENERATION CURVE
00:30 | 8820.17 | 6024.325 | 14844.495
01:00 | 8549.42 | 5914.97 | 14464.39 | 12-09-2026
01:30 | 8514.42 | 5908.51 | 14422.93
02:00 | 8479.42 | 5902.05 | 14381.47
02:30 | 8426.42 | 5940.35 | 14366.77
03:00 | 8373.42 | 5978.65 | 14352.07
03:30 | 8377.42 | 5956.845 | 14334.265
04:00 | 8381.42 | 5935.04 | 14316.46
04:30 | 8397.92 | 5907.255 | 14305.175
05:00 | 8414.42 | 5879.47 | 14293.89
05:30 | 8242.49 | 5828.735 | 14071.225
06:00 | 8070.56 | 5778 | 13848.56
06:30 | 8048.21 | 5766.805 | 13815.015
07:00 | 8025.86 | 5755.61 | 13781.47
07:30 | 8083.395 | 5765.575 | 13848.97
08:00 | 8140.93 | 5775.54 | 13916.47
08:30 | 8029.88 | 5786.575 | 13816.455
09:00 | 7918.83 | 5797.61 | 13716.44
09:30 | 7946.355 | 5856.49 | 13802.845
10:00 | 7973.88 | 5915.37 | 13889.25
10:30 | 8090.385 | 5963.695 | 14054.08
11:00 | 8206.89 | 6012.02 | 14218.91
11:30 | 8372.26 | 6073.895 | 14446.155
12:00 | 8537.63 | 6135.77 | 14673.4
12:30 | 8544.955 | 6209.785 | 14754.74
13:00 | 8552.28 | 6283.8 | 14836.08
13:30 | 8596.8 | 6238.32 | 14835.12
14:00 | 8641.32 | 6192.84 | 14834.16
14:30 | 8642.165 | 6120.175 | 14762.34
15:00 | 8643.01 | 6047.51 | 14690.52
15:30 | 8580.18 | 5992.68 | 14572.86
16:00 | 8517.35 | 5937.85 | 14455.2
16:30 | 8473.995 | 5947.29 | 14421.285
17:00 | 8430.64 | 5956.73 | 14387.37
17:30 | 8548.305 | 5999.51 | 14547.815
18:00 | 8665.97 | 6042.29 | 14708.26
18:30 | 8760.045 | 6045.58 | 14805.625
19:00 | 8854.12 | 6048.87 | 14902.99
19:30 | 9045.12 | 5630.4 | 14675.52
20:00 | 9121.12 | 5732.2 | 14853.32
20:30 | 9204.62 | 5849.78 | 15054.4 |  | Executive Engineer
21:00 | 9288.12 | 5967.36 | 15255.48 |  | Network Operation Division
21:30 | 9323.12 | 5989.795 | 15312.915
22:00 | 9358.12 | 6012.23 | 15370.35
22:30 | 9240.12 | 6068.415 | 15308.535
23:00 | 9122.12 | 6124.6 | 15246.72

## En-Curve
QF-LDC-12
Date | 12-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3773 | 1362.5 | 835 | 0 | 158 | 752.48 | 222 | 5107 | 0 | 519.42 | 2258.2 | 230 | 0 | 7 | 1882 | DAILY ENERGY CURVE
00:30 | 3756 | 1371.25 | 835 | 0 | 154 | 752.125 | 221.5 | 5108.5 | 0 | 492.42 | 1918.7 | 220.5 | 0 | 14.5 | 1951.5 | 12-09-2026
01:00 | 3739 | 1380 | 835 | 0 | 150 | 751.77 | 221 | 5110 | 0 | 465.42 | 1579.2 | 211 | 0 | 22 | 2021
01:30 | 3763.5 | 1381 | 835 | 0 | 148 | 755.31 | 220 | 5080.5 | 0 | 461.92 | 1547.2 | 211 | 0 | 19.5 | 1806 | Energy Generated | 352.9808 |  | MKWHr
02:00 | 3788 | 1382 | 835 | 0 | 146 | 758.85 | 219 | 5051 | 0 | 458.42 | 1515.2 | 211 | 0 | 17 | 1591 | Energy not Served | 24.639 |  | MKWHr
02:30 | 3807.5 | 1358.5 | 835 | 0 | 145 | 757.15 | 218.5 | 5049 | 0 | 457.92 | 1514.2 | 211 | 0 | 13 | 1303 | Total Energy Requirement | 377.6198 |  | MKWHr
03:00 | 3827 | 1335 | 835 | 0 | 144 | 755.45 | 218 | 5047 | 0 | 457.42 | 1513.2 | 211 | 0 | 9 | 1015
03:30 | 3821 | 1357 | 835 | 0 | 144 | 757.145 | 195 | 5078 | 0 | 451.92 | 1478.2 | 211 | 0 | 6 | 975
04:00 | 3815 | 1379 | 835 | 0 | 144 | 758.84 | 172 | 5109 | 0 | 446.42 | 1443.2 | 211 | 0 | 3 | 935
04:30 | 3775.5 | 1406.5 | 835 | 0 | 142 | 758.055 | 172.5 | 5110.5 | 0 | 444.92 | 1442.7 | 211 | 0 | 6.5 | 630.5
05:00 | 3736 | 1434 | 835 | 0 | 140 | 757.27 | 173 | 5112 | 0 | 443.42 | 1442.2 | 211 | 0 | 10 | 326
05:30 | 3664.5 | 1414.5 | 835 | 0 | 141 | 758.715 | 173.5 | 5077 | 2.89 | 383.92 | 1420.2 | 193 | 0 | 7 | 248.5
06:00 | 3593 | 1395 | 835 | 0 | 142 | 760.16 | 174 | 5042 | 5.78 | 324.42 | 1398.2 | 175 | 0 | 4 | 171
06:30 | 3592.5 | 1393 | 835 | 0 | 139 | 759.74 | 174.5 | 5042.5 | 46.655 | 319.42 | 1359.7 | 147.5 | 0 | 5.5 | 166
07:00 | 3592 | 1391 | 835 | 0 | 136 | 759.32 | 175 | 5043 | 87.53 | 314.42 | 1321.2 | 120 | 0 | 7 | 161
07:30 | 3609 | 1377.9 | 835 | 0 | 139 | 759.91 | 175.5 | 5033 | 166.04 | 314.42 | 1315.2 | 120 | 0 | 4 | 160
08:00 | 3626 | 1364.8 | 835 | 0 | 142 | 760.5 | 176 | 5023 | 244.55 | 314.42 | 1309.2 | 120 | 0 | 1 | 159
08:30 | 3583.5 | 1356.8 | 882.5 | 0 | 143 | 756.385 | 199 | 5007.5 | 294.75 | 284.92 | 1187.6 | 120 | 0 | 0.5 | 191.5
09:00 | 3541 | 1348.8 | 930 | 0 | 144 | 752.27 | 222 | 4992 | 344.95 | 255.42 | 1066 | 120 | 0 | 0 | 224
09:30 | 3667 | 1351.3 | 930 | 0 | 142 | 751.535 | 221.5 | 4991.5 | 387.3 | 239.71 | 1001 | 120 | 0 | 0 | 172
10:00 | 3793 | 1353.8 | 930 | 0 | 140 | 750.8 | 221 | 4991 | 429.65 | 224 | 936 | 120 | 0 | 0 | 120
10:30 | 3890.5 | 1351.3 | 930 | 0 | 146 | 754.915 | 221.5 | 4969 | 507.365 | 230 | 933.5 | 120 | 0 | 0 | 116
11:00 | 3988 | 1348.8 | 930 | 0 | 152 | 759.03 | 222 | 4947 | 585.08 | 236 | 931 | 120 | 0 | 0 | 112
11:30 | 3960.5 | 1341.3 | 930 | 0 | 156 | 758.24 | 222 | 4997 | 572.905 | 255.21 | 1120 | 130 | 0 | 3 | 192.5
12:00 | 3933 | 1333.8 | 930 | 0 | 160 | 757.45 | 222 | 5047 | 560.73 | 274.42 | 1309 | 140 | 0 | 6 | 273
12:30 | 3867.5 | 1339.8 | 930 | 0 | 160 | 758.295 | 221 | 5028.5 | 581.125 | 276.92 | 1403.6 | 185 | 0 | 3 | 311
13:00 | 3802 | 1345.8 | 930 | 0 | 160 | 759.14 | 220 | 5010 | 601.52 | 279.42 | 1498.2 | 230 | 0 | 0 | 349
13:30 | 3811.5 | 1309.3 | 930 | 0 | 158 | 759.38 | 219 | 5009 | 602.82 | 278.42 | 1536.2 | 219 | 0 | 2.5 | 342.5
14:00 | 3821 | 1272.8 | 930 | 0 | 156 | 759.62 | 218 | 5008 | 604.12 | 277.42 | 1574.2 | 208 | 0 | 5 | 336
14:30 | 3821 | 1276.15 | 930 | 0 | 157 | 760.795 | 217.5 | 4983.5 | 519.775 | 272.92 | 1614.2 | 206 | 0 | 3.5 | 493
15:00 | 3821 | 1279.5 | 930 | 0 | 158 | 761.97 | 217 | 4959 | 435.43 | 268.42 | 1654.2 | 204 | 0 | 2 | 650
15:30 | 3815.5 | 1307.25 | 929.5 | 0 | 158 | 756.94 | 217.5 | 4856.5 | 358.55 | 265.92 | 1696.7 | 204 | 0 | 6.5 | 613.5
16:00 | 3810 | 1335 | 929 | 0 | 158 | 751.91 | 218 | 4754 | 281.67 | 263.42 | 1739.2 | 204 | 0 | 11 | 577
16:30 | 3814 | 1306 | 929.5 | 0 | 154 | 751.705 | 218.5 | 4729.5 | 187.46 | 291.92 | 1829.7 | 203 | 0 | 6 | 581
17:00 | 3818 | 1277 | 930 | 0 | 150 | 751.5 | 219 | 4705 | 93.25 | 320.42 | 1920.2 | 202 | 0 | 1 | 585
17:30 | 3802.5 | 1328.75 | 930 | 0 | 150 | 751.295 | 217 | 4693 | 48.15 | 419.42 | 2004.2 | 203 | 0 | 0.5 | 450.5
18:00 | 3787 | 1380.5 | 930 | 0 | 150 | 751.09 | 215 | 4681 | 3.05 | 518.42 | 2088.2 | 204 | 0 | 0 | 316
18:30 | 3762 | 1353.35 | 875 | 0 | 149 | 751.38 | 215.5 | 4746.5 | 1.525 | 560.92 | 2185.45 | 205 | 0 | 0 | 1417
19:00 | 3737 | 1326.2 | 820 | 0 | 148 | 751.67 | 216 | 4812 | 0 | 603.42 | 2282.7 | 206 | 0 | 0 | 2518
19:30 | 3756 | 1351.2 | 820 | 0 | 146 | 752.2 | 216 | 4297 | 0 | 611.42 | 2416.7 | 305 | 0 | 4 | 2722
20:00 | 3780 | 1357.2 | 820 | 0 | 132 | 754 | 217 | 4280 | 0 | 621.42 | 2462.7 | 423 | 0 | 6 | 2813
20:30 | 3774 | 1383.2 | 808.5 | 0 | 136 | 758.08 | 217 | 4321.5 | 0 | 657.42 | 2490.2 | 501.5 | 0 | 7 | 2805
21:00 | 3768 | 1409.2 | 797 | 0 | 140 | 762.16 | 217 | 4363 | 0 | 693.42 | 2517.7 | 580 | 0 | 8 | 2797
21:30 | 3795 | 1396.2 | 808.5 | 0 | 144 | 763.595 | 219.5 | 4385.5 | 0 | 696.42 | 2530.2 | 570 | 0 | 4 | 2570.5
22:00 | 3822 | 1383.2 | 820 | 0 | 148 | 765.03 | 222 | 4408 | 0 | 699.42 | 2542.7 | 560 | 0 | 0 | 2344
22:30 | 3794 | 1357.2 | 867.5 | 0 | 149 | 759.215 | 221.5 | 4419 | 0 | 700.42 | 2483.2 | 554.5 | 0 | 3 | 2354
23:00 | 3766 | 1331.2 | 915 | 0 | 150 | 753.4 | 221 | 4430 | 0 | 701.42 | 2423.7 | 549 | 0 | 6 | 2364
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 12-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 86 | 46 | 252 | 185 | 1164 | 656 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 90 | 46 | 240 | 180 | 1162 | 648
2:00 | 90 | 46 | 244 | 184 | 1166 | 652 |  | Import | 0
3:00 | 83 | 38 | 236 | 170 | 1142 | 626
4:00 | 83 | 37 | 226 | 170 | 1098 | 602 | Ishurdi-Ghorashal Ckt-2 | Export | 2174545.45
5:00 | 84 | 41 | 228 | 178 | 1086 | 610
6:00 | 92 | 45 | 294 | 200 | 1154 | 626 |  | Import | 0
7:00 | 82 | 44 | 256 | 196 | 1332 | 646
8:00 | 52 | 52 | 160 | 220 | 1462 | 658 | Sirajganj-Sreepur Ckt-1 | Export | 1322000
9:00 | 111 | 62 | 200 | 176 | 1540 | 675
10:00 | 129 | 62 | 300 | 184 | 1594 | 740 |  | Import | 1000
11:00 | 140 | 65 | 296 | 182 | 1610 | 800
12:00 | 135 | 62 | 280 | 210 | 1572 | 796 | Sirajganj-Sreepur Ckt-2 | Export | 1326000
13:00 | 111 | 57 | 260 | 226 | 1548 | 784
14:00 | 108 | 57 | 216 | 244 | 1584 | 842 |  | Import | 1000
15:00 | 95 | 64 | 216 | 272 | 1590 | 820
16:00 | 92 | 45 | 206 | 248 | 1610 | 780 | Gopalganj-Aminbazar Ckt-1 | Export | 15870000
17:00 | 95 | 43 | 228 | 234 | 1660 | 770
18:00 | 94 | 46 | 192 | 220 | 1630 | 744 |  | Import | 0
18:30 | 62 | 37 | 116 | 220 | 1368 | 678
19:00 | 25 | 48 | 2 | 190 | 1480 | 660 | Gopalganj-Aminbazar Ckt-2 | Export | 15910000
19:30 | 49 | 47 | 80 | 180 | 1060 | 624
20:00 | 39 | 37 | 84 | 180 | 1044 | 584 |  | Import | 0
21:00 | 79 | 34 | 230 | 206 | 980 | 640
22:00 | 72 | 23 | 220 | 186 | 934 | 580 |  | Total Export | 36602545.45
23:00 | 87 | 12 | 284 | 190 | 1060 | 604 |  | Total Import | 2000
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 22:00 | 357 | 13:00 | Madunaghat | 400 | 21:00 | 388 | 12:00
Amtali | 413 | 20:00 | 408 | 11:00 | Meghnaghat | 383 | 22:00 | 363 | 13:00
Ashuganj | 399 | 20:00 | 373 | 13:00 | Mirsorai | 398 | 20:00 | 380 | 14:00
Bhulta | 389 | 04:00 | 364 | 12:00 | Payra | 414 | 06:00 | 409 | 12:00
Bibiana | 381 | 20:00 | 372 | 12:00 | Rahanpur | 409 | 19:00 | 389 | 16:00
BIPTC | 404 | 05:00 | 393 | 12:00 | Rampal | 398 | 22:00 | 385 | 12:00
Bogura | 394 | 19:30 | 378 | 16:00
Gopalganj | 393 | 22:00 | 378 | 14:00
Kaliakoir | 372 | 20:00 | 347 | 12:00
Korerhat | 398 | 22:00 | 380 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 20:00 | 212 | 12:00 | Hasnabad | 225 | 22:00 | 209 | 11:00
AKSML | 237 | 22:00 | 225 | 11:00 | Hathazari | 235 | 21:00 | 226 | 10:00
Aminbazar | 230 | 20:00 | 212 | 12:00 | Ishurdi | 237 | 19:30 | 223 | 16:00
Ashuganj | 225 | 19:30 | 211 | 13:00 | Jhenaidah | 228 | 19:30 | 217 | 16:00
Ashuganj-400 | 225 | 19:30 | 211 | 13:00 | Kachua | 229 | 22:00 | 217 | 11:00
Baghabari | 233 | 19:30 | 224 | 13:00 | Kaliakoir | 231 | 22:00 | 211 | 12:00
Barapukuria | 228 | 19:30 | 222 | 08:00 | Keranigonj | 226 | 22:00 | 209 | 12:00
Barapukuria-230 | 228 | 19:00 | 221 | 8:00 | Khulna(S) | 230 | 20:00 | 223 | 12:00
Barapukuria(N) | 230 | 20:00 | 223 | 08:00 | Korerhat | 227 | 22:00 | 216 | 12:00
Barishal | 227 | 19:30 | 221 | 12:00 | Madunaghat | 238 | 18:00 | 230 | 12:00
Bheramara | 235 | 20:00 | 220 | 16:00 | Madunaghat-400 | 240 | 21:00 | 230 | 12:00
Bhulta | 221 | 04:00 | 205 | 12:00 | Maniknagar | 219 | 04:00 | 203 | 13:00
Bibiana | 217 | 03:00 | 210 | 13:00 | Meghnaghat | 226 | 05:00 | 210 | 12:00
BIPTC | 238 | 19:30 | 221 | 16:00 | Meghnaghat-400 | 223 | 20:00 | 208 | 13:00
Birulia | 229 | 22:00 | 212 | 12:00 | Mirsorai | 231 | 20:00 | 222 | 11:00
Bogura | 239 | 19:30 | 229 | 16:00 | Naogaon | 228 | 19:30 | 210 | 13:00
Bogura-400 | 238 | 20:00 | 229 | 16:00 | Purbasadipur | 225 | 19:30 | 219 | 09:00
Borhanuddin | 229 | 19:30 | 225 | 13:00 | Rajshahi | 233 | 00:00 | 219 | 16:00
BSRM | 227 | 19:30 | 217 | 13:00 | Rampal | 229 | 22:00 | 220 | 13:00
Charfasson | 231 | 20:00 | 225 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 09:00 | 216 | 11:00 | Rampura | 221 | 22:00 | 202 | 13:00
Cumilla(N) | 220 | 20:00 | 208 | 12:00 | Shikalbaha | 237 | 18:30 | 228 | 11:00
Faridpur | 222 | 19:30 | 215 | 12:00 | Shyampur | 223 | 20:00 | 207 | 12:00
Fenchuganj | 218 | 04:00 | 211 | 15:00 | Siddhirganj | 222 | 22:00 | 204 | 12:00
Feni | 225 | 20:00 | 213 | 12:00 | Sirajgonj | 237 | 19:00 | 229 | 15:00
Ghorashal | 222 | 21:00 | 210 | 14:00 | Sreepur | 222 | 19:30 | 210 | 15:00
Ghorashal-230 | 219 | 22:00 | 198 | 12:00 | Tongi | 221 | 19:30 | 200 | 11:00
Gopalganj | 223 | 21:00 | 216 | 12:00
GPH | 233 | 21:00 | 227 | 16:00
Haripur | 234 | 19:00 | 205 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 06:00 | 124 | 13:00 | Madanganj | 131 | 01:00 | 121 | 12:00
Agargaon | 135 | 03:00 | 124 | 12:00 | Madaripur | 132 | 19:30 | 127 | 12:00
Agrabad | 136 | 03:00 | 128 | 10:00 | Madartek | 137 | 20:00 | 124 | 13:00
AKS | 135 | 21:00 | 127 | 11:00 | Madunaghat | 138 | 19:00 | 132 | 10:00
Aminbazar | 131 | 04:00 | 119 | 12:00 | Magura | 135 | 00:00 | 128 | 13:00
Amnura | 136 | 19:30 | 127 | 13:00 | Mahasthangarh | 135 | 00:00 | 128 | 07:00
Araihazar | 127 | 20:00 | 116 | 12:00 | Maijdee | 128 | 00:00 | 121 | 11:00
Ashuganj | 132 | 19:30 | 122 | 12:00 | Manikganj | 130 | 22:00 | 121 | 14:00
Ashuganj-230 | 133 | 19:00 | 128 | 12:00 | Maniknagar | 137 | 04:00 | 124 | 12:00
Bagerhat | 128 | 17:00 | 125 | 00:00 | Matarbari | 128 | 18:30 | 113 | 10:00
Bajitpur | 126 | 19:30 | 117 | 15:00 | Matuail | 131 | 01:00 | 120 | 12:00
Bakerganj | 134 | 22:00 | 130 | 03:00 | Metrorail_Motijheel | 137 | 03:00 | 124 | 10:00
Bakulia | 137 | 18:30 | 130 | 10:00 | Metrorail_Uttara | 134 | 22:00 | 118 | 11:00
Banani | 136 | 04:00 | 123 | 13:00 | Millgate | 134 | 22:00 | 119 | 11:00
Bangabhaban | 136 | 03:00 | 123 | 13:00 | Mirpur | 131 | 22:00 | 119 | 12:00
Barapukuria | 139 | 19:30 | 130 | 08:00 | Mirzapur | 132 | 20:00 | 121 | 14:00
Barguna | 133 | 19:30 | 129 | 12:00 | Mithapukur | 133 | 19:30 | 127 | 04:00
Barishal | 133 | 20:00 | 128 | 12:00 | MI_Cement | 132 | 03:00 | 120 | 12:00
Barishal-230 | 133 | 23:00 | 128 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 136 | 20:00 | 129 | 11:00 | Mogbazar | 138 | 03:00 | 125 | 13:00
Baroirhat | 132 | 19:30 | 125 | 12:00 | Mongla | 128 | 18:00 | 125 | 12:00
Bashundhara | 138 | 03:00 | 118 | 11:00 | Motijheel | 136 | 03:00 | 123 | 13:00
BashundharaCement | 131 | 01:00 | 121 | 12:00 | Muktagacha | 132 | 18:30 | 116 | 06:00
Beanibazar | 125 | 03:00 | 118 | 14:00 | Munshiganj | 131 | 22:00 | 119 | 13:00
Benapole | 130 | 06:00 | 123 | 13:00 | Muradnagar | 125 | 19:30 | 116 | 13:00
Bhaluka | 132 | 19:00 | 121 | 16:00 | Mymensingh | 133 | 18:30 | 111 | 15:00
Bhandaria | 130 | 20:00 | 125 | 07:00 | Nabinagar | 134 | 20:00 | 121 | 12:00
Bhangura | 134 | 19:30 | 128 | 16:00 | Naogaon | 137 | 19:30 | 126 | 13:00
Bheramara | 138 | 19:30 | 129 | 16:00 | Narail | 136 | 20:00 | 127 | 16:00
Bheramara(GK) | 138 | 19:00 | 130 | 12:00 | Narinda | 137 | 4:00 | 124 | 12:00
Bhulta | 126 | 20:00 | 118 | 12:00 | Narshingdi | 130 | 19:30 | 114 | 12:00
Bhulta-400 | 127 | 04:00 | 117 | 12:00 | Natore | 136 | 19:30 | 128 | 16:00
Birulia | 134 | 22:00 | 125 | 12:00 | Nawabganj | 135 | 04:00 | 125 | 12:00
Bog-Sherpur | 136 | 19:30 | 129 | 16:00 | Netrakona | 122 | 19:00 | 109 | 07:00
Bogura | 138 | 19:30 | 131 | 16:00 | New | 136 | 22:00 | 120 | 11:00
Bogura-230 | 139 | 19:30 | 132 | 13:00 | Niamatpur | 134 | 19:00 | 128 | 13:00
Brahmanbaria | 129 | 19:00 | 121 | 13:00 | Noapara | 133 | 06:00 | 128 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 135 | 04:00 | 124 | 12:00 | Pabna | 135 | 19:00 | 128 | 16:00
Chandina | 128 | 19:30 | 121 | 12:00 | Palashbari | 132 | 19:30 | 124 | 04:00
Chandpur | 136 | 19:30 | 124 | 11:00 | Panchagarh | 139 | 06:00 | 132 | 10:00
Chandraghona | 138 | 20:00 | 133 | 10:00 | Patiya | 136 | 18:30 | 127 | 10:00
Chapai | 133 | 00:00 | 128 | 13:00 | Patnitala | 134 | 19:30 | 127 | 13:00
Charsaidpur | 131 | 01:00 | 121 | 12:00 | Patuakhali | 134 | 20:00 | 130 | 04:00
Chauddagram | 129 | 19:30 | 122 | 11:00 | Payra | 136 | 20:00 | 133 | 11:00
Chhatak | 124 | 03:00 | 115 | 13:00 | PHP | 132 | 19:30 | 125 | 11:00
Chowmuhani | 129 | 22:00 | 121 | 11:00 | Postogola | 133 | 04:00 | 122 | 12:00
Chuadanga | 134 | 19:00 | 126 | 11:00 | Pubail | 130 | 20:00 | 117 | 15:00
Coxsbazar | 132 | 18:30 | 118 | 14:00 | Purbachal | 137 | 04:00 | 123 | 13:00
Cumilla(N) | 131 | 00:00 | 120 | 12:00 | Purbasadipur | 136 | 01:00 | 132 | 09:00
Cumilla(S) | 128 | 20:00 | 121 | 12:00 | Rahanpur | 137 | 19:00 | 130 | 13:00
Daganbhuiyan | 129 | 19:00 | 122 | 11:00 | Rahanpur-400 | 137 | 19:30 | 130 | 13:00
Daudkandi | 124 | 05:00 | 115 | 12:00 | Rahim | 131 | 04:00 | 120 | 13:00
DhakaUniversity | 137 | 20:00 | 124 | 13:00 | Rajbari | 126 | 06:00 | 120 | 13:00
Dhamrai | 135 | 00:00 | 122 | 13:00 | Rajendrapur | 134 | 19:00 | 125 | 15:00
Dhanmondi | 138 | 04:00 | 123 | 13:00 | Rajshahi | 134 | 19:30 | 125 | 16:00
Dohazari | 132 | 19:00 | 125 | 10:00 | Rajshahi-230 | 134 | 00:00 | 126 | 16:00
Faridpur | 128 | 23:00 | 124 | 13:00 | Ramganj | 130 | 19:30 | 121 | 10:00
Fatullah | 134 | 22:00 | 121 | 12:00 | Rampur | 136 | 19:00 | 129 | 12:00
Fenchuganj | 129 | 02:00 | 124 | 13:00 | Rampura | 137 | 05:00 | 123 | 13:00
Feni | 130 | 19:30 | 123 | 15:00 | Rangamati | 137 | 19:30 | 132 | 10:00
Feni-230 | 131 | 19:30 | 123 | 13:00 | Rangpur | 128 | 15:00 | 125 | 08:00
Ghatail | 131 | 18:30 | 116 | 04:00 | Ruppur | 138 | 19:30 | 130 | 16:00
Ghorashal | 131 | 21:00 | 118 | 11:00 | Saidpur | 137 | 19:30 | 130 | 09:00
Goalpara | 137 | 20:00 | 132 | 11:00 | Santhia | 135 | 19:30 | 128 | 16:00
Gollamari | 135 | 19:30 | 130 | 13:00 | Satkhira | 131 | 17:00 | 127 | 07:00
Gopalganj | 134 | 20:00 | 126 | 12:00 | Satmasjid | 135 | 20:00 | 124 | 12:00
Gopalganj-400 | 133 | 20:00 | 127 | 13:00 | Savar | 131 | 22:00 | 120 | 12:00
Gulshan | 137 | 22:00 | 124 | 13:00 | SevenRings | 131 | 21:00 | 120 | 12:00
Halishahar | 138 | 18:30 | 129 | 10:00 | ShahCement | 132 | 20:00 | 121 | 12:00
Haripur | 131 | 04:00 | 121 | 12:00 | Shahjadpur | 136 | 04:00 | 130 | 15:00
HaripurSBU | 131 | 07:00 | 121 | 12:00 | Shahjibazar | 128 | 19:00 | 121 | 15:00
Hasnabad | 133 | 01:00 | 122 | 12:00 | Shahmirpur | 137 | 04:00 | 130 | 11:00
Hathazari | 138 | 20:00 | 132 | 10:00 | Shariatpur | 131 | 19:30 | 125 | 13:00
Hatirjheel | 137 | 04:00 | 123 | 14:00 | Sherpur | 134 | 18:30 | 110 | 01:00
Ishurdi | 139 | 19:30 | 131 | 16:00 | Shikalbaha | 127 | 04:00 | 121 | 13:00
Jaldhaka | 134 | 20:00 | 124 | 13:00 | Shikalbaha-230 | 139 | 18:30 | 131 | 11:00
Jamalpur | 136 | 18:30 | 114 | 01:00 | Shitalakhya | 132 | 03:00 | 120 | 12:00
Jashore | 132 | 20:00 | 125 | 13:00 | Sholosohor | 137 | 20:00 | 130 | 12:00
Jhenaidah | 138 | 19:30 | 130 | 13:00 | Shomvuganj | 121 | 19:00 | 112 | 13:00
Jhenaidah-230 | 138 | 19:30 | 131 | 12:00 | Shyampur | 132 | 20:00 | 120 | 13:00
Joydebpur | 129 | 22:00 | 115 | 08:00 | Shyampur-230 | 133 | 03:00 | 123 | 12:00
Joypurhat | 134 | 19:30 | 127 | 13:00 | Siddhirganj | 131 | 01:00 | 121 | 12:00
Juldah | 139 | 18:30 | 131 | 10:00 | Sirajganj | 131 | 19:30 | 125 | 16:00
Kabirpur | 135 | 22:00 | 112 | 11:00 | Sitakunda | 137 | 20:00 | 130 | 11:00
Kachua | 131 | 19:30 | 123 | 11:00 | Sonargaon | 128 | 03:00 | 118 | 13:00
Kaliakoir | 137 | 20:00 | 126 | 12:00 | Sreemongol | 127 | 19:30 | 120 | 13:00
Kaliganj | 136 | 19:30 | 128 | 16:00 | Sreepur | 135 | 19:00 | 126 | 15:00
Kallyanpur | 131 | 01:00 | 121 | 11:00 | Srinagar | 136 | 20:00 | 125 | 12:00
Kalurghat | 138 | 18:30 | 133 | 10:00 | SSM | 140 | 00:00 | 135 | 13:00
Kamrangirchar | 136 | 20:00 | 116 | 12:00 | Sunamganj | 120 | 01:00 | 113 | 15:00
Kaptai | 139 | 0:00 | 136 | 10:00 | Sylhet | 124 | 03:00 | 120 | 13:00
Kasba | 123 | 01:00 | 117 | 13:00 | Sylhet_(South) | 125 | 03:00 | 120 | 13:00
Kazla | 136 | 04:00 | 123 | 13:00 | Tangail | 129 | 20:00 | 119 | 08:00
Keranigonj | 136 | 04:00 | 126 | 12:00 | Taraganj | 135 | 19:30 | 129 | 07:00
Khagrachori | 135 | 00:00 | 130 | 11:00 | Tasnim | 128 | 01:00 | 118 | 13:00
Khulna | 135 | 03:00 | 130 | 13:00 | Thakurgaon | 140 | 06:00 | 132 | 11:00
Khulna(S) | 135 | 19:30 | 130 | 13:00 | TK | 136 | 18:00 | 134 | 01:00
Khulshi | 135 | 03:00 | 128 | 10:00 | Tongi | 136 | 23:00 | 120 | 11:00
Kishoreganj | 126 | 19:30 | 116 | 13:00 | Ullahpara | 133 | 00:00 | 127 | 16:00
Kodda | 133 | 18:30 | 119 | 11:00 | Ullon | 136 | 01:00 | 124 | 13:00
Korerhat | 134 | 20:00 | 127 | 12:00 | Uttara | 133 | 22:00 | 114 | 12:00
KSRM | 137 | 21:00 | 129 | 11:00 | UttaraNew | 134 | 22:00 | 118 | 11:00
Kulaura | 130 | 03:00 | 123 | 13:00 | Zigatola | 136 | 05:00 | 125 | 13:00
Kurigram | 128 | 18:30 | 119 | 07:00
Kushtia | 137 | 19:30 | 129 | 12:00
Laksam | 130 | 19:30 | 122 | 11:00
Lakshmipur | 127 | 19:30 | 120 | 11:00
Lalbag | 136 | 22:00 | 123 | 12:00
Lalmonirhat | 128 | 19:30 | 120 | 07:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division