## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-09-2026 | during | 18-09-2026 | during | 18-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 311 | 362 | 412 | 412 | 377 | 377 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 298 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 32 | 47 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 338 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 72 | 140 | 149.36 | 149.36 | 30 | 78 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 11 | 11 | 33 | 33 | 8.5 | 8.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 18 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 33 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 245 | 300 | 300 | 97 | 196 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 59 | 121 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 35 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 440 | 370 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | STG Under Shutdown & Gas Shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6221.494 | 2091.42 | 2407.42 | 5404.16 | 5370.16 | 2358.92 | 2662.89
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 12 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 25 | 25 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 51 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 44 | 50 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 10 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 24 | 37 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 5.16 | 0 | 5.16 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 52 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 16 | 108 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 30 | 87 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 840 | 970 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2915 | 3345.36 | 4122.12 | 4172.96 | 3467.16 | 3572.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 100 | 186 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 310 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 290 | 342.01 | 342.01 | 307 | 307 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 18 | 32 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 20 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 68 | 150 | 150 | 13 | 55 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 22 | 32 | 32 | 32 | 32 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 141 | 163 | 163 | 140 | 140 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 36 | 129 | 200 | 200 | 120 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 38 | 84 | 78 | 32 | 40 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 20 | 88 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 56 | 70 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 75 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1592 | 1933 | 2764.44 | 2688.44 | 1888.26 | 2022.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-09-2026 | during | 18-09-2026 | during | 18-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 2.08 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.5 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 164 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 4.62 | 0 | 36 | 0 | 36 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 3 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 198.2 | 271 | 524.6 | 546.5 | 238.1 | 272
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 29 | 0 | 0 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 30 | 30 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 139 | 140 | 140 | 140 | 140 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 25 | 79 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 292 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 317 | 393 | 350 | 390 | 350 | 390 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 400 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1362 | 1479 | 1486 | 1526 | 1471 | 1511
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 899 | 804 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 11 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 120 | 120 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 34 | 51 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 32 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 66 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 612 | 616 | 617.1 | 617.1 | 617.1 | 617.1 | U-2 Under maint.
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1777 | 1700 | 3007.1 | 2912.1 | 2297.1 | 2234.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 1100 | 1000 | 1100 | 1000 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 48 | 75 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 574 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.75 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2174.75 | 2257 | 2488 | 2587 | 2339 | 2438
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 0.59 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 168 | 156 | 214 | 214 | 193 | 193 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 320 | 413.79 | 413.79 | 372 | 372 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 43 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 44 | 97 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.22 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1130.31 | 1409.21 | 1000 | 1400 | 1130 | 1420 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 2.86 | 0 | 63 | 0 | 63 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 17 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1839.98 | 2158.21 | 2756.11 | 2935.99 | 2078.12 | 2369
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 51 | 52 | 52 | 52 | 52 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 152 | 156 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 93 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 56 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 207 | 0 | 152.12 | 0 | 152.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 573.3 | 414 | 661.12 | 474 | 582.12 | 474
System Total |  |  |  |  | 28843.2 | 28708.791 | 14523.65 | 15964.99 | 23213.65 | 23213.15 | 16719.78 | 17556.11
Forecast Scenario (18-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15930 |  | 143.25 |  | 16080
|  |  |  | 1:00 | 14800 |  | 620.75 |  | 15450
|  |  |  | 2:00 | 14440 |  | 792.65 |  | 15270
|  |  |  | 3:00 | 14110 |  | 849.95 |  | 15000
|  |  |  | 4:00 | 14030 |  | 725.8 |  | 14790
|  |  |  | 5:00 | 13940 |  | 639.85 |  | 14610
|  |  |  | 6:00 | 13440 |  | 0 |  | 13440
|  |  |  | 7:00 | 12960 |  | 0 |  | 12960
|  |  |  | 8:00 | 12690 |  | 0 |  | 12690
|  |  |  | 9:00 | 12410 |  | 0 |  | 12410
|  |  |  | 10:00 | 12390 |  | 0 |  | 12390
|  |  |  | 11:00 | 12540 |  | 0 |  | 12540
|  |  |  | 12:00 | 13300 |  | 0 |  | 13300
|  |  |  | 13:00 | 13900 |  | 0 |  | 13900
|  |  |  | 14:00 | 13260 |  | 0 |  | 13260
|  |  |  | 15:00 | 13280 |  | 0 |  | 13280
|  |  |  | 16:00 | 12870 |  | 0 |  | 12870
|  |  |  | 17:00 | 12410 |  | 0 |  | 12410
|  |  |  | 18:00 | 12140 |  | 0 |  | 12140
|  |  |  | 18:30 | 13135 |  | 0 |  | 13135
|  |  |  | 19:00 | 14130 |  | 0 |  | 14130
|  |  |  | 19:30 | 14900 |  | 0 |  | 14900
|  |  |  | 20:00 | 15090 |  | 0 |  | 15090
|  |  |  | 21:00 | 15390 |  | 0 |  | 15390
|  |  |  | 22:00 | 15470 |  | 0 |  | 15470
|  |  |  | 23:00 | 15740 |  | 0 |  | 15740
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15390.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15390.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 330.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:30 hrs on 18-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-09-2026 | [28 empty] | Date: | 17-09-2026 | [28 empty] | Date: | 17-09-2026 | [28 empty] | Date: | 17-09-2026 | [28 empty] | Date: | 17-09-2026 | [17 empty] | Date: | 17-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 72 | 138 | 196 | 55 | 55 | 162 | 0 | 281 | 0 | 0 | 35 | 297 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 400 | 94 | 52 | 57 | 0 | 0 | 51 | 58 | 35 | 100 | 100 | 0 | 222 | 17 | 23 | 550 | 90 | 0 | 30 | 8 | 17 | 219 | 0 | 0 | 0 | 1202 | 0 | 11 | 45 | 350 | 354 | 265 | 44 | 0 | 196 | 0 | 89 | 142 | 169 | 69 | 19 | 87 | 42 | 52.2 | 0 | 23 | 300 | 400 | 387 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 0 | 8953.12 | 814 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 210 | 0 | 32 | 0 | 617.1 | 13 | 0 | 0 | 1395.97 | 0 | 0 | 0 | 55 | 50 | 0 | 100 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 52 | 107 | 0 | 70 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 220 | 0 | 1011 | 578 | 17 | 6978.07 | 15931.19 | 105.78
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 54 | 141 | 196 | 55 | 35 | 72 | 0 | 291 | 0 | 0 | 35 | 308 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 420 | 95 | 52 | 35 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0 | 222 | 17 | 31 | 550 | 53 | 0 | 31 | 8 | 17 | 219 | 0 | 0 | 0 | 1202 | 0 | 13 | 45 | 350 | 354 | 265 | 44 | 0 | 199 | 0 | 87 | 140 | 111 | 40 | 19 | 34 | 40 | 52.2 | 0 | 23 | 290 | 400 | 394 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8477.12 | 776 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 217 | 0 | 0 | 0 | 617.1 | 17 | 0 | 0 | 1150.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 18 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 52 | 102 | 0 | 35 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 115 | 220 | 0 | 985 | 575 | 17 | 6327.36 | 14804.48 | 105.79
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 0 | 53 | 143 | 157 | 55 | 35 | 72 | 0 | 282 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 375 | 99 | 52 | 24 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0 | 222 | 17 | 22 | 550 | 53 | 0 | 31 | 8 | 17 | 219 | 0 | 0 | 0 | 1192 | 0 | 13 | 45 | 320 | 356 | 250 | 44 | 0 | 221 | 0 | 76 | 140 | 50 | 58 | 19 | 34 | 40 | 52.2 | 0 | 23 | 295 | 400 | 393 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 142 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8282.12 | 777 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 215 | 0 | 0 | 0 | 617.1 | 17 | 0 | 0 | 996.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 18 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 52 | 100 | 0 | 35 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 115 | 219 | 0 | 991 | 570 | 17 | 6153.6 | 14435.72 | 105.81
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 0 | 53 | 143 | 146 | 55 | 35 | 72 | 0 | 291 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 8.5 | 0 | 0 | 435 | 92 | 52 | 24 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0 | 222 | 17 | 29 | 550 | 53 | 0 | 31 | 8 | 17 | 217 | 0 | 0 | 0 | 1192 | 0 | 13 | 26 | 340 | 355 | 270 | 44 | 0 | 199 | 0 | 65 | 141 | 50 | 0 | 19 | 34 | 38 | 52.2 | 0 | 23 | 290 | 400 | 393 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8246.12 | 830 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 51 | 0 | 0 | 0 | 617.1 | 17 | 0 | 0 | 910.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 18 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 151 | 52 | 99 | 0 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 200 | 115 | 218 | 0 | 979 | 570 | 17 | 5860.02 | 14106.14 | 105.82
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 53 | 143 | 146 | 55 | 35 | 72 | 0 | 285 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 8.5 | 15 | 0 | 435 | 101 | 52 | 25 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0 | 219 | 17 | 24 | 675 | 53 | 0 | 31 | 8 | 17 | 219 | 0 | 0 | 0 | 1192 | 0 | 13 | 26 | 340 | 354 | 270 | 44 | 0 | 200 | 0 | 69 | 140 | 51 | 0 | 19 | 34 | 38 | 52.2 | 0 | 23 | 290 | 400 | 392 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8375.12 | 785 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 25 | 0 | 0 | 0 | 617.1 | 17 | 0 | 0 | 913.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 151 | 53 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 115 | 219 | 0 | 993 | 570 | 17 | 5650.78 | 14025.9 | 105.82
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 53 | 142 | 146 | 55 | 35 | 72 | 0 | 285 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 405 | 90 | 52 | 24 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0 | 217 | 17 | 38 | 720 | 53 | 0 | 31 | 8 | 17 | 219 | 0 | 0 | 0 | 1192 | 0 | 13 | 26 | 320 | 354 | 270 | 44 | 0 | 200 | 0 | 69 | 141 | 51 | 0 | 19 | 34 | 36 | 52.2 | 0 | 23 | 290 | 400 | 354 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8324.12 | 785 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 25 | 0 | 0 | 0 | 615 | 17 | 0 | 0 | 909.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 151 | 52 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 116 | 219 | 0 | 966 | 570 | 17 | 5620.83 | 13944.95 | 105.82
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 53 | 142 | 146 | 55 | 17 | 72 | 0 | 282 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 385 | 86 | 52 | 24 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0.06 | 217 | 17 | 37 | 720 | 53 | 0 | 31 | 8 | 17 | 219 | 0 | 0 | 0 | 1160 | 0 | 13 | 53 | 320 | 355 | 265 | 44 | 0 | 193 | 0 | 69 | 140 | 50 | 0 | 8 | 34 | 36 | 52.2 | 1 | 23 | 295 | 400 | 342 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 30 | 141 | 0 | 65 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8172.18 | 784 | 0 | 0 | 24 | 0 | 0 | 230 | 0 | 25 | 0 | 0 | 0.92 | 615 | 17 | 0 | 0 | 908.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.31 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 150 | 52 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 16 | 200 | 117 | 219 | 0 | 951 | 570 | 17 | 5530.86 | 13703.04 | 105.83
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 30 | 142 | 146 | 55 | 17 | 72 | 0 | 284 | 0 | 0 | 35 | 295 | 0 | 0 | 3 | 143.42 | 8.5 | 19 | 0 | 410 | 96 | 52 | 24 | 0 | 0 | 51 | 46 | 0 | 100 | 100 | 0.6 | 217 | 17 | 37 | 720 | 53 | 0 | 25 | 8 | 17 | 219 | 0 | 0 | 0 | 1224 | 4 | 11 | 90 | 340 | 354 | 260 | 44 | 0 | 198 | 0 | 69 | 140 | 51 | 0 | 19 | 34 | 34 | 52.2 | 10 | 23 | 295 | 400 | 390 | 29 | 30 | 0 | 1 | 8 | 0 | 81 | 30 | 140 | 0 | 25 | 0.72 | 58 | 0.02 | 67 | 0 | 0 | 0 | 0 | 8346.46 | 784 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 25 | 0 | 0 | 19.29 | 617.1 | 17 | 0 | 0 | 915.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5.55 | 8 | 0 | 0 | 2.01 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.17 | 154 | 52 | 108 | 0 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0.09 | 16 | 200 | 116 | 220 | 0 | 983 | 570 | 17 | 5658.18 | 14004.64 | 105.83
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 17 | 143 | 146 | 55 | 17 | 72 | 0 | 287 | 0 | 0 | 35 | 306 | 0 | 0 | 5 | 143.42 | 8.5 | 19 | 0 | 430 | 87 | 52 | 24 | 0 | 0 | 17 | 45 | 0 | 100 | 100 | 1.82 | 220 | 17 | 9 | 720 | 53 | 0 | 25 | 8 | 17 | 219 | 0 | 0 | 0 | 1180 | 6 | 13 | 90 | 340 | 315 | 275 | 44 | 0 | 180 | 0 | 69 | 138 | 53 | 1 | 19 | 34 | 32 | 52.2 | 40 | 22 | 285 | 400 | 392 | 29 | 30 | 0 | 1 | 8 | 0 | 81 | 30 | 140 | 0 | 25 | 0 | 58 | 0.13 | 67 | 0 | 0.1 | 0.24 | 0 | 8227.41 | 852 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 0 | 45.19 | 617.1 | 17 | 0 | 0 | 913.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20.02 | 17 | 0 | 0 | 9.31 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.88 | 153 | 52 | 107 | 0 | 0 | 0 | 0 | 0 | 1.8 | 10 | 0.34 | 16 | 200 | 115 | 220 | 0 | 951 | 570 | 17 | 5625.65 | 13853.06 | 105.84
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 17 | 142 | 146 | 55 | 17 | 72 | 0 | 292 | 0 | 0 | 17 | 328 | 0 | 0 | 16 | 143.42 | 8.5 | 0 | 0 | 420 | 60 | 52 | 24 | 0 | 0 | 17 | 45 | 0 | 50 | 100 | 2.95 | 221 | 17 | 8 | 770 | 53 | 0 | 25 | 8 | 17 | 217 | 0 | 0 | 0 | 1166 | 6 | 13 | 90 | 340 | 300 | 280 | 35 | 0 | 180 | 0 | 69 | 139 | 51 | 16 | 19 | 17 | 32 | 8 | 53 | 22 | 285 | 400 | 380 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 30 | 140 | 0 | 25 | 0 | 58 | 2.9 | 104 | 0 | 0.6 | 5.11 | 0 | 8164.48 | 899 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 18 | 0 | 0 | 65.89 | 616 | 17 | 0 | 0 | 1090.37 | 0 | 0 | 0 | 54 | 4 | 0 | 0 | 0 | 8 | 25.4 | 18 | 0 | 0 | 17 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.89 | 155 | 52 | 70 | 7 | 0 | 0 | 0 | 0 | 2.7 | 2 | 0.45 | 16 | 200 | 115 | 220 | 0 | 975 | 570 | 17 | 5877.7 | 14042.18 | 105.85
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 60 | 146 | 30 | 35 | 72 | 0 | 294 | 0 | 0 | 17 | 340 | 0 | 0 | 12 | 143.42 | 8.5 | 19 | 0 | 370 | 16 | 52 | 20 | 0 | 0 | 0 | 44 | 30 | 12 | 50 | 0.93 | 221 | 17 | 7 | 840 | 16 | 0 | 19 | 8 | 17 | 217 | 0 | 0 | 0 | 1160 | 11 | 13 | 125 | 340 | 330 | 300 | 35 | 0 | 110 | 0 | 34 | 138 | 17 | 66 | 19 | 17 | 32 | 8 | 68 | 14 | 280 | 400 | 340 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 30 | 141 | 0 | 25 | 0 | 59 | 8.35 | 114 | 0 | 0.3 | 18.2 | 0 | 7984.7 | 899 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 62 | 612 | 17 | 0 | 0 | 1105.88 | 0 | 0 | 0 | 54 | 50 | 0 | 0 | 0 | 8 | 32.74 | 26 | 0 | 0 | 2.51 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.2 | 154 | 51 | 35 | 27 | 68 | 0 | 0 | 0 | 5.4 | 35 | 0.64 | 16 | 200 | 115 | 219 | 0 | 1000 | 570 | 17 | 6106.37 | 14091.07 | 105.85
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 0 | 35 | 45 | 95 | 30 | 35 | 72 | 0 | 300 | 0 | 0 | 35 | 341 | 0 | 0 | 2 | 143.42 | 10.5 | 19 | 0 | 380 | 16 | 30 | 21 | 0 | 0 | 0 | 44 | 36 | 12 | 50 | 1.06 | 222 | 17 | 7 | 840 | 16 | 0 | 19 | 8 | 17 | 217 | 0 | 0 | 0 | 1200 | 10 | 13 | 153 | 350 | 354 | 280 | 44 | 0 | 85 | 0 | 34 | 138 | 17 | 65 | 19 | 17 | 28 | 8 | 68 | 14 | 295 | 400 | 306 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 30 | 141 | 0 | 25 | 2 | 59 | 12.4 | 116 | 0 | 0.7 | 29.2 | 0 | 8019.28 | 900 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 62 | 612 | 34 | 0 | 0 | 1115.81 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 17.82 | 63 | 0 | 0 | 9.99 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.95 | 153 | 50 | 35 | 28 | 49 | 0 | 0 | 0 | 6.6 | 178 | 0.71 | 16 | 200 | 115 | 220 | 0 | 1000 | 570 | 17 | 6251.88 | 14271.16 | 105.86
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 17 | 0 | 59 | 72 | 145 | 32 | 35 | 72 | 0 | 304 | 0 | 0 | 35 | 338 | 0 | 0 | 0 | 143.42 | 11 | 0 | 0 | 440 | 16 | 50 | 24 | 0 | 1 | 0 | 44 | 36 | 50 | 100 | 0 | 222 | 17 | 3 | 840 | 30 | 0 | 19 | 8 | 17 | 214 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 300 | 354 | 310 | 44 | 0 | 100 | 18 | 48 | 136 | 36 | 56 | 19 | 20 | 34 | 8 | 74 | 14 | 300 | 400 | 317 | 30 | 30 | 0 | 1 | 8 | 0 | 81 | 30 | 140 | 0 | 25 | 17 | 59 | 2.08 | 115 | 0 | 0.5 | 4.62 | 0 | 8158.62 | 899 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 15 | 97 | 612 | 34 | 0 | 0 | 1130.31 | 0 | 0 | 0 | 55 | 44 | 0 | 0 | 0 | 8 | 0.59 | 17 | 0 | 0 | 2.86 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.22 | 152 | 51 | 56 | 35 | 70 | 0 | 0 | 0 | 2.3 | 207 | 0.75 | 48 | 200 | 115 | 220 | 0 | 1000 | 574 | 17 | 6365.03 | 14523.65 | 105.86
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 35 | 0 | 131 | 92 | 195 | 55 | 35 | 72 | 0 | 283 | 0 | 0 | 35 | 337 | 0 | 0 | 0 | 143.42 | 11 | 0 | 0 | 370 | 87 | 50 | 23 | 0 | 3 | 0 | 44 | 36 | 100 | 100 | 4.16 | 222 | 17 | 3 | 860 | 66 | 0 | 19 | 8 | 17 | 213 | 0 | 0 | 0 | 1160 | 18 | 11 | 8 | 310 | 354 | 295 | 44 | 0 | 190 | 30 | 69 | 137 | 109 | 57 | 19 | 34 | 32 | 8 | 71 | 14 | 300 | 400 | 375 | 30 | 30 | 0 | 8 | 8 | 0 | 81 | 30 | 140 | 0 | 25 | 17 | 59 | 6.67 | 116 | 0 | 0.8 | 17.77 | 0 | 8650.82 | 898 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 93 | 617.1 | 66 | 0 | 0 | 1121.08 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 8 | 1.1 | 2 | 0 | 0 | 18.2 | 166 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 1.98 | 156 | 51 | 75 | 31 | 71 | 0 | 0 | 0 | 4.9 | 162 | 0.3 | 48 | 200 | 35 | 180 | 0 | 987 | 575 | 17 | 6160.66 | 14811.48 | 105.87
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 0 | 149 | 45 | 145 | 30 | 35 | 72 | 0 | 292 | 0 | 0 | 17 | 337 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 420 | 60 | 50 | 23 | 0 | 6 | 0 | 15 | 36 | 12 | 100 | 3.3 | 222 | 17 | 2 | 850 | 71 | 0 | 19 | 8 | 17 | 213 | 0 | 0 | 0 | 1164 | 16 | 13 | 8 | 310 | 320 | 290 | 44 | 0 | 202 | 35 | 69 | 139 | 100 | 51 | 19 | 17 | 36 | 8 | 60 | 14 | 292 | 400 | 393 | 30 | 30 | 0 | 4 | 8 | 0 | 81 | 30 | 141 | 0 | 25 | 17 | 59 | 5.6 | 116 | 0 | 0.8 | 15.73 | 0 | 8325.43 | 899 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 73 | 613 | 66 | 0 | 0 | 1129.87 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 8 | 0.31 | 0 | 0 | 0 | 11.88 | 165 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 1.09 | 156 | 51 | 110 | 12 | 34 | 0 | 0 | 0 | 6.1 | 123 | 0.62 | 16 | 200 | 113 | 220 | 0 | 991 | 572 | 17 | 6173.87 | 14499.3 | 105.87
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 35 | 0 | 149 | 45 | 145 | 30 | 35 | 126 | 0 | 271 | 0 | 0 | 35 | 339 | 0 | 0 | 0 | 51 | 11 | 18 | 0 | 380 | 62 | 50 | 23 | 0 | 5 | 0 | 14 | 36 | 12 | 76 | 1.79 | 222 | 17 | 0 | 890 | 71 | 0 | 19 | 8 | 17 | 212 | 0 | 0 | 0 | 1130 | 13 | 11 | 8 | 350 | 355 | 280 | 44 | 0 | 188 | 34 | 69 | 140 | 100 | 26 | 19 | 17 | 34 | 8 | 49 | 15 | 295 | 400 | 382 | 30 | 30 | 0 | 4 | 8 | 0 | 81 | 30 | 141 | 0 | 22 | 17 | 59 | 6.8 | 116 | 0 | 0.5 | 13.09 | 0 | 8325.18 | 899 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 26 | 0 | 0 | 64 | 616 | 30 | 0 | 0 | 1121.68 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 8 | 0.3 | 1 | 0 | 0 | 5.25 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.46 | 156 | 51 | 115 | 20 | 34 | 0 | 0 | 0 | 1.9 | 113 | 0.51 | 16 | 200 | 115 | 220 | 0 | 1000 | 570 | 17 | 6188.1 | 14513.28 | 105.88
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35 | 0 | 119 | 45 | 160 | 30 | 35 | 144 | 0 | 300 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 380 | 57 | 52 | 26 | 0 | 3 | 0 | 14 | 36 | 12 | 24 | 1.31 | 222 | 17 | 0 | 895 | 16 | 0 | 19 | 8 | 17 | 212 | 0 | 0 | 0 | 1160 | 8 | 13 | 8 | 393 | 300 | 305 | 44 | 0 | 196 | 33 | 69 | 139 | 51 | 26 | 19 | 17 | 36 | 8 | 32 | 15 | 290 | 400 | 387 | 29 | 30 | 0 | 4 | 8 | 0 | 81 | 30 | 141 | 0 | 57 | 17 | 59 | 3.2 | 117 | 0 | 0.4 | 7.79 | 0 | 8317.12 | 900 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 26 | 0 | 0 | 43 | 617 | 17 | 0 | 0 | 1120.97 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 8 | 0.01 | 0 | 0 | 0 | 2.41 | 161 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.22 | 156 | 51 | 35 | 12 | 34 | 0 | 0 | 0 | 1.7 | 47 | 0.3 | 16 | 200 | 114 | 180 | 0 | 989 | 570 | 17 | 5878.61 | 14195.73 | 105.88
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 0 | 98 | 45 | 160 | 30 | 35 | 90 | 0 | 284 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 380 | 17 | 52 | 30 | 0 | 0 | 34 | 14 | 36 | 12 | 24 | 0.39 | 220 | 17 | 9 | 930 | 16 | 0 | 19 | 8 | 17 | 213 | 0 | 0 | 0 | 1160 | 2 | 13 | 8 | 393 | 355 | 295 | 44 | 0 | 190 | 32 | 69 | 139 | 51 | 26 | 19 | 17 | 34 | 8 | 6 | 16 | 288 | 400 | 392 | 29 | 30 | 0 | 1 | 8 | 0 | 81 | 30 | 141 | 0 | 58 | 17 | 59 | 1.3 | 126 | 0 | 0.2 | 2.81 | 0 | 8253.12 | 900 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 32 | 6 | 615 | 17 | 0 | 0 | 1127.56 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 0.06 | 0 | 0 | 0 | 0.88 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.09 | 155 | 51 | 35 | 2 | 34 | 0 | 0 | 0 | 0.8 | 33 | 0.05 | 16 | 200 | 114 | 220 | 0 | 1000 | 570 | 17 | 5943.44 | 14196.56 | 105.88
18:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 0 | 88 | 30 | 160 | 30 | 35 | 110 | 0 | 309 | 0 | 0 | 35 | 308 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 480 | 17 | 52 | 35 | 0 | 0 | 34 | 14 | 36 | 12 | 50 | 0 | 220 | 17 | 14 | 935 | 20 | 0 | 19 | 8 | 17 | 214 | 0 | 0 | 0 | 1056 | 0 | 43 | 8 | 340 | 354 | 295 | 44 | 0 | 205 | 32 | 69 | 141 | 51 | 43 | 19 | 17 | 38 | 8 | 0 | 22 | 289 | 400 | 330 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 30 | 139 | 0 | 69 | 17 | 66 | 0 | 134 | 0 | 0 | 0 | 0 | 8361.42 | 852 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 56 | 0 | 32 | 0 | 613 | 17 | 0 | 0 | 1315.25 | 0 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0.24 | 157 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 157 | 52 | 50 | 0 | 73 | 0 | 0 | 0 | 0 | 1 | 0.01 | 44 | 200 | 114 | 220 | 0 | 987 | 570 | 17 | 6155.5 | 14516.92 | 105.88
19:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 0 | 121 | 140 | 245 | 47 | 55 | 144 | 0 | 298 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 370 | 108 | 52 | 37 | 0 | 0 | 51 | 50 | 54.36 | 100 | 100 | 0 | 220 | 17 | 10 | 970 | 87 | 0 | 19 | 12 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 68 | 20 | 393 | 310 | 290 | 44 | 0 | 186 | 32 | 75 | 141 | 129 | 70 | 19 | 88 | 38 | 8 | 0 | 22 | 292 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 28 | 139 | 0 | 79 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 3 | 9435.78 | 804 | 0 | 0 | 11 | 0 | 0 | 120 | 0 | 66 | 0 | 32 | 0 | 616 | 51 | 0 | 0 | 1409.21 | 0 | 0 | 0 | 113 | 97 | 0 | 43 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 156 | 51 | 114 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 200 | 115 | 180 | 0 | 1100 | 570 | 17 | 6529.21 | 15964.99 | 105.88
19:30 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 0 | 149 | 78 | 195 | 30 | 55 | 144 | 0 | 307 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 420 | 53 | 52 | 20 | 0 | 0 | 51 | 50 | 54 | 12 | 100 | 0 | 220 | 17 | 10 | 1015 | 106 | 0 | 19 | 25.5 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 60 | 26 | 360 | 345 | 310 | 44 | 0 | 200 | 31 | 115 | 143 | 68 | 71 | 19 | 17 | 38 | 8 | 0 | 22 | 291 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 81 | 25 | 140 | 0 | 79 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9284.92 | 805 | 0 | 0 | 18 | 0 | 0 | 120 | 0 | 75 | 0 | 32 | 0 | 615 | 51 | 0 | 0 | 1417.87 | 0 | 0 | 0 | 113 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 155 | 51 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 115 | 180 | 0 | 1100 | 570 | 35 | 6549.87 | 15834.79
20:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 0 | 149 | 78 | 195 | 30 | 55 | 162 | 0 | 302 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 430 | 53 | 52 | 22 | 0 | 0 | 51 | 50 | 54.36 | 12 | 100 | 0 | 221 | 17 | 17 | 1050 | 106 | 0 | 19 | 25.5 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 60 | 51 | 320 | 355 | 255 | 44 | 0 | 203 | 31 | 111 | 143 | 68 | 70 | 19 | 17 | 40 | 8 | 0 | 22 | 290 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 83 | 25 | 141 | 0 | 86 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9284.28 | 805 | 0 | 0 | 23 | 0 | 0 | 120 | 0 | 73 | 0 | 32 | 0 | 614 | 51 | 0 | 0 | 1419.04 | 0 | 0 | 0 | 113 | 50 | 0 | 50 | 6 | 0 | 0 | 0 | 20 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 153 | 50 | 50 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 115 | 180 | 0 | 1100 | 570 | 35 | 6556.04 | 15840.32 | 105.89
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 0 | 149 | 78 | 195 | 30 | 55 | 162 | 0 | 296 | 0 | 0 | 35 | 297 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 400 | 53 | 52 | 12 | 0 | 0 | 51 | 50 | 54.36 | 12 | 100 | 0 | 221 | 17 | 30 | 1050 | 106 | 0 | 12 | 19 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 61 | 53 | 300 | 354 | 260 | 44 | 0 | 195 | 31 | 109 | 143 | 68 | 73 | 19 | 17 | 40 | 8 | 0 | 22 | 290 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 103 | 15 | 87 | 0 | 165 | 0 | 0 | 0 | 12 | 9247.78 | 805 | 0 | 0 | 22 | 0 | 0 | 120 | 0 | 86 | 0 | 32 | 0 | 614 | 53 | 0 | 0 | 1422.81 | 0 | 0 | 0 | 113 | 50 | 0 | 50 | 29 | 0 | 0 | 0 | 20 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 153 | 51 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1100 | 570 | 17 | 6578.81 | 15826.59 | 105.89
22:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35 | 0 | 123 | 45 | 145 | 30 | 55 | 162 | 0 | 289 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 370 | 17 | 52 | 12 | 0 | 0 | 51 | 50 | 54.36 | 12 | 100 | 0 | 221 | 4 | 33 | 1050 | 84 | 0 | 6 | 19 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 60 | 53 | 300 | 354 | 250 | 44 | 0 | 201 | 31 | 68 | 143 | 68 | 73 | 19 | 17 | 42 | 0 | 0 | 22 | 291 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 103 | 17 | 87 | 0 | 165 | 0 | 0 | 0 | 12 | 8955.78 | 900 | 0 | 0 | 17 | 0 | 0 | 120 | 0 | 175 | 0 | 32 | 0 | 616 | 53 | 0 | 0 | 1420.52 | 0 | 0 | 0 | 113 | 35 | 0 | 50 | 30 | 0 | 0 | 0 | 20 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 152 | 51 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 570 | 17 | 6782.52 | 15738.3 | 105.89
23:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35 | 0 | 123 | 45 | 95 | 30 | 55 | 162 | 0 | 299 | 0 | 0 | 35 | 293 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 480 | 17 | 52 | 12 | 0 | 0 | 51 | 50 | 35 | 12 | 100 | 0 | 222 | 17 | 20 | 1050 | 73 | 0 | 6 | 8 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 61 | 26 | 300 | 355 | 265 | 44 | 0 | 221 | 10 | 68 | 140 | 34 | 73 | 19 | 17 | 38 | 0 | 0 | 22 | 288 | 400 | 393 | 29 | 30 | 0 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 107 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 0 | 8933.42 | 900 | 0 | 0 | 17 | 0 | 0 | 120 | 0 | 220 | 0 | 32 | 0 | 617.1 | 17 | 0 | 0 | 1424.57 | 0 | 0 | 0 | 113 | 35 | 0 | 50 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 153 | 50 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1084 | 570 | 17 | 6738.67 | 15672.09 | 105.9
Total KWH | 0 | 867840 | 413280 | 0 | 0 | 0 | 0 | 0 | 8604000 | 0 | 0 | 470520 | 0 | 2056032 | 2234400 | 3757865 | 1036942 | 861525 | 2409120 | 0 | 7058240 | 0 | 0 | 795993 | 7472912 | 0 | 0 | 48185 | 3302400 | 240000 | 367560 | 0 | 10085454.55 | 1553127 | 1234473 | 566400 | 0 | 16800 | 767786 | 1077360 | 583447 | 1288320 | 2068800 | 18945 | 5302404 | 411491 | 392160 | 19781818.18 | 1401745 | 0 | 521280 | 254115 | 409818 | 5091194 | 0 | 0 | 0 | 28450906 | 121770 | 638981 | 1037091 | 8136500 | 8620400 | 6818000 | 1032232 | 0 | 4601000 | 344160 | 1747200 | 3344490 | 1639200 | 993720 | 444550 | 699960 | 863040 | 543994 | 536736 | 472272 | 6991000 | 9571800 | 9101000 | 696000 | 714600 | 0 | 27734 | 242928 | 0 | 1947840 | 689952 | 3184000 | 0 | 2236980 | 334440 | 1575600 | 44100 | 2666400 | 0 | 4950 | 111940 | 42000 | 206093217.73 | 20629818 | 0 | 0 | 230400 | 0 | 0 | 3806016 | 0 | 1505120 | 0 | 255312 | 671040 | 14778181 | 710400 | 0 | 0 | 27392212 | 0 | 0 | 0 | 1137024 | 786912 | 0 | 249728 | 147102 | 161011 | 99896 | 192980 | 186000 | 0 | 74256 | 3989455 | 0 | 0 | 0 | 0 | 0 | 9460945 | 0 | 6240 | 3678000 | 1254545 | 1951521 | 185296 | 1202582 | 0 | 503842.5 | 0 | 31026.72 | 905040 | 4777 | 832704 | 4844000 | 2656000 | 5135410 | 0 | 24305455 | 14029090.91 | 450000 | 148439338.13 | 354532555.86

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14523.65 | MW | 12:00 Hr. | Energy Generated |  |  | 354.5326 |  | MKWHr.
| Day Peak Demand |  |  | 14598.65 | MW | 12:00 Hr. | Energy Unserverd |  |  | 14.282 |  | MKWHr.
| Evening Peak Generation |  |  | 15964.99 | MW | 19:00 Hr. | Energy Demand |  |  | 368.8146 |  | MKWHr.
| Evening Peak Demand |  |  | 16180.99 | MW | 19:00 Hr. | Maximum Temperature |  |  | 28.6 |  | °C
| Minimum Generation of the Day |  |  | 13703.04 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 905.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 15964.99 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 7.9406 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.8282 | 0 | 18.2059 | 0 | 0 | 0.048185 | 0 | 0 | 52.0823 | Gas | 130.3079 | Gas | 454717292.9735
| Chattogram Zone |  |  | 5.4834 | 48.2327 | 12.1382 | 0 | 5.3024 | 0.14072 | 0 | 0.0168 | 71.3142 | Coal | 111.122 | Coal | 798846229.6481
| Cumilla Zone |  |  | 34.3784 | 0 | 6.7353 | 0 | 0 | 0.53674 | 0.86304 | 0 | 42.5135 | HFO | 49.9985 | HFO | 1065508929.13
| Mymensingh Zone |  |  | 0 | 0 | 4.6184 | 0 | 0 | 0.16099 | 0 | 0 | 4.7794 | HSD | 5.815 | HSD | 135479576.72
| Sylhet Zone |  |  | 35.3761 | 0 | 0 | 0 | 0 | 0.027734 | 0 | 0 | 35.4038 | Hydro | 5.3024 | Hydro | 530240.4
| Khulna Zone |  |  | 0 | 14.7782 | 1.1961 | 5.3111 | 0 | 0.67104 | 20.6298 | 0 | 42.5863 | Solar | 3.0849 | Solar | 50010842.7604
| Barishal Zone |  |  | 7.7914 | 43.1785 | 1.2827 | 0 | 0 | 0.004777 | 0 | 0 | 52.2574 | Import | 48.8851 | Import | 309868965.86
| Rajshahi Zone |  |  | 13.4504 | 0 | 2.6678 | 0 | 0 | 0.37337 | 27.3922 | 0 | 43.8838 | Wind | 0.0168 | Wind | 249312
| Rangpur Zone |  |  | 0 | 4.9325 | 3.1541 | 0.50384 | 0 | 1.1214 | 0 | 0 | 9.7119
| Total |  |  | 130.3079 | 111.122 | 49.9985 | 5.815 | 5.3024 | 3.0849 | 48.8851 | 0.0168 | 354.5326
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 454717292.9735 |  | Hydro | 530240.4
|  |  |  | Coal | 798846229.6481 |  | Solar | 50010842.7604
|  |  |  | HFO | 1065508929.13 |  | Import | 309868965.86
|  |  |  | HSD | 135479576.72 |  | Wind | 249312
[5 empty] | Total: | 281,52,11,389 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6298 | Peak Hr Flow | 804.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37552909.14 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.3922 | Peak Hr Flow | 1409.21 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1720 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.86304 | Peak Hr Flow | 38.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2416 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.8851 | Peak Hr Flow | 2251.21 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 94 |  | 6002
|  |  |  | Chattogram |  | 12 |  | 1586
|  |  |  | Cumilla |  | 39 |  | 1562
|  |  |  | Mymensingh |  | 44 |  | 1242
|  |  |  | Sylhet |  | 4 |  | 648
|  |  |  | Khulna |  | 0 |  | 1662
|  |  |  | Barishal |  | 0 |  | 522
|  |  |  | Rajshahi |  | 10 |  | 1479
|  |  |  | Rangpur |  | 4 |  | 1005
|  |  |  | Total |  | 207 |  | 15708
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[5 empty] | Total | 300 |  |  |  | Total | 143.5
|  |  |  | Total Unavailable Capacity |  |  |  | 443.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:33 | 09:42 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing EF, R Phase, Distance relay zone -1 5.1 K.M relays Due to Distance relay
| 09:10 | 09:48 | Chapai 132/33kV S/S T-2 (415T) HT Tripped showing Differential protection p632 relays.
| 09:10 | 09:48 | Chapai 132/33kV S/S T-2 (415T) LT Tripped showing DOC/DEF relays.
| 09:10 | 09:48 | Chapai 132/33kV S/S T-4 (435T) LT Tripped showing Inst E/F relays. | [7 empty] | 7.0MW load interrup.
| 09:14 | 16:40 | Birulia 230/132kV S/S Birulia-Aminbazar 230KV Ckt-2 Scheduled S/D Due to NLDC rerquest
forTele-protection work at Aminbazar end.
| 09:20 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 09:21 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- running
|  | 09:40 | Cox'sbazar-Dohazari 132 kV Ckt-1 is restored.
| 10:05 |  | Charsaidpur 132/33kV S/S 132/33 kV GT-1 LT Scheduled S/D Due to Yarly Maintenance
| 10:06 | 16:25 | Charsaidpur 132/33kV S/S 132/33 kV GT-1 HT Scheduled S/D Due to yearly maintenance
| 10:48 | 11:50 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to BBP block signal Trouble shooting
| 10:48 | 11:49 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to BBP Block signal Trouble shooting
|  | 11:06 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
| 11:08 |  | Bhola Nutan Biddut BD LTD, FGMO is OFF with remarks:- FGMO kept off as per NLDC Request
at 11:01 hrs
| 12:45 | 16:14 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Red hot Maintanance of 33kV T-1 Bus | [7 empty] | 15.0MW load interrup.
| 12:45 | 16:15 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Red hot Maintanance of 33kV T-1 Bus | [7 empty] | 15.0MW load interrup.
| 14:59 | 15:07 | Jashore 132/33kV S/S T-1 HT Tripped showing no relay operated from jashore end relays Due | [7 empty] | 45.0MW load
|  |  | to From jashore s/s end no breaker tripped. CB tripped from Jhenaidah 230/132 kv S/s | [7 empty] | interrup.
end.Information got from ALDC KHULNA.
| 14:59 | 15:07 | Jashore 132/33kV S/S T-2 HT Tripped showing no relay operated from jashore end relays Due | [7 empty] | 45.0MW load
|  |  | to From jashore s/s end no breaker tripped. CB tripped from Jhenaidah 230/132 kv S/s | [7 empty] | interrup.
end.Information got from ALDC KHULNA
| 14:59 | 15:07 | Benapole-Jashore 132 kV Ckt-2 Tripped from Benapole 132/33kV end showing no relay | [7 empty] | 25.0MW load
|  |  | operated relays Due to Jhinaidah-kaligong 230 kv ckt -2 differential earth fault and | [7 empty] | interrup. Benapole
|  |  | Jashore end Bus-B earth fault. | [7 empty] | 132/33kV end
| 15:07 | 16:41 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Shutdown takek by pbs. | [7 empty] | 25.0MW load interrup.
| 15:07 | 16:40 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Shutdown Taken by PBS. | [7 empty] | 25.0MW load interrup.
| 15:35 |  | Sylhet 225 MW CCPP Synchronized with remarks:- ST
| 15:51 | 16:25 | Jashore-Noapara 132kV Ckt-2 Tripped from Jashore 132/33kV end showing Distance relay
relays Due to Distance Zone-1 Trip and from Noapara 132/33kV end showing ALSTOM Signal
Shown in Relay Phase= A Zone= Z1 Distance= 0.8km Trip= ABC relays Due to Distance
Fault
| 17:08 |  | Khulna 330 MW CCPP (HSD) ST was synchronized.
| 17:19 | 17:47 | Birulia 230/132kV S/S Birulia-Aminbazar 230KV Ckt-1 Scheduled S/D Due to Shutdown taken by NLDC
| 19:00 |  | Evening peak generation is 15965 MW.
| 19:00 |  | Evening Peak Generation: 15965 MW.
| 20:55 | 21:51 | Khagrachori 132/33kV S/S TR-2 HT Forced S/D Due to Red hot romoving at TR-02 Y Ph Bushing | [7 empty] | 7.0MW load interrup.
| 22:36 | 22:44 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Tripped showing micom p122 relays Due to
T-3(A+B) incomer feeder triped affected by 33kv pbs(Debiganj) feeder fault
| 06:00 |  | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Red hot maintenance work | [7 empty] | 10.0MW load interrup.
| 06:00 |  | Ramganj 132/33kV S/S Transformer -02 HT Scheduled S/D Due to Red hot maintenance work | [7 empty] | 10.0MW load interrup.
| 07:07 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Solving oil leakage problem
of T2 33kv incoming CT Y Phase.
| 07:07 | 07:59 | Munshiganj 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Solving oil leakage problem
of T2 33kv incoming CT Y Phase.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 8604000 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 7058240 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 47 | 1036942 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7472912 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 470520 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 2234400 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 861525 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 795993 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 240000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 367560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 413280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 3757865 | Line Overload
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 121 | 2056032 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 867840 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2409120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 48185 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 370 | 10085454.55 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | STG Under Shutdown & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3302400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6221.494 | 2407.42 | 52082268.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 12 | 254115 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121770 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 521280 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5302404 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5091194 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 409818 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 1077360 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 767786 | ps availability is less
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1288320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 392160 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 37 | 566400 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18945 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1234473 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 583447 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 411491 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2068800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 1553127 | Fuel Shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 87 | 1401745 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28450906 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 16800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 970 | 19781818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3345.36 | 71314159.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 186 | 4601000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 310 | 8620400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 6818000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8136500 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 344160 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 20 | 1037091 | Line Overload
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1032232 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 68 | 638981 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 472272 | ps availability is less
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3344490 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 129 | 1639200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 38 | 863040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 543994 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 444550 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 699960 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 993720 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 75 | 1747200 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 536736 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1933 | 42513526
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 44100 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2666400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1575600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 111940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 3 | 42000 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 334440 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 271 | 4779430
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 27734 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 696000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714600 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3184000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 689952 | ps availability is less
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1947840 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 79 | 2236980 | ps availability is less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 242928 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 292 | 6991000 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 393 | 9101000 | ps availability is less
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9571800 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1479 | 35403834
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 804 | 20629818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 11 | 230400 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 120 | 3806016 | Fuel Shortage
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 710400 | Fuel Shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 255312 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 671040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 66 | 1505120 | ST synch process going on
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 616 | 14778181 | U-2 Under maint.
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1700 | 42586287
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24305455 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 75 | 832704 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2656000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 14029090.91 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5135410 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 450000 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4844000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4777 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2257 | 52257436.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 99896 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 147102 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 3989455 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 320 | 9460945 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 186000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 161011 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 249728 | Fuel Shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 97 | 786912 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1137024 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 6240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1409.21 | 27392212 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 74256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 192980 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2158.21 | 43883761
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 503842.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1254545 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3678000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 93 | 1202582 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31026.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1951521 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185296 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 905040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 414 | 9711853.22
Eastern Grid Total |  |  |  |  | 16977.666 | 9435.78 | 206093217.73
Western Grid Total |  |  |  |  | 11731.125 | 6529.21 | 148439338.13
National Grid Total |  |  |  |  | 28708.791 | 15964.99 | 354532555.86
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-09-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10847.34 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4654.6 | MW
i) Dhaka area |  |  | 5908.04 |  | MW | i) Khulna area |  |  |  | 1662 | MW
ii) Chattogram area |  |  | 1574.3 |  | MW | ii) Barishal area |  |  |  | 522.4 | MW
iii) Cumilla area |  |  | 1523 |  | MW | iii) Rajshahi area |  |  |  | 1469.2 | MW
iv) Mymensingh area |  |  | 1198 |  | MW | iv) Rangpur area |  |  |  | 1001 | MW
v) Sylhet area |  |  | 644 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15501.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 72 | Ishurdi | 78 | 12:00 | 143 | Palashbari | 133 | 18:30
2 | AKSML | 159.4 | 02:00 | 73 | Jaldhaka | 86 | 19:00 | 144 | Panchagarh | 62 | 19:00
3 | Aftabnagar | 46 | 00:00 | 74 | Jamalpur | 124 | 21:00 | 145 | Patiya | 31 | 22:00
4 | Agargaon | 134 | 13:00 | 75 | Jashore | 165 | 13:00 | 146 | Patnitala | 33 | 21:00
5 | Agrabad | 78 | 14:00 | 76 | Jhenaidah | 87 | 00:00 | 147 | Patuakhali | 79 | 22:00
6 | Amnura | 29 | 00:00 | 77 | Joydebpur | 166 | 13:00 | 148 | Payra | 40 | 21:00
7 | Araihazar | 106 | 19:00 | 78 | Joypurhat | 60 | 19:00 | 149 | Postogola | 66 | 01:00
8 | Ashuganj | 97 | 00:00 | 79 | Juldah | 16 | 00:00 | 150 | Pubail | 45 | 21:00
9 | BSRM | 178 | 04:00 | 80 | KSRM | 26 | 17:00 | 151 | Purbachal | 31 | 00:00
10 | Bagerhat | 91 | 18:30 | 81 | Kabirpur | 287 | 15:00 | 152 | Purbasadipur | 130 | 00:00
11 | Bajitpur | 100 | 23:00 | 82 | Kachua | 100 | 21:00 | 153 | Rahanpur | 43 | 22:00
12 | Bakerganj | 15.6 | 23:00 | 83 | Kaliganj | 39 | 07:00 | 154 | Rahim | 26 | 23:00
13 | Bakulia | 101 | 19:00 | 84 | Kallyanpur | 123 | 00:00 | 155 | Rajbari | 81 | 07:00
14 | Banani | 64 | 10:00 | 85 | Kalurghat | 40 | 09:00 | 156 | Rajendrapur | 127 | 15:00
15 | Bangabhaban | 16 | 10:00 | 86 | Kamrangirchar | 86 | 13:00 | 157 | Rajshahi | 113 | 00:00
16 | Barapukuria | 58 | 18:30 | 87 | Kaptai | N/A | N/A | 158 | Rajshahi-230 | 120 | 13:00
17 | Barguna | 24 | 20:00 | 88 | Kasba | 38 | 22:00 | 159 | Ramganj | 120 | 19:00
18 | Barishal | 113 | 12:00 | 89 | Kazla | 122 | 13:00 | 160 | Rampur | 46 | 20:00
19 | Barishal-230 | 112 | 18:30 | 90 | Keranigonj | 86 | 19:00 | 161 | Rangamati | 18 | 18:00
20 | Baroaulia | 43 | 11:00 | 91 | Khagrachori | 34 | 18:00 | 162 | Rangpur | 137 | 19:00
21 | Baroirhat | 66 | 21:00 | 92 | Khulna | 63 | 13:00 | 163 | Ruppur | 4.4 | 11:00
22 | Bashundhara | 199 | 00:00 | 93 | Khulshi | 185 | 18:00 | 164 | SSM | 0 | 00:00
23 | BashundharaCement | 0 | 00:00 | 94 | Kishoreganj | 139 | 21:00 | 165 | Saidpur | 104 | 00:00
24 | Beanibazar | 76 | 19:30 | 95 | Kodda | 322 | 14:00 | 166 | Santhia | 30 | 05:00
25 | Benapole | 77 | 00:00 | 96 | Kulaura | 53 | 21:00 | 167 | Satkhira | 136 | 21:00
26 | Bhaluka | 165 | 18:30 | 97 | Kurigram | 70 | 19:00 | 168 | Satmasjid | 107 | 13:00
27 | Bhandaria | 62 | 18:30 | 98 | Kushtia | 151 | 12:00 | 169 | Savar | 234 | 12:00
28 | Bhangura | 36 | 07:00 | 99 | Laksam | 36 | 20:00 | 170 | SevenRings | 15 | 16:00
29 | Bheramara(GK) | 63 | 18:30 | 100 | Lakshmipur | 55 | 19:30 | 171 | ShahCement | 24 | 01:00
30 | Bhulta | 204 | 06:00 | 101 | Lalbag | 78 | 17:00 | 172 | Shahjadpur | 78 | 00:00
31 | Bog-Sherpur | 68 | 18:30 | 102 | Lalmonirhat | 62 | 18:30 | 173 | Shahjibazar | 134 | 18:30
32 | Bogura | 213 | 00:00 | 103 | MI_Cement | 16 | 05:00 | 174 | Shahmirpur | 61 | 23:00
33 | Borhanuddin | 85 | 22:00 | 104 | Madanganj | 45 | 19:30 | 175 | Shariatpur | 99 | 22:00
34 | Brahmanbaria | 141 | 20:00 | 105 | Madaripur | 110 | 22:00 | 176 | Sherpur | 154 | 00:00
35 | Cantonment | 134 | 13:00 | 106 | Madartek | 92 | 00:00 | 177 | Shikalbaha | 21 | 18:30
36 | Chandina | 39 | 06:00 | 107 | Madunaghat | 55 | 19:00 | 178 | Shitalakhya | 78.2 | 10:00
37 | Chandpur | 84 | 22:00 | 108 | Magura | 67 | 07:00 | 179 | Sholosohor | 50 | 15:00
38 | Chandraghona | 39 | 19:00 | 109 | Mahasthangarh | 77 | 19:00 | 180 | Shomvuganj | 52 | 00:00
39 | Chapai | 73 | 20:00 | 110 | Maijdee | 44 | 22:00 | 181 | Shyampur | 168 | 03:00
40 | Charfasson | 37 | 23:00 | 111 | Manikganj | 140 | 19:00 | 182 | Siddhirganj | 127 | 10:00
41 | Charsaidpur | 32 | 16:00 | 112 | Maniknagar | 74 | 13:00 | 183 | Sirajganj | 120 | 00:00
42 | Chauddagram | 77 | 19:00 | 113 | Matarbari | 58 | 19:30 | 184 | Sitakunda | 35 | 20:00
43 | Chhatak | 40 | 19:30 | 114 | Matuail | 78 | 12:00 | 185 | Sonargaon | 132 | 15:00
44 | Chowmuhani | 168 | 20:00 | 115 | Metrorail_Motijheel | 21 | 19:00 | 186 | Sreemongol | 83 | 19:30
45 | Chuadanga | 108 | 06:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 187 | Sreepur | 132 | 18:00
46 | Coxsbazar | 153 | 20:00 | 117 | Millgate | 105 | 12:00 | 188 | Srinagar | 47.08 | 04:00
47 | Cumilla(N) | 144 | 07:00 | 118 | Mirpur | 154 | 12:00 | 189 | Sunamganj | 61 | 20:00
48 | Cumilla(S) | 173 | 14:00 | 119 | Mirsorai | 49 | 12:00 | 190 | Sylhet | 126 | 16:00
49 | Daganbhuiyan | 36 | 00:00 | 120 | Mirzapur | 51 | 07:00 | 191 | Sylhet_(South) | 69 | 00:00
50 | Daudkandi | 139 | 20:00 | 121 | Mithapukur | 78 | 18:30 | 192 | TK | 0 | 00:00
51 | DhakaUniversity | 92 | 13:00 | 122 | Modern | N/A | N/A | 193 | Tangail | 180 | 00:00
52 | Dhamrai | 96 | 19:30 | 123 | Mogbazar | 67.7 | 00:00 | 194 | Taraganj | 39 | 18:30
53 | Dhanmondi | 117.7 | 13:00 | 124 | Mongla | 46 | 11:00 | 195 | Tasnim | 42 | 18:30
54 | Dohazari | 113 | 19:00 | 125 | Motijheel | 50 | 12:00 | 196 | Thakurgaon | 112 | 19:00
55 | Faridpur | 176 | 00:00 | 126 | Muktagacha | 37 | 00:00 | 197 | Tongi | 169 | 08:00
56 | Fatullah | 115 | 11:00 | 127 | Munshiganj | 107 | 18:00 | 198 | Ullahpara | 40 | 07:00
57 | Fenchuganj | 42 | 19:00 | 128 | Muradnagar | 56 | 20:00 | 199 | Ullon | 54 | 23:00
58 | Feni | 110 | 18:30 | 129 | Mymensingh | 152 | 01:00 | 200 | Uttara | 102 | 12:00
59 | GPH | 72 | 13:00 | 130 | Nabinagar | 110 | 06:00 | 201 | UttaraNew | 61 | 00:00
60 | Ghatail | 94 | 18:30 | 131 | Naogaon | 118 | 13:00 | 202 | Zigatola | 96 | 00:00
61 | Ghorashal | 0 | 00:00 | 132 | Narail | 63.5 | 07:00
62 | Ghorashal-230 | 108 | 16:00 | 133 | Narinda | 79 | 13:00
63 | Goalpara | 42 | 07:00 | 134 | Narshingdi | 188 | 20:00
64 | Gollamari | 120 | 13:00 | 135 | Natore | 147 | 21:00
65 | Gopalganj | 114 | 18:30 | 136 | Nawabganj | 56.5 | 22:00
66 | Gulshan | 116 | 13:00 | 137 | Netrakona | 142 | 18:00
67 | Halishahar | 111.5 | 15:00 | 138 | New | 82 | 12:00
68 | HaripurSBU | 135 | 08:00 | 139 | Niamatpur | 65 | 22:00
69 | Hasnabad | 93 | 00:00 | 140 | Noapara | 49 | 19:00
70 | Hathazari | 99 | 19:00 | 141 | PHP | 13 | 15:00
71 | Hatirjheel | 79 | 13:00 | 142 | Pabna | 101 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15931.19 | 2143 |  | 18170.19
1:00 | 14804.48 | 2073 |  | 16970.77
2:00 | 14435.72 | 2190 |  | 16724.27
3:00 | 14106.14 | 2089 |  | 16289.14
4:00 | 14025.9 | 1996 |  | 16111.9
5:00 | 13944.95 | 1837 |  | 15864.95
6:00 | 13703.04 | 535 |  | 14262.12
7:00 | 14004.64 | 36 |  | 14042.64
8:00 | 13853.06 | 50 |  | 13905.06
9:00 | 14042.18 | 50 |  | 14094.18
10:00 | 14091.07 | 59 |  | 14152.73
11:00 | 14271.16 | 52 |  | 14325.16
12:00 | 14523.65 | 72 |  | 14598.65
13:00 | 14811.48 | 67 |  | 14881.48
14:00 | 14499.3 | 67 |  | 14569.3
15:00 | 14513.28 | 144 |  | 14663.28
16:00 | 14195.73 | 67 |  | 14265.73
17:00 | 14196.56 | 52 |  | 14250.9
18:00 | 14516.92 | 119 |  | 14640.92
19:00 | 15964.99 | 207 |  | 16180.99
19:30 | 15834.79 | 113 |  | 15952.88
20:00 | 15840.32 | 98 |  | 15942.32
21:00 | 15826.59 | 98 |  | 15928.59
22:00 | 15738.3 | 103 |  | 15846.3
23:00 | 15672.09 | 78 |  | 15754.09
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8953.12 | 6978.07 | 15931.19 | DAILY GENERATION CURVE
00:30 | 8715.12 | 6652.715 | 15367.835
01:00 | 8477.12 | 6327.36 | 14804.48 | 17-09-2026
01:30 | 8379.62 | 6240.48 | 14620.1
02:00 | 8282.12 | 6153.6 | 14435.72
02:30 | 8264.12 | 6006.81 | 14270.93
03:00 | 8246.12 | 5860.02 | 14106.14
03:30 | 8310.62 | 5755.4 | 14066.02
04:00 | 8375.12 | 5650.78 | 14025.9
04:30 | 8349.62 | 5635.805 | 13985.425
05:00 | 8324.12 | 5620.83 | 13944.95
05:30 | 8248.15 | 5575.845 | 13823.995
06:00 | 8172.18 | 5530.86 | 13703.04
06:30 | 8259.32 | 5594.52 | 13853.84
07:00 | 8346.46 | 5658.18 | 14004.64
07:30 | 8286.935 | 5641.915 | 13928.85
08:00 | 8227.41 | 5625.65 | 13853.06
08:30 | 8195.945 | 5751.675 | 13947.62
09:00 | 8164.48 | 5877.7 | 14042.18
09:30 | 8074.59 | 5992.035 | 14066.625
10:00 | 7984.7 | 6106.37 | 14091.07
10:30 | 8001.99 | 6179.125 | 14181.115
11:00 | 8019.28 | 6251.88 | 14271.16
11:30 | 8088.95 | 6308.455 | 14397.405
12:00 | 8158.62 | 6365.03 | 14523.65
12:30 | 8404.72 | 6262.845 | 14667.565
13:00 | 8650.82 | 6160.66 | 14811.48
13:30 | 8488.125 | 6167.265 | 14655.39
14:00 | 8325.43 | 6173.87 | 14499.3
14:30 | 8325.305 | 6180.985 | 14506.29
15:00 | 8325.18 | 6188.1 | 14513.28
15:30 | 8321.15 | 6033.355 | 14354.505
16:00 | 8317.12 | 5878.61 | 14195.73
16:30 | 8285.12 | 5911.025 | 14196.145
17:00 | 8253.12 | 5943.44 | 14196.56
17:30 | 8307.27 | 6049.47 | 14356.74
18:00 | 8361.42 | 6155.5 | 14516.92
18:30 | 8898.6 | 6342.355 | 15240.955
19:00 | 9435.78 | 6529.21 | 15964.99
19:30 | 9284.92 | 6549.87 | 15834.79
20:00 | 9284.28 | 6556.04 | 15840.32
20:30 | 9266.03 | 6567.425 | 15833.455 |  | Executive Engineer
21:00 | 9247.78 | 6578.81 | 15826.59 |  | Network Operation Division
21:30 | 9101.78 | 6680.665 | 15782.445
22:00 | 8955.78 | 6782.52 | 15738.3
22:30 | 8944.6 | 6760.595 | 15705.195
23:00 | 8933.42 | 6738.67 | 15672.09

## En-Curve
QF-LDC-12
Date | 17-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4015 | 1456.5 | 814 | 0 | 42 | 1395.97 | 222 | 4365.1 | 0 | 666.42 | 2349.2 | 605 | 0 | 0 | 2143 | DAILY ENERGY CURVE
00:30 | 4023.5 | 1470.5 | 795 | 0 | 41 | 1273.115 | 222 | 4350.1 | 0 | 578.92 | 2005.2 | 608.5 | 0 | 0 | 2108 | 17-09-2026
01:00 | 4032 | 1484.5 | 776 | 0 | 40 | 1150.26 | 222 | 4335.1 | 0 | 491.42 | 1661.2 | 612 | 0 | 0 | 2073
01:30 | 4009.5 | 1455 | 776.5 | 0 | 40 | 1073.38 | 222 | 4330.1 | 0 | 492.42 | 1610.2 | 611 | 0 | 0 | 2131.5 | Energy Generated | 354.5326 |  | MKWHr
02:00 | 3987 | 1425.5 | 777 | 0 | 40 | 996.5 | 222 | 4325.1 | 0 | 493.42 | 1559.2 | 610 | 0 | 0 | 2190 | Energy not Served | 14.282 |  | MKWHr
02:30 | 3997 | 1441.5 | 803.5 | 0 | 39 | 953.71 | 222 | 4318.1 | 0 | 493.42 | 1507.2 | 495.5 | 0 | 0 | 2139.5 | Total Energy Requirement | 368.8146 |  | MKWHr
03:00 | 4007 | 1457.5 | 830 | 0 | 38 | 910.92 | 222 | 4311.1 | 0 | 493.42 | 1455.2 | 381 | 0 | 0 | 2089
03:30 | 4009.5 | 1460 | 807.5 | 0 | 38 | 912.3 | 220.5 | 4381.1 | 0 | 483.42 | 1435.7 | 318 | 0 | 0 | 2042.5
04:00 | 4012 | 1462.5 | 785 | 0 | 38 | 913.68 | 219 | 4451.1 | 0 | 473.42 | 1416.2 | 255 | 0 | 0 | 1996
04:30 | 3980 | 1456.5 | 785 | 0 | 37 | 911.755 | 218 | 4458.55 | 0 | 472.92 | 1410.7 | 255 | 0 | 0 | 1916.5
05:00 | 3948 | 1450.5 | 785 | 0 | 36 | 909.83 | 217 | 4466 | 0 | 472.42 | 1405.2 | 255 | 0 | 0 | 1837
05:30 | 3882 | 1445 | 784.5 | 0 | 36 | 909.225 | 217 | 4442 | 1.15 | 463.42 | 1388.7 | 255 | 0 | 0 | 1186
06:00 | 3816 | 1439.5 | 784 | 0 | 36 | 908.62 | 217 | 4418 | 2.3 | 454.42 | 1372.2 | 255 | 0 | 0 | 535
06:30 | 3867.5 | 1477.5 | 784 | 0 | 35 | 912.195 | 217 | 4469.05 | 30.115 | 442.42 | 1364.06 | 255 | 0 | 0 | 285.5
07:00 | 3919 | 1515.5 | 784 | 0 | 34 | 915.77 | 217 | 4520.1 | 57.93 | 430.42 | 1355.92 | 255 | 0 | 0 | 36
07:30 | 3864.5 | 1508 | 818 | 0 | 33 | 914.39 | 218.5 | 4481.6 | 108.38 | 412.92 | 1346.56 | 223 | 0 | 0 | 43
08:00 | 3810 | 1500.5 | 852 | 0 | 32 | 913.01 | 220 | 4443.1 | 158.83 | 395.42 | 1337.2 | 191 | 0 | 0 | 50
08:30 | 3814.5 | 1483.5 | 875.5 | 0 | 32 | 1001.69 | 220.5 | 4473.55 | 192.36 | 394.92 | 1294.6 | 164.5 | 0 | 0 | 50
09:00 | 3819 | 1466.5 | 899 | 0 | 32 | 1090.37 | 221 | 4504 | 225.89 | 394.42 | 1252 | 138 | 0 | 0 | 50
09:30 | 3822 | 1466 | 899 | 0 | 32 | 1098.125 | 221 | 4545.5 | 268.08 | 366.42 | 1209.5 | 139 | 0 | 0 | 54.5
10:00 | 3825 | 1465.5 | 899 | 0 | 32 | 1105.88 | 221 | 4587 | 310.27 | 338.42 | 1167 | 140 | 0 | 0 | 59
10:30 | 3797 | 1501 | 899.5 | 0 | 30 | 1110.845 | 221.5 | 4606 | 400.35 | 330.92 | 1144 | 140 | 0 | 0 | 55.5
11:00 | 3769 | 1536.5 | 900 | 0 | 28 | 1115.81 | 222 | 4625 | 490.43 | 323.42 | 1121 | 140 | 0 | 0 | 52
11:30 | 3759.5 | 1487.25 | 899.5 | 0 | 31 | 1123.06 | 222 | 4639 | 467.675 | 344.42 | 1293.5 | 130 | 0 | 0.5 | 62
12:00 | 3750 | 1438 | 899 | 0 | 34 | 1130.31 | 222 | 4653 | 444.92 | 365.42 | 1466 | 120 | 0 | 1 | 72
12:30 | 3745 | 1372.5 | 898.5 | 0 | 33 | 1125.695 | 222 | 4629.55 | 442.9 | 367.92 | 1708.5 | 120 | 0 | 2 | 69.5
13:00 | 3740 | 1307 | 898 | 0 | 32 | 1121.08 | 222 | 4606.1 | 440.88 | 370.42 | 1951 | 120 | 0 | 3 | 67
13:30 | 3788 | 1346.5 | 898.5 | 0 | 34 | 1125.475 | 222 | 4601.55 | 387.155 | 296.21 | 1819 | 132.5 | 0 | 4.5 | 67
14:00 | 3836 | 1386 | 899 | 0 | 36 | 1129.87 | 222 | 4597 | 333.43 | 222 | 1687 | 145 | 0 | 6 | 67
14:30 | 3915 | 1370.5 | 899 | 0 | 35 | 1125.775 | 222 | 4605 | 314.015 | 186 | 1683 | 145.5 | 0 | 5.5 | 105.5
15:00 | 3994 | 1355 | 899 | 0 | 34 | 1121.68 | 222 | 4613 | 294.6 | 150 | 1679 | 146 | 0 | 5 | 144
15:30 | 3971.5 | 1347 | 899.5 | 0 | 35 | 1121.325 | 222 | 4625.5 | 228.97 | 196.21 | 1557.5 | 146 | 0 | 4 | 105.5
16:00 | 3949 | 1339 | 900 | 0 | 36 | 1120.97 | 222 | 4638 | 163.34 | 242.42 | 1436 | 146 | 0 | 3 | 67
16:30 | 3994 | 1354.5 | 900 | 0 | 35 | 1124.265 | 221 | 4659.5 | 109.96 | 275.92 | 1375 | 145.5 | 0 | 1.5 | 59.5
17:00 | 4039 | 1370 | 900 | 0 | 34 | 1127.56 | 220 | 4681 | 56.58 | 309.42 | 1314 | 145 | 0 | 0 | 52
17:30 | 3982.5 | 1435.5 | 876 | 0 | 36 | 1221.405 | 220 | 4625.5 | 28.915 | 343.92 | 1426.5 | 160.5 | 0 | 0 | 85.5
18:00 | 3926 | 1501 | 852 | 0 | 38 | 1315.25 | 220 | 4570 | 1.25 | 378.42 | 1539 | 176 | 0 | 0 | 119
18:30 | 3913 | 1426 | 828 | 0 | 38 | 1362.23 | 220 | 4728.5 | 0.625 | 496.92 | 2046.68 | 181 | 0 | 0 | 163
19:00 | 3900 | 1351 | 804 | 0 | 38 | 1409.21 | 220 | 4887 | 0 | 615.42 | 2554.36 | 186 | 0 | 0 | 207
19:30 | 4033 | 1415 | 805 | 0 | 38 | 1417.87 | 220 | 4930 | 0 | 567.42 | 2213.5 | 195 | 0 | 0 | 113
20:00 | 3942 | 1453 | 805 | 0 | 40 | 1419.04 | 221 | 4961 | 0 | 578.42 | 2227.86 | 193 | 0 | 0 | 98
20:30 | 3944 | 1443 | 805 | 0 | 40 | 1420.925 | 221 | 4961.5 | 0 | 589.42 | 2209.11 | 199.5 | 0 | 0 | 98
21:00 | 3946 | 1433 | 805 | 0 | 40 | 1422.81 | 221 | 4962 | 0 | 600.42 | 2190.36 | 206 | 0 | 0 | 98
21:30 | 3932.5 | 1436.5 | 852.5 | 0 | 41 | 1421.665 | 221 | 4962.5 | 0 | 581.92 | 2082.36 | 250.5 | 0 | 0 | 100.5
22:00 | 3919 | 1440 | 900 | 0 | 42 | 1420.52 | 221 | 4963 | 0 | 563.42 | 1974.36 | 295 | 0 | 0 | 103
22:30 | 3933 | 1458.5 | 900 | 0 | 40 | 1422.545 | 221.5 | 4955.55 | 0 | 562.42 | 1894.18 | 317.5 | 0 | 0 | 90.5
23:00 | 3947 | 1477 | 900 | 0 | 38 | 1424.57 | 222 | 4948.1 | 0 | 561.42 | 1814 | 340 | 0 | 0 | 78
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 17-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 136 | 40 | 404 | 172 | 1344 | 596 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 103 | 38 | 336 | 152 | 1228 | 526
2:00 | 100 | 32 | 320 | 142 | 1234 | 522 |  | Import | 0
3:00 | 93 | 31 | 270 | 142 | 1072 | 526
4:00 | 73 | 32 | 214 | 140 | 896 | 486 | Ishurdi-Ghorashal Ckt-2 | Export | 3102909.14
5:00 | 72 | 29 | 184 | 124 | 944 | 472
6:00 | 75 | 32 | 172 | 128 | 962 | 500 |  | Import | 0
7:00 | 64 | 27 | 108 | 116 | 854 | 486
8:00 | 92 | 31 | 184 | 128 | 988 | 556 | Sirajganj-Sreepur Ckt-1 | Export | 2138000
9:00 | 134 | 44 | 250 | 140 | 1216 | 608
10:00 | 168 | 47 | 400 | 146 | 1432 | 622 |  | Import | 0
11:00 | 176 | 52 | 410 | 176 | 1412 | 638
12:00 | 165 | 48 | 470 | 206 | 1400 | 678 | Sirajganj-Sreepur Ckt-2 | Export | 2142000
13:00 | 147 | 36 | 406 | 182 | 1316 | 644
14:00 | 174 | 58 | 472 | 216 | 1600 | 740 |  | Import | 0
15:00 | 212 | 75 | 554 | 226 | 1650 | 728
16:00 | 194 | 64 | 474 | 194 | 1564 | 698 | Gopalganj-Aminbazar Ckt-1 | Export | 15070000
17:00 | 176 | 48 | 470 | 184 | 1510 | 712
18:00 | 172 | 44 | 490 | 200 | 1518 | 672 |  | Import | 0
18:30 | 172 | 44 | 390 | 192 | 1244 | 576
19:00 | 172 | 44 | 374 | 192 | 1174 | 578 | Gopalganj-Aminbazar Ckt-2 | Export | 15100000
19:30 | 114 | 23 | 376 | 180 | 1202 | 576
20:00 | 110 | 20 | 380 | 180 | 1164 | 554 |  | Import | 0
21:00 | 107 | 14 | 384 | 182 | 1122 | 528
22:00 | 128 | 16 | 424 | 182 | 1292 | 562 |  | Total Export | 37552909.14
23:00 | 138 | 20 | 440 | 190 | 1282 | 564 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 05:00 | 366 | 12:00 | Madunaghat | 401 | 04:00 | 392 | 23:00
Amtali | 413 | 04:00 | 409 | 00:00 | Meghnaghat | 389 | 05:00 | 375 | 12:00
Ashuganj | 408 | 5:00 | 389 | 12:00 | Mirsorai | 401 | 02:00 | 389 | 22:00
Bhulta | 398 | 05:00 | 378 | 12:00 | Payra | 414 | 02:00 | 410 | 23:00
Bibiana | 382 | 03:00 | 376 | 12:00 | Rahanpur | 411 | 06:00 | 399 | 23:00
BIPTC | 404 | 06:00 | 393 | 00:00 | Rampal | 398 | 05:00 | 387 | 23:00
Bogura | 397 | 06:00 | 384 | 21:00
Gopalganj | 394 | 05:00 | 384 | 12:00
Kaliakoir | 375 | 05:00 | 358 | 12:00
Korerhat | 400 | 04:00 | 388 | 22:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 219 | 12:00 | Hasnabad | 233 | 07:00 | 217 | 12:00
AKSML | 238 | 08:00 | 228 | 23:00 | Hathazari | 236 | 03:00 | 229 | 16:00
Aminbazar | 231 | 05:00 | 220 | 12:00 | Ishurdi | 236 | 01:00 | 223 | 23:00
Ashuganj | 228 | 05:00 | 218 | 23:00 | Jhenaidah | 232 | 15:00 | 214 | 21:00
Ashuganj-400 | 228 | 5:00 | 218 | 23:00 | Kachua | 228 | 02:00 | 219 | 23:00
Baghabari | 232 | 06:00 | 225 | 19:30 | Kaliakoir | 232 | 05:00 | 220 | 11:00
Barapukuria | 229 | 06:00 | 222 | 19:30 | Keranigonj | 228 | 04:00 | 217 | 12:00
Barapukuria-230 | 229 | 6:00 | 221 | 19:00 | Khulna(S) | 230 | 03:00 | 223 | 12:00
Barapukuria(N) | 230 | 06:00 | 224 | 19:30 | Korerhat | 227 | 03:00 | 220 | 22:00
Barishal | 225 | 00:00 | 221 | 22:00 | Madunaghat | 239 | 01:00 | 232 | 15:00
Bheramara | 235 | 01:00 | 222 | 21:00 | Madunaghat-400 | 240 | 01:00 | 234 | 16:00
Bhulta | 227 | 04:00 | 213 | 12:00 | Maniknagar | 221 | 02:00 | 212 | 12:00
Bibiana | 218 | 04:00 | 212 | 16:00 | Meghnaghat | 232 | 05:00 | 221 | 12:00
BIPTC | 236 | 01:00 | 221 | 23:00 | Meghnaghat-400 | 227 | 04:00 | 217 | 12:00
Birulia | 231 | 05:00 | 219 | 12:00 | Mirsorai | 233 | 02:00 | 226 | 17:00
Bogura | 239 | 06:00 | 233 | 19:30 | Naogaon | 224 | 09:00 | 210 | 22:00
Bogura-400 | 239 | 06:00 | 232 | 21:00 | Purbasadipur | 227 | 06:00 | 219 | 19:30
Borhanuddin | 228 | 01:00 | 226 | 12:00 | Rajshahi | 233 | 06:00 | 219 | 23:00
BSRM | 229 | 02:00 | 220 | 23:00 | Rampal | 228 | 02:00 | 222 | 12:00
Charfasson | 229 | 09:00 | 225 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 00:00 | 219 | 23:00 | Rampura | 226 | 04:00 | 212 | 12:00
Cumilla(N) | 224 | 06:00 | 215 | 12:00 | Shikalbaha | 238 | 01:00 | 231 | 11:00
Faridpur | 224 | 13:00 | 217 | 12:00 | Shyampur | 227 | 04:00 | 215 | 12:00
Fenchuganj | 218 | 02:00 | 211 | 15:00 | Siddhirganj | 226 | 04:00 | 215 | 12:00
Feni | 226 | 02:00 | 217 | 17:00 | Sirajgonj | 237 | 09:00 | 231 | 23:00
Ghorashal | 230 | 01:00 | 215 | 12:00 | Sreepur | 225 | 07:00 | 215 | 15:00
Ghorashal-230 | 219 | 05:00 | 203 | 12:00 | Tongi | 221 | 01:00 | 208 | 15:00
Gopalganj | 223 | 03:00 | 218 | 11:00
GPH | 244 | 07:00 | 227 | 23:00
Haripur | 226 | 05:00 | 214 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 04:00 | 129 | 12:00 | Madanganj | 132 | 04:00 | 127 | 11:00
Agargaon | 137 | 05:00 | 129 | 12:00 | Madaripur | 132 | 05:00 | 128 | 22:00
Agrabad | 137 | 01:00 | 130 | 15:00 | Madartek | 140 | 05:00 | 129 | 12:00
AKS | 135 | 00:00 | 129 | 15:00 | Madunaghat | 138 | 00:00 | 133 | 17:00
Aminbazar | 131 | 03:00 | 125 | 12:00 | Magura | 138 | 15:00 | 125 | 22:00
Amnura | 132 | 00:00 | 128 | 19:30 | Mahasthangarh | 135 | 10:00 | 130 | 22:00
Araihazar | 129 | 02:00 | 121 | 12:00 | Maijdee | 128 | 01:00 | 122 | 23:00
Ashuganj | 134 | 07:00 | 126 | 21:00 | Manikganj | 130 | 01:00 | 125 | 14:00
Ashuganj-230 | 137 | 06:00 | 132 | 00:00 | Maniknagar | 139 | 04:00 | 131 | 12:00
Bagerhat | 128 | 17:00 | 121 | 23:00 | Matarbari | 125 | 07:00 | 109 | 23:00
Bajitpur | 130 | 06:00 | 121 | 18:30 | Matuail | 133 | 02:00 | 127 | 11:00
Bakerganj | 132 | 17:00 | 128 | 22:00 | Metrorail_Motijheel | 139 | 04:00 | 131 | 12:00
Bakulia | 138 | 00:00 | 130 | 15:00 | Metrorail_Uttara | 132 | 01:00 | 122 | 12:00
Banani | 140 | 04:00 | 128 | 12:00 | Millgate | 134 | 04:00 | 122 | 12:00
Bangabhaban | 139 | 03:00 | 131 | 12:00 | Mirpur | 131 | 02:00 | 124 | 12:00
Barapukuria | 139 | 06:00 | 131 | 18:30 | Mirzapur | 133 | 05:00 | 127 | 08:00
Barguna | 131 | 05:00 | 127 | 22:00 | Mithapukur | 133 | 06:00 | 128 | 00:00
Barishal | 132 | 01:00 | 128 | 11:00 | MI_Cement | 134 | 05:00 | 125 | 12:00
Barishal-230 | 132 | 01:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 01:00 | 131 | 15:00 | Mogbazar | 141 | 03:00 | 130 | 12:00
Baroirhat | 132 | 01:00 | 129 | 11:00 | Mongla | 126 | 01:00 | 122 | 23:00
Bashundhara | 140 | 04:00 | 121 | 12:00 | Motijheel | 139 | 03:00 | 131 | 12:00
BashundharaCement | 132 | 04:00 | 127 | 11:00 | Muktagacha | 129 | 07:00 | 121 | 08:00
Beanibazar | 121 | 08:00 | 116 | 19:30 | Munshiganj | 133 | 02:00 | 126 | 12:00
Benapole | 137 | 16:00 | 120 | 12:00 | Muradnagar | 128 | 04:00 | 120 | 23:00
Bhaluka | 135 | 06:00 | 124 | 19:00 | Mymensingh | 130 | 10:00 | 113 | 21:00
Bhandaria | 130 | 01:00 | 122 | 23:00 | Nabinagar | 135 | 02:00 | 126 | 11:00
Bhangura | 134 | 06:00 | 129 | 22:00 | Naogaon | 135 | 03:00 | 126 | 22:00
Bheramara | 137 | 01:00 | 130 | 21:00 | Narail | 141 | 15:00 | 123 | 22:00
Bheramara(GK) | 137 | 02:00 | 129 | 22:00 | Narinda | 139 | 4:00 | 131 | 12:00
Bhulta | 126 | 09:00 | 120 | 12:00 | Narshingdi | 130 | 03:00 | 119 | 12:00
Bhulta-400 | 130 | 04:00 | 122 | 12:00 | Natore | 134 | 03:00 | 127 | 21:00
Birulia | 136 | 05:00 | 128 | 12:00 | Nawabganj | 137 | 04:00 | 130 | 12:00
Bog-Sherpur | 136 | 09:00 | 132 | 00:00 | Netrakona | 123 | 06:00 | 109 | 18:00
Bogura | 138 | 10:00 | 133 | 23:00 | New | 133 | 01:00 | 124 | 11:00
Bogura-230 | 138 | 09:00 | 134 | 21:00 | Niamatpur | 134 | 06:00 | 129 | 00:00
Brahmanbaria | 133 | 09:00 | 123 | 23:00 | Noapara | 134 | 16:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 05:00 | 128 | 12:00 | Pabna | 135 | 15:00 | 128 | 21:00
Chandina | 130 | 05:00 | 123 | 22:00 | Palashbari | 132 | 10:00 | 126 | 00:00
Chandpur | 134 | 00:00 | 128 | 22:00 | Panchagarh | 139 | 03:00 | 131 | 19:30
Chandraghona | 139 | 05:00 | 134 | 16:00 | Patiya | 137 | 07:00 | 129 | 10:00
Chapai | 133 | 18:30 | 128 | 23:00 | Patnitala | 133 | 05:00 | 127 | 22:00
Charsaidpur | 132 | 02:00 | 127 | 10:00 | Patuakhali | 131 | 01:00 | 128 | 21:00
Chauddagram | 129 | 01:00 | 124 | 21:00 | Payra | 135 | 00:00 | 133 | 23:00
Chhatak | 121 | 00:00 | 111 | 19:30 | PHP | 132 | 02:00 | 127 | 15:00
Chowmuhani | 128 | 00:00 | 123 | 23:00 | Postogola | 132 | 01:00 | 128 | 06:00
Chuadanga | 139 | 15:00 | 123 | 21:00 | Pubail | 128 | 04:00 | 120 | 14:00
Coxsbazar | 126 | 12:00 | 116 | 20:00 | Purbachal | 140 | 04:00 | 128 | 12:00
Cumilla(N) | 130 | 05:00 | 124 | 12:00 | Purbasadipur | 138 | 06:00 | 124 | 19:30
Cumilla(S) | 133 | 04:00 | 123 | 22:00 | Rahanpur | 137 | 08:00 | 133 | 19:30
Daganbhuiyan | 130 | 02:00 | 124 | 23:00 | Rahanpur-400 | 137 | 02:00 | 133 | 19:30
Daudkandi | 128 | 02:00 | 119 | 15:00 | Rahim | 129 | 19:00 | 127 | 17:00
DhakaUniversity | 140 | 04:00 | 129 | 12:00 | Rajbari | 129 | 13:00 | 122 | 23:00
Dhamrai | 135 | 03:00 | 127 | 12:00 | Rajendrapur | 136 | 05:00 | 128 | 23:00
Dhanmondi | 140 | 04:00 | 128 | 12:00 | Rajshahi | 131 | 01:00 | 125 | 22:00
Dohazari | 133 | 08:00 | 124 | 15:00 | Rajshahi-230 | 133 | 02:00 | 126 | 21:00
Faridpur | 129 | 13:00 | 125 | 07:00 | Ramganj | 129 | 00:00 | 121 | 23:00
Fatullah | 135 | 05:00 | 126 | 12:00 | Rampur | 137 | 00:00 | 130 | 15:00
Fenchuganj | 129 | 06:00 | 124 | 15:00 | Rampura | 140 | 04:00 | 129 | 12:00
Feni | 131 | 01:00 | 125 | 15:00 | Rangamati | 137 | 00:00 | 133 | 22:00
Feni-230 | 131 | 02:00 | 126 | 16:00 | Rangpur | 133 | 06:00 | 127 | 01:00
Ghatail | 129 | 05:00 | 119 | 08:00 | Ruppur | 136 | 14:00 | 130 | 21:00
Ghorashal | 131 | 01:00 | 124 | 14:00 | Saidpur | 136 | 05:00 | 130 | 19:30
Goalpara | 135 | 03:00 | 131 | 21:00 | Santhia | 134 | 03:00 | 129 | 21:00
Gollamari | 134 | 02:00 | 130 | 12:00 | Satkhira | 133 | 17:00 | 123 | 23:00
Gopalganj | 131 | 15:00 | 127 | 23:00 | Satmasjid | 136 | 04:00 | 129 | 12:00
Gopalganj-400 | 132 | 01:00 | 129 | 22:00 | Savar | 131 | 04:00 | 123 | 12:00
Gulshan | 140 | 05:00 | 128 | 12:00 | SevenRings | 131 | 05:00 | 123 | 12:00
Halishahar | 139 | 07:00 | 131 | 16:00 | ShahCement | 133 | 05:00 | 127 | 10:00
Haripur | 135 | 04:00 | 127 | 11:00 | Shahjadpur | 136 | 15:00 | 132 | 00:00
HaripurSBU | 135 | 04:00 | 127 | 12:00 | Shahjibazar | 131 | 09:00 | 122 | 23:00
Hasnabad | 134 | 02:00 | 128 | 11:00 | Shahmirpur | 139 | 00:00 | 131 | 17:00
Hathazari | 139 | 07:00 | 133 | 16:00 | Shariatpur | 130 | 14:00 | 125 | 22:00
Hatirjheel | 141 | 05:00 | 129 | 12:00 | Sherpur | 129 | 07:00 | 115 | 03:00
Ishurdi | 138 | 01:00 | 131 | 21:00 | Shikalbaha | 127 | 01:00 | 121 | 14:00
Jaldhaka | 134 | 05:00 | 128 | 19:30 | Shikalbaha-230 | 139 | 01:00 | 132 | 15:00
Jamalpur | 133 | 00:00 | 118 | 02:00 | Shitalakhya | 134 | 05:00 | 125 | 00:00
Jashore | 137 | 16:00 | 121 | 12:00 | Sholosohor | 137 | 00:00 | 133 | 16:00
Jhenaidah | 142 | 15:00 | 128 | 12:00 | Shomvuganj | 127 | 07:00 | 113 | 19:30
Jhenaidah-230 | 142 | 15:00 | 128 | 12:00 | Shyampur | 132 | 03:00 | 127 | 14:00
Joydebpur | 126 | 03:00 | 119 | 12:00 | Shyampur-230 | 136 | 05:00 | 128 | 11:00
Joypurhat | 133 | 06:00 | 127 | 22:00 | Siddhirganj | 134 | 02:00 | 127 | 12:00
Juldah | 138 | 00:00 | 131 | 14:00 | Sirajganj | 131 | 05:00 | 127 | 21:00
Kabirpur | 134 | 01:00 | 119 | 10:00 | Sitakunda | 137 | 00:00 | 131 | 20:00
Kachua | 130 | 00:00 | 124 | 23:00 | Sonargaon | 129 | 07:00 | 124 | 12:00
Kaliakoir | 138 | 05:00 | 131 | 11:00 | Sreemongol | 128 | 09:00 | 121 | 19:00
Kaliganj | 138 | 16:00 | 127 | 12:00 | Sreepur | 136 | 05:00 | 129 | 15:00
Kallyanpur | 130 | 07:00 | 124 | 12:00 | Srinagar | 138 | 05:00 | 130 | 12:00
Kalurghat | 138 | 00:00 | 134 | 14:00 | SSM | 141 | 00:00 | 138 | 17:00
Kamrangirchar | 137 | 02:00 | 122 | 12:00 | Sunamganj | 118 | 02:00 | 109 | 23:00
Kaptai | 140 | 5:00 | 136 | 12:00 | Sylhet | 122 | 02:00 | 118 | 14:00
Kasba | 127 | 02:00 | 120 | 23:00 | Sylhet_(South) | 124 | 04:00 | 118 | 14:00
Kazla | 139 | 05:00 | 130 | 13:00 | Tangail | 129 | 10:00 | 121 | 14:00
Keranigonj | 138 | 04:00 | 131 | 12:00 | Taraganj | 134 | 06:00 | 129 | 21:00
Khagrachori | 137 | 08:00 | 132 | 17:00 | Tasnim | 132 | 03:00 | 124 | 12:00
Khulna | 134 | 04:00 | 129 | 23:00 | Thakurgaon | 141 | 15:00 | 132 | 19:30
Khulna(S) | 135 | 03:00 | 130 | 23:00 | TK | 138 | 04:00 | 134 | 14:00
Khulshi | 136 | 01:00 | 129 | 15:00 | Tongi | 135 | 01:00 | 124 | 11:00
Kishoreganj | 132 | 07:00 | 119 | 19:00 | Ullahpara | 133 | 04:00 | 129 | 19:30
Kodda | 133 | 02:00 | 117 | 16:00 | Ullon | 139 | 04:00 | 129 | 12:00
Korerhat | 134 | 00:00 | 130 | 12:00 | Uttara | 131 | 02:00 | 122 | 12:00
KSRM | 138 | 00:00 | 132 | 14:00 | UttaraNew | 134 | 05:00 | 122 | 12:00
Kulaura | 127 | 03:00 | 121 | 23:00 | Zigatola | 138 | 05:00 | 131 | 15:00
Kurigram | 132 | 06:00 | 123 | 00:00
Kushtia | 137 | 15:00 | 127 | 12:00
Laksam | 129 | 00:00 | 123 | 23:00
Lakshmipur | 127 | 00:00 | 121 | 23:00
Lalbag | 135 | 08:00 | 129 | 01:00
Lalmonirhat | 130 | 06:00 | 123 | 18:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division