## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-09-2026 | during | 20-09-2026 | during | 20-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 395 | 348 | 412 | 412 | 377 | 377 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 300 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 311 | 300 | 335 | 335 | 335 | 335 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 135 | 149.36 | 149.36 | 30 | 78 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 13 | 33 | 33 | 8.5 | 8.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 25 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 163 | 163 | 300 | 300 | 97 | 196 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 30 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 35 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 547 | 410 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | STG Under Shutdown & Gas Shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 17 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6221.494 | 2126 | 2346 | 5583.16 | 5553.16 | 2354.92 | 2662.89
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50 | 25 | 25 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 219 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 199 | 219 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 51 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 28 | 52 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 30 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 56 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.81 | 0 | 4.66 | 0 | 4.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 60 | 68 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 92 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 49 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 6 | 142 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1190 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 3 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1050 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2864.81 | 3608.86 | 4110.62 | 4172.96 | 3455.66 | 3572.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 190 | 198 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 340 | 354 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 340 | 300 | 342.01 | 342.01 | 307 | 307 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 43 | 0 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 48 | 150 | 150 | 150 | 13 | 55 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 20 | 15 | 15 | 32 | 32 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 134 | 135 | 163 | 163 | 140 | 140 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 6 | 171 | 200 | 200 | 120 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 80 | 84 | 78 | 32 | 40 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 6 | 86 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 41 | 74 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 7 | 108 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1628 | 2204.2 | 2747.44 | 2671.44 | 1888.26 | 2022.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-09-2026 | during | 20-09-2026 | during | 20-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.18 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 164 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.44 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 265.82 | 280 | 538.4 | 546.5 | 251.9 | 272
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 27 | 29 | 30 | 30 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 30 | 30 | 30 | 30 | 30 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 141 | 140 | 140 | 140 | 140 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 0 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 242 | 308 | 350 | 390 | 350 | 390 | machine problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 380 | 395 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1364 | 1424 | 1506 | 1546 | 1471 | 1511
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 804 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 30 | 30 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 120 | 160 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 602 | 588 | 617.1 | 617.1 | 980 | 980 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1710 | 1677 | 2937.1 | 2867.1 | 2272.1 | 2234.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 1100 | 1000 | 1100 | 1000 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 112 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2068.55 | 2332 | 2488 | 2587 | 2339 | 2438
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 35.72 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 169 | 214 | 214 | 193 | 193 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 7 | 20 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 5 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.72 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1019.22 | 1414.15 | 1000 | 1400 | 1000 | 1400 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.69 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1869.35 | 2376.15 | 2785.91 | 2967.99 | 1945.92 | 2349
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 0 | 50 | 50 | 52 | 52 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 159 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 80 | 94 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 13 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 198 | 0 | 166.37 | 0 | 166.37 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 540.2 | 343 | 673.37 | 472 | 596.37 | 474
System Total |  |  |  |  | 28843.2 | 28708.791 | 14436.73 | 16591.21 | 23370 | 23384.15 | 16575.13 | 17536.11
Forecast Scenario (20-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16320 |  | 2030 |  | 18350
|  |  |  | 1:00 | 15780 |  | 2380 |  | 18160
|  |  |  | 2:00 | 15270 |  | 2330 |  | 17600
|  |  |  | 3:00 | 14820 |  | 2110 |  | 16930
|  |  |  | 4:00 | 14320 |  | 650 |  | 14970
|  |  |  | 5:00 | 14020 |  | 120 |  | 14140
|  |  |  | 6:00 | 13710 |  | 0 |  | 13710
|  |  |  | 7:00 | 13700 |  | 0 |  | 13700
|  |  |  | 8:00 | 13520 |  | 0 |  | 13520
|  |  |  | 9:00 | 13410 |  | 0 |  | 13410
|  |  |  | 10:00 | 13720 |  | 220 |  | 13940
|  |  |  | 11:00 | 13910 |  | 330 |  | 14240
|  |  |  | 12:00 | 14440 |  | 320 |  | 14760
|  |  |  | 13:00 | 15040 |  | 270 |  | 15310
|  |  |  | 14:00 | 15150 |  | 280 |  | 15430
|  |  |  | 15:00 | 15540 |  | 310 |  | 15850
|  |  |  | 16:00 | 15420 |  | 280 |  | 15700
|  |  |  | 17:00 | 15300 |  | 270 |  | 15570
|  |  |  | 18:00 | 15650 |  | 550 |  | 16200
|  |  |  | 18:30 | 16100 |  | 424.975 |  | 16545
|  |  |  | 19:00 | 15740 |  | 1575.75 |  | 17390
|  |  |  | 19:30 | 15740 |  | 1747.65 |  | 17570
|  |  |  | 20:00 | 15930 |  | 1604.4 |  | 17610
|  |  |  | 21:00 | 15900 |  | 1795.4 |  | 17780
|  |  |  | 22:00 | 15990 |  | 1356.1 |  | 17410
|  |  |  | 23:00 | 16260 |  | 1193.75 |  | 17510
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14760.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1795
Probable Maximum Demand at Evening Peak: |  |  | 17780.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 358.86 MKWHr. |  | 97 | 0 | 202 | 550 | 167 | 382 | 16 | 303 | 78 | 1795
*** This report is generated digitally from Operation Information System (OIS) at 08:29 hrs on 20-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-09-2026 | [28 empty] | Date: | 19-09-2026 | [28 empty] | Date: | 19-09-2026 | [28 empty] | Date: | 19-09-2026 | [28 empty] | Date: | 19-09-2026 | [17 empty] | Date: | 19-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 35 | 137 | 124 | 245 | 55 | 55 | 158 | 0 | 281 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 34 | 16 | 22 | 0 | 405 | 109 | 105 | 19 | 0 | 0 | 49 | 42 | 35 | 100 | 88 | 0 | 221 | 17 | 36 | 1050 | 162 | 0 | 18 | 25.5 | 17 | 216 | 0 | 0 | 0 | 1170 | 0 | 13 | 100 | 240 | 354 | 255 | 44 | 0 | 221 | 0 | 115 | 138 | 173 | 73 | 19 | 88 | 42 | 8 | 0 | 15 | 297 | 400 | 330 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 141 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9578.5 | 900 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 257 | 0 | 67 | 0 | 612 | 32 | 0 | 0 | 1393.84 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 12 | 0 | 0 | 0 | 13 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 157 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6737.84 | 16316.34 | 105.86
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 35 | 142 | 138 | 245 | 55 | 35 | 72 | 0 | 294 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 520 | 107 | 52 | 18 | 0 | 0 | 49 | 28 | 0 | 100 | 76 | 0 | 222 | 17 | 35 | 1050 | 120 | 0 | 24 | 25.5 | 17 | 215 | 0 | 0 | 0 | 1224 | 0 | 20 | 100 | 240 | 354 | 270 | 44 | 0 | 221 | 0 | 109 | 138 | 172 | 73 | 19 | 88 | 42 | 8 | 0 | 15 | 290 | 400 | 330 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 141 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 9380.5 | 899 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 249 | 0 | 67 | 0 | 607 | 35 | 0 | 0 | 1091.55 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 48 | 115 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6400.55 | 15781.05 | 105.85
02:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 54 | 35 | 142 | 139 | 245 | 55 | 35 | 72 | 0 | 277 | 0 | 0 | 17 | 290 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 395 | 109 | 52 | 18 | 0 | 0 | 49 | 28 | 0 | 100 | 100 | 0 | 222 | 17 | 34 | 1050 | 53 | 0 | 24 | 25.5 | 17 | 215 | 0 | 0 | 0 | 1130 | 0 | 26 | 100 | 240 | 354 | 245 | 44 | 0 | 222 | 0 | 108 | 138 | 172 | 73 | 19 | 88 | 40 | 8 | 0 | 15 | 287 | 400 | 330 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 9057.5 | 844 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 251 | 0 | 74 | 0 | 608 | 50 | 0 | 0 | 1000.99 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 50 | 115 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6216.99 | 15274.49 | 105.85
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 35 | 119 | 138 | 247 | 55 | 35 | 72 | 0 | 291 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 17 | 16 | 14 | 0 | 415 | 107 | 52 | 18 | 0 | 0 | 0 | 28 | 0 | 50 | 100 | 0 | 222 | 17 | 36 | 1050 | 55 | 0 | 24 | 25.5 | 17 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 100 | 240 | 356 | 260 | 44 | 0 | 205 | 0 | 106 | 138 | 172 | 0 | 19 | 88 | 40 | 8 | 0 | 15 | 285 | 400 | 352 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8848.5 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 85 | 0 | 608 | 50 | 0 | 0 | 1013.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 161 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5973.74 | 14822.24 | 105.85
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 35 | 52 | 75 | 250 | 55 | 35 | 72 | 0 | 282 | 0 | 0 | 17 | 301 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 415 | 72 | 52 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 100 | 0 | 222 | 17 | 36 | 1050 | 53 | 0 | 24 | 0 | 17 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 100 | 240 | 353 | 255 | 44 | 0 | 197 | 0 | 78 | 140 | 172 | 0 | 19 | 0 | 38 | 0 | 0 | 15 | 284 | 400 | 354 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8471 | 844 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 206 | 0 | 50 | 0 | 607 | 50 | 0 | 0 | 1018.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5853.27 | 14324.27 | 105.84
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35 | 17 | 52 | 45 | 246 | 15 | 35 | 72 | 0 | 284 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 425 | 17 | 52 | 18 | 0 | 5 | 0 | 28 | 0 | 0 | 100 | 0 | 221 | 17 | 38 | 1050 | 55 | 0 | 24 | 0 | 17 | 217 | 0 | 0 | 0 | 1160 | 0 | 28 | 100 | 240 | 355 | 260 | 44 | 0 | 200 | 0 | 69 | 140 | 120 | 0 | 19 | 0 | 38 | 0 | 0 | 15 | 285 | 400 | 354 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 30 | 141 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8269 | 843 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 206 | 0 | 15 | 0 | 605 | 17 | 0 | 0 | 1010.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5749.41 | 14018.41 | 105.84
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 17 | 52 | 45 | 145 | 15 | 17 | 72 | 0 | 282 | 0 | 0 | 17 | 290 | 0 | 0 | 1 | 17 | 16 | 22 | 0 | 385 | 17 | 52 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 88 | 0.06 | 220 | 17 | 40 | 1050 | 53 | 0 | 24 | 0 | 17 | 217 | 0 | 0 | 0 | 1150 | 0 | 26 | 107 | 240 | 353 | 260 | 44 | 0 | 195 | 0 | 69 | 140 | 68 | 0 | 19 | 0 | 36 | 0 | 2 | 15 | 284 | 400 | 354 | 29 | 30 | 0 | 0 | 8 | 0 | 86 | 30 | 141 | 0 | 100 | 17 | 58 | 0.21 | 67 | 0 | 0 | 0.46 | 12 | 8014.73 | 797 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 206 | 0 | 15 | 1 | 606 | 17 | 0 | 0 | 1005.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0 | 0 | 0 | 0.34 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 159 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 64 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5692.92 | 13707.65 | 105.84
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 17 | 52 | 45 | 45 | 15 | 17 | 72 | 0 | 285 | 0 | 0 | 17 | 300 | 0 | 0 | 5 | 17 | 16 | 22 | 0 | 510 | 17 | 51 | 18 | 0 | 3 | 0 | 28 | 0 | 0 | 100 | 0.69 | 219 | 17 | 39 | 1050 | 17 | 0 | 8 | 0 | 17 | 220 | 0 | 0 | 0 | 1160 | 0 | 26 | 107 | 240 | 355 | 270 | 44 | 0 | 208 | 0 | 30 | 140 | 17 | 0 | 19 | 0 | 32 | 0 | 18 | 15 | 285 | 397 | 353 | 29 | 30 | 0 | 3 | 16 | 0 | 86 | 30 | 140 | 0 | 100 | 17 | 58 | 4 | 67 | 0 | 0.4 | 9.41 | 10 | 7986.5 | 797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 15 | 20 | 605 | 17 | 0 | 0 | 1013.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.95 | 10 | 0 | 0 | 9.31 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.9 | 157 | 51 | 35 | 5 | 0 | 0 | 0 | 0 | 1.6 | 35 | 0.1 | 16 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5715.33 | 13701.83 | 105.83
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 52 | 15 | 15 | 15 | 17 | 72 | 0 | 288 | 0 | 0 | 17 | 290 | 0 | 0 | 14 | 17 | 16 | 22 | 0 | 440 | 0 | 15 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 50 | 1.47 | 218 | 17 | 11 | 1050 | 17 | 0 | 6 | 0 | 17 | 219 | 0 | 0 | 0 | 1160 | 0 | 26 | 107 | 240 | 354 | 240 | 44 | 0 | 194 | 0 | 16 | 138 | 0 | 5 | 19 | 0 | 32 | 0 | 38 | 0 | 280 | 400 | 353 | 29 | 30 | 0 | 5 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 17 | 58 | 10.15 | 67 | 0 | 1 | 23.09 | 10 | 7631.71 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 43 | 602 | 0 | 0 | 0 | 1012.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.71 | 42 | 0 | 0 | 23.18 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.37 | 157 | 52 | 0 | 15 | 0 | 0 | 0 | 0 | 3.1 | 90 | 0.29 | 16 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 5892.04 | 13523.75 | 105.83
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 17 | 52 | 15 | 15 | 15 | 17 | 72 | 0 | 289 | 0 | 0 | 17 | 292 | 0 | 0 | 22 | 17 | 12.8 | 22 | 0 | 385 | 0 | 15 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 24 | 3.15 | 218 | 17 | 3 | 1020 | 0 | 0 | 3 | 0 | 17 | 214 | 0 | 0 | 0 | 1111 | 0 | 26 | 107 | 240 | 353 | 255 | 44 | 0 | 199 | 0 | 16 | 136 | 0 | 51 | 19 | 0 | 30 | 0 | 56 | 0 | 285 | 398 | 282 | 29 | 29 | 0 | 8 | 0 | 0 | 83 | 30 | 141 | 0 | 100 | 17 | 58 | 15.59 | 114 | 0 | 1.5 | 37.71 | 0 | 7505.75 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 62 | 595 | 0 | 0 | 0 | 1014.19 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 39.12 | 67 | 0 | 0 | 40.18 | 182 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.78 | 155 | 51 | 0 | 24 | 0 | 0 | 0 | 0 | 4.9 | 142 | 0.45 | 16 | 200 | 115 | 180 | 0 | 990 | 570 | 17 | 5899.62 | 13405.37 | 105.83
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 45 | 15 | 15 | 15 | 20 | 34 | 0 | 284 | 0 | 0 | 0 | 296 | 0 | 0 | 26 | 17 | 12 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 36 | 0 | 12 | 3.58 | 218 | 0 | 5 | 1020 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 1090 | 0 | 26 | 107 | 393 | 354 | 280 | 44 | 0 | 199 | 8 | 0 | 138 | 0 | 42 | 19 | 0 | 32 | 0 | 68 | 0 | 310 | 394 | 242 | 28 | 29 | 0 | 11 | 0 | 0 | 82 | 30 | 141 | 0 | 100 | 17 | 58 | 20 | 116 | 0 | 1.9 | 45.87 | 0 | 7684.35 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 89 | 592 | 0 | 0 | 0 | 1020.89 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 53.07 | 40 | 0 | 0 | 54.18 | 182 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 160 | 51 | 0 | 31 | 0 | 0 | 0 | 0 | 6.3 | 179 | 0.61 | 0 | 200 | 115 | 220 | 0 | 959 | 570 | 0 | 6031.05 | 13715.4 | 105.82
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 17 | 18 | 15 | 50 | 15 | 35 | 33 | 0 | 301 | 0 | 0 | 0 | 314 | 0 | 0 | 11 | 17 | 12 | 20 | 0 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 36 | 0 | 12 | 3.65 | 218 | 0 | 6 | 1050 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 1160 | 0 | 28 | 86 | 300 | 350 | 335 | 44 | 0 | 193 | 20 | 0 | 134 | 0 | 26 | 19 | 0 | 34 | 0 | 51 | 0 | 310 | 385 | 242 | 28 | 28 | 0 | 12 | 8 | 0 | 82 | 30 | 141 | 0 | 100 | 17 | 58 | 22 | 116 | 0 | 1.8 | 51.53 | 0 | 7816.98 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 83 | 598 | 0 | 0 | 0 | 1023.88 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 58.96 | 71 | 6 | 0 | 52.68 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.61 | 157 | 51 | 0 | 35 | 33 | 0 | 0 | 0 | 7.1 | 199 | 0.68 | 0 | 190 | 114 | 220 | 0 | 968 | 570 | 0 | 6088.91 | 13905.89 | 105.82
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17 | 17 | 30 | 30 | 163 | 15 | 35 | 90 | 0 | 301 | 0 | 0 | 17 | 311 | 0 | 0 | 33 | 17 | 12 | 20 | 0 | 547 | 0 | 60 | 0 | 0 | 1 | 0 | 28 | 36 | 0 | 49 | 3.81 | 222 | 0 | 3 | 1050 | 6 | 0 | 0 | 0 | 17 | 199 | 0 | 0 | 0 | 1190 | 0 | 48 | 43 | 280 | 340 | 340 | 44 | 0 | 190 | 20 | 7 | 134 | 6 | 41 | 19 | 6 | 36 | 0 | 74 | 0 | 320 | 380 | 242 | 27 | 28 | 0 | 12 | 8 | 0 | 82 | 25 | 140 | 0 | 100 | 17 | 58 | 22.18 | 116 | 0 | 2.2 | 50.44 | 0 | 8248.63 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 96 | 602 | 0 | 0 | 0 | 1019.22 | 0 | 0 | 0 | 55 | 5 | 0 | 0 | 0 | 0 | 35.72 | 80 | 7 | 0 | 64.69 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.72 | 156 | 50 | 13 | 36 | 80 | 0 | 0 | 0 | 7.2 | 198 | 0.55 | 16 | 150 | 112 | 220 | 0 | 1000 | 570 | 0 | 6188.1 | 14436.73 | 105.82
13:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 101 | 104 | 163 | 42 | 35 | 108 | 0 | 301 | 0 | 0 | 17 | 291 | 0 | 0 | 29 | 17 | 12 | 20 | 0 | 380 | 67 | 65 | 7 | 0 | 13 | 0 | 26 | 36 | 50 | 73 | 3.67 | 222 | 27 | 3 | 1050 | 68 | 0 | 0 | 8 | 17 | 199 | 0 | 0 | 0 | 1140 | 7 | 53 | 8 | 330 | 351 | 285 | 44 | 0 | 215 | 20 | 58 | 133 | 132 | 70 | 19 | 85 | 36 | 8 | 66 | 10 | 315 | 385 | 243 | 27 | 28 | 0 | 12 | 8 | 0 | 81 | 25 | 140 | 0 | 100 | 17 | 58 | 22.01 | 116 | 0 | 2 | 51.27 | 0 | 8708.95 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 87 | 604 | 16 | 0 | 0 | 1005.25 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 54.22 | 60 | 0 | 0 | 45.69 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.92 | 158 | 50 | 85 | 34 | 85 | 0 | 0 | 0 | 7.1 | 190 | 0.19 | 80 | 150 | 114 | 220 | 0 | 983 | 570 | 17 | 6335.37 | 15044.32 | 105.81
14:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 17 | 149 | 117 | 163 | 50 | 35 | 108 | 0 | 299 | 0 | 0 | 17 | 300 | 0 | 0 | 28 | 17 | 12 | 20 | 0 | 405 | 96 | 68 | 15 | 0 | 22 | 0 | 26 | 36 | 60 | 73 | 3.44 | 221 | 60 | 3 | 1050 | 147 | 0 | 2 | 8 | 17 | 198 | 0 | 0 | 0 | 1100 | 0 | 53 | 0 | 386 | 351 | 310 | 44 | 0 | 215 | 20 | 93 | 133 | 172 | 62 | 19 | 63 | 34 | 8 | 63 | 14 | 305 | 390 | 243 | 27 | 0 | 0 | 10 | 8 | 0 | 80 | 25 | 141 | 0 | 100 | 17 | 57 | 19.29 | 116 | 0 | 1.6 | 39.92 | 0 | 8963.25 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 80 | 602 | 50 | 0 | 0 | 1007.59 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 31.96 | 88 | 0 | 0 | 50.22 | 180 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.89 | 160 | 51 | 101 | 31 | 91 | 0 | 0 | 0 | 6.1 | 170 | 0.63 | 96 | 150 | 105 | 180 | 0 | 940 | 570 | 17 | 6182.39 | 15145.64 | 105.81
15:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 148 | 132 | 163 | 51 | 35 | 126 | 0 | 298 | 0 | 0 | 17 | 310 | 0 | 0 | 21 | 17 | 13 | 20 | 0 | 525 | 94 | 70 | 21 | 0 | 0 | 0 | 26 | 35 | 60 | 73 | 0.63 | 221 | 87 | 7 | 1050 | 144 | 0 | 6 | 8 | 17 | 212 | 0 | 0 | 0 | 1166 | 12 | 51 | 0 | 380 | 347 | 325 | 44 | 0 | 212 | 20 | 96 | 132 | 171 | 63 | 19 | 64 | 38 | 8 | 48 | 14 | 320 | 390 | 243 | 27 | 0 | 0 | 5 | 8 | 0 | 80 | 25 | 142 | 0 | 102 | 17 | 58 | 14.93 | 116 | 0 | 1.5 | 34.5 | 1 | 9256.56 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 40 | 603 | 48 | 0 | 0 | 1012.85 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 39.26 | 71 | 0 | 0 | 43.09 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.83 | 160 | 50 | 100 | 17 | 91 | 0 | 0 | 0 | 4.7 | 134 | 0.49 | 99 | 153 | 113 | 220 | 0 | 986 | 570 | 17 | 6287.22 | 15543.78 | 105.8
16:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17 | 17 | 136 | 132 | 163 | 50 | 35 | 162 | 0 | 296 | 0 | 0 | 35 | 308 | 0 | 0 | 13 | 17 | 13 | 20 | 0 | 490 | 90 | 70 | 25 | 0 | 0 | 0 | 32 | 35 | 60 | 96 | 0 | 222 | 87 | 4 | 1050 | 139 | 0 | 6 | 8 | 17 | 214 | 0 | 0 | 0 | 1162 | 0 | 51 | 0 | 385 | 349 | 320 | 44 | 0 | 212 | 20 | 95 | 132 | 172 | 66 | 19 | 60 | 36 | 8 | 31 | 16 | 310 | 387 | 243 | 27 | 0 | 0 | 4 | 0 | 0 | 81 | 25 | 140 | 0 | 100 | 17 | 58 | 9.37 | 116 | 0 | 0.8 | 20.94 | 11 | 9216.11 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 20 | 603 | 50 | 0 | 0 | 1009.38 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 23.29 | 43 | 0 | 0 | 26.36 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.33 | 160 | 52 | 101 | 15 | 79 | 0 | 0 | 0 | 3.1 | 80 | 0.16 | 110 | 200 | 113 | 220 | 0 | 996 | 570 | 17 | 6202.62 | 15418.73 | 105.78
17:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 17 | 132 | 130 | 163 | 50 | 35 | 162 | 0 | 292 | 0 | 0 | 35 | 292 | 0 | 0 | 6 | 17 | 13 | 20 | 0 | 425 | 96 | 70 | 28 | 0 | 0 | 0 | 48 | 35 | 60 | 98 | 0 | 222 | 88 | 9 | 1050 | 152 | 0 | 3 | 8 | 17 | 216 | 0 | 0 | 0 | 1160 | 1 | 53 | 0 | 390 | 355 | 270 | 44 | 0 | 214 | 20 | 107 | 133 | 171 | 71 | 19 | 76 | 74 | 8 | 9 | 19 | 310 | 395 | 230 | 28 | 0 | 0 | 1 | 8 | 0 | 82 | 25 | 140 | 0 | 100 | 17 | 58 | 3 | 116 | 0 | 0.1 | 6.35 | 12 | 9149.45 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 38 | 8 | 600 | 50 | 0 | 0 | 1006.65 | 0 | 0 | 0 | 113 | 62 | 0 | 0 | 0 | 0 | 8.23 | 7 | 0 | 0 | 5.41 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.64 | 160 | 51 | 103 | 5 | 92 | 0 | 0 | 0 | 1 | 27 | 0.05 | 110 | 200 | 115 | 220 | 0 | 982 | 570 | 17 | 6153.98 | 15303.43 | 105.76
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 140 | 130 | 163 | 47 | 35 | 162 | 0 | 303 | 0 | 0 | 17 | 314 | 0 | 0 | 0 | 17 | 13.5 | 20 | 0 | 510 | 89 | 68 | 40 | 0 | 0 | 0 | 53 | 35 | 90 | 98 | 0 | 221 | 89 | 15 | 1050 | 141 | 0 | 2 | 8 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 380 | 344 | 335 | 44 | 0 | 211 | 20 | 100 | 136 | 173 | 65 | 19 | 86 | 78 | 8 | 0 | 19 | 305 | 388 | 247 | 28 | 20 | 0 | 0 | 8 | 0 | 82 | 28 | 140 | 0 | 100 | 17 | 58 | 0 | 125 | 0 | 0 | 0 | 12 | 9485.5 | 891 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 131 | 0 | 50 | 0 | 597 | 48 | 0 | 0 | 1131.66 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 50 | 105 | 0 | 92 | 0 | 70 | 0 | 0 | 1 | 0 | 110 | 200 | 114 | 220 | 0 | 954 | 570 | 17 | 6335.66 | 15821.16 | 105.74
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 54 | 35 | 149 | 134 | 163 | 53 | 55 | 162 | 0 | 293 | 0 | 0 | 35 | 288 | 0 | 0 | 0 | 17 | 13 | 20 | 0 | 385 | 104 | 68 | 54 | 0 | 0 | 50 | 53 | 35 | 88 | 98 | 0 | 221 | 94 | 13 | 1050 | 142 | 0 | 12 | 13 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 85 | 0 | 393 | 354 | 275 | 44 | 0 | 185 | 20 | 115 | 135 | 172 | 73 | 19 | 86 | 78 | 8 | 0 | 20 | 315 | 398 | 252 | 28 | 30 | 0 | 0 | 8 | 0 | 84 | 30 | 140 | 0 | 100 | 17 | 87 | 0 | 161 | 0 | 0 | 0 | 12 | 9609 | 796 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 155 | 0 | 50 | 0 | 594 | 45 | 0 | 0 | 1399.77 | 0 | 0 | 0 | 113 | 113 | 0 | 70 | 27 | 0 | 0 | 0 | 20 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 160 | 0 | 115 | 0 | 104 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 180 | 0 | 1100 | 570 | 17 | 6765.77 | 16374.77 | 105.74
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 35 | 149 | 137 | 163 | 55 | 55 | 162 | 0 | 303 | 0 | 0 | 35 | 304 | 0 | 0 | 0 | 17 | 13 | 0 | 0 | 460 | 107 | 68 | 56 | 0 | 0 | 50 | 53 | 35 | 88 | 98 | 0 | 220 | 94 | 20 | 1050 | 142 | 0 | 12 | 25.5 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 390 | 354 | 310 | 44 | 0 | 192 | 20 | 115 | 135 | 171 | 73 | 19 | 86 | 80 | 25 | 0 | 20 | 320 | 392 | 268 | 28 | 30 | 0 | 0 | 8 | 0 | 86 | 30 | 140 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9855.5 | 797 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 155 | 0 | 50 | 0 | 586 | 45 | 0 | 0 | 1424.41 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 35 | 0 | 0 | 0 | 20 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 159 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 114 | 180 | 0 | 1100 | 570 | 17 | 6548.41 | 16403.91
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 35 | 149 | 135 | 163 | 55 | 55 | 162 | 0 | 288 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 17 | 13 | 20 | 0 | 395 | 109 | 68 | 56 | 0 | 0 | 50 | 53 | 54.36 | 88 | 88 | 0 | 219 | 93 | 23 | 1050 | 142 | 0 | 12 | 25.5 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 393 | 354 | 285 | 44 | 0 | 189 | 20 | 115 | 135 | 173 | 74 | 19 | 86 | 82 | 52.2 | 0 | 20 | 315 | 395 | 268 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 30 | 141 | 0 | 100 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9795.06 | 796 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 155 | 0 | 50 | 0 | 585 | 51 | 0 | 0 | 1426.55 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 34 | 0 | 0 | 0 | 20 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 220 | 0 | 1100 | 570 | 17 | 6552.55 | 16347.61 | 105.73
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 54 | 35 | 149 | 135 | 163 | 55 | 55 | 162 | 0 | 300 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 13 | 20 | 0 | 410 | 107 | 68 | 56 | 0 | 3 | 50 | 52 | 54.36 | 100 | 88 | 0 | 219 | 92 | 30 | 1050 | 142 | 0 | 12 | 25.5 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 393 | 354 | 300 | 44 | 0 | 198 | 20 | 108 | 135 | 171 | 74 | 19 | 86 | 80 | 52.2 | 0 | 20 | 305 | 395 | 308 | 29 | 30 | 0 | 0 | 0 | 0 | 86 | 30 | 141 | 0 | 100 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9863.06 | 804 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 160 | 0 | 50 | 0 | 588 | 51 | 0 | 0 | 1414.15 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 33 | 0 | 0 | 0 | 20 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 0 | 90 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 220 | 0 | 1100 | 570 | 17 | 6728.15 | 16591.21 | 105.73
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 54 | 35 | 149 | 137 | 163 | 55 | 55 | 162 | 0 | 292 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 13 | 20 | 0 | 475 | 109 | 52 | 56 | 0 | 0 | 50 | 52 | 54.36 | 100 | 98 | 0 | 219 | 97 | 34 | 1050 | 17 | 0 | 12 | 17 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 393 | 353 | 305 | 44 | 0 | 197 | 20 | 108 | 138 | 172 | 74 | 19 | 86 | 78 | 52.2 | 0 | 20 | 302 | 393 | 333 | 29 | 30 | 0 | 0 | 10 | 0 | 86 | 30 | 141 | 0 | 100 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9855.56 | 804 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 220 | 0 | 50 | 0 | 600 | 51 | 0 | 0 | 1419.22 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 33 | 0 | 0 | 0 | 20 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 160 | 0 | 95 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 220 | 0 | 1100 | 570 | 17 | 6818.22 | 16673.78 | 105.72
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 54 | 35 | 91 | 137 | 163 | 55 | 55 | 162 | 0 | 290 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 13 | 20 | 0 | 470 | 106 | 52 | 53 | 0 | 5 | 50 | 52 | 54.36 | 100 | 88 | 0 | 220 | 110 | 35 | 1050 | 17 | 0 | 12 | 8 | 17 | 220 | 0 | 0 | 0 | 1224 | 0 | 46 | 26 | 350 | 355 | 270 | 44 | 0 | 202 | 20 | 84 | 136 | 172 | 73 | 19 | 86 | 74 | 52.2 | 0 | 21 | 296 | 397 | 347 | 28 | 30 | 0 | 0 | 13 | 0 | 86 | 25 | 139 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9620.56 | 805 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 235 | 0 | 50 | 0 | 603 | 51 | 0 | 0 | 1419.51 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 33 | 0 | 0 | 0 | 20 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 95 | 0 | 104 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 200 | 115 | 220 | 0 | 1100 | 570 | 17 | 6999.51 | 16620.07 | 105.72
Total KWH | 0 | 1234560 | 484800 | 0 | 0 | 0 | 0 | 0 | 8913600 | 0 | 0 | 825480 | 607680 | 2392848 | 2253920 | 3717720 | 1002204 | 859700 | 2563200 | 0 | 7101731 | 0 | 0 | 516545 | 7266958 | 0 | 0 | 211804 | 433200 | 337800 | 487440 | 0 | 10864090.91 | 1719982 | 1231964 | 597120 | 0 | 62880 | 358936 | 682860 | 594291 | 1213440 | 1886400 | 22223 | 5350596 | 1222763 | 493440 | 25185454.55 | 1798182 | 0 | 269760 | 232155 | 387236 | 5059876 | 0 | 0 | 0 | 28118179 | 18090 | 1271272 | 1271273 | 7664000 | 8822700 | 6990000 | 1033744 | 0 | 5006000 | 281232 | 1816320 | 3307915 | 3048960 | 1178520 | 441730 | 1217520 | 1184640 | 316704 | 539873 | 316752 | 7215000 | 9437100 | 7307000 | 676000 | 579240 | 0 | 83857 | 249696 | 0 | 2008320 | 655104 | 3189000 | 0 | 2409320 | 429120 | 1552800 | 157219 | 2661600 | 0 | 14650 | 363190 | 214320 | 213492799.46 | 20696000 | 0 | 0 | 286080 | 0 | 0 | 0 | 0 | 3977913 | 0 | 738720 | 588240 | 14407272 | 806880 | 0 | 0 | 26913769 | 0 | 0 | 0 | 1452960 | 1294464 | 0 | 512800 | 159166 | 0 | 367088 | 600367 | 180588 | 0 | 448496 | 4200636 | 0 | 0 | 0 | 0 | 0 | 9536218 | 0 | 38040 | 3905000 | 903272 | 1705816 | 254754 | 1226112 | 0 | 486045 | 0 | 50538.24 | 1453680 | 4342 | 1798272 | 4669000 | 2745000 | 5221960 | 0 | 24370909 | 13812363.64 | 367200 | 150179960.88 | 363672760.34

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14436.73 | MW | 12:00 Hr. | Energy Generated |  |  | 363.6728 |  | MKWHr.
| Day Peak Demand |  |  | 14776.73 | MW | 12:00 Hr. | Energy Unserverd |  |  | 13.208 |  | MKWHr.
| Evening Peak Generation |  |  | 16591.21 | MW | 21:00 Hr. | Energy Demand |  |  | 376.8808 |  | MKWHr.
| Evening Peak Demand |  |  | 18277.21 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13405.37 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 925.51 |  | MMCFD
| Maximum Generation of the Day |  |  | 16673.78 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.9663 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.9716 | 0 | 16.8919 | 0 | 0 | 0.2118 | 0 | 0 | 52.0753 | Gas | 130.7731 | Gas | 456300463.7147
| Chattogram Zone |  |  | 5.5533 | 53.3036 | 12.1951 | 0 | 5.3506 | 0.040313 | 0 | 0.06288 | 76.5058 | Coal | 115.3715 | Coal | 824962339.0223
| Cumilla Zone |  |  | 34.8186 | 0 | 9.166 | 0 | 0 | 0.53987 | 1.1846 | 0 | 45.7092 | HFO | 53.6399 | HFO | 1125934131.27
| Mymensingh Zone |  |  | 0 | 0 | 4.8578 | 0 | 0 | 0.53506 | 0 | 0 | 5.3929 | HSD | 4.464 | HSD | 95362912.2
| Sylhet Zone |  |  | 33.7258 | 0 | 0 | 0 | 0 | 0.083857 | 0 | 0 | 33.8096 | Hydro | 5.3506 | Hydro | 535059.6
| Khulna Zone |  |  | 0 | 14.4073 | 1.8317 | 3.9779 | 0 | 0.58824 | 20.696 | 0 | 41.5011 | Solar | 5.2165 | Solar | 84018778.0868
| Barishal Zone |  |  | 7.967 | 42.8523 | 2.1655 | 0 | 0 | 0.004342 | 0 | 0 | 52.989 | Import | 48.7944 | Import | 309090429.61
| Rajshahi Zone |  |  | 13.7369 | 0 | 3.6 | 0 | 0 | 1.454 | 26.9138 | 0 | 45.7046 | Wind | 0.06288 | Wind | 933139.2
| Rangpur Zone |  |  | 0 | 4.8083 | 2.9319 | 0.48605 | 0 | 1.759 | 0 | 0 | 9.9852
| Total |  |  | 130.7731 | 115.3715 | 53.6399 | 4.464 | 5.3506 | 5.2165 | 48.7944 | 0.06288 | 363.6728
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 456300463.7147 |  | Hydro | 535059.6
|  |  |  | Coal | 824962339.0223 |  | Solar | 84018778.0868
|  |  |  | HFO | 1125934131.27 |  | Import | 309090429.61
|  |  |  | HSD | 95362912.2 |  | Wind | 933139.2
[5 empty] | Total: | 289,71,37,252 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.696 | Peak Hr Flow | 804.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34379036.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.9138 | Peak Hr Flow | 1414.15 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1400 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.1846 | Peak Hr Flow | 80.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2102 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.7944 | Peak Hr Flow | 2298.15 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 87 |  | 6216
|  |  |  | Chattogram |  | 0 |  | 1540
|  |  |  | Cumilla |  | 182 |  | 1756
|  |  |  | Mymensingh |  | 493 |  | 1580
|  |  |  | Sylhet |  | 150 |  | 768
|  |  |  | Khulna |  | 343 |  | 2160
|  |  |  | Barishal |  | 15 |  | 591
|  |  |  | Rajshahi |  | 273 |  | 1879
|  |  |  | Rangpur |  | 70 |  | 1153
|  |  |  | Total |  | 1613 |  | 17643
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Kanchan Purbachal Power Generation Ltd. |  |  | 55
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Fenchugonj CCPP Phase-2 ST |  |  | 35
[7 empty] | 4 | Karnaphuli Hydro PP Unit-1 |  |  | 40
[7 empty] | 5 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 6 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[5 empty] | Total | 300 |  |  |  | Total | 278.5
|  |  |  | Total Unavailable Capacity |  |  |  | 578.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 | 16:31 | Monakasha-Rahanpur 400kV Ckt-2 Project Work S/D from Rahanpur 400/132kV end.
| 08:31 | 12:03 | Madaripur 132/33kV S/S T3-426T HT Scheduled S/D Due to For working in the section 3 | [7 empty] | 25.0MW load
interrup.
| 08:31 | 12:03 | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D Due to For working in the section 3 | [7 empty] | 25.0MW load
interrup.
| 08:48 | 09:18 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micom relays Due to Jumper out of 33 kv | [7 empty] | 81.0MW load
|  |  | boroibari feeder | [7 empty] | interrup.
| 08:48 | 09:18 | Kabirpur 132/33kV S/S XFR, T-2 LT Tripped showing Micom relays Due to Jumper out of 33 kV | [7 empty] | 81.0MW load
|  |  | boroibari feeder | [7 empty] | interrup.
|  | 09:05 | Ramganj 132/33kV S/S Transformer-01 HT is restored.
|  | 09:06 | Ramganj 132/33kV S/S Transformer-01 LT is restored.
| 09:15 | 18:09 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ruppur 132/11kV end.
| 09:17 | 18:07 | Ishwardi-Rooppur 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to DS
maintenance at Ruppur substation
|  | 09:21 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 09:23 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 10:05 | 17:28 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Disc clean and from Bibiana 400/230kV end Due to Kaliakoir side disk clean
|  | 10:47 | Bajitpur 132/33kV S/S 132 kV Bus-1 is restored.
| 11:08 |  | TR-2 S/D at Monirampur S/S Due to Project Work.
|  | 11:10 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
|  | 12:25 | Coxsbazar 132/33kV S/S T3 HT is restored.
| 16:32 |  | Barapukuria TPP Unit-1 Tripped
| 16:51 | 17:38 | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to City
Corporation garbage cleaning work with excavator near the transmission line.
| 18:32 |  | Barapukuria TPP Unit-1 Tripped
| 18:57 | 20:50 | Patiya 132/33kV S/S TRAFO-02 LT Forced S/D Due to Pbs Load side Redhot | [7 empty] | 15.0MW load
interrup.
| 19:16 |  | At Manirampur SS,(132/33)KV T-2 Transformer is Charged.
| 19:28 | 20:06 | Saidpur - Taraganj 132kV Ckt-1 Tripped from Taraganj 132/33kV end showing F21 (MiCOM P40
Agile) relays Due to None
| 19:28 | 20:06 | Saidpur - Taraganj 132kV Ckt-2 Tripped from Taraganj 132/33kV end showing F21 (MiCOM P40
Agile) relays Due to None
| 19:28 |  | Saidpur 132/33kV S/S TR-01 HT Tripped showing Over current realy. relays Due to 20 MW | [7 empty] | 108.0MW load
|  |  | GTPS 132kv CT (R Phase) blast. At the same time grid power off. | [7 empty] | interrup.
| 19:28 |  | Saidpur 132/33kV S/S TR-01 LT Tripped showing Same relays Due to Same | [7 empty] | 108.0MW load
interrup.
| 19:28 | 20:15 | Purbasadipur-Saidpur 132kV Ckt-2 Tripped from Purbasadipur 230/132/33kV end showing
Distance Relay relays Due to None
| 19:28 | 20:10 | Barapukuria-Saidpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing | [7 empty] | 50.0MW load
|  |  | REL-511 relays Due to None | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 19:28 | 20:11 | Barapukuria-Saidpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing | [7 empty] | 50.0MW load
|  |  | REL=511 relays Due to None | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 19:28 | 20:14 | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Purbasadipur 230/132/33kV end showing
Distance Relay relays.
|  | 19:30 | Nabinagar 132/33kV S/S T-2 HT is restored.
| 20:04 | 20:07 | Saidpur - Taraganj 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing No relays Due to | [7 empty] | 108.0MW load
|  |  | Commander by NLDC SDE | [7 empty] | interrup. Saidpur
132/33kV end
| 20:04 | 20:19 | Purbasadipur-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing No relays Due | [7 empty] | 108.0MW load
|  |  | to Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:04 | 20:11 | Barapukuria-Saidpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing No relays Due | [7 empty] | 108.0MW load
|  |  | to Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:04 | 20:10 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing No relays Due | [7 empty] | 108.0MW load
|  |  | to Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:04 | 20:08 | Saidpur - Taraganj 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing No relays Due to | [7 empty] | 108.0MW load
|  |  | Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:05 | 20:20 | Jaldhaka-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing No relays Due to | [7 empty] | 108.0MW load
|  |  | Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:05 | 20:20 | Jaldhaka-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing No relays Due to | [7 empty] | 108.0MW load
|  |  | Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:05 | 20:35 | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing No relays Due | [7 empty] | 108.0MW load
|  |  | to Commander by NLDC SDE. | [7 empty] | interrup. Saidpur
132/33kV end
| 20:08 | 22:05 | Hasnabad 230/132kV S/S AUTO TR-2 HT Forced S/D Due to Red hot at HT bushing connector. of
y-ph
| 20:08 | 22:05 | Hasnabad 230/132kV S/S AUTO TR-2 LT Forced S/D Due to Red hot at HT bushing y-ph
|  | 20:10 | Nabinagar 132/33kV S/S T-2 LT is restored.
|  | 22:51 | Maniknagar 132/33kV S/S Transformer GT-1 HT is restored.
| 02:54 | 04:23 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Ins o/c,Definite O/C relays Due to | [7 empty] | 32.0MW load
|  |  | Wzpdco 33 kv Chadmari feeder Fault | [7 empty] | interrup.
| 02:54 | 03:45 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Ins o/c,Definite o/c relays Due to | [7 empty] | 53.0MW load
|  |  | Wzpdco Chadmari 33 kv Feeder Fault. | [7 empty] | interrup.
| 03:53 |  | Barapukuria TPP Unit-1 Synchronized
| 04:21 |  | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Distance relay relays Due | [7 empty] | 45.0MW load
|  |  | to Heavy Storm | [7 empty] | interrup.
| 04:45 | 05:31 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing MVAJ relays Due to O/C e 33 kv side trip | [7 empty] | 50.0MW load
interrup.
| 05:07 | 05:59 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent Relay relays Due to Due to
Nikra and Kushumhati feeder fault.
| 05:38 | 06:15 | Ullon grid s/s (DPDC) GT-1 and GT-2 transformers tripped showing REF and differential | [7 empty] | 20MW load interrup.
relay in GT-1 caused by cable fault.
| 07:00 |  | Minimum generation is 11982 MW.
| 07:07 |  | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance
relay relays Due to Control panel signals Main prot trip & Zone-1 fault and from
Sonargaon 132/33kV end showing Line distance, z1 7.7 km relays Due to Bad weather
| 07:07 | 07:50 | Haripur-Sonargaon 132kV Ckt-1 Tripped from Sonargaon 132/33kV end showing line
distance, z1 8 km relays Due to Bad weather and from Haripur 230/132kV end showing
Distance Z1, BCN relays Due to Raining
| 07:48 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8913600 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7101731 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1002204 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7266958 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 825480 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 135 | 2253920 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 859700 | Fuel Shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 516545 | Fuel Shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 337800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 487440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 484800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 163 | 3717720 | Fuel Shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2392848 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1234560 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2563200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 211804 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 607680 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 410 | 10864090.91 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 433200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6221.494 | 2346 | 52075280.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 232155 | Fuel Shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 18090 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 269760 | Fuel Shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5350596 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5059876 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 387236 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 682860 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 358936 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1213440 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 493440 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 56 | 597120 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22223 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 68 | 1231964 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 594291 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1222763 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1886400 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1719982 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 142 | 1798182 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28118179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 62880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1050 | 25185454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3608.86 | 76505827.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 198 | 5006000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 354 | 8822700 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 6990000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7664000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 281232 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 1271273 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1033744 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1271272 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 20 | 316752 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3307915 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 171 | 3048960 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1184640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 316704 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 441730 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 1217520 | Fuel Shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 1178520 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 108 | 1816320 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 539873 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2204.2 | 45709155
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 157219 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2661600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1552800 | Plant availability less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 363190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 214320 | Fuel Shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 280 | 5392899
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 83857 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 676000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 579240 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3189000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 655104 | ps availability is less
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2008320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2409320 | ps availability is less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 249696 | Line Shut Down
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7215000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 308 | 7307000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 395 | 9437100 | -
Sylhet Area Total |  |  |  |  | 2325 | 1424 | 33809637
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 804 | 20696000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 286080 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | Fuel Shortage
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | plant availability zero
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 806880 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 738720 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 588240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 160 | 3977913 | Machine Problem
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 588 | 14407272 | U-2 Under maint.
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1677 | 41501105
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24370909 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1798272 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2745000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 13812363.64 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5221960 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 367200 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4669000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4342 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2332 | 52989046.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 367088 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 159166 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 169 | 4200636 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9536218 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 180588 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 512800 | Fuel Shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1294464 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1452960 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 38040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1414.15 | 26913769 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 448496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 600367 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2376.15 | 45704592
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 486045 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 903272 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3905000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 94 | 1226112 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50538.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 1705816 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 254754 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1453680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 343 | 9985217.24
Eastern Grid Total |  |  |  |  | 16977.666 | 9863.06 | 213492799.46
Western Grid Total |  |  |  |  | 11731.125 | 6728.15 | 150179960.88
National Grid Total |  |  |  |  | 28708.791 | 16591.21 | 363672760.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10947.81 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5082.6 | MW
i) Dhaka area |  |  | 6129.21 |  | MW | i) Khulna area |  |  |  | 1817 | MW
ii) Chattogram area |  |  | 1539.6 |  | MW | ii) Barishal area |  |  |  | 576.2 | MW
iii) Cumilla area |  |  | 1574 |  | MW | iii) Rajshahi area |  |  |  | 1606.4 | MW
iv) Mymensingh area |  |  | 1087 |  | MW | iv) Rangpur area |  |  |  | 1083 | MW
v) Sylhet area |  |  | 618 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16030.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 72 | Ishurdi | 85 | 15:00 | 143 | Palashbari | 146 | 23:00
2 | AKSML | 123 | 04:00 | 73 | Jaldhaka | 106 | 21:00 | 144 | Panchagarh | 70 | 19:00
3 | Aftabnagar | 50 | 23:00 | 74 | Jamalpur | 155 | 22:00 | 145 | Patiya | 30.6 | 21:00
4 | Agargaon | 137 | 13:00 | 75 | Jashore | 172 | 19:00 | 146 | Patnitala | 34 | 00:00
5 | Agrabad | 74 | 13:00 | 76 | Jhenaidah | 104 | 22:00 | 147 | Patuakhali | 77.4 | 22:00
6 | Amnura | 34 | 13:00 | 77 | Joydebpur | 183 | 19:00 | 148 | Payra | 42 | 22:00
7 | Araihazar | 138 | 00:00 | 78 | Joypurhat | 66 | 20:00 | 149 | Postogola | 67 | 23:00
8 | Ashuganj | 97 | 23:00 | 79 | Juldah | 18 | 14:00 | 150 | Pubail | 52 | 18:30
9 | BSRM | 187 | 16:00 | 80 | KSRM | 26 | 00:00 | 151 | Purbachal | 36 | 18:30
10 | Bagerhat | 93 | 00:00 | 81 | Kabirpur | 280 | 18:00 | 152 | Purbasadipur | 132 | 18:30
11 | Bajitpur | 108 | 00:00 | 82 | Kachua | 106 | 00:00 | 153 | Rahanpur | 46 | 22:00
12 | Bakerganj | 16.2 | 21:00 | 83 | Kaliganj | 40 | 00:00 | 154 | Rahim | 30 | 14:00
13 | Bakulia | 104 | 18:00 | 84 | Kallyanpur | 129 | 22:00 | 155 | Rajbari | 87 | 00:00
14 | Banani | 62 | 13:00 | 85 | Kalurghat | 40 | 16:00 | 156 | Rajendrapur | 119 | 11:00
15 | Bangabhaban | 7 | 11:00 | 86 | Kamrangirchar | 86 | 13:00 | 157 | Rajshahi | 110 | 00:00
16 | Barapukuria | 58 | 20:00 | 87 | Kaptai | N/A | N/A | 158 | Rajshahi-230 | 107 | 18:30
17 | Barguna | 32 | 22:00 | 88 | Kasba | 40 | 22:00 | 159 | Ramganj | 122 | 01:00
18 | Barishal | 115 | 20:00 | 89 | Kazla | 131 | 12:00 | 160 | Rampur | 48 | 00:00
19 | Barishal-230 | 122 | 19:30 | 90 | Keranigonj | 97 | 12:00 | 161 | Rangamati | 19 | 11:00
20 | Baroaulia | 41 | 12:00 | 91 | Khagrachori | 32 | 16:00 | 162 | Rangpur | 152 | 18:30
21 | Baroirhat | 69 | 19:30 | 92 | Khulna | 61 | 17:00 | 163 | Ruppur | 2.8 | 09:00
22 | Bashundhara | 224 | 19:00 | 93 | Khulshi | 192 | 19:00 | 164 | SSM | 0 | 00:00
23 | BashundharaCement | 0 | 00:00 | 94 | Kishoreganj | 145 | 00:00 | 165 | Saidpur | 115 | 21:00
24 | Beanibazar | 82 | 00:00 | 95 | Kodda | 308 | 20:00 | 166 | Santhia | 36 | 18:00
25 | Benapole | 76 | 18:30 | 96 | Kulaura | 61 | 18:00 | 167 | Satkhira | 136 | 23:00
26 | Bhaluka | 120 | 15:00 | 97 | Kurigram | 75 | 23:00 | 168 | Satmasjid | 113 | 18:30
27 | Bhandaria | 66 | 21:00 | 98 | Kushtia | 148 | 14:00 | 169 | Savar | 232 | 18:00
28 | Bhangura | 40 | 00:00 | 99 | Laksam | 38 | 00:00 | 170 | SevenRings | 16.49 | 15:00
29 | Bheramara(GK) | 62 | 00:00 | 100 | Lakshmipur | 56 | 18:30 | 171 | ShahCement | 21 | 09:00
30 | Bhulta | 217 | 23:00 | 101 | Lalbag | 82 | 13:00 | 172 | Shahjadpur | 79 | 19:30
31 | Bog-Sherpur | 72 | 00:00 | 102 | Lalmonirhat | 58 | 00:00 | 173 | Shahjibazar | 153 | 18:30
32 | Bogura | 210 | 22:00 | 103 | MI_Cement | 11.6 | 18:30 | 174 | Shahmirpur | 66 | 18:30
33 | Borhanuddin | 88 | 21:00 | 104 | Madanganj | 46 | 23:00 | 175 | Shariatpur | 110 | 00:00
34 | Brahmanbaria | 152 | 00:00 | 105 | Madaripur | 119 | 00:00 | 176 | Sherpur | 162 | 19:30
35 | Cantonment | 142 | 13:00 | 106 | Madartek | 102 | 23:00 | 177 | Shikalbaha | 26 | 23:00
36 | Chandina | 37 | 00:00 | 107 | Madunaghat | 59 | 19:00 | 178 | Shitalakhya | 85.3 | 13:00
37 | Chandpur | 96 | 00:00 | 108 | Magura | 69 | 00:00 | 179 | Sholosohor | 52 | 15:00
38 | Chandraghona | 38 | 18:00 | 109 | Mahasthangarh | 88 | 00:00 | 180 | Shomvuganj | 50 | 00:00
39 | Chapai | 77 | 23:00 | 110 | Maijdee | 44 | 00:00 | 181 | Shyampur | 172 | 15:00
40 | Charfasson | 39 | 22:00 | 111 | Manikganj | 156 | 20:00 | 182 | Siddhirganj | 138 | 13:00
41 | Charsaidpur | 41 | 01:00 | 112 | Maniknagar | 55 | 22:00 | 183 | Sirajganj | 130 | 20:00
42 | Chauddagram | 81 | 00:00 | 113 | Matarbari | 58 | 07:00 | 184 | Sitakunda | 38 | 18:30
43 | Chhatak | 41 | 18:00 | 114 | Matuail | 80 | 15:00 | 185 | Sonargaon | 136 | 19:30
44 | Chowmuhani | 172 | 19:30 | 115 | Metrorail_Motijheel | 20 | 10:00 | 186 | Sreemongol | 95 | 18:00
45 | Chuadanga | 111 | 20:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 187 | Sreepur | 116 | 08:00
46 | Coxsbazar | 154 | 21:00 | 117 | Millgate | 108 | 15:00 | 188 | Srinagar | 56.3 | 22:00
47 | Cumilla(N) | 173 | 21:00 | 118 | Mirpur | 169 | 18:30 | 189 | Sunamganj | 56 | 00:00
48 | Cumilla(S) | 175 | 13:00 | 119 | Mirsorai | 35 | 23:00 | 190 | Sylhet | 147 | 18:00
49 | Daganbhuiyan | 39 | 00:00 | 120 | Mirzapur | 47 | 13:00 | 191 | Sylhet_(South) | 65 | 20:00
50 | Daudkandi | 139 | 00:00 | 121 | Mithapukur | 80 | 22:00 | 192 | TK | 0 | 00:00
51 | DhakaUniversity | 98 | 13:00 | 122 | Modern | N/A | N/A | 193 | Tangail | 194 | 22:00
52 | Dhamrai | 108 | 18:00 | 123 | Mogbazar | 69.9 | 15:00 | 194 | Taraganj | 33 | 18:00
53 | Dhanmondi | 115 | 13:00 | 124 | Mongla | 42 | 18:30 | 195 | Tasnim | 42 | 16:00
54 | Dohazari | 121 | 00:00 | 125 | Motijheel | 53 | 13:00 | 196 | Thakurgaon | 127 | 19:00
55 | Faridpur | 192 | 22:00 | 126 | Muktagacha | 43 | 00:00 | 197 | Tongi | 166 | 15:00
56 | Fatullah | 109 | 11:00 | 127 | Munshiganj | 124 | 20:00 | 198 | Ullahpara | 40 | 00:00
57 | Fenchuganj | 50 | 18:00 | 128 | Muradnagar | 58 | 00:00 | 199 | Ullon | 66 | 23:00
58 | Feni | 115 | 22:00 | 129 | Mymensingh | 140 | 18:30 | 200 | Uttara | 108 | 18:30
59 | GPH | 2 | 09:00 | 130 | Nabinagar | 112 | 22:00 | 201 | UttaraNew | 65 | 23:00
60 | Ghatail | 90 | 00:00 | 131 | Naogaon | 127 | 23:00 | 202 | Zigatola | 102 | 13:00
61 | Ghorashal | 0 | 00:00 | 132 | Narail | 64 | 00:00
62 | Ghorashal-230 | 101 | 21:00 | 133 | Narinda | 79 | 13:00
63 | Goalpara | 42 | 00:00 | 134 | Narshingdi | 209 | 19:30
64 | Gollamari | 112 | 00:00 | 135 | Natore | 159 | 00:00
65 | Gopalganj | 116 | 00:00 | 136 | Nawabganj | 69.8 | 22:00
66 | Gulshan | 112 | 13:00 | 137 | Netrakona | 96 | 00:00
67 | Halishahar | 105 | 14:00 | 138 | New | 88 | 15:00
68 | HaripurSBU | 131 | 23:00 | 139 | Niamatpur | 74 | 22:00
69 | Hasnabad | 99 | 20:00 | 140 | Noapara | 44 | 13:00
70 | Hathazari | 102 | 21:00 | 141 | PHP | 13 | 19:00
71 | Hatirjheel | 76 | 13:00 | 142 | Pabna | 110 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16316.34 | 386 |  | 16719.71
1:00 | 15781.05 | 348 |  | 16145.05
2:00 | 15274.49 | 355 |  | 15645.49
3:00 | 14822.24 | 335 |  | 15172.24
4:00 | 14324.27 | 317 |  | 14655.27
5:00 | 14018.41 | 284 |  | 14315.41
6:00 | 13707.65 | 262 |  | 13981.65
7:00 | 13701.83 | 358 |  | 14075.83
8:00 | 13523.75 | 372 |  | 13912.75
9:00 | 13405.37 | 322 |  | 13741.37
10:00 | 13715.4 | 215 |  | 13940.4
11:00 | 13905.89 | 335 |  | 14255.89
12:00 | 14436.73 | 325 |  | 14776.73
13:00 | 15044.32 | 273 |  | 15329.32
14:00 | 15145.64 | 274 |  | 15431.64
15:00 | 15543.78 | 304 |  | 15861.78
16:00 | 15418.73 | 278 |  | 15709.73
17:00 | 15303.43 | 270 |  | 15585.43
18:00 | 15821.16 | 549 |  | 16395.16
19:00 | 16374.77 | 1402 |  | 17839.77
19:30 | 16403.91 | 1312 |  | 17774.91
20:00 | 16347.61 | 1289 |  | 17694.61
21:00 | 16591.21 | 1613 |  | 18277.21
22:00 | 16673.78 | 1227 |  | 17955.78
23:00 | 16620.07 | 1515 |  | 18203.07
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9578.5 | 6737.84 | 16316.34 | DAILY GENERATION CURVE
00:30 | 9479.5 | 6569.195 | 16048.695
01:00 | 9380.5 | 6400.55 | 15781.05 | 19-09-2026
01:30 | 9219 | 6308.77 | 15527.77
02:00 | 9057.5 | 6216.99 | 15274.49
02:30 | 8953 | 6095.365 | 15048.365
03:00 | 8848.5 | 5973.74 | 14822.24
03:30 | 8659.75 | 5913.505 | 14573.255
04:00 | 8471 | 5853.27 | 14324.27
04:30 | 8370 | 5801.34 | 14171.34
05:00 | 8269 | 5749.41 | 14018.41
05:30 | 8141.865 | 5721.165 | 13863.03
06:00 | 8014.73 | 5692.92 | 13707.65
06:30 | 8000.615 | 5704.125 | 13704.74
07:00 | 7986.5 | 5715.33 | 13701.83
07:30 | 7809.105 | 5803.685 | 13612.79
08:00 | 7631.71 | 5892.04 | 13523.75
08:30 | 7568.73 | 5895.83 | 13464.56
09:00 | 7505.75 | 5899.62 | 13405.37
09:30 | 7595.05 | 5965.335 | 13560.385
10:00 | 7684.35 | 6031.05 | 13715.4
10:30 | 7750.665 | 6059.98 | 13810.645
11:00 | 7816.98 | 6088.91 | 13905.89
11:30 | 8032.805 | 6138.505 | 14171.31
12:00 | 8248.63 | 6188.1 | 14436.73
12:30 | 8478.79 | 6261.735 | 14740.525
13:00 | 8708.95 | 6335.37 | 15044.32
13:30 | 8836.1 | 6258.88 | 15094.98
14:00 | 8963.25 | 6182.39 | 15145.64
14:30 | 9109.905 | 6234.805 | 15344.71
15:00 | 9256.56 | 6287.22 | 15543.78
15:30 | 9236.335 | 6244.92 | 15481.255
16:00 | 9216.11 | 6202.62 | 15418.73
16:30 | 9182.78 | 6178.3 | 15361.08
17:00 | 9149.45 | 6153.98 | 15303.43
17:30 | 9317.475 | 6244.82 | 15562.295
18:00 | 9485.5 | 6335.66 | 15821.16
18:30 | 9547.25 | 6550.715 | 16097.965
19:00 | 9609 | 6765.77 | 16374.77
19:30 | 9855.5 | 6548.41 | 16403.91
20:00 | 9795.06 | 6552.55 | 16347.61
20:30 | 9829.06 | 6640.35 | 16469.41 |  | Executive Engineer
21:00 | 9863.06 | 6728.15 | 16591.21 |  | Network Operation Division
21:30 | 9859.31 | 6773.185 | 16632.495
22:00 | 9855.56 | 6818.22 | 16673.78
22:30 | 9738.06 | 6908.865 | 16646.925
23:00 | 9620.56 | 6999.51 | 16620.07

## En-Curve
QF-LDC-12
Date | 19-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3803 | 1542 | 900 | 0 | 42 | 1393.84 | 221 | 4809 | 0 | 535 | 2813.5 | 257 | 0 | 0 | 386 | DAILY ENERGY CURVE
00:30 | 3829 | 1602 | 899.5 | 0 | 42 | 1242.695 | 221.5 | 4832 | 0 | 520.5 | 2606.5 | 253 | 0 | 0 | 367 | 19-09-2026
01:00 | 3855 | 1662 | 899 | 0 | 42 | 1091.55 | 222 | 4855 | 0 | 506 | 2399.5 | 249 | 0 | 0 | 348
01:30 | 3832 | 1589 | 871.5 | 0 | 41 | 1046.27 | 222 | 4811 | 0 | 510 | 2355 | 250 | 0 | 0 | 351.5 | Energy Generated | 363.6728 |  | MKWHr
02:00 | 3809 | 1516 | 844 | 0 | 40 | 1000.99 | 222 | 4767 | 0 | 514 | 2310.5 | 251 | 0 | 0 | 355 | Energy not Served | 13.208 |  | MKWHr
02:30 | 3827 | 1529 | 844 | 0 | 40 | 1007.365 | 222 | 4783 | 0 | 430 | 2122 | 244 | 0 | 0 | 345 | Total Energy Requirement | 376.8808 |  | MKWHr
03:00 | 3845 | 1542 | 844 | 0 | 40 | 1013.74 | 222 | 4799 | 0 | 346 | 1933.5 | 237 | 0 | 0 | 335
03:30 | 3840 | 1541 | 844 | 0 | 39 | 1016.005 | 222 | 4796.5 | 0 | 309 | 1744.25 | 221.5 | 0 | 0 | 326
04:00 | 3835 | 1540 | 844 | 0 | 38 | 1018.27 | 222 | 4794 | 0 | 272 | 1555 | 206 | 0 | 0 | 317
04:30 | 3842 | 1547.5 | 843.5 | 0 | 38 | 1014.34 | 221.5 | 4792.5 | 0 | 239.5 | 1424 | 206 | 0 | 2.5 | 300.5
05:00 | 3849 | 1555 | 843 | 0 | 38 | 1010.41 | 221 | 4791 | 0 | 207 | 1293 | 206 | 0 | 5 | 284
05:30 | 3845.5 | 1534 | 820 | 0 | 37 | 1008.085 | 220.5 | 4788 | 3.945 | 198 | 1199.5 | 206 | 0 | 2.5 | 273
06:00 | 3842 | 1513 | 797 | 0 | 36 | 1005.76 | 220 | 4785 | 7.89 | 189 | 1106 | 206 | 0 | 0 | 262
06:30 | 3864 | 1581 | 797 | 0 | 34 | 1009.615 | 219.5 | 4789 | 69.125 | 179.5 | 956.5 | 204 | 0 | 1.5 | 310
07:00 | 3886 | 1649 | 797 | 0 | 32 | 1013.47 | 219 | 4793 | 130.36 | 170 | 807 | 202 | 0 | 3 | 358
07:30 | 3857.5 | 1597.5 | 844 | 0 | 32 | 1012.93 | 218.5 | 4792 | 231.86 | 140 | 683 | 202 | 0 | 1.5 | 365
08:00 | 3829 | 1546 | 891 | 0 | 32 | 1012.39 | 218 | 4791 | 333.36 | 110 | 559 | 202 | 0 | 0 | 372
08:30 | 3734.5 | 1487.9 | 891 | 0 | 31 | 1013.29 | 218 | 4741.5 | 430.37 | 110 | 613 | 194 | 0 | 0 | 347
09:00 | 3640 | 1429.8 | 891 | 0 | 30 | 1014.19 | 218 | 4692 | 527.38 | 110 | 667 | 186 | 0 | 0 | 322
09:30 | 3761 | 1501.9 | 891 | 0 | 31 | 1017.54 | 218 | 4667 | 578.445 | 123 | 596 | 175.5 | 0 | 0 | 268.5
10:00 | 3882 | 1574 | 891 | 0 | 32 | 1020.89 | 218 | 4642 | 629.51 | 136 | 525 | 165 | 0 | 0 | 215
10:30 | 3879 | 1608.5 | 891 | 0 | 33 | 1022.385 | 218 | 4693 | 647.76 | 139 | 535.5 | 143.5 | 0 | 0 | 275
11:00 | 3876 | 1643 | 891 | 0 | 34 | 1023.88 | 218 | 4744 | 666.01 | 142 | 546 | 122 | 0 | 0 | 335
11:30 | 3868 | 1631 | 891.5 | 0 | 35 | 1021.55 | 220 | 4756 | 693.76 | 150 | 783 | 121 | 0 | 0.5 | 330
12:00 | 3860 | 1619 | 892 | 0 | 36 | 1019.22 | 222 | 4768 | 721.51 | 158 | 1020 | 120 | 0 | 1 | 325
12:30 | 3859.5 | 1515 | 891.5 | 0 | 36 | 1012.235 | 222 | 4736.5 | 698.79 | 178.5 | 1461.5 | 122 | 0 | 7 | 299
13:00 | 3859 | 1411 | 891 | 0 | 36 | 1005.25 | 222 | 4705 | 676.07 | 199 | 1903 | 124 | 0 | 13 | 273
13:30 | 3812.5 | 1393 | 891 | 0 | 35 | 1006.42 | 221.5 | 4664 | 652.06 | 207.5 | 2071 | 123.5 | 0 | 17.5 | 273.5
14:00 | 3766 | 1375 | 891 | 0 | 34 | 1007.59 | 221 | 4623 | 628.05 | 216 | 2239 | 123 | 0 | 22 | 274
14:30 | 3858 | 1464.5 | 891 | 0 | 36 | 1010.22 | 221 | 4680.5 | 559.49 | 223.5 | 2266.5 | 123 | 0 | 11 | 289
15:00 | 3950 | 1554 | 891 | 0 | 38 | 1012.85 | 221 | 4738 | 490.93 | 231 | 2294 | 123 | 0 | 0 | 304
15:30 | 3951 | 1525.5 | 891 | 0 | 37 | 1011.115 | 221.5 | 4765.5 | 391.64 | 235 | 2329 | 123 | 0 | 0 | 291
16:00 | 3952 | 1497 | 891 | 0 | 36 | 1009.38 | 222 | 4793 | 292.35 | 239 | 2364 | 123 | 0 | 0 | 278
16:30 | 3919 | 1469.5 | 891.5 | 0 | 55 | 1008.015 | 222 | 4783 | 190.565 | 266.5 | 2433 | 123 | 0 | 0 | 274
17:00 | 3886 | 1442 | 892 | 0 | 74 | 1006.65 | 222 | 4773 | 88.78 | 294 | 2502 | 123 | 0 | 0 | 270
17:30 | 3928 | 1490.75 | 891.5 | 0 | 76 | 1069.155 | 221.5 | 4789 | 44.89 | 336 | 2553.5 | 162 | 0 | 0 | 409.5
18:00 | 3970 | 1539.5 | 891 | 0 | 78 | 1131.66 | 221 | 4805 | 1 | 378 | 2605 | 201 | 0 | 0 | 549
18:30 | 3915.5 | 1456.75 | 843.5 | 0 | 78 | 1265.715 | 221 | 4851.5 | 0.5 | 470.5 | 2734.5 | 260.5 | 0 | 0 | 975.5
19:00 | 3861 | 1374 | 796 | 0 | 78 | 1399.77 | 221 | 4898 | 0 | 563 | 2864 | 320 | 0 | 0 | 1402
19:30 | 3921 | 1453 | 797 | 0 | 80 | 1424.41 | 220 | 4889 | 0 | 613 | 2851.5 | 155 | 0 | 0 | 1312
20:00 | 3939 | 1439 | 796 | 0 | 82 | 1426.55 | 219 | 4889 | 0 | 607 | 2795.06 | 155 | 0 | 0 | 1289
20:30 | 3968.5 | 1443 | 800 | 0 | 81 | 1420.35 | 219 | 4890 | 0 | 601.5 | 2887.06 | 157.5 | 0 | 1.5 | 1451
21:00 | 3998 | 1447 | 804 | 0 | 80 | 1414.15 | 219 | 4891 | 0 | 596 | 2979.06 | 160 | 0 | 3 | 1613
21:30 | 4026 | 1481 | 804 | 0 | 79 | 1416.685 | 219 | 4897.5 | 0 | 597 | 2920.81 | 190 | 0 | 1.5 | 1420
22:00 | 4054 | 1515 | 804 | 0 | 78 | 1419.22 | 219 | 4904 | 0 | 598 | 2862.56 | 220 | 0 | 0 | 1227
22:30 | 4026.5 | 1523.5 | 804.5 | 0 | 76 | 1419.365 | 219.5 | 4904 | 0 | 598.5 | 2762.56 | 310 | 0 | 2.5 | 1371
23:00 | 3999 | 1532 | 805 | 0 | 74 | 1419.51 | 220 | 4904 | 0 | 599 | 2662.56 | 400 | 0 | 5 | 1515
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 19-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 88 | 3 | 364 | 172 | 1030 | 458 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 67 | 4 | 284 | 172 | 930 | 448
2:00 | 58 | 14 | 272 | 178 | 912 | 436 |  | Import | 0
3:00 | 59 | 16 | 264 | 172 | 940 | 430
4:00 | 60 | 18 | 280 | 172 | 968 | 448 | Ishurdi-Ghorashal Ckt-2 | Export | 2770036.36
5:00 | 62 | 19 | 270 | 170 | 968 | 448
6:00 | 85 | 27 | 310 | 166 | 1092 | 484 |  | Import | 0
7:00 | 78 | 27 | 250 | 158 | 1008 | 498
8:00 | 126 | 35 | 310 | 146 | 1260 | 580 | Sirajganj-Sreepur Ckt-1 | Export | 2055000
9:00 | 148 | 37 | 370 | 152 | 1340 | 388
10:00 | 172 | 50 | 430 | 158 | 1500 | 660 |  | Import | 0
11:00 | 175 | 61 | 410 | 182 | 1456 | 808
12:00 | 162 | 59 | 440 | 230 | 1380 | 824 | Sirajganj-Sreepur Ckt-2 | Export | 2064000
13:00 | 142 | 54 | 400 | 220 | 1208 | 732
14:00 | 137 | 56 | 370 | 224 | 1162 | 738 |  | Import | 0
15:00 | 147 | 69 | 380 | 228 | 1226 | 782
16:00 | 147 | 72 | 380 | 230 | 1230 | 802 | Gopalganj-Aminbazar Ckt-1 | Export | 13720000
17:00 | 142 | 72 | 380 | 240 | 1220 | 800
18:00 | 139 | 70 | 400 | 238 | 1104 | 748 |  | Import | 0
18:30 | 141 | 65 | 380 | 218 | 1148 | 740
19:00 | 132 | 68 | 380 | 202 | 1226 | 710 | Gopalganj-Aminbazar Ckt-2 | Export | 13770000
19:30 | 124 | 62 | 340 | 192 | 1086 | 680
20:00 | 117 | 52 | 340 | 168 | 1140 | 640 |  | Import | 0
21:00 | 104 | 50 | 290 | 168 | 1006 | 636
22:00 | 106 | 49 | 300 | 176 | 1014 | 608 |  | Total Export | 34379036.36
23:00 | 119 | 49 | 382 | 192 | 1134 | 656 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 02:00 | 353 | 12:00 | Madunaghat | 398 | 03:00 | 386 | 12:00
Amtali | 412 | 02:00 | 406 | 12:00 | Meghnaghat | 387 | 02:00 | 362 | 12:00
Ashuganj | 402 | 6:00 | 381 | 13:00 | Mirsorai | 397 | 02:00 | 379 | 12:00
Bhulta | 394 | 04:00 | 341 | 13:00 | Payra | 414 | 06:00 | 408 | 11:00
Bibiana | 382 | 02:00 | 373 | 10:00 | Rahanpur | 408 | 02:00 | 390 | 11:00
BIPTC | 403 | 06:00 | 393 | 18:30 | Rampal | 395 | 03:00 | 380 | 12:00
Bogura | 393 | 02:00 | 380 | 11:00
Gopalganj | 392 | 02:00 | 376 | 11:00
Kaliakoir | 375 | 02:00 | 345 | 12:00
Korerhat | 396 | 02:00 | 379 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 04:00 | 210 | 12:00 | Hasnabad | 226 | 06:00 | 206 | 11:00
AKSML | 232 | 02:00 | 221 | 22:00 | Hathazari | 232 | 19:00 | 225 | 11:00
Aminbazar | 232 | 01:00 | 211 | 12:00 | Ishurdi | 235 | 06:00 | 224 | 00:00
Ashuganj | 227 | 07:00 | 214 | 12:00 | Jhenaidah | 225 | 06:00 | 212 | 12:00
Ashuganj-400 | 227 | 07:00 | 214 | 12:00 | Kachua | 226 | 02:00 | 215 | 11:00
Baghabari | 232 | 05:00 | 224 | 11:00 | Kaliakoir | 233 | 03:00 | 210 | 12:00
Barapukuria | 227 | 17:00 | 216 | 21:00 | Keranigonj | 229 | 04:00 | 207 | 12:00
Barapukuria-230 | 227 | 17:00 | 216 | 21:00 | Khulna(S) | 227 | 04:00 | 218 | 12:00
Barapukuria(N) | 228 | 17:00 | 218 | 21:00 | Korerhat | 225 | 02:00 | 214 | 11:00
Barishal | 225 | 03:00 | 220 | 11:00 | Madunaghat | 236 | 02:00 | 228 | 12:00
Bheramara | 233 | 04:00 | 220 | 12:00 | Madunaghat-400 | 238 | 03:00 | 230 | 12:00
Bhulta | 225 | 04:00 | 206 | 12:00 | Maniknagar | 223 | 03:00 | 204 | 12:00
Bibiana | 217 | 04:00 | 208 | 16:00 | Meghnaghat | 230 | 02:00 | 213 | 13:00
BIPTC | 236 | 05:00 | 220 | 12:00 | Meghnaghat-400 | 226 | 03:00 | 208 | 12:00
Birulia | 232 | 02:00 | 209 | 12:00 | Mirsorai | 231 | 00:00 | 220 | 11:00
Bogura | 238 | 02:00 | 230 | 11:00 | Naogaon | 226 | 18:30 | 207 | 13:00
Bogura-400 | 238 | 18:00 | 229 | 22:00 | Purbasadipur | 225 | 18:30 | 211 | 21:00
Borhanuddin | 228 | 04:00 | 224 | 22:00 | Rajshahi | 231 | 05:00 | 219 | 00:00
BSRM | 226 | 02:00 | 215 | 12:00 | Rampal | 226 | 04:00 | 216 | 12:00
Charfasson | 229 | 07:00 | 224 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 215 | 12:00 | Rampura | 224 | 04:00 | 204 | 12:00
Cumilla(N) | 221 | 06:00 | 208 | 12:00 | Shikalbaha | 236 | 01:00 | 226 | 11:00
Faridpur | 222 | 05:00 | 213 | 12:00 | Shyampur | 226 | 03:00 | 206 | 12:00
Fenchuganj | 216 | 05:00 | 206 | 18:00 | Siddhirganj | 225 | 03:00 | 208 | 11:00
Feni | 223 | 02:00 | 211 | 12:00 | Sirajgonj | 236 | 05:00 | 230 | 12:00
Ghorashal | 230 | 01:00 | 215 | 11:00 | Sreepur | 220 | 02:00 | 212 | 12:00
Ghorashal-230 | 222 | 02:00 | 197 | 11:00 | Tongi | 216 | 07:00 | 198 | 15:00
Gopalganj | 223 | 06:00 | 214 | 12:00
GPH | 232 | 02:00 | 222 | 12:00
Haripur | 224 | 03:00 | 206 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 124 | 11:00 | Madanganj | 136 | 04:00 | 123 | 16:00
Agargaon | 137 | 02:00 | 122 | 12:00 | Madaripur | 130 | 04:00 | 126 | 15:00
Agrabad | 135 | 23:00 | 127 | 11:00 | Madartek | 137 | 03:00 | 123 | 12:00
AKS | 133 | 01:00 | 128 | 12:00 | Madunaghat | 137 | 02:00 | 132 | 11:00
Aminbazar | 133 | 02:00 | 119 | 12:00 | Magura | 133 | 17:00 | 123 | 00:00
Amnura | 132 | 06:00 | 125 | 11:00 | Mahasthangarh | 134 | 17:00 | 126 | 19:30
Araihazar | 128 | 02:00 | 117 | 12:00 | Maijdee | 125 | 02:00 | 120 | 11:00
Ashuganj | 134 | 08:00 | 125 | 12:00 | Manikganj | 130 | 00:00 | 115 | 11:00
Ashuganj-230 | 134 | 03:00 | 128 | 15:00 | Maniknagar | 139 | 03:00 | 124 | 12:00
Bagerhat | 125 | 06:00 | 119 | 22:00 | Matarbari | 123 | 14:00 | 110 | 13:00
Bajitpur | 124 | 04:00 | 119 | 12:00 | Matuail | 134 | 05:00 | 121 | 12:00
Bakerganj | 131 | 06:00 | 127 | 22:00 | Metrorail_Motijheel | 139 | 03:00 | 124 | 12:00
Bakulia | 136 | 23:00 | 128 | 11:00 | Metrorail_Uttara | 135 | 03:00 | 116 | 12:00
Banani | 137 | 03:00 | 122 | 12:00 | Millgate | 137 | 04:00 | 117 | 12:00
Bangabhaban | 139 | 04:00 | 125 | 12:00 | Mirpur | 132 | 04:00 | 118 | 12:00
Barapukuria | 138 | 17:00 | 126 | 19:30 | Mirzapur | 131 | 01:00 | 121 | 11:00
Barguna | 131 | 06:00 | 125 | 22:00 | Mithapukur | 131 | 17:00 | 122 | 20:00
Barishal | 132 | 04:00 | 127 | 11:00 | MI_Cement | 134 | 02:00 | 118 | 12:00
Barishal-230 | 131 | 03:00 | 127 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 135 | 01:00 | 129 | 11:00 | Mogbazar | 141 | 04:00 | 125 | 11:00
Baroirhat | 131 | 02:00 | 124 | 12:00 | Mongla | 124 | 03:00 | 119 | 22:00
Bashundhara | 138 | 04:00 | 118 | 12:00 | Motijheel | 139 | 04:00 | 125 | 12:00
BashundharaCement | 133 | 01:00 | 123 | 16:00 | Muktagacha | 127 | 19:00 | 118 | 07:00
Beanibazar | 118 | 04:00 | 112 | 16:00 | Munshiganj | 134 | 03:00 | 121 | 12:00
Benapole | 131 | 18:00 | 117 | 12:00 | Muradnagar | 125 | 03:00 | 115 | 12:00
Bhaluka | 130 | 08:00 | 123 | 12:00 | Mymensingh | 128 | 10:00 | 114 | 07:00
Bhandaria | 126 | 05:00 | 122 | 21:00 | Nabinagar | 136 | 03:00 | 120 | 11:00
Bhangura | 132 | 19:00 | 127 | 00:00 | Naogaon | 136 | 18:30 | 124 | 13:00
Bheramara | 137 | 06:00 | 129 | 09:00 | Narail | 134 | 18:00 | 122 | 00:00
Bheramara(GK) | 137 | 06:00 | 129 | 12:00 | Narinda | 139 | 03:00 | 124 | 12:00
Bhulta | 127 | 02:00 | 118 | 11:00 | Narshingdi | 131 | 01:00 | 118 | 11:00
Bhulta-400 | 129 | 03:00 | 118 | 12:00 | Natore | 132 | 06:00 | 126 | 11:00
Birulia | 136 | 02:00 | 123 | 12:00 | Nawabganj | 139 | 07:00 | 123 | 12:00
Bog-Sherpur | 135 | 02:00 | 130 | 11:00 | Netrakona | 121 | 20:00 | 112 | 12:00
Bogura | 137 | 17:00 | 131 | 11:00 | New | 136 | 04:00 | 119 | 12:00
Bogura-230 | 138 | 02:00 | 132 | 11:00 | Niamatpur | 134 | 06:00 | 127 | 12:00
Brahmanbaria | 129 | 07:00 | 122 | 12:00 | Noapara | 129 | 04:00 | 122 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 138 | 04:00 | 122 | 12:00 | Pabna | 133 | 03:00 | 127 | 11:00
Chandina | 127 | 03:00 | 119 | 12:00 | Palashbari | 130 | 17:00 | 116 | 19:30
Chandpur | 132 | 20:00 | 123 | 11:00 | Panchagarh | 138 | 17:00 | 125 | 20:00
Chandraghona | 136 | 00:00 | 132 | 11:00 | Patiya | 133 | 07:00 | 127 | 11:00
Chapai | 133 | 04:00 | 125 | 13:00 | Patnitala | 132 | 06:00 | 126 | 11:00
Charsaidpur | 134 | 02:00 | 121 | 12:00 | Patuakhali | 132 | 04:00 | 127 | 11:00
Chauddagram | 126 | 01:00 | 120 | 12:00 | Payra | 135 | 04:00 | 133 | 11:00
Chhatak | 117 | 08:00 | 107 | 18:00 | PHP | 130 | 02:00 | 124 | 11:00
Chowmuhani | 125 | 00:00 | 120 | 10:00 | Postogola | 136 | 04:00 | 121 | 12:00
Chuadanga | 133 | 17:00 | 120 | 00:00 | Pubail | 130 | 00:00 | 116 | 15:00
Coxsbazar | 125 | 09:00 | 113 | 17:00 | Purbachal | 138 | 04:00 | 123 | 12:00
Cumilla(N) | 127 | 05:00 | 119 | 12:00 | Purbasadipur | 136 | 17:00 | 127 | 21:00
Cumilla(S) | 134 | 05:00 | 119 | 12:00 | Rahanpur | 136 | 05:00 | 131 | 11:00
Daganbhuiyan | 128 | 02:00 | 122 | 11:00 | Rahanpur-400 | 136 | 02:00 | 130 | 11:00
Daudkandi | 124 | 04:00 | 114 | 12:00 | Rahim | 134 | 04:00 | 122 | 12:00
DhakaUniversity | 137 | 02:00 | 124 | 12:00 | Rajbari | 126 | 04:00 | 120 | 12:00
Dhamrai | 137 | 03:00 | 121 | 11:00 | Rajendrapur | 132 | 04:00 | 125 | 12:00
Dhanmondi | 137 | 06:00 | 124 | 12:00 | Rajshahi | 131 | 06:00 | 124 | 00:00
Dohazari | 130 | 07:00 | 124 | 12:00 | Rajshahi-230 | 131 | 03:00 | 125 | 00:00
Faridpur | 129 | 06:00 | 123 | 15:00 | Ramganj | 126 | 09:00 | 118 | 12:00
Fatullah | 136 | 05:00 | 120 | 12:00 | Rampur | 135 | 01:00 | 127 | 11:00
Fenchuganj | 127 | 04:00 | 120 | 18:00 | Rampura | 137 | 03:00 | 124 | 12:00
Feni | 129 | 02:00 | 122 | 11:00 | Rangamati | 135 | 00:00 | 131 | 11:00
Feni-230 | 129 | 02:00 | 122 | 12:00 | Rangpur | 131 | 17:00 | 118 | 19:30
Ghatail | 125 | 10:00 | 116 | 16:00 | Ruppur | 136 | 04:00 | 129 | 12:00
Ghorashal | 130 | 00:00 | 120 | 12:00 | Saidpur | 135 | 19:00 | 125 | 21:00
Goalpara | 132 | 04:00 | 125 | 12:00 | Santhia | 132 | 06:00 | 128 | 11:00
Gollamari | 131 | 06:00 | 125 | 12:00 | Satkhira | 126 | 05:00 | 120 | 00:00
Gopalganj | 131 | 03:00 | 123 | 12:00 | Satmasjid | 137 | 03:00 | 123 | 11:00
Gopalganj-400 | 132 | 04:00 | 126 | 12:00 | Savar | 131 | 01:00 | 118 | 11:00
Gulshan | 137 | 05:00 | 124 | 12:00 | SevenRings | 134 | 02:00 | 119 | 15:00
Halishahar | 136 | 02:00 | 128 | 11:00 | ShahCement | 134 | 02:00 | 121 | 12:00
Haripur | 134 | 03:00 | 122 | 12:00 | Shahjadpur | 135 | 03:00 | 132 | 00:00
HaripurSBU | 134 | 03:00 | 122 | 12:00 | Shahjibazar | 129 | 08:00 | 121 | 18:00
Hasnabad | 134 | 03:00 | 121 | 12:00 | Shahmirpur | 137 | 21:00 | 128 | 11:00
Hathazari | 135 | 02:00 | 132 | 19:00 | Shariatpur | 129 | 05:00 | 124 | 00:00
Hatirjheel | 138 | 04:00 | 124 | 12:00 | Sherpur | 133 | 08:00 | 111 | 07:00
Ishurdi | 137 | 04:00 | 130 | 12:00 | Shikalbaha | 125 | 18:00 | 118 | 12:00
Jaldhaka | 132 | 17:00 | 122 | 21:00 | Shikalbaha-230 | 138 | 00:00 | 130 | 11:00
Jamalpur | 132 | 00:00 | 117 | 03:00 | Shitalakhya | 134 | 02:00 | 118 | 12:00
Jashore | 132 | 17:00 | 119 | 00:00 | Sholosohor | 136 | 02:00 | 128 | 11:00
Jhenaidah | 135 | 19:00 | 127 | 00:00 | Shomvuganj | 123 | 07:00 | 111 | 00:00
Jhenaidah-230 | 136 | 06:00 | 127 | 12:00 | Shyampur | 131 | 09:00 | 120 | 12:00
Joydebpur | 128 | 00:00 | 114 | 16:00 | Shyampur-230 | 136 | 04:00 | 121 | 12:00
Joypurhat | 132 | 06:00 | 126 | 12:00 | Siddhirganj | 134 | 04:00 | 122 | 12:00
Juldah | 136 | 00:00 | 128 | 11:00 | Sirajganj | 131 | 18:00 | 125 | 11:00
Kabirpur | 137 | 02:00 | 115 | 11:00 | Sitakunda | 135 | 23:00 | 130 | 11:00
Kachua | 128 | 02:00 | 121 | 11:00 | Sonargaon | 130 | 05:00 | 119 | 12:00
Kaliakoir | 138 | 01:00 | 125 | 11:00 | Sreemongol | 126 | 07:00 | 119 | 16:00
Kaliganj | 135 | 03:00 | 125 | 12:00 | Sreepur | 133 | 06:00 | 128 | 12:00
Kallyanpur | 132 | 06:00 | 118 | 12:00 | Srinagar | 138 | 04:00 | 124 | 11:00
Kalurghat | 137 | 01:00 | 131 | 11:00 | SSM | 140 | 00:00 | 138 | 10:00
Kamrangirchar | 138 | 05:00 | 116 | 12:00 | Sunamganj | 113 | 07:00 | 106 | 18:00
Kaptai | 138 | 2:00 | 135 | 11:00 | Sylhet | 120 | 08:00 | 113 | 18:00
Kasba | 124 | 03:00 | 116 | 12:00 | Sylhet_(South) | 121 | 06:00 | 114 | 17:00
Kazla | 139 | 04:00 | 125 | 12:00 | Tangail | 126 | 09:00 | 118 | 15:00
Keranigonj | 139 | 04:00 | 124 | 12:00 | Taraganj | 134 | 00:00 | 119 | 19:30
Khagrachori | 135 | 07:00 | 131 | 11:00 | Tasnim | 131 | 03:00 | 119 | 12:00
Khulna | 130 | 03:00 | 124 | 12:00 | Thakurgaon | 140 | 17:00 | 126 | 20:00
Khulna(S) | 131 | 02:00 | 125 | 12:00 | TK | 136 | 00:00 | 133 | 16:00
Khulshi | 134 | 21:00 | 127 | 11:00 | Tongi | 132 | 04:00 | 120 | 15:00
Kishoreganj | 127 | 07:00 | 117 | 00:00 | Ullahpara | 133 | 03:00 | 127 | 11:00
Kodda | 137 | 02:00 | 115 | 12:00 | Ullon | 137 | 02:00 | 124 | 12:00
Korerhat | 133 | 02:00 | 127 | 11:00 | Uttara | 136 | 04:00 | 115 | 12:00
KSRM | 136 | 07:00 | 130 | 11:00 | UttaraNew | 135 | 03:00 | 116 | 12:00
Kulaura | 126 | 07:00 | 119 | 16:00 | Zigatola | 139 | 05:00 | 124 | 12:00
Kurigram | 126 | 13:00 | 111 | 19:00
Kushtia | 134 | 19:00 | 127 | 00:00
Laksam | 128 | 03:00 | 121 | 11:00
Lakshmipur | 125 | 02:00 | 119 | 11:00
Lalbag | 137 | 02:00 | 123 | 12:00
Lalmonirhat | 127 | 23:00 | 117 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division