## Forecast
6086.1 |  |  |  |  | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-12-17 | Monday
|  | Date (day): | 2018-12-17 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10624 | MW |  |  | (b) At Evening Peak Hour : |  | 11701 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-12-16 | 2018-12-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 38 | 38 | 38 | 38 |  | 47 | Unit #2 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 253 | 100 | 100 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 175 | 200 | 250 | 300
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 40 | 0 | 0 |  |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 82 | 91 | 91 | 17 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 10 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 340 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 305 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 350 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 39 | 62 | 100 | 100 | 110 |  | Machine problem.
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 155 | 217 | 217
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Contract expired
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 47 | 47
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 18 | 54 | 54
25 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 118 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 36 | 36 |  | 19 | Engine problem
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 45 | 45 |  | 63 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 32 | 55 | 55 |  | 25 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
35 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 1672 | 2001 | 4118 | 4329 | 437 | 550
39 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 180 | 180 | 180 | 180
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 26 | 25 | 25
41 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.4 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 48 | 50 | 50
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 78 | 76 | 108 |  | 122 | Low water lavel
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage.
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 70 | 70
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 0 | 0 | 10 | 90 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 16 | 20 | 25
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| Chattogram area Total |  |  |  |  | 1661 | 1581 | 347.4 | 578 | 861 | 878 | 330 | 416
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 90 | 80 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 135 | 135
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 130 | 185 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 260 | 265 | 265 |  | 95 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 298 | 300 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 37 | 35 | 37 | 35 |  | Gas shortage
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 51 | 51 | 51
| Midland 150MW |  | HFO | IPP | 23*7.015 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 6 | 85 | 85 | 85
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | STG under maint.
| Chandpur Desh 200MW |  | HFO | IPP | 0 | 0 | 0 | 0 | 51 | 190 | 190
65 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
66 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 80 | 104 | 88 | 111
67 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
68 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
69 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 22 | 22 | 22
70 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2601 | 2541 | 1128 | 1436 | 1833 | 2050 | 484 | 158
71 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 203 | 208 | 210 | 210 |  |  | Gas shortage
72 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
73 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 21 | 79 | 79 |  | 16 | Engine problem.
74 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 2 | 0
75 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 7 | 150 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 231.9 | 256 | 463 | 511 | 0 | 16
76 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 57 | 57 | 57
77 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 63 | 63 | 63 | 63
78 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
79 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 305 | 286 | 300 | 300
80 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 49 | 51 | 51
81 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 21 | 44 | 44
82 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
83 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 60 | 66 | 66
84 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 86 | 86 | 86
85 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 49 | 50 | 50
86 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 98 | 78 | 100 | 130
87 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
88 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 48 | 50 | 50
89 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 25 | 25 | 25
90 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
91 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 853 | 942 | 1076 | 1106 | 0 | 361
92 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 353 | 668 | 540 | 688
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 0 | 80
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 306 | 300 | 300 |  |  | STG under maint.
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
99 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
101 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 105 | 105
| Khulna Area Total |  |  |  |  | 2278 | 2209 | 603 | 1124 | 1200 | 1504 | 0 | 0
102 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
103 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
104 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 28 | 33
105 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 186 | 187 | 190 | 190
106 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 215 | 309 | 423 | 458 | 0 | 0
107 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
108 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
109 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 42
110 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 40 | 50 | 50
111 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
112 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
113 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
114 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 178 | 220 | 220
115 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
116 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
117 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 0 | 40
118 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
119 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
120 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
121 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
122 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 9 | 52 | 90 | 102
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 257 | 383 | 500 | 679 | 71 | 105
123 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
124 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124
125 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
126 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 165 | 150 | 186 | 209 | 85
| Total |  |  |  |  | 17340 | 16742 | 5456.3 | 7194 | 10624 | 11701 | 1531 | 1691
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5097.5524 | 6721 | 9925.4801 | 10931.6682
A. |  | 2018-12-16 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 7194 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4876 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7194 | MW
3 | Day peak Generation : |  |  | 5456.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6721 | MW
4 | Evening peak Generation : |  |  | 7194 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 137.3282 | MKWHr | By Solar | 0.13136 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 114.4234 | MKWHr |  | By Oil: | 5.3509 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6751 | MKWHr |  | By Hydro: | 1.7676 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1531 | MW | Dhaka | 2206 | 2206 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1691 | MW | Chittagong | 687 | 687 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3222 | MW | Khulna | 888 | 888 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 996.04 | MMCFD |  |  | Rajshahi | 774 | 774 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 83908030.898 | ii) Oil : | Taka | 36818924.41 | Comilla | 644 | 644 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14185886 | Total | Taka | 134912841.308 | Mymensingh | 524 | 524 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.3475 | MKWHr. | Sylhet | 295 | 295 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -660 | MW at | 19:00 | hrs | Barisal | 191 | 191 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -680 | MW at | 18:00 | hrs | Rangpur | 512 | 512 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.5° C |  |  | Total | 6721 | 6721 |  | 0
B. |  | 2018-12-17 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 20.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11701 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve(Generation end) |  |  |  | 3301 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 160.3498 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4491 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.0502 | MKWHr. | ii) HVDC Flow at Peak Time |  | 668 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9296 | MKWHr. | iii) Maximum HVDC Flow : |  | 681 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.4 |  | (b) Today: | 99.2 |  | (c) Rule Curve: |  | 104.5
.
14

## YesterdayGen
2018-12-16
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 38 | 0 | 0 | 0 | 330 | 13 | 40 | 348 | 300 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 150 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 30 | 0 | 90 | 80 | 260 | 309 | 192 | 8 | 100 | 37 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 74 | 214 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 130 | 290 | 63 | 5 | 5 | 78 | 0 | 3 | 0 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 54 | 0 | 0 |  | 304 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4429 | 1171 | 5600 | 3868 | 304 | 979 | 151 | 149 | 75 | 0 | 74 | 0 | 0 | 99.41
2:00 | 38 | 0 | 0 | 0 | 300 | 13 | 20 | 348 | 300 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 90 | 80 | 260 | 309 | 185 | 8 | 100 | 34 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 72 | 183 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 130 | 290 | 63 | 5 | 5 | 78 | 0 | 3 | 0 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 303 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4180 | 1145 | 5325 | 3709 | 303 | 940 | 77 | 149 | 75 | 0 | 72 | 0 | 0 | 99.41
3:00 | 38 | 0 | 0 | 0 | 270 | 13 | 0 | 315 | 260 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 90 | 80 | 260 | 309 | 183 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 72 | 171 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 130 | 302 | 67 | 5 | 5 | 80 | 0 | 3 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 0 | 0 | 0 |  | 304 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 3961 | 1087 | 5048 | 3539 | 304 | 858 | 51 | 149 | 75 | 0 | 72 | 0 | 0 | 99.41
4:00 | 38 | 0 | 0 | 0 | 0 | 13 | 0 | 300 | 300 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 173 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 90 | 80 | 260 | 309 | 183 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 70 | 149 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 0 | 290 | 40 | 5 | 5 | 78 | 0 | 3 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 304 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3672 | 1221 | 4893 | 3449 | 304 | 813 | 33 | 149 | 75 | 0 | 70 | 0 | 0 | 99.4
5:00 | 38 | 0 | 0 | 0 | 70 | 13 | 0 | 300 | 300 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 140 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 90 | 80 | 260 | 327 | 190 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 70 | 149 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 0 | 299 | 40 | 5 | 5 | 78 | 0 | 3 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 304 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3693 | 1183 | 4876 | 3440 | 304 | 813 | 25 | 149 | 75 | 0 | 70 | 0 | 0 | 99.4
6:00 | 38 | 0 | 0 | 0 | 95 | 13 | 0 | 335 | 300 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 140 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 90 | 80 | 260 | 327 | 196 | 8 | 95 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 70 | 150 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 40 | 294 | 52 | 5 | 5 | 78 | 0 | 3 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 304 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3804 | 1195 | 4999 | 3516 | 304 | 858 | 25 | 149 | 77 | 0 | 70 | 0 | 0 | 99.4
7:00 | 38 | 0 | 0 | 0 | 135 | 13 | 0 | 345 | 252 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 140 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 30 | 0 | 90 | 80 | 260 | 309 | 182 | 8 | 95 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 16 | 70 | 150 | 0 | 20 | 0.1 | 57 | 63 | 5 | 5 | 70 | 286 | 40 | 5 | 46 | 77 | 0 | 46 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 10 | 0 | 0 | 0 |  | 303 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3861.1 | 1173 | 5034.1 | 3490 | 303 | 919 | 25 | 149 | 77 | 0 | 70 | 1.1 | 0 | 99.4
8:00 | 38 | 0 | 0 | 0 | 175 | 13 | 0 | 350 | 300 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 140 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 26 | 0 | 90 | 80 | 260 | 338 | 195 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 20 | 68 | 151 | 0 | 20 | 0.3 | 57 | 63 | 5 | 5 | 70 | 302 | 52 | 5 | 47 | 78 | 0 | 47 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.2 | 10 | 0 | 0 | 0 |  | 304 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4063.5 | 1186 | 5249.5 | 3635 | 304 | 983 | 25 | 149 | 77 | 0 | 68 | 8.5 | 0 | 99.31
9:00 | 38 | 0 | 0 | 0 | 175 | 12 | 0 | 350 | 308 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 140 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 80 | 260 | 309 | 185 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 20 | 74 | 150 | 0 | 20 | 0.5 | 57 | 63 | 5 | 5 | 90 | 288 | 67 | 5 | 47 | 80 | 0 | 47 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 13 | 10 | 0 | 0 | 0 |  | 304 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 202 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4046.5 | 1230 | 5276.5 | 3618 | 304 | 983 | 58 | 149 | 77 | 0 | 74 | 13.5 | 0 | 99.3
10:00 | 38 | 0 | 0 | 0 | 175 | 12 | 0 | 345 | 301 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 120 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 80 | 260 | 309 | 184 | 8 | 95 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 16 | 20 | 74 | 169 | 0 | 20 | 0.8 | 57 | 63 | 5 | 5 | 100 | 290 | 40 | 5 | 47 | 80 | 0 | 44 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16.7 | 10 | 0 | 0 | 0 |  | 353 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4024.5 | 1234 | 5258.5 | 3534 | 353 | 963 | 82 | 149 | 77 | 9 | 74 | 17.5 | 0 | 99.3
11:00 | 38 | 0 | 100 | 0 | 175 | 12 | 0 | 360 | 289 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 80 | 250 | 301 | 155 | 8 | 101 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 16 | 16 | 76 | 165 | 0 | 20 | 1.3 | 57 | 63 | 5 | 5 | 130 | 288 | 62 | 5 | 47 | 98 | 0 | 45 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.9 | 10 | 0 | 0 | 0 |  | 353 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4131.2 | 1154 | 5285.2 | 3566 | 353 | 954 | 82 | 149 | 77 | 9 | 76 | 19.2 | 0 | 99.29
12:00 | 38 | 0 | 140 | 0 | 175 | 12 | 0 | 355 | 331 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 28 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 80 | 250 | 298 | 130 | 8 | 100 | 10 | 5 | 5 | 7 | 6 | 0 | 0 | 22 | 5 | 16 | 16 | 80 | 203 | 0 | 20 | 1.9 | 57 | 63 | 5 | 5 | 130 | 305 | 63 | 5 | 47 | 98 | 0 | 44 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18.4 | 10 | 0 | 0 | 0 |  | 353 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4232.3 | 1224 | 5456.3 | 3690 | 353 | 996 | 82 | 149 | 77 | 9 | 80 | 20.3 | 0 | 99.29
13:00 | 38 | 0 | 150 | 0 | 210 | 12 | 0 | 355 | 350 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 120 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 28 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 0 | 90 | 80 | 220 | 280 | 214 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 5 | 16 | 22 | 80 | 205 | 0 | 20 | 2.2 | 57 | 63 | 5 | 5 | 163 | 316 | 65 | 5 | 47 | 99 | 0 | 45 | 0 | 0 | 23 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16.8 | 10 | 0 | 0 | 0 |  | 330 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4419 | 1256 | 5675 | 3841 | 330 | 1081 | 82 | 149 | 77 | 16 | 80 | 19 | 0 | 99.28
14:00 | 38 | 0 | 200 | 0 | 210 | 12 | 0 | 295 | 276 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 28 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 0 | 90 | 80 | 220 | 268 | 183 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 16 | 22 | 80 | 204 | 0 | 9 | 1.1 | 57 | 63 | 5 | 5 | 130 | 288 | 40 | 5 | 47 | 97 | 0 | 46 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.7 | 10 | 0 | 0 | 0 |  | 330 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4146.8 | 1245 | 5391.8 | 3708 | 330 | 939 | 82 | 149 | 77 | 16 | 80 | 10.8 | 0 | 99.38
15:00 | 38 | 0 | 200 | 0 | 230 | 12 | 0 | 280 | 267 | 0 | 10 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 28 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 90 | 80 | 220 | 272 | 183 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 8 | 12 | 74 | 177 | 0 | 20 | 0.5 | 30 | 63 | 5 | 5 | 100 | 289 | 40 | 5 | 5 | 78 | 0 | 5 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5.4 | 10 | 0 | 0 | 0 |  | 330 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3963.9 | 1130 | 5093.9 | 3574 | 330 | 809 | 57 | 150 | 78 | 16 | 74 | 5.9 | 0 | 99.38
16:00 | 38 | 0 | 255 | 0 | 200 | 12 | 0 | 270 | 255 | 0 | 10 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 28 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 80 | 80 | 220 | 268 | 205 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 8 | 12 | 76 | 153 | 0 | 20 | 0.2 | 30 | 40 | 5 | 5 | 100 | 278 | 51 | 5 | 5 | 78 | 0 | 6 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5.6 | 10 | 0 | 0 | 0 |  | 331 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 185 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3931.8 | 1076 | 5007.8 | 3496 | 331 | 797 | 57 | 149 | 78 | 18 | 76 | 5.8 | 0 | 99.37
17:00 | 38 | 0 | 253 | 0 | 200 | 12 | 0 | 270 | 304 | 0 | 10 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 19 | 25 | 31 | 28 | 25 | 3 | 0 | 78 | 0 | 0 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 10 | 0 | 8 | 22 | 16 | 0 | 80 | 80 | 260 | 276 | 186 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 8 | 15 | 88 | 188 | 5 | 20 | 0 | 30 | 40 | 5 | 5 | 100 | 256 | 55 | 5 | 5 | 78 | 0 | 6 | 0 | 0 | 24 | 8 | 0 | 3 | 0 | 0 | 14 | 0 | 0 | 0.1 | 40 | 8 | 5 | 0 |  | 348 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 182 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 8 | 15 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 12 | 0 | 0 | 0 | 0 | 17 |  | 4177.1 | 1245 | 5422.1 | 3608 | 348 | 879 | 210 | 149 | 78 | 62 | 88 | 0.1 | 0 | 99.37
18:00 | 38 | 0 | 253 | 0 | 200 | 51 | 40 | 290 | 305 | 0 | 10 | 350 | 0 | 0 | 0 | 15 | 120 | 0 | 37 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 4 | 18 | 18 | 17 | 19 | 25 | 26 | 28 | 25 | 23 | 0 | 78 | 0 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 26 | 22 | 16 | 0 | 80 | 80 | 260 | 264 | 204 | 8 | 100 | 32 | 5 | 5 | 17 | 50 | 8 | 0 | 22 | 8 | 21 | 22 | 104 | 207 | 31 | 20 | 0 | 57 | 63 | 11 | 13 | 100 | 288 | 51 | 50 | 49 | 77 | 0 | 47 | 9 | 0 | 25 | 11 | 0 | 15 | 0 | 0 | 14 | 0 | 23 | 0 | 90 | 52 | 18 | 0 |  | 668 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 172 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 52 | 40 | 22 | 5 | 11 | 0 | 0 | 149 | 17 | 15 | 0 | 0 | 154 | 0 | 31 | 0 | 0 | 0 | 0 | 90 |  | 5003 | 1895 | 6898 | 3732 | 668 | 1209 | 708 | 149 | 78 | 250 | 104 | 0 | 0 | 99.36
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 38 | 0 | 253 | 0 | 200 | 82 | 40 | 340 | 305 | 0 | 10 | 350 | 0 | 0 | 0 | 15 | 155 | 0 | 62 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 19 | 0 | 32 | 33 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 48 | 22 | 16 | 0 | 80 | 80 | 260 | 300 | 185 | 8 | 100 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 22 | 104 | 208 | 21 | 20 | 0 | 57 | 63 | 49 | 21 | 100 | 286 | 60 | 86 | 49 | 78 | 0 | 48 | 9 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 90 | 51 | 0 | 0 |  | 668 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 187 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 52 | 23 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 15 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 90 |  | 5213 | 1981 | 7194 | 3986 | 668 | 1458 | 572 | 150 | 78 | 178 | 104 | 0 | 0 | 99.36
19:30 | 38 | 0 | 253 | 0 | 200 | 92 | 40 | 353 | 307 | 0 | 10 | 350 | 0 | 0 | 0 | 15 | 160 | 0 | 62 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 19 | 25 | 32 | 33 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 40 | 22 | 16 | 0 | 80 | 80 | 260 | 300 | 185 | 8 | 100 | 34 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 22 | 104 | 209 | 0 | 20 | 0 | 57 | 63 | 50 | 21 | 100 | 285 | 59 | 86 | 49 | 78 | 0 | 48 | 9 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 51 | 0 | 0 |  | 668 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 184 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 90 |  | 5245 | 1944 | 7189 | 4025 | 668 | 1471 | 553 | 150 | 78 | 140 | 104 | 0 | 0 | 0
20:00 | 38 | 0 | 253 | 0 | 200 | 101 | 81 | 348 | 308 | 0 | 10 | 350 | 0 | 0 | 0 | 15 | 160 | 0 | 62 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 36 | 22 | 16 | 0 | 80 | 80 | 260 | 300 | 184 | 8 | 100 | 34 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 22 | 106 | 210 | 0 | 20 | 0 | 57 | 63 | 48 | 21 | 100 | 290 | 61 | 86 | 49 | 77 | 0 | 48 | 9 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 51 | 0 | 0 |  | 668 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 186 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 90 |  | 5256 | 1920 | 7176 | 4024 | 668 | 1520 | 513 | 150 | 77 | 118 | 106 | 0 | 0 | 99.35
21:00 | 38 | 0 | 253 | 0 | 200 | 101 | 82 | 350 | 336 | 0 | 10 | 380 | 0 | 0 | 0 | 15 | 160 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 32 | 33 | 25 | 0 | 0 | 76 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 19 | 22 | 22 | 0 | 100 | 80 | 260 | 312 | 185 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 0 | 15 | 104 | 208 | 0 | 20 | 0 | 57 | 63 | 50 | 21 | 100 | 290 | 66 | 5 | 49 | 78 | 0 | 49 | 0 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 52 | 0 | 0 |  | 669 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 30 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 0 | 0 | 35 |  | 5278 | 1834 | 7112 | 4073 | 669 | 1496 | 451 | 149 | 76 | 94 | 104 | 0 | 0 | 99.35
22:00 | 38 | 0 | 225 | 0 | 200 | 101 | 40 | 350 | 335 | 0 | 10 | 380 | 0 | 0 | 0 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 51 | 10 | 0 | 18 | 22 | 22 | 0 | 100 | 80 | 260 | 298 | 184 | 8 | 100 | 40 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 15 | 96 | 212 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 130 | 291 | 58 | 5 | 49 | 77 | 0 | 48 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 67 | 0 | 0 |  | 681 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 178 | 0 | 38 | 0 | 0 | 0 | 0 | 0 |  | 4870 | 1639 | 6509 | 3884 | 681 | 1238 | 337 | 147 | 75 | 51 | 96 | 0 | 0 | 99.24
23:00 | 38 | 0 | 225 | 0 | 200 | 13 | 40 | 350 | 302 | 0 | 10 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 0 | 0 | 0 | 22 | 23 | 0 | 100 | 80 | 260 | 301 | 185 | 8 | 100 | 40 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 15 | 86 | 213 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 100 | 285 | 54 | 5 | 5 | 80 | 0 | 6 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 80 | 80 | 0 | 0 |  | 680 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 8 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4460 | 1499 | 5959 | 3769 | 680 | 945 | 223 | 147 | 75 | 34 | 86 | 0 | 0 | 99.23
24:00 | 38 | 0 | 224 | 0 | 200 | 13 | 0 | 325 | 262 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 75 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 0 | 0 | 0 | 22 | 22 | 0 | 100 | 80 | 260 | 272 | 185 | 8 | 100 | 40 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 22 | 76 | 180 | 0 | 0 | 0 | 57 | 63 | 5 | 5 | 100 | 280 | 57 | 5 | 5 | 80 | 0 | 6 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 34 | 0 | 0 |  | 501 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4177 | 1282 | 5459 | 3657 | 501 | 826 | 141 | 149 | 75 | 34 | 76 | 0 | 0 | 99.23
KWH | 895000 | 0 | 2720820 | 0 | 4458218 | 646091 | 562912 | 8083460 | 7190000 | 0 | 92400 | 8585250 | 0 | 0 | 0 | 86885 | 3383510 | 0 | 1350000 | 0 | 0 | 56592 | 0 | 0 | 3840 | 0 | 13248 | 80280 | 27380 | 51000 | 252828 | 600000 | 731700 | 790403 | 603900 | 32208 | 0 | 1767585 | 0 | 0 | 4400000 | 144000 | 0 | 0 | 0 | 0 | 0 | 820800 | 0 | 401733 | 51480 | 0 | 174240 | 534624 | 431040 | 0 | 2147215 | 1933474 | 6248900 | 7274500 | 4491000 | 200727 | 2343000 | 511848 | 153600 | 120000 | 366841 | 414680 | 4464 | 0 | 512136 | 195660 | 198500 | 445520 | 1929600 | 4251640 | 72000 | 291564 | 8500 | 1237000 | 1484040 | 266400 | 176000 | 2513168 | 6689000 | 1322000 | 401280 | 731520 | 2043040 | 0 | 636260 | 27540 | 0 | 549840 | 219168 | 0 | 20073 | 0 | 0 | 230400 | 0 | 23040 | 122860 | 931200 | 447000 | 36800 | 0 |  | 10050182 | 0 | 7094880 | 0 | 0 | 0 | 0 | 0 | 0 | 130432 | 175500 | 4461328 | 451500 | 41280 | 0 | 0 | 0 | 0 | 0 | 239628 | 172120 | 0 | 0 | 416640 | 71271 | 385920 | 125388 | 180504 | 0 | 0 | 3675100 | 25000 | 31000 | 0 | 0 | 4420373 | 0 | 594329 | 0 | 0 | 0 | 0 | 339360 |  | 104246425 | 33081735 | 137328160 | 89442993 | 10050182 | 24980446 | 4447366 | 3675100 | 1767585 | 903528 | 1929600 | 131360 | 0
Fuel Cost | 769700 | 0 | 2339905.2 | 0 | 2853259.52 | 523333.71 | 529137.28 | 4930910.6 | 4385900 | 0 | 126588 | 5752117.5 | 0 | 0 | 0 | 530867.35 | 2199281.5 | 0 | 1498500 | 0 | 0 | 372941.28 | 0 | 0 | 23001.6 | 0 | 88364.16 | 572396.4 | 171125 | 319770 | 189621 | 450000 | 0 | 0 | 0 | 304687.68 | 0 | 0 | 0 | 0 | 4840000 | 1363680 | 0 | 0 | 0 | 0 | 0 | 7214832 | 0 | 3908862.09 | 318661.2 | 0 | 1139529.6 | 454430.4 | 0 | 0 | 1953965.65 | 1759461.34 | 3874318 | 5019405 | 3143700 | 138501.63 | 2249280 | 342938.16 | 132096 | 110400 | 300809.62 | 393946 | 48389.76 | 0 | 394344.72 | 146745 | 152845 | 334140 | 13198464 | 3188730 | 661680 | 224504.28 | 0 | 1286480 | 1543401.6 | 255744 | 158400 | 1960271.04 | 4682300 | 1507080 | 429369.6 | 804672 | 2329065.6 | 0 | 591721.8 | 25612.2 | 0 | 412380 | 166567.68 | 0 | 145729.98 | 0 | 0 | 1647360 | 0 | 0 | 0 | 0 | 4174980 | 343712 | 0 |  | 51255928.2 | 0 | 4753569.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1536488.96 | 1382940 | 3078316.32 | 446985 | 305472 | 0 | 0 | 0 | 0 | 0 | 2147066.88 | 1488838 | 0 | 0 | 4133068.8 | 838859.67 | 424512 | 117864.72 | 136641.528 | 0 | 0 | 14185886 | 805750 | 829870 | 0 | 0 | 3094261.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 108404914.73 | 90962318.778 | 199367233.508 | 66426636.798 | 51255928.2 | 17481394.1 | 26703637.05 | 14185886 | 0 | 10115287.36 | 13198464 | 0 | 0
Yesterday Day Peak | 38 | 0 | 140 | 0 | 175 | 12 | 0 | 355 | 331 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 28 | 25 | 0 | 0 | 77 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 90 | 80 | 250 | 298 | 130 | 8 | 100 | 10 | 5 | 5 | 7 | 6 | 0 | 0 | 22 | 5 | 16 | 16 | 80 | 203 | 0 | 20 | 1.9 | 57 | 63 | 5 | 5 | 130 | 305 | 63 | 5 | 47 | 98 | 0 | 44 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18.4 | 10 | 0 | 0 | 0 |  | 353 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 5456.3 | DayPeak
Yesterday Evening Peak | 38 | 0 | 253 | 0 | 200 | 82 | 40 | 340 | 305 | 0 | 10 | 350 | 0 | 0 | 0 | 15 | 155 | 0 | 62 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 19 | 0 | 32 | 33 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 68 | 10 | 0 | 48 | 22 | 16 | 0 | 80 | 80 | 260 | 300 | 185 | 8 | 100 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 22 | 104 | 208 | 21 | 20 | 0 | 57 | 63 | 49 | 21 | 100 | 286 | 60 | 86 | 49 | 78 | 0 | 48 | 9 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 90 | 51 | 0 | 0 |  | 668 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 187 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 52 | 23 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 15 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 90 |  | 7194 | EvPeak
Forecast for Evening | 38 | 0 | 100 | 0 | 300 | 91 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 217 | 0 | 100 | 100 | 100 | 102 | 149 | 100 | 45 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 78 | 30 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 68 | 100 | 90 | 50 | 22 | 25 | 0 | 100 | 135 | 265 | 360 | 221 | 8 | 100 | 37 | 5 | 5 | 51 | 85 | 40 | 52 | 22 | 8 | 33 | 22 | 111 | 210 | 79 | 22 | 0 | 57 | 63 | 51 | 44 | 163 | 300 | 66 | 86 | 50 | 130 | 0 | 50 | 10 | 0 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 190 | 0 |  |  | 688 | 46 | 300 | 0 | 115 | 0 | 0 | 0 | 30 | 80 | 40 | 190 | 33 | 110 | 30 | 0 | 0 | 50 | 42 | 102 | 50 | 50 | 35 | 52 | 40 | 22 | 5 | 11 | 0 | 0 | 150 | 18 | 18 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 38 | 0 | 100 | 0 | 250 | 91 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 217 | 0 | 100 | 100 | 100 | 102 | 118 | 100 | 45 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 76 | 0 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 68 | 100 | 90 | 50 | 22 | 20 | 0 | 100 | 135 | 265 | 360 | 221 | 8 | 100 | 35 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 22 | 88 | 210 | 79 | 22 | 2 | 57 | 63 | 51 | 44 | 163 | 300 | 66 | 86 | 50 | 100 | 0 | 50 | 10 | 0 | 25 | 11 | 100 | 300 | 300 | 0 | 150 | 100 | 100 | 20 | 100 | 190 | 0 |  |  | 540 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 |  | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 38 | 0 | 100 | 0 | 240 | 91 | 0 | 310 | 360 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 150 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 26 | 33 | 25 | 0 | 0 | 78 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 1 | 22 | 10 | 0 | 100 | 80 | 230 | 309 | 204 | 8 | 100 | 37 | 5 | 5 | 7 | 20 | 0 | 0 | 22 | 8 | 0 | 16 | 80 | 213 | 0 | 20 | 0.2 | 57 | 63 | 5 | 40 | 130 | 279 | 67 | 20 | 47 | 100 | 0 | 21 | 0 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.4 | 22 | 5 | 0 | 0 | 0 | 340 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 187 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 195 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4876 | 5:00
| Highest Generation |  | 7194 | 19:00
| Day Peak Generation |  | 5456.3 | 12:00
| Evening Peak Generation |  | 7194 | 19:00
| HVDC Max Flow |  | 681 | 22:00
| HVDC EvPeak Flow |  | 668 | 19:00
| Load factor L.F |  | 79.54%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-12-17
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-12-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5456.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4491 | MW
Evening Peak Generation : |  | 7194 | MW Hour : | 19:00 | Available Max Generation : |  | 11701 | MW
E.P. Demand (at gen end) : |  | 7194 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8400 | MW
Maximum Generation : |  | 7194 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3301 | MW
Total Gen. (MKWH) : |  | 137.3282 | System Load Factor : | 79.54% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -680 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-12-17
Actual : | 99.2 | Ft.(MSL) , | Rule curve : | 104.5 | Ft.( MSL )
Gas Consumed : | Total = | 996.04 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 83908030.898
|  | Coal : | 14185886 | Oil : | 36818924.41 | Total : | 134912841.308
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2937.4364 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 991.5647 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 887.1037 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 801.1095 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 724.2067 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 584.3907 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 336.1902 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 150.7144 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 450.666 |  |  | 0 | 0%
Total | 0 |  | 7863.3823 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Bhagabari 71,100MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Raozan # 01
|  |  |  | 3) Ghorasal Unit-2,3,5 |  | 11) Sirajganj Unit-1,3,4
|  |  |  | 4) Tongi GT |  | 12) Haripur GT-1,2
5) Sikalbaha 150 MW
6) Baghabari 100 MW
7) Siddhirganj ST 210 MW
8) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) After maintenance Ghorasal #04 was synchronized at 10:36 and was shut down at 22:00 due Low demand.
b) Lalbagh-Kallayanpur 132 kV Ckt-1 was tripped at 06:17(17/12/2018) from Lalbagh end showing 67N, at
Lalbag end .
c) Rajshahi-Amnura 132 kV Ckt was shut at 07:49(17/12/18) due to project work.
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-12-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 38 | 895000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 253 | 2720820 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4458218 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 40 | 562912
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 82 | 646091 | Engine problem
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 10 | 92400 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8083460 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 305 | 7190000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 350 | 8585250 | Frequency Control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 86885 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 252828
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 62 | 1350000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 155 | 3383510
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 56592 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 0 | 13248 | Reserve
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 18 | 80280 | Low demand
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 0 | 27380 | Reserve
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 17 | 51000 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 3840 | Reserve
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 32 | 1331700 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 790403
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 603900 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 32208 | Reserve
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 20073 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 23040 | Reserve
| Dhaka area Total |  |  |  | 5848 | 2001 | 41341038
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 180 | 4400000
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 26 | 144000
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122860 | Reserve
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 48 | 174240
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 78 | 1767585 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Combustion inspection.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 820800 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 401733
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 51480 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 0 | 90 | 931200 | On test
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 534624
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 431040
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 1581 | 578 | 9779562
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2147215 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 185 | 4491000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6248900 | ST Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7274500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 37 | 511848 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 153600 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 366841
| Midland 150MW |  | IPP | 23*7.015 | 0 | 0 | 36800 | On test
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 414680
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 4464 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2343000 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 0 | 51 | 447000 | On Test
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512136
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 195660 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 104 | 1929600
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 198500
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 445520
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2541 | 1436 | 29975465
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 208 | 4251640 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 291564
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 21 | 72000 | Low demand
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 8500
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 7 | 230400 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 256 | 4854104
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 57 | 1237000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1484040
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 2513168 | Frequency Control.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 286 | 6689000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 49 | 266400
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 21 | 176000 | Engine problem
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 219168
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 60 | 1322000
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 401280
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 731520
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 2043040
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 48 | 636260
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 549840
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 27540
| Sylhet Area Total |  |  |  | 1549 | 942 | 18296256
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 668 | 10050182
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 0 | 0 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 20 | 130432
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 306 | 7094880 | ST Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 175500
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 90 | 339360 | Engine problem
| Khulna Area Total |  |  |  | 2209 | 1124 | 17790354
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 0 | 41280 | Reserve
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 25 | 451500 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 187 | 4461328 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 594329
| Barisal Area Total |  |  |  | 462 | 309 | 5548437
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 172120
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4420373 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 23 | 71271
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 385920
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 125388 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 180504
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 416640
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 52 | 239628 | Low demand
| Rajshahi Area Total |  |  |  | 1546 | 383 | 6011844
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 150 | 3675100
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 25000 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 31000
| Rangpur Area Total |  |  |  | 484 | 165 | 3731100
| Total |  |  |  | 16742 | 7194 | 137328160
| Eastern Grid Total |  |  |  | 12041 | 5213 | 104246425
| Western Grid Total |  |  |  | 4701 | 1981 | 33081735
| National Grid Total |  |  |  | 16742 | 7194 | 137328160
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-12-16 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4356 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2365 | MW
i) Dhaka area |  |  | 2206 | MW | i) Khulna area |  |  | 888 | MW
ii) Chittagong area |  |  | 687 | MW | ii) Rajshahi area |  |  | 774 | MW
iii) Comilla area |  |  | 644 | MW | iii) Barisal area |  |  | 191 | MW
iv) Mymensingh area |  |  | 524 | MW | iv) Rangpur area |  |  | 512 | MW
v) Sylhet area |  |  | 295 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6721 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 66 | 100 | Netrokona | 59 | 1830 | Goalpara | 21 | 2100
Munsiganj | 70 | 2000 | Jamalpur | 78 | 1930 | Central s/s | 57 | 1900
Sonargaon | 31 | 1800 | Sherpur | 64 | 1800 | Noapara | 63 | 1800
Shyampur | 120 | 100 | Srimongal | 21 | 1800 | Jessore | 98 | 1830
Bhulta | 141 | 600 | Shahjibazar | 71 | 1830 | Jhenida | 73 | 1800
Madanganj | 42 | 100 | Fenchuganj | 26 | 1800 | Bottail | 66 | 1800
Shitalakhya | 66 | 100 | Kulawara | 26 | 1800 | G.K Project | 31 | 1800
Rahim steel | 0 | 0 | Sylhet | 87 | 1800 | Faridpur | 108 | 1830
Matuail | 54 | 100 | Chatak | 18 | 1800 | Madaripur | 88 | 2000
Ghorasal | 46 | 1930 | Sunamganj | 23 | 1800 | Gopalganj | 58 | 1830
Narsingdi | 102 | 2000 | Biani Bazar | 27 | 1800 | Bagerhat | 62 | 1830
Haripur (SBU) | 69 | 200 | Comilla (S) | 106 | 2000 | Mongla | 18 | 2300
Ullon | 50 | 1800 | Comilla(N) | 85 | 1800 | Satkhira | 62 | 1800
Hasnabad | 115 | 1900 | Chandpur | 74 | 1830 | Gallamari | 31 | 1900
Magbazar | 56 | 2000 | Feni | 84 | 1800 | Magura | 32 | 2000
Maniknagar | 58 | 2000 | Chowmuhani | 118 | 2000 | Chuadanga | 65 | 1830
Bangabhaban | 8 | 1300 | Ashuganj | 36 | 2100 | Barisal | 76 | 2000
Narinda | 54 | 1800 | Daudkandi | 74 | 1830 | Patuakhali | 59 | 1900
Dhanmondi | 52 | 1800 | B.Baria | 78 | 1830 | Bhandaria | 36 | 1900
Lalbag | 46 | 100 | Ramganj | 24 | 1830 | Ishurdi | 35 | 1830
Madartek | 34 | 2000 | Madunaghat | 40 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 53 | 1800 | Hathazari | 60 | 1830 | Natore | 79 | 1800
Kalyanpur | 66 | 1800 | Khulshi | 124 | 100 | Bogra | 156 | 1830
Gulshan | 60 | 1800 | Halishahar | 82 | 1800 | Noagaon | 83 | 1830
Uttara | 31 | 1800 | Baraulia | 127 | 100 | Rajshahi | 83 | 1930
Uttara(New) | 4 | 1200 | Sikalbaha | 21 | 1200 | C.Nawabganj | 53 | 1830
Kamrangirchar | 38 | 1800 | Dohazari | 70 | 1800 | Amnura | 29 | 1830
Savar | 58 | 1800 | Cox'sbazar | 58 | 1200 | Pabna | 68 | 1900
Bhasantec | 85 | 1900 | Chandraghona | 18 | 1800 | Shahjadpur | 64 | 1800
Agargaon | 31 | 1800 | Kaptai | 3 | 1800 | Serajganj | 60 | 1830
Satmosjid | 53 | 1800 | A. Khaer Stl. | 15 | 1600 | Niyamatpur | 39 | 1800
Tongi | 80 | 1100 | Bakulia | 58 | 1830 | Joypurhat | 39 | 1830
Kabirpur | 88 | 1900 | Julda | 18 | 100 | Rangpur | 90 | 1800
Basundhara | 76 | 1800 | TK chemical | 1 | 100 | Lalmonirhat | 69 | 1800
Manikganj | 68 | 1800 | Modern Steel | 13 | 400 | Saidpur | 89 | 1830
Joydevpur | 122 | 2000 | Shahmirpur | 16 | 800 | Purbasadipur | 72 | 1800
New Tongi | 52 | 100 | Khagrachhari | 14 | 1800 | Thakurgaon | 56 | 1830
Korda | 111 | 100 | Matarbari | 19 | 1800 | Palashbari | 80 | 1800
Dhamrai | 30 | 1800 | Baroiar Hat | 18 | 1800 | Barapukuria | 33 | 1800
Tangail | 119 | 1800 | Rangamati | 8 | 1800 | Panchagar | 32 | 1800
Mymensing | 154 | 1800 | Abul Khair 230 | 166 | 800
Kishorganj | 68 | 1930 | BSRM | 44 | 200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-12-16
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 399 | 17:00 | 392 | 19:00 | Kaliakoir | 387 | 7:00 | 380 | 18:30
Bheramara | 411 | 24:00 | 401 | 13:00 | Bhulta | 406 | 22:00 | 400 | 10:00
Ashuganj(N) | 407 | 2:00 | 400 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 225 | 19:00 | 220 | 3:00
Ishurdi | 237 | 1:00 | 226 | 11:00 | Megnaghat | 235 | 24:00 | 232 | 1:00
Ashuganj | 243 | 3:00 | 238 | 13:00 | Fenchuganj | 243 | 10:00 | 237 | 3:00
Serajganj | 230 | 1:00 | 220 | 20:00 | Siddhirganj | 233 | 2:00 | 229 | 13:00
Baghabari | 232 | 24:00 | 222 | 18:00 | Maniknagar | 231 | 6:00 | 228 | 15:00
Barapukuria | 235 | 4:00 | 228 | 18:00 | Old Airport | 232 | 3:00 | 228 | 13:00
Bogra | 232 | 5:00 | 218 | 19:30 | Barisal | 237 | 5:00 | 225 | 19:30
Khulna South | 239 | 5:00 | 222 | 12:00 | AKSML | 224 | 20:00 | 218 | 12:00
Rampura | 231 | 5:00 | 228 | 12:00 | BSRM | 227 | 18:00 | 221 | 11:00
Haripur | 230 | 1:00 | 228 | 12:00 | Bibiyana | 240 | 24:00 | 233 | 20:00
Hasnabad | 233 | 5:00 | 230 | 1:00 | Bhulta | 233 | 2:00 | 229 | 12:00
Aminbazar | 233 | 4:00 | 230 | 1:00 | Ashuganj (S) | 241 | 3:00 | 237 | 12:00
Tongi | 232 | 7:00 | 229 | 11:00 | Kaliakoir | 235 | 15:00 | 231 | 1:00
Comilla (N) | 241 | 22:00 | 235 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 700 | 135 | 100 | Ramganj | 134 | 1830 | 132 | 1100
Munsiganj | 135 | 1800 | 133 | 1300 | Madanhat | 134 | 1800 | 129 | 1200
Megnaghat | 135 | 2000 | 134 | 100 | Hathazari | 135 | 1930 | 130 | 700
Shyampur | 133 | 1800 | 130 | 1200 | Khulshi | 131 | 1800 | 125 | 1100
Bhulta | 134 | 300 | 126 | 1300 | Halishahar | 134 | 1830 | 128 | 1100
Madanganj | 140 | 1800 | 136 | 1200 | Baraulia | 133 | 1800 | 127 | 600
Shitalakhya | 140 | 700 | 133 | 1300 | Sikalbaha | 133 | 1830 | 125 | 1200
Rahim steal | 0 | 0 | 0 | 0 | Dohazari | 130 | 100 | 124 | 1000
Matuail | 136 | 600 | 134 | 1200 | Cox'sbazar | 127 | 1300 | 120 | 700
Ghorasal | 140 | 100 | 140 | 200 | Chandraghona | 135 | 1930 | 129 | 1100
Narsinghdi | 137 | 1800 | 134 | 900 | Kaptai | 135 | 1830 | 131 | 700
Haripur (SBU) | 136 | 1800 | 132 | 700 | A. Khaer Stl. | 132 | 1900 | 127 | 1100
Ullon | 135 | 700 | 133 | 1700 | Bakulia | 131 | 1800 | 125 | 1100
Hasnabad | 138 | 600 | 134 | 1400 | Julda | 132 | 1830 | 125 | 1200
Magbazar | 137 | 700 | 134 | 1200 | TK Chemical | 135 | 1300 | 131 | 500
Maniknagar | 138 | 600 | 137 | 1200 | Modern Steel | 133 | 1830 | 125 | 1200
Bangabhaban | 139 | 600 | 137 | 1100 | Shahmirpur | 132 | 1800 | 126 | 1100
Narinda | 136 | 600 | 133 | 1300 | Khagrachhari | 133 | 1800 | 128 | 1100
Dhanmondi | 138 | 600 | 137 | 1200 | Matarbari | 128 | 100 | 120 | 1100
Lalbag | 139 | 600 | 137 | 1100 | Baroiar Hat | 133 | 200 | 130 | 1300
Madartek | 136 | 600 | 133 | 1300 | Rangamati | 133 | 200 | 129 | 800
Mirpur | 134 | 400 | 131 | 1600 | Goalpara | 137 | 100 | 127 | 1200
Kalyanpur | 137 | 300 | 135 | 1300 | Central s/s | 136 | 600 | 125 | 1200
Gulshan | 135 | 400 | 133 | 1100 | Noapara | 136 | 500 | 123 | 1200
Uttara | 138 | 100 | 136 | 1100 | Jessore | 132 | 300 | 120 | 1200
Uttara(New) | 136 | 600 | 132 | 1300 | Jhenida | 136 | 400 | 125 | 1200
Kamrangirchar | 138 | 400 | 136 | 1300 | Bottail | 140 | 400 | 130 | 1200
Savar | 134 | 200 | 132 | 1100 | G.K.Project | 143 | 200 | 137 | 1200
Bhasantec | 138 | 300 | 135 | 1200 | Faridpur | 136 | 500 | 127 | 1900
Agargaon | 132 | 400 | 130 | 1200 | Madaripur | 136 | 2300 | 127 | 1930
Satmosjid | 138 | 300 | 135 | 1200 | Gopalganj | 136 | 400 | 125 | 1930
Tongi | 140 | 800 | 137 | 1800 | Bagerhat | 135 | 500 | 126 | 1200
Kabirpur | 135 | 700 | 131 | 1900 | Mongla | 135 | 600 | 124 | 1200
Basundhara | 131 | 300 | 128 | 1600 | Satkhira | 136 | 200 | 125 | 1200
Manikganj | 140 | 700 | 137 | 1830 | Gallamari | 138 | 400 | 127 | 1200
Joydevpur | 142 | 1800 | 138 | 1830 | Magura | 136 | 500 | 125 | 1200
New Tongi | 140 | 600 | 137 | 1300 | Chuadanga | 133 | 300 | 121 | 1200
Kodda | 140 | 1800 | 136 | 2000 | Barisal | 139 | 600 | 131 | 2000
Dhamrai | 135 | 300 | 131 | 1900 | Patuakhali | 135 | 300 | 125 | 1930
Tangail | 136 | 300 | 132 | 1930 | Bhandaria | 135 | 100 | 128 | 1200
Mymensing | 136 | 400 | 130 | 1930 | Ishurdi | 142 | 300 | 134 | 1930
Kishorganj | 137 | 400 | 132 | 2000 | Ruppur Paromanobik | 142 | 700 | 136 | 1200
Netrokona | 137 | 500 | 130 | 2000 | Natore | 139 | 300 | 131 | 1200
Jamalpur | 133 | 1100 | 125 | 1930 | Bogra | 137 | 100 | 129 | 1900
Sherpur | 132 | 500 | 122 | 1930 | Noagaon | 135 | 400 | 125 | 1930
Srimongal | 140 | 1800 | 137 | 100 | Rajshahi | 135 | 100 | 128 | 1200
Shahjibazar | 139 | 300 | 137 | 500 | C.Nawabganj | 130 | 100 | 124 | 1100
Fenchuganj | 135 | 100 | 133 | 1100 | Amnura | 135 | 1700 | 123 | 1200
Khulawara | 135 | 700 | 134 | 100 | Pabna | 137 | 100 | 130 | 1830
Sylhet | 135 | 500 | 133 | 1600 | Shahjadpur | 143 | 100 | 138 | 1100
Chatak | 135 | 1000 | 133 | 1700 | Serajganj | 138 | 100 | 130 | 1830
Sunamganj | 135 | 300 | 132 | 1700 | Niyamatpur | 135 | 400 | 123 | 1930
Biani Bazar | 134 | 200 | 133 | 100 | Joypurhat | 136 | 100 | 125 | 1930
Cumilla(s) | 132 | 100 | 128 | 1800 | Rangpur | 134 | 500 | 121 | 1800
Cumilla(n) | 143 | 1500 | 139 | 1300 | Lalmonirhat | 131 | 600 | 115 | 1800
Chandpur | 139 | 2100 | 138 | 800 | Saidpur | 133 | 500 | 121 | 1800
Feni | 135 | 2300 | 131 | 1600 | Purbasadipur | 132 | 200 | 118 | 2000
Chowmuhani | 133 | 900 | 130 | 1300 | Thakurgaon | 130 | 400 | 110 | 1800
Ashuganj | 142 | 400 | 140 | 2000 | Palashbari | 133 | 400 | 122 | 1930
Daudkandi | 138 | 800 | 136 | 1100 | Barapukuria | 135 | 400 | 128 | 1800
B.Baria | 139 | 1800 | 137 | 100 | Panchagar | 130 | 600 | 106 | 1930

## L-Curve
Date | 2018-12-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 500 | 4177 | 1282 | 5459 |  |  |  | QF-LDC-12
0:30 | 510 | 4303 | 1226.5 | 5529.5 | Date: | 2018-12-16
1:00 | 520 | 4429 | 1171 | 5600
1:30 | 510 | 4304.5 | 1158 | 5462.5
2:00 | 500 | 4180 | 1145 | 5325
2:30 | 430 | 4070.5 | 1116 | 5186.5 | [5 empty] | Gen. at Eve. Peak | 7194 | 7194 MW (19:00 )
3:00 | 360 | 3961 | 1087 | 5048 | [6 empty] | 19:00
3:30 | 350 | 3816.5 | 1154 | 4970.5 | [5 empty] | Gen. at Day Peak | 5456.3 | 5456.3 MW (12:00 )
4:00 | 340 | 3672 | 1221 | 4893 | [6 empty] | 12:00
4:30 | 315 | 3682.5 | 1202 | 4884.5 | [5 empty] | Highest Generation | 7194
5:00 | 290 | 3693 | 1183 | 4876 | [6 empty] | 19:00
5:30 | 340 | 3748.5 | 1189 | 4937.5
6:00 | 390 | 3804 | 1195 | 4999
6:30 | 435 | 3832.55 | 1184 | 5016.55
7:00 | 480 | 3861.1 | 1173 | 5034.1
7:30 | 530 | 3962.3 | 1179.5 | 5141.8
8:00 | 580 | 4063.5 | 1186 | 5249.5
8:30 | 565 | 4055 | 1208 | 5263
9:00 | 550 | 4046.5 | 1230 | 5276.5
9:30 | 535 | 4035.5 | 1232 | 5267.5
10:00 | 520 | 4024.5 | 1234 | 5258.5
10:30 | 535 | 4077.85 | 1194 | 5271.85
11:00 | 550 | 4131.2 | 1154 | 5285.2
11:30 | 575 | 4181.75 | 1189 | 5370.75
12:00 | 600 | 4232.3 | 1224 | 5456.3
12:30 | 600 | 4325.65 | 1240 | 5565.65
13:00 | 600 | 4419 | 1256 | 5675
13:30 | 550 | 4282.9 | 1250.5 | 5533.4
14:00 | 500 | 4146.8 | 1245 | 5391.8
14:30 | 470 | 4055.35 | 1187.5 | 5242.85
15:00 | 440 | 3963.9 | 1130 | 5093.9
15:30 | 445 | 3947.85 | 1103 | 5050.85
16:00 | 450 | 3931.8 | 1076 | 5007.8
16:30 | 450 | 4054.45 | 1160.5 | 5214.95
17:00 | 450 | 4177.1 | 1245 | 5422.1
17:30 | 565 | 4590.05 | 1570 | 6160.05
18:00 | 680 | 5003 | 1895 | 6898
18:30 | 670 | 5108 | 1938 | 7046
19:00 | 660 | 5213 | 1981 | 7194
19:30 | 680 | 5245 | 1944 | 7189
20:00 | 630 | 5256 | 1920 | 7176 |  |  |  | Executive Engineer
20:30 | 620 | 5267 | 1877 | 7144 |  |  |  | Network Operation Division
21:00 | 610 | 5278 | 1834 | 7112
21:30 | 585 | 5074 | 1736.5 | 6810.5
22:00 | 560 | 4870 | 1639 | 6509 |  |  |  |  | Page 6 of 7
22:30 | 500 | 4665 | 1569 | 6234
23:00 | 440 | 4460 | 1499 | 5959
23:30 | 470 | 4318.5 | 1390.5 | 5709
24:00 | 500 | 4177 | 1282 | 5459
7194 MW (19:00 )
5456.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-12-16 |  | Energy | 137328160
[10 empty] | 2018-12-16 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3657 | 501 | 826 | 141 | 149 | 75 | 34 | 0 | 76
0:30 | 3762.5 | 402.5 | 902.5 | 146 | 149 | 75 | 17 | 0 | 75 | Date: | 2018-12-16
1:00 | 3868 | 304 | 979 | 151 | 149 | 75 | 0 | 0 | 74
1:30 | 3788.5 | 303.5 | 959.5 | 114 | 149 | 75 | 0 | 0 | 73 | [7 empty] | Total Energy | 137.3282 | Total Energy Gen 137.328 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 137.328 MKWHr
2:00 | 3709 | 303 | 940 | 77 | 149 | 75 | 0 | 0 | 72 | [7 empty] | Energy not Served | 0
2:30 | 3624 | 303.5 | 899 | 64 | 149 | 75 | 0 | 0 | 72 | [7 empty] | Energy Requirement | 137.3282
3:00 | 3539 | 304 | 858 | 51 | 149 | 75 | 0 | 0 | 72
3:30 | 3494 | 304 | 835.5 | 42 | 149 | 75 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3449 | 304 | 813 | 33 | 149 | 75 | 0 | 0 | 70
4:30 | 3444.5 | 304 | 813 | 29 | 149 | 75 | 0 | 0 | 70
5:00 | 3440 | 304 | 813 | 25 | 149 | 75 | 0 | 0 | 70
5:30 | 3478 | 304 | 835.5 | 25 | 149 | 76 | 0 | 0 | 70
6:00 | 3516 | 304 | 858 | 25 | 149 | 77 | 0 | 0 | 70
6:30 | 3503 | 303.5 | 888.5 | 25 | 149 | 77 | 0 | 0 | 70 |  |  |  |  | Coal
7:00 | 3490 | 303 | 919 | 25 | 149 | 77 | 0 | 0 | 70
7:30 | 3562.5 | 303.5 | 951 | 25 | 149 | 77 | 0 | 0 | 69 |  |  |  | Oil |  |  |  | ,
8:00 | 3635 | 304 | 983 | 25 | 149 | 77 | 0 | 0 | 68
8:30 | 3626.5 | 304 | 983 | 41.5 | 149 | 77 | 0 | 0 | 71
9:00 | 3618 | 304 | 983 | 58 | 149 | 77 | 0 | 0 | 74
9:30 | 3576 | 328.5 | 973 | 70 | 149 | 77 | 4.5 | 0 | 74
10:00 | 3534 | 353 | 963 | 82 | 149 | 77 | 9 | 0 | 74
10:30 | 3550 | 353 | 958.5 | 82 | 149 | 77 | 9 | 0 | 75
11:00 | 3566 | 353 | 954 | 82 | 149 | 77 | 9 | 0 | 76
11:30 | 3628 | 353 | 975 | 82 | 149 | 77 | 9 | 0 | 78
12:00 | 3690 | 353 | 996 | 82 | 149 | 77 | 9 | 0 | 80
12:30 | 3765.5 | 341.5 | 1038.5 | 82 | 149 | 77 | 12.5 | 0 | 80
13:00 | 3841 | 330 | 1081 | 82 | 149 | 77 | 16 | 0 | 80
13:30 | 3841 | 330 | 1081 | 82 | 149 | 77 | 16 | 0 | 80
14:00 | 3841 | 330 | 1081 | 82 | 149 | 77 | 16 | 0 | 80
14:30 | 3707.5 | 330 | 945 | 69.5 | 149.5 | 77.5 | 16 | 0 | 77
15:00 | 3574 | 330 | 809 | 57 | 150 | 78 | 16 | 0 | 74
15:30 | 3535 | 330.5 | 803 | 57 | 149.5 | 78 | 17 | 0 | 75
16:00 | 3496 | 331 | 797 | 57 | 149 | 78 | 18 | 0 | 76
16:30 | 3552 | 339.5 | 838 | 133.5 | 149 | 78 | 40 | 0 | 82
17:00 | 3608 | 348 | 879 | 210 | 149 | 78 | 62 | 0 | 88
17:30 | 3670 | 508 | 1044 | 459 | 149 | 78 | 156 | 0 | 96
18:00 | 3732 | 668 | 1209 | 708 | 149 | 78 | 250 | 0 | 104
18:30 | 3859 | 668 | 1333.5 | 640 | 149.5 | 78 | 214 | 0 | 104
19:00 | 3986 | 668 | 1458 | 572 | 150 | 78 | 178 | 0 | 104
19:30 | 4025 | 668 | 1471 | 553 | 150 | 78 | 140 | 0 | 104
20:00 | 4024 | 668 | 1520 | 513 | 150 | 77 | 118 | 0 | 106
20:30 | 4048.5 | 668.5 | 1508 | 482 | 149.5 | 76.5 | 106 | 0 | 105
21:00 | 4073 | 669 | 1496 | 451 | 149 | 76 | 94 | 0 | 104
21:30 | 3978.5 | 675 | 1367 | 394 | 148 | 75.5 | 72.5 | 0 | 100
22:00 | 3884 | 681 | 1238 | 337 | 147 | 75 | 51 | 0 | 96
22:30 | 3826.5 | 680.5 | 1091.5 | 280 | 147 | 75 | 42.5 | 0 | 91
23:00 | 3769 | 680 | 945 | 223 | 147 | 75 | 34 | 0 | 86
23:30 | 3713 | 590.5 | 885.5 | 182 | 148 | 75 | 34 | 0 | 81 | Max Temp. in Dhaka |  | 26.5° C
24:00 | 3657 | 501 | 826 | 141 | 149 | 75 | 34 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 137.328 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 137.328 MKWHr
Note on W13: Author:

## Generation
2018-12-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 78 |  | 78 | 78 | 77 | 76 | 75 | 75 | 75 | 1767585
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4400000
5 | Raozan 25 MW (RPCL) | [16 empty] | 8 | 25 |  | 26 | 26 | 25 | 26 | 25 | 8 | 0 | 144000
| Teknaf Solartech 20MW | [6 empty] | 1 | 8.2 | 13 | 16.7 | 17.9 | 18.4 | 16.8 | 9.7 | 5.4 | 5.6 | 0.1 | 0 | [8 empty] | 122860
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 10 | 68 |  | 68 | 68 | 68 | 68 | 51 | 34 | 34 | 401733
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 8 |  | 0 | 0 | [5 empty] | 4464
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 97 | 63 | 36 | 102 | 60 | 60 | 55 | 60 | 60 | 32 | 39 | 39 | 39 | 38 | 37 | 37 | 37 | 37 |  | 62 | 62 | 62 | 100 | 37 | 32 | 37 | 1350000
17 | Siddhirganj CCPP-335 MW | 150 | 120 | 120 | 173 | 140 | 140 | 140 | 140 | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 155 | 160 | 160 | 160 | 160 | 120 | 120 | 3383510
18 | Summit Gazipur -2 | [16 empty] | 3 | 15 |  | 0 | [6 empty] | 20073
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 895000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | [9 empty] | 0 | 100 | 140 | 150 | 200 | 200 | 255 | 253 | 253 |  | 253 | 253 | 253 | 253 | 225 | 225 | 224 | 2720820
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 330 | 300 | 270 | 0 | 70 | 95 | 135 | 175 | 175 | 175 | 175 | 175 | 210 | 210 | 230 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4458218
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 80 |  | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 2147215
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj Engines TSK | 37 | 34 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 32 |  | 37 | 34 | 34 | 40 | 40 | 40 | 40 | 511848
33 | Ashuganj CCPP 225 MW | 192 | 185 | 183 | 183 | 190 | 196 | 182 | 195 | 185 | 184 | 155 | 130 | 214 | 183 | 183 | 205 | 186 | 204 |  | 185 | 185 | 184 | 185 | 184 | 185 | 185 | 4491000
34 | Ashuganj CCPP(South) | 309 | 309 | 309 | 309 | 327 | 327 | 309 | 338 | 309 | 309 | 301 | 298 | 280 | 268 | 272 | 268 | 276 | 264 |  | 300 | 300 | 300 | 312 | 298 | 301 | 272 | 7274500
| Ashuganj CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 220 | 220 | 220 | 220 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6248900
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 153600
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 100 | 95 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2343000
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | [14 empty] | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 92400
39 | Haripur 412 MW CCPP | 348 | 348 | 315 | 300 | 300 | 335 | 345 | 350 | 350 | 345 | 360 | 355 | 355 | 295 | 280 | 270 | 270 | 290 |  | 340 | 353 | 348 | 350 | 350 | 350 | 325 | 8083460
40 | Meghnaghat CCPP 450MW | 370 | 350 | 330 | 380 | 380 | 380 | 360 | 380 | 380 | 360 | 330 | 330 | 360 | 320 | 320 | 320 | 350 | 350 |  | 350 | 350 | 350 | 380 | 380 | 350 | 330 | 8585250
41 | Haripur Power CCPP 360MW | 300 | 300 | 260 | 300 | 300 | 300 | 252 | 300 | 308 | 301 | 289 | 331 | 350 | 276 | 267 | 255 | 304 | 305 |  | 305 | 307 | 308 | 336 | 335 | 302 | 262 | 7190000
42 | Mymensingh RPCL 210MW | 214 | 183 | 171 | 149 | 149 | 150 | 150 | 151 | 150 | 169 | 165 | 203 | 205 | 204 | 177 | 153 | 188 | 207 |  | 208 | 209 | 210 | 208 | 212 | 213 | 180 | 4251640
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 30 | 30 | 30 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1237000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 40 | 40 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1484040
46 | Shajibazar 330 MW | 290 | 290 | 302 | 290 | 299 | 294 | 286 | 302 | 288 | 290 | 288 | 305 | 316 | 288 | 289 | 278 | 256 | 288 |  | 286 | 285 | 290 | 290 | 291 | 285 | 280 | 6689000
47 | Shahjibazar GT: Unit- 8, 9 | 63 | 63 | 67 | 40 | 40 | 52 | 40 | 52 | 67 | 40 | 62 | 63 | 65 | 40 | 40 | 51 | 55 | 51 |  | 60 | 59 | 61 | 66 | 58 | 54 | 57 | 1322000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 |  | 86 | 86 | 86 | 5 | 5 | 5 | 5 | 401280
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 5 | 5 | 5 | 49 |  | 49 | 49 | 49 | 49 | 49 | 5 | 5 | 731520
50 | Sylhet GT 150 MW | 78 | 78 | 80 | 78 | 78 | 78 | 77 | 78 | 80 | 80 | 98 | 98 | 99 | 97 | 78 | 78 | 78 | 77 |  | 78 | 78 | 77 | 78 | 77 | 80 | 80 | 2043040
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 3 | 3 | 3 | 3 | 3 | 3 | 46 | 47 | 47 | 44 | 45 | 44 | 45 | 46 | 5 | 6 | 6 | 47 |  | 48 | 48 | 48 | 49 | 48 | 6 | 6 | 636260
53 | Sylhet (Desh) 10MW | [16 empty] | 0 | 9 |  | 9 | 9 | 9 | 0 |  |  |  | 27540
54 | Hobiganj 11MW | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219168
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 49 | 50 | 48 | 50 | 5 | 5 | 5 | 266400
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 25 |  | 25 | 24 | 24 | 25 | 0 |  |  | 549840
57 | Summit Bibiana- 2
58 | Southern 55MW | 0 | [16 empty] | 17 |  | 17 | 17 | 0 |  |  |  |  | 51000
59 | Sikalbaha (Energis) | 40 | 40 | 24 | 16 | 8 | 8 | 8 | 8 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 820800
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 534624
61 | Narshingdi (Doreen) | 0 | [7 empty] | 0 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 0 |  |  | 252828
62 | Tangail (Doreen) 22MW | 0 | [5 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 9 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 0 |  |  | 291564
63 | Tripura | 74 | 72 | 72 | 70 | 70 | 70 | 70 | 68 | 74 | 74 | 76 | 80 | 80 | 80 | 74 | 76 | 88 | 104 |  | 104 | 104 | 106 | 104 | 96 | 86 | 76 | 1929600
64 | Malancha, Ctg. EPZ (United) | 30 | 32 | 32 | 32 | 32 | 32 | 30 | 26 | 0 |  |  |  | 6 | 6 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 22 | 22 | 23 | 22 | 431040
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512136
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195660
67 | Jangalia (Summit) 33MW | [8 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 21 |  | 33 | 33 | 33 | 0 |  |  |  | 198500
68 | Summit Cumilla 25MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 16 | 16 | 22 | 22 | 12 | 12 | 15 | 22 |  | 22 | 22 | 22 | 15 | 15 | 15 | 22 | 445520
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 26 |  | 32 | 32 | 32 | 32 | 32 | 32 | 22 | 731700
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790403
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603900
73 | Ghorashal (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 51 |  | 82 | 92 | 101 | 101 | 101 | 13 | 13 | 646091
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [16 empty] | 3 | 23 |  | 0 | [6 empty] | 32208
79 | Kodda 149MW
80 | Jamalpur 95MW | [16 empty] | 5 | 31 |  | 21 | 0 | 0 |  |  |  |  | 72000
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 50 |  | 85 | 85 | 85 | 85 | 5 | 5 | 5 | 414680
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | 40 | 20 | 0 | [14 empty] | 40 |  | 40 | 40 | 81 | 82 | 40 | 40 | 0 | 562912
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [16 empty] | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 51480
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 13 |  | 21 | 21 | 21 | 21 | 5 | 5 | 5 | 176000
93 | Ashuganj (Midland) 51MW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 17 |  | 51 | 51 | 51 | 51 | 7 | 7 | 7 | 366841
94 | Gagnagar (Orion) | [16 empty] | 5 | 7 |  | 7 | 7 | 7 | 7 | 0 |  |  | 56592
95 | Patenga 50MW | 0 | [15 empty] | 8 | 26 |  | 48 | 40 | 36 | 19 | 18 | 0 |  | 174240
96 | Chattogram ECPV 108 MW | 0
97 | Katpotti 51 MW | [17 empty] | 4 |  | 0 | 0 | [5 empty] | 13248
98 | Bosila 108MW | 0 | [15 empty] | 6 | 8 |  | 0 | [6 empty] | 3840
99 | Madanganj-55 MW | [16 empty] | 0 | 15 |  | 15 | 15 | 15 | 15 | 0 |  |  | 86885
100 | Northern 55 MW | [17 empty] | 18 |  | 0 | [6 empty] | 27380
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 0 | 0 | 40 | 70 | 70 | 90 | 100 | 130 | 130 | 163 | 130 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 2513168
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.3 | 0.5 | 0.8 | 1.3 | 1.9 | 2.2 | 1.1 | 0.5 | 0.2 | 0 | [9 empty] | 8500
103 | Banco Energy 54MW | 0 | [15 empty] | 6 | 18 |  | 18 | 18 | 0 | 18 | 18 | 0 |  | 80280
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 14 | 14 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 230400
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [17 empty] | 23 |  | 0 | [6 empty] | 23040
115 | Juldah 100 MW Unit-3 | 50 | 30 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 90 |  | 90 | 100 | 100 | 100 | 100 | 80 | 60 | 931200
116 | Chandpur Desh 200MW | 54 | 0 | [14 empty] | 8 | 52 |  | 51 | 51 | 51 | 52 | 67 | 80 | 34 | 447000
117 | Midland 150MW | [16 empty] | 5 | 18 |  | 0 | [6 empty] | 36800
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4429 | 4180 | 3961 | 3672 | 3693 | 3804 | 3861.1 | 4063.5 | 4046.5 | 4024.5 | 4131.2 | 4232.3 | 4419 | 4146.8 | 3963.9 | 3931.8 | 4177.1 | 5003 |  | 5213 | 5245 | 5256 | 5278 | 4870 | 4460 | 4177 | 104246425
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [16 empty] | 17 | 90 |  | 90 | 90 | 90 | 35 | 0 |  |  | 339360
130
131
132
133
| Summit Barisal 110 MW | [16 empty] | 16 | 32 |  | 0 | [6 empty] | 41280
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 12 | 12 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 11 | 11 | 12 | 31 |  | 97 | 97 | 97 | 95 | 38 | 11 | 11 | 594329
| Bhola CCPP 194MW | 187 | 188 | 161 | 188 | 188 | 188 | 180 | 188 | 188 | 158 | 186 | 186 | 187 | 180 | 179 | 185 | 182 | 172 |  | 187 | 184 | 186 | 187 | 172 | 163 | 181 | 4461328
140 | Bhola (Venture) 33MW | 21 | 20 | 20 | 14 | 14 | 19 | 19 | 17 | 16 | 16 | 18 | 18 | 14 | 18 | 18 | 17 | 19 | 25 |  | 25 | 25 | 25 | 25 | 23 | 23 | 22 | 451500
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [16 empty] | 8 | 40 |  | 40 | 40 | 40 | 40 | 0 |  |  | 175500
143 | Gopalganj Peaking | [15 empty] | 2 | 28 | 50 |  | 20 | 20 | 20 | 0 |  |  |  | 130432
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 304 | 303 | 304 | 304 | 304 | 304 | 303 | 304 | 304 | 353 | 353 | 353 | 330 | 330 | 330 | 331 | 348 | 668 |  | 668 | 668 | 668 | 669 | 681 | 680 | 501 | 10050182
147 | Bheramara 360 MW | 300 | 300 | 280 | 360 | 320 | 320 | 300 | 300 | 300 | 300 | 180 | 250 | 300 | 298 | 240 | 200 | 260 | 230 |  | 306 | 310 | 306 | 308 | 310 | 250 | 250 | 7094880
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 149 | 149 |  | 150 | 150 | 150 | 149 | 147 | 147 | 149 | 3675100
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 180 | 158 | 148 | 180 | 182 | 189 | 179 | 185 | 202 | 178 | 188 | 188 | 188 | 185 | 171 | 150 | 159 | 154 |  | 178 | 178 | 178 | 180 | 178 | 182 | 153 | 4420373
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 5 | 5 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 385920
163 | Bogra (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 125388
164 | Ullapara (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 180504
165 | Amnura 50MW | [17 empty] | 40 |  | 40 | 40 | 40 | 30 | 0 |  |  | 172120
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking | [16 empty] | 15 | 40 |  | 23 | 0 | 0 |  |  |  |  | 71271
169 | Rajlanka 52 MW | [7 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 8 | 52 |  | 52 | 52 | 52 | 52 | 52 | 8 | 0 | 416640
170 | Chapainawabganj-100 MW | [8 empty] | 0 | 9 | 9 | 9 | 16 | 16 | 16 | 16 | 9 | 52 |  | 52 | 52 | 30 | 26 | 0 |  |  | 239628
171
172
173 | Rangpur GT | [17 empty] | 17 |  | 0 | [6 empty] | 25000
175 | Saidpur GT | [17 empty] | 15 |  | 15 | [6 empty] | 31000
176
177
178
178 | Western Zone Total | 1171 | 1145 | 1087 | 1221 | 1183 | 1195 | 1173 | 1186 | 1230 | 1234 | 1154 | 1224 | 1256 | 1245 | 1130 | 1076 | 1245 | 1895 |  | 1981 | 1944 | 1920 | 1834 | 1639 | 1499 | 1282 | 33081735