## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-09-2026 | during | 24-09-2026 | during | 24-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 366 | 354 | 412 | 412 | 375 | 375 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 342 | 299 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 18 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 307 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 31 | 31 | 149.36 | 149.36 | 30 | 132 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 17 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12.2 | 13 | 33 | 33 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 33 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 245 | 130 | 300 | 300 | 154 | 245 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 69 | 144 | 149 | 149 | 52 | 133 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 52 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 415 | 450 | 584 | 584 | 526 | 526 | AGC, Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 17 | 68 | 143.42 | 143.42 | 51 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2081.2 | 2276 | 5478.16 | 5449.16 | 2114.5 | 2698.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 7 | 8 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 6 | 6 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 221 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 38 | 0 | 0 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 12 | 100 | 100 | 12 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 16 | 25 | 30 | 25 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 15 | 24 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.44 | 0 | 3.18 | 0 | 3.18 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 64 | 51 | 300 | 300 | 68 | 68 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 30 | 17 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 121 | 17 | 163 | 163 | 65 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 22 | 27 | 46 | 35 | 46 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1050 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3121.44 | 3153.36 | 4123.14 | 4145.96 | 3260.18 | 3546.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 194 | 203 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 353 | 335 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 290 | 310 | 342.01 | 342.01 | 307 | 307 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 39 | 41.65 | 41.65 | 20 | 20.01 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 5 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 103 | 8 | 195 | 195 | 25 | 25 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 102 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 0 | 14 | 14 | 14 | 14 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 107 | 107 | 163 | 163 | 140 | 140 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 112 | 34 | 200 | 200 | 120 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 74 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 9 | 25 | 52.2 | 52.2 | 0 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 50 | 17 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 65 | 74 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 46 | 115 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1941 | 1904 | 2746.44 | 2672.44 | 1991.26 | 2225.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-09-2026 | during | 24-09-2026 | during | 24-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.27 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.7 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 163 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.77 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 266.74 | 279 | 538.1 | 546.5 | 268.6 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 12 | 28 | 0 | 0 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 28 | 40 | 40 | 40 | 40 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 95 | 95 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 30 | 30 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 295 | 341 | 341 | 295 | 295 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 142 | 274 | 350 | 380 | 350 | 380
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 390 | 400 | 383 | 383 | 383 | 383
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 979 | 1227 | 1316 | 1346 | 1424 | 1454
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 774 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 15 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 9 | 0 | 33 | 0 | 33 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 220 | 220 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1015 | 1015 | 1015 | 1015 | 950 | 950 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1981 | 1901 | 2828 | 2795 | 2566 | 2565
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 951 | 1100 | 1000 | 1100 | 1000 | 1100 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 96 | 32 | 110 | 110 | 32 | 48 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 86 | 115 | 120 | 120 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 580 | 580 | 580 | 580 | 570 | 570 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 200 | 200 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.26 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2257.26 | 2371 | 2488 | 2587 | 2110 | 2225
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 21.56 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 125 | 139 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 398 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 37 | 50 | 113 | 113 | 50 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.98 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 818.08 | 1313.05 | 800 | 1300 | 800 | 1300 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 31.35 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 56 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1544.97 | 2204.05 | 2607.91 | 2889.99 | 1798.71 | 2301.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 44 | 49 | 49 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 155 | 153 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 62 | 35 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 73 | 0 | 157.91 | 0 | 157.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 419.9 | 345 | 649.91 | 457 | 560.91 | 447
System Total |  |  |  |  | 28843.2 | 28692.211 | 14592.51 | 15660.41 | 22775.66 | 22889.05 | 16094.16 | 17752.59
Forecast Scenario (24-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15830 |  | 849.95 |  | 16720
|  |  |  | 1:00 | 14880 |  | 1231.95 |  | 16170
|  |  |  | 2:00 | 14810 |  | 467.95 |  | 15300
|  |  |  | 3:00 | 14580 |  | 420.2 |  | 15020
|  |  |  | 4:00 | 14060 |  | 391.55 |  | 14470
|  |  |  | 5:00 | 13660 |  | 334.25 |  | 14010
|  |  |  | 6:00 | 13400 |  | 410.65 |  | 13830
|  |  |  | 7:00 | 13320 |  | 296.05 |  | 13630
|  |  |  | 8:00 | 13150 |  | 248.3 |  | 13410
|  |  |  | 9:00 | 13200 |  | 305.6 |  | 13520
|  |  |  | 10:00 | 13600 |  | 343.8 |  | 13960
|  |  |  | 11:00 | 13900 |  | 362.9 |  | 14280
|  |  |  | 12:00 | 14400 |  | 496.6 |  | 14920
|  |  |  | 13:00 | 14640 |  | 439.3 |  | 15100
|  |  |  | 14:00 | 14500 |  | 429.75 |  | 14950
|  |  |  | 15:00 | 14660 |  | 410.65 |  | 15090
|  |  |  | 16:00 | 14290 |  | 382 |  | 14690
|  |  |  | 17:00 | 14100 |  | 534.8 |  | 14660
|  |  |  | 18:00 | 14830 |  | 439.3 |  | 15290
|  |  |  | 18:30 | 15620 |  | 66.85 |  | 15690
|  |  |  | 19:00 | 15920 |  | 105.05 |  | 16030
|  |  |  | 19:30 | 15950 |  | 143.25 |  | 16100
|  |  |  | 20:00 | 15800 |  | 95.5 |  | 15900
|  |  |  | 21:00 | 15670 |  | 28.65 |  | 15700
|  |  |  | 22:00 | 15610 |  | 85.95 |  | 15700
|  |  |  | 23:00 | 15590 |  | 200.55 |  | 15800
Probable Maximum Temperature: |  |  | 32.2 °C
Probable Maximum Demand at Day Peak: |  |  | 14920.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 143.25
Probable Maximum Demand at Evening Peak: |  |  | 16100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15950.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.83 MKWHr. |  | 50 | 0 | 0 | 83 | 10 | 0 | 0 | 0 | 0 | 143
*** This report is generated digitally from Operation Information System (OIS) at 08:41 hrs on 24-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-09-2026 | [28 empty] | Date: | 23-09-2026 | [28 empty] | Date: | 23-09-2026 | [28 empty] | Date: | 23-09-2026 | [28 empty] | Date: | 23-09-2026 | [16 empty] | Date: | 23-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 49 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 17 | 78 | 30 | 213 | 34 | 55 | 162 | 0 | 271 | 0 | 0 | 35 | 284 | 0 | 0 | 0 | 34 | 13 | 21 | 0 | 400 | 92 | 104 | 25 | 0 | 32 | 51 | 52 | 35 | 100 | 100 | 0 | 218 | 17 | 29 | 1050 | 35 | 0 | 6 | 8.5 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 150 | 100 | 330 | 355 | 230 | 44 | 0 | 210 | 40 | 115 | 107 | 105 | 69 | 16 | 68 | 38 | 19 | 0 | 21 | 265 | 400 | 280 | 29 | 38 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 8995.5 | 726 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1015 | 25 | 0 | 0 | 1409.35 | 0 | 38 | 0 | 113 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 155 | 48 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 280 | 114 | 180 | 0 | 1000 | 580 | 17 | 6837.35 | 15832.85 | 105.5
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 17 | 52 | 31 | 229 | 40 | 35 | 72 | 0 | 294 | 0 | 0 | 35 | 293 | 0 | 0 | 0 | 34 | 13 | 21 | 0 | 415 | 87 | 50 | 44 | 0 | 29 | 51 | 38 | 0 | 100 | 100 | 0 | 218 | 17 | 29 | 1050 | 36 | 0 | 6 | 8 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 20 | 98 | 320 | 354 | 255 | 44 | 0 | 209 | 40 | 110 | 107 | 136 | 69 | 16 | 86 | 36 | 52.2 | 0 | 22 | 282 | 400 | 330 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8653.2 | 765 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1015 | 50 | 0 | 0 | 1158.71 | 0 | 38 | 0 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 154 | 49 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 280 | 118 | 180 | 0 | 873 | 580 | 17 | 6224.71 | 14877.91 | 105.51
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 17 | 52 | 31 | 246 | 40 | 35 | 72 | 0 | 295 | 0 | 0 | 35 | 292 | 0 | 0 | 0 | 34 | 13.5 | 21 | 0 | 420 | 82 | 50 | 47 | 0 | 33 | 51 | 38 | 0 | 100 | 100 | 0 | 218 | 17 | 29 | 1050 | 35 | 0 | 6 | 8 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 12 | 98 | 320 | 354 | 255 | 44 | 0 | 205 | 40 | 108 | 107 | 136 | 73 | 16 | 86 | 36 | 52.2 | 0 | 21 | 278 | 400 | 392 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8717.7 | 765 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1015 | 52 | 0 | 0 | 916.16 | 0 | 38 | 0 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 156 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 280 | 118 | 220 | 0 | 848 | 580 | 17 | 6094.16 | 14811.86 | 105.52
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 17 | 52 | 31 | 246 | 40 | 35 | 72 | 0 | 295 | 0 | 0 | 35 | 293 | 0 | 0 | 0 | 34 | 13.5 | 21 | 0 | 405 | 90 | 50 | 46 | 0 | 48 | 51 | 38 | 0 | 12 | 100 | 0 | 220 | 17 | 29 | 1050 | 36 | 0 | 6 | 8 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 12 | 98 | 320 | 355 | 255 | 44 | 0 | 210 | 40 | 96 | 107 | 137 | 0 | 16 | 50 | 34 | 16 | 0 | 14 | 268 | 400 | 392 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8485.5 | 811 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1015 | 52 | 0 | 0 | 831.13 | 0 | 39 | 0 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 117 | 220 | 0 | 861 | 580 | 17 | 6097.13 | 14582.63 | 105.53
04:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 17 | 52 | 31 | 246 | 0 | 35 | 72 | 0 | 298 | 0 | 0 | 35 | 302 | 0 | 0 | 0 | 34 | 13.5 | 21 | 0 | 425 | 0 | 51 | 12 | 0 | 28 | 51 | 38 | 0 | 0 | 100 | 0 | 220 | 17 | 29 | 1050 | 35 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1165 | 0 | 13 | 98 | 270 | 355 | 270 | 44 | 0 | 211 | 40 | 69 | 107 | 120 | 0 | 16 | 17 | 32 | 0 | 0 | 14 | 270 | 400 | 392 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8171.5 | 812 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 824.42 | 0 | 39 | 0 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 50 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 118 | 220 | 0 | 883 | 580 | 17 | 5892.42 | 14063.92 | 105.54
05:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 35 | 17 | 52 | 31 | 95 | 0 | 0 | 72 | 0 | 308 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 34 | 13.5 | 21 | 0 | 465 | 0 | 51 | 0 | 0 | 25 | 51 | 38 | 0 | 0 | 60 | 0 | 220 | 17 | 29 | 1050 | 36 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1165 | 0 | 13 | 98 | 270 | 353 | 265 | 44 | 0 | 203 | 40 | 58 | 107 | 34 | 0 | 16 | 0 | 32 | 0 | 0 | 14 | 270 | 400 | 392 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7741.5 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 820.54 | 0 | 39 | 0 | 38 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 117 | 220 | 0 | 933 | 580 | 17 | 5913.54 | 13655.04 | 105.55
06:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 17 | 40 | 31 | 95 | 0 | 0 | 72 | 0 | 297 | 0 | 0 | 17 | 295 | 0 | 0 | 0 | 34 | 13.5 | 21 | 0 | 420 | 0 | 51 | 0 | 0 | 26 | 51 | 38 | 0 | 0 | 60 | 0.02 | 220 | 17 | 29 | 1050 | 35 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1162 | 1 | 12 | 103 | 270 | 355 | 255 | 44 | 0 | 194 | 40 | 51 | 107 | 34 | 0 | 16 | 0 | 32 | 0 | 2 | 14 | 268 | 400 | 392 | 29 | 40 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 17 | 58 | 0.09 | 66 | 0 | 0 | 0 | 9 | 7652.61 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1015 | 0 | 0 | 0 | 826.44 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 64 | 280 | 118 | 220 | 0 | 970 | 580 | 17 | 5879.46 | 13532.07 | 105.56
07:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 17 | 17 | 35 | 31 | 45 | 0 | 0 | 54 | 0 | 295 | 0 | 0 | 17 | 288 | 0 | 0 | 3 | 34 | 13.5 | 0 | 0 | 415 | 0 | 51 | 0 | 0 | 25 | 51 | 38 | 0 | 0 | 60 | 0.79 | 220 | 17 | 6 | 1050 | 40 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 3 | 13 | 107 | 270 | 354 | 245 | 44 | 0 | 192 | 40 | 51 | 107 | 17 | 0 | 16 | 0 | 24 | 0 | 9 | 14 | 272 | 400 | 392 | 29 | 40 | 0 | 2 | 16 | 0 | 86 | 0 | 0 | 0 | 0 | 17 | 58 | 1.81 | 66 | 0 | 0.1 | 2.11 | 12 | 7479.31 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 1015 | 0 | 0 | 0 | 821.07 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.84 | 12 | 25 | 0 | 6.15 | 148 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.48 | 157 | 50 | 50 | 3 | 0 | 0 | 0 | 0 | 0.6 | 14 | 0.14 | 32 | 280 | 118 | 220 | 0 | 912 | 580 | 17 | 5836 | 13315.31 | 105.57
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 35 | 31 | 45 | 0 | 0 | 54 | 0 | 300 | 0 | 0 | 17 | 300 | 0 | 0 | 14 | 17 | 13.5 | 0 | 0 | 425 | 0 | 50 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 60 | 2.23 | 220 | 17 | 2 | 1050 | 53 | 0 | 6 | 0 | 0 | 221 | 0 | 0 | 0 | 1160 | 8 | 13 | 97 | 270 | 300 | 260 | 44 | 0 | 195 | 40 | 51 | 109 | 17 | 8 | 16 | 0 | 24 | 0 | 41 | 14 | 276 | 400 | 368 | 29 | 40 | 0 | 1 | 16 | 0 | 83 | 0 | 0 | 0 | 0 | 17 | 58 | 4.4 | 67 | 0 | 0.4 | 10.86 | 12 | 7436.39 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.83 | 1015 | 0 | 0 | 0 | 833.57 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.44 | 27 | 18 | 0 | 15.44 | 148 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.49 | 157 | 50 | 35 | 6 | 0 | 0 | 0 | 0 | 1.5 | 3 | 0.33 | 32 | 280 | 116 | 180 | 0 | 905 | 580 | 17 | 5714.6 | 13150.99 | 105.58
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 17 | 35 | 31 | 45 | 0 | 0 | 54 | 0 | 307 | 0 | 0 | 17 | 303 | 0 | 0 | 18 | 17 | 13.5 | 0 | 0 | 450 | 0 | 15 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 50 | 2.73 | 220 | 17 | 5 | 1050 | 17 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 9 | 13 | 76 | 270 | 300 | 265 | 44 | 0 | 200 | 40 | 16 | 109 | 17 | 35 | 5 | 0 | 24 | 0 | 58 | 14 | 279 | 400 | 393 | 29 | 40 | 0 | 6 | 16 | 0 | 83 | 0 | 0 | 0 | 0 | 17 | 59 | 10.68 | 70 | 0 | 0.9 | 29.52 | 12 | 7468.33 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.04 | 1015 | 0 | 0 | 0 | 817.5 | 0 | 39 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 18.18 | 84 | 16 | 0 | 25.76 | 150 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.54 | 158 | 50 | 0 | 3 | 0 | 0 | 0 | 0 | 1.4 | 30 | 0.17 | 16 | 281 | 118 | 180 | 0 | 945 | 580 | 17 | 5848.59 | 13316.92 | 105.59
10:00 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 17 | 35 | 31 | 95 | 0 | 35 | 54 | 0 | 305 | 0 | 0 | 17 | 303 | 0 | 0 | 27 | 17 | 13.5 | 14 | 0 | 470 | 0 | 15 | 0 | 0 | 29 | 0 | 36 | 17 | 0 | 50 | 3.62 | 219 | 17 | 7 | 1050 | 17 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 12 | 13 | 76 | 320 | 354 | 260 | 44 | 0 | 202 | 39 | 15 | 107 | 17 | 36 | 16 | 0 | 30 | 0 | 69 | 14 | 280 | 400 | 381 | 29 | 40 | 0 | 12 | 16 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 59 | 20.15 | 115 | 0 | 1.7 | 33.46 | 12 | 7827.43 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1015 | 0 | 0 | 0 | 819.01 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 17.81 | 39 | 0 | 0 | 29.67 | 150 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.83 | 160 | 50 | 0 | 1 | 45 | 0 | 0 | 0 | 2.4 | 61 | 0.11 | 16 | 307 | 117 | 220 | 0 | 957 | 580 | 17 | 5948.83 | 13776.26 | 105.6
11:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 17 | 46 | 31 | 140 | 0 | 35 | 54 | 0 | 308 | 0 | 0 | 17 | 315 | 0 | 0 | 22 | 17 | 12.2 | 22 | 0 | 515 | 0 | 15 | 0 | 0 | 26 | 0 | 36 | 35 | 0 | 75 | 3.88 | 218 | 17 | 5 | 1050 | 17 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 1180 | 18 | 11 | 103 | 393 | 350 | 325 | 44 | 3 | 214 | 39 | 16 | 107 | 17 | 49 | 16 | 0 | 34 | 0 | 75 | 14 | 300 | 393 | 173 | 10 | 40 | 0 | 8 | 16 | 0 | 82 | 0 | 0 | 0 | 0 | 4 | 59 | 20 | 115 | 0 | 2.6 | 58.02 | 12 | 8053.7 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 1015 | 0 | 0 | 0 | 813.26 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 2.56 | 23 | 0 | 0 | 51.45 | 150 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 3.75 | 155 | 51 | 0 | 13 | 52 | 0 | 0 | 0 | 1.3 | 59 | 0.17 | 16 | 307 | 86 | 220 | 0 | 983 | 580 | 17 | 5987.49 | 14041.19 | 105.61
12:00 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 17 | 69 | 31 | 245 | 18 | 35 | 54 | 0 | 342 | 0 | 0 | 17 | 300 | 0 | 0 | 4 | 17 | 12.2 | 22 | 0 | 415 | 30 | 64 | 15 | 0 | 22 | 0 | 36 | 35 | 36 | 88 | 4.44 | 217 | 0 | 2 | 1050 | 121 | 0 | 6 | 7 | 0 | 213 | 0 | 0 | 0 | 1160 | 15 | 13 | 103 | 393 | 353 | 290 | 44 | 10 | 194 | 39 | 46 | 107 | 112 | 65 | 11 | 50 | 32 | 9 | 56 | 14 | 325 | 390 | 142 | 12 | 0 | 0 | 12 | 16 | 0 | 82 | 0 | 0 | 0 | 0 | 17 | 58 | 22.27 | 115 | 0 | 2.7 | 39.77 | 12 | 8389.38 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 9 | 1015 | 0 | 0 | 0 | 818.08 | 0 | 0 | 0 | 55 | 37 | 0 | 0 | 0 | 0 | 21.56 | 56 | 0 | 0 | 31.35 | 125 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 2.98 | 155 | 50 | 62 | 7 | 70 | 0 | 0 | 0 | 2.9 | 73 | 0.26 | 96 | 307 | 86 | 220 | 0 | 951 | 580 | 17 | 6203.13 | 14592.51 | 105.63
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 79 | 31 | 278 | 40 | 35 | 54 | 0 | 286 | 0 | 0 | 17 | 300 | 0 | 0 | 2 | 17 | 12.2 | 22 | 0 | 410 | 92 | 68 | 29 | 0 | 16 | 0 | 34 | 35 | 36 | 100 | 3.12 | 217 | 0 | 0 | 1050 | 143 | 0 | 6 | 17 | 0 | 212 | 0 | 0 | 0 | 1100 | 16 | 13 | 66 | 345 | 299 | 275 | 44 | 10 | 217 | 30 | 51 | 107 | 154 | 80 | 11 | 85 | 38 | 25 | 71 | 0 | 310 | 387 | 202 | 12 | 0 | 0 | 12 | 16 | 0 | 78 | 0 | 0 | 0 | 50 | 17 | 58 | 18 | 115 | 0 | 0.6 | 54.53 | 12 | 8483.45 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 1015 | 17 | 0 | 0 | 815.56 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 12.11 | 13 | 0 | 0 | 32.88 | 125 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 2.6 | 152 | 49 | 95 | 4 | 75 | 0 | 0 | 0 | 0.4 | 93 | 0.22 | 96 | 307 | 86 | 220 | 0 | 943 | 580 | 17 | 6158.77 | 14642.22 | 105.66
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 17 | 95 | 30 | 278 | 40 | 35 | 54 | 0 | 282 | 0 | 0 | 35 | 296 | 0 | 0 | 4 | 17 | 12.5 | 22 | 0 | 425 | 60 | 68 | 43 | 0 | 14 | 0 | 34 | 35 | 12 | 100 | 2.35 | 217 | 0 | 2 | 1050 | 126 | 0 | 7 | 17 | 0 | 212 | 0 | 0 | 0 | 1120 | 12 | 13 | 61 | 300 | 295 | 260 | 44 | 10 | 183 | 27 | 51 | 107 | 120 | 73 | 11 | 28 | 36 | 8 | 64 | 0 | 305 | 389 | 274 | 15 | 18 | 0 | 9 | 16 | 0 | 79 | 0 | 0 | 0 | 100 | 17 | 58 | 22 | 115 | 0 | 1.1 | 48.37 | 12 | 8418.32 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 27 | 1015 | 17 | 0 | 0 | 817.56 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 19.87 | 43 | 0 | 0 | 7.64 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.99 | 150 | 49 | 62 | 9 | 85 | 0 | 0 | 0 | 0.6 | 150 | 0.32 | 96 | 307 | 82 | 180 | 0 | 951 | 580 | 17 | 6178.98 | 14597.3 | 105.69
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 17 | 97 | 30 | 262 | 40 | 0 | 54 | 0 | 293 | 0 | 0 | 35 | 307 | 0 | 0 | 15 | 17 | 12.2 | 22 | 0 | 425 | 60 | 51 | 50 | 0 | 10 | 0 | 34 | 35 | 12 | 100 | 2.89 | 217 | 0 | 0 | 1050 | 120 | 0 | 9 | 17 | 0 | 212 | 0 | 0 | 0 | 1160 | 12 | 11 | 63 | 330 | 320 | 255 | 44 | 10 | 198 | 30 | 55 | 107 | 120 | 73 | 11 | 17 | 36 | 8 | 51 | 0 | 300 | 389 | 271 | 12 | 30 | 0 | 8 | 16 | 0 | 79 | 0 | 0 | 0 | 100 | 17 | 58 | 17 | 115 | 0 | 1.8 | 23.78 | 12 | 8424.67 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 24 | 1015 | 17 | 0 | 0 | 820.4 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 21.67 | 30 | 0 | 0 | 9.62 | 142 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.79 | 157 | 49 | 66 | 12 | 86 | 0 | 0 | 0 | 0.7 | 96 | 0.45 | 110 | 307 | 85 | 220 | 0 | 956 | 580 | 17 | 6234.63 | 14659.3 | 105.81
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 35 | 0 | 97 | 21 | 195 | 15 | 49 | 108 | 0 | 298 | 0 | 0 | 35 | 307 | 0 | 0 | 7 | 17 | 12 | 22 | 0 | 455 | 16 | 51 | 51 | 0 | 9 | 0 | 34 | 35 | 0 | 100 | 1.89 | 219 | 0 | 0 | 1050 | 72 | 0 | 10 | 17 | 0 | 212 | 0 | 0 | 0 | 1160 | 7 | 13 | 100 | 393 | 335 | 300 | 44 | 10 | 203 | 37 | 69 | 107 | 51 | 73 | 11 | 0 | 38 | 8 | 17 | 0 | 310 | 386 | 7 | 8 | 30 | 0 | 1 | 8 | 0 | 79 | 0 | 0 | 0 | 100 | 17 | 58 | 8 | 121 | 0 | 0.3 | 23.3 | 12 | 8153.49 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 1015 | 17 | 0 | 0 | 818.69 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 18.87 | 34 | 0 | 0 | 5.58 | 145 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0.57 | 150 | 50 | 35 | 8 | 76 | 0 | 0 | 0 | 1.1 | 31 | 0.1 | 99 | 307 | 113 | 220 | 0 | 948 | 580 | 17 | 6138.91 | 14292.4 | 105.82
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 54 | 0 | 92 | 15 | 195 | 15 | 55 | 130 | 0 | 268 | 0 | 0 | 55 | 295 | 0 | 0 | 2 | 34 | 11.5 | 22 | 0 | 445 | 16 | 51 | 24 | 0 | 19 | 0 | 40 | 54.36 | 0 | 100 | 0.67 | 219 | 0 | 8 | 1050 | 68 | 0 | 6 | 17 | 0 | 211 | 0 | 0 | 0 | 1224 | 2 | 13 | 26 | 310 | 315 | 290 | 44 | 9 | 203 | 40 | 69 | 107 | 51 | 73 | 19 | 0 | 36 | 8 | 6 | 0 | 315 | 396 | 74 | 16 | 30 | 0 | 2 | 16 | 0 | 84 | 0 | 0 | 0 | 100 | 17 | 58 | 0.68 | 123 | 0 | 0 | 2.3 | 12 | 8103.51 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 1015 | 17 | 0 | 0 | 902.89 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 5.03 | 6 | 0 | 0 | 2.67 | 145 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0.24 | 152 | 49 | 35 | 2 | 78 | 0 | 0 | 0 | 0.2 | 12 | 0.02 | 64 | 307 | 115 | 220 | 0 | 989 | 580 | 17 | 6166.05 | 14269.56 | 105.83
18:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 0 | 92 | 30 | 195 | 15 | 55 | 162 | 0 | 304 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 60 | 11.5 | 22 | 0 | 510 | 15 | 51 | 24 | 0 | 31 | 0 | 41 | 54.36 | 24 | 100 | 0 | 219 | 0 | 5 | 1050 | 102 | 0 | 6 | 17 | 0 | 211 | 0 | 0 | 0 | 1224 | 0 | 13 | 26 | 393 | 320 | 285 | 44 | 5 | 214 | 40 | 95 | 107 | 87 | 73 | 19 | 14 | 80 | 8 | 0 | 0 | 305 | 386 | 28 | 14 | 28 | 0 | 0 | 16 | 0 | 84 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 145 | 0 | 0 | 0 | 12 | 8549.86 | 774 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 1015 | 17 | 0 | 0 | 1102.71 | 0 | 0 | 0 | 100 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 154 | 48 | 55 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 307 | 114 | 220 | 0 | 1000 | 580 | 17 | 6280.71 | 14830.57 | 105.84
19:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 12 | 98 | 31 | 195 | 37 | 0 | 162 | 0 | 279 | 0 | 0 | 55 | 295 | 0 | 0 | 0 | 68 | 12 | 22 | 0 | 395 | 72 | 51 | 36 | 0 | 47 | 51 | 41 | 54.36 | 12 | 100 | 0 | 220 | 0 | 16 | 1050 | 72 | 0 | 6 | 18 | 15 | 212 | 0 | 0 | 0 | 1224 | 0 | 55 | 8 | 350 | 270 | 230 | 44 | 5 | 186 | 40 | 109 | 107 | 120 | 73 | 19 | 41 | 74 | 52.2 | 0 | 0 | 303 | 393 | 274 | 28 | 28 | 0 | 0 | 16 | 0 | 84 | 0 | 0 | 0 | 100 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 12 | 8779.56 | 773 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 1015 | 17 | 0 | 0 | 1309.65 | 0 | 32 | 0 | 113 | 50 | 0 | 100 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 143 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1100 | 580 | 17 | 6800.65 | 15580.21 | 105.84
19:30 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 17 | 149 | 31 | 130 | 30 | 55 | 162 | 0 | 290 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 68 | 12 | 22 | 0 | 430 | 17 | 51 | 30 | 0 | 21 | 51 | 45 | 54.36 | 12 | 100 | 0 | 221 | 0 | 18 | 1050 | 34 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 1224 | 0 | 100 | 8 | 365 | 330 | 280 | 44 | 5 | 201 | 36 | 115 | 107 | 34 | 74 | 19 | 17 | 76 | 25 | 0 | 0 | 290 | 398 | 274 | 28 | 28 | 0 | 0 | 16 | 0 | 85 | 0 | 0 | 0 | 100 | 17 | 87 | 0 | 171 | 0 | 0 | 0 | 12 | 8769.36 | 773 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1015 | 17 | 0 | 0 | 1313.69 | 0 | 39 | 0 | 113 | 50 | 0 | 100 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 48 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1100 | 580 | 17 | 6851.69 | 15621.05
20:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 17 | 144 | 31 | 130 | 30 | 55 | 162 | 0 | 299 | 0 | 0 | 55 | 307 | 0 | 0 | 0 | 68 | 13 | 22 | 0 | 450 | 17 | 51 | 24 | 0 | 27 | 51 | 38 | 54.36 | 12 | 100 | 0 | 220 | 0 | 16 | 1050 | 17 | 0 | 6 | 8 | 17 | 221 | 0 | 0 | 0 | 1224 | 0 | 102 | 8 | 393 | 335 | 310 | 44 | 5 | 203 | 39 | 115 | 107 | 34 | 74 | 19 | 17 | 74 | 25 | 0 | 0 | 295 | 400 | 274 | 28 | 28 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 8839.36 | 774 | 0 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1313.05 | 0 | 40 | 0 | 113 | 50 | 0 | 100 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 44 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 1100 | 580 | 17 | 6821.05 | 15660.41 | 105.85
21:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 2 | 134 | 31 | 45 | 15 | 55 | 162 | 0 | 301 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 68 | 12.5 | 22 | 0 | 430 | 17 | 51 | 11 | 0 | 32 | 51 | 38 | 54.36 | 12 | 50 | 0 | 221 | 0 | 19 | 1050 | 17 | 0 | 6 | 8 | 17 | 221 | 0 | 0 | 0 | 1224 | 0 | 100 | 8 | 393 | 320 | 300 | 44 | 5 | 222 | 40 | 50 | 107 | 17 | 74 | 19 | 17 | 54 | 25 | 0 | 0 | 285 | 400 | 274 | 28 | 28 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 8552.86 | 773 | 0 | 27 | 46 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1316.36 | 0 | 40 | 0 | 95 | 35 | 0 | 100 | 35 | 0 | 0 | 0 | 12 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 48 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 116 | 220 | 0 | 1100 | 580 | 20 | 6792.36 | 15345.22 | 105.86
22:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 54 | 15 | 134 | 31 | 45 | 15 | 55 | 162 | 0 | 313 | 0 | 0 | 55 | 314 | 0 | 0 | 0 | 68 | 12.5 | 22 | 0 | 525 | 17 | 51 | 11 | 0 | 49 | 51 | 38 | 54.36 | 12 | 50 | 0 | 221 | 0 | 23 | 1050 | 17 | 0 | 6 | 8 | 17 | 221 | 0 | 0 | 0 | 1224 | 0 | 31 | 53 | 393 | 315 | 305 | 44 | 5 | 209 | 40 | 34 | 107 | 17 | 75 | 19 | 17 | 72 | 25 | 0 | 0 | 284 | 398 | 144 | 28 | 28 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 96 | 0 | 182 | 0 | 0 | 0 | 12 | 8534.86 | 772 | 0 | 23 | 33 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1326.99 | 0 | 39 | 0 | 113 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 48 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1100 | 580 | 17 | 6785.99 | 15320.85 | 105.87
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 54 | 17 | 110 | 31 | 135 | 28 | 55 | 162 | 0 | 297 | 0 | 0 | 55 | 289 | 0 | 0 | 0 | 68 | 13 | 22 | 0 | 415 | 17 | 51 | 12 | 0 | 16 | 51 | 38 | 54.36 | 12 | 100 | 0 | 218 | 0 | 17 | 1050 | 50 | 0 | 6 | 8 | 17 | 221 | 0 | 0 | 0 | 1224 | 0 | 13 | 55 | 350 | 285 | 255 | 44 | 5 | 222 | 40 | 74 | 107 | 58 | 76 | 19 | 17 | 70 | 25 | 0 | 0 | 335 | 400 | 74 | 28 | 28 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 96 | 0 | 182 | 0 | 0 | 0 | 12 | 8544.36 | 773 | 0 | 23 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1319.9 | 0 | 39 | 0 | 113 | 71 | 0 | 100 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 116 | 220 | 0 | 1100 | 580 | 17 | 6843.9 | 15388.26 | 105.88
Total KWH | 0 | 1006080 | 653760 | 0 | 0 | 0 | 0 | 0 | 8640000 | 0 | 0 | 811440 | 376920 | 1824336 | 729600 | 3952069 | 543052 | 771055 | 2292480 | 0 | 7178676 | 0 | 0 | 847784 | 7330521 | 0 | 0 | 111501 | 913200 | 311400 | 445320 | 0 | 10879545.45 | 843055 | 1194327 | 485760 | 0 | 653760 | 670946 | 889662 | 650737 | 491520 | 2043840 | 24000 | 5295104 | 200726 | 359040 | 25250909.09 | 1614182 | 0 | 158400 | 200851.2 | 104545 | 5509785 | 0 | 0 | 0 | 28314543 | 112995 | 557018 | 1756364 | 8089500 | 8361400 | 6716000 | 1045136 | 107040 | 5027000 | 918288 | 1658880 | 2535746 | 2002560 | 1241520 | 371960 | 607620 | 1024320 | 428112 | 543845 | 189616 | 7067000 | 9485100 | 6479000 | 556000 | 715680 | 0 | 78612 | 381168 | 0 | 2003520 | 0 | 0 | 0 | 1551110 | 414360 | 1592400 | 124747 | 2683200 | 0 | 10700 | 333380 | 293280 | 201638608.74 | 20449455 | 0 | 225600 | 297728 | 0 | 0 | 0 | 0 | 0 | 728928 | 295920 | 24450912 | 374400 | 0 | 0 | 23465454 | 0 | 568937 | 0 | 1354848 | 1042368 | 0 | 595152 | 68826 | 0 | 185704 | 400647 | 292474 | 0 | 248416 | 3510636 | 0 | 0 | 0 | 0 | 0 | 9198327 | 0 | 22080 | 3832000 | 1174254 | 1448050 | 75028 | 1409836 | 0 | 0 | 0 | 13658.4 | 681840 | 1578 | 1586688 | 7113000 | 2586000 | 5157010 | 0 | 23367273 | 14155636.36 | 442800 | 150821463.76 | 352460072.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14592.51 | MW | 12:00 Hr. | Energy Generated |  |  | 352.4601 |  | MKWHr.
| Day Peak Demand |  |  | 14926.51 | MW | 12:00 Hr. | Energy Unserverd |  |  | 9.891 |  | MKWHr.
| Evening Peak Generation |  |  | 15660.41 | MW | 20:00 Hr. | Energy Demand |  |  | 362.3511 |  | MKWHr.
| Evening Peak Demand |  |  | 16256.41 | MW | 20:00 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 13150.99 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 884.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 15832.85 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.5163 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.7855 | 0 | 14.7218 | 0 | 0 | 0.1115 | 0 | 0 | 49.6187 | Gas | 124.2733 | Gas | 431637295.4565
| Chattogram Zone |  |  | 5.8688 | 53.5655 | 9.5486 | 0 | 5.2951 | 0.137 | 0 | 0.65376 | 75.0687 | Coal | 127.6585 | Coal | 918596905.9269
| Cumilla Zone |  |  | 34.9284 | 0 | 6.6853 | 0 | 0 | 0.54385 | 1.0243 | 0 | 43.1819 | HFO | 46.3755 | HFO | 958727129.696
| Mymensingh Zone |  |  | 0 | 0 | 4.9832 | 0 | 0 | 0.46883 | 0 | 0 | 5.4521 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.2386 | 0 | 0 | 0 | 0 | 0.078612 | 0 | 0 | 28.3172 | Hydro | 5.2951 | Hydro | 529510.4
| Khulna Zone |  |  | 0 | 24.4509 | 1.6267 | 0 | 0 | 0.29592 | 20.4495 | 0 | 46.8229 | Solar | 3.2647 | Solar | 51203087.508
| Barishal Zone |  |  | 7.743 | 44.6359 | 2.0295 | 0 | 0 | 0.001578 | 0 | 0 | 54.41 | Import | 44.9392 | Import | 278817151.11
| Rajshahi Zone |  |  | 12.709 | 0 | 3.9226 | 0 | 0 | 0.85685 | 23.4655 | 0 | 40.9539 | Wind | 0.65376 | Wind | 9701798.4
| Rangpur Zone |  |  | 0 | 5.0063 | 2.8579 | 0 | 0 | 0.77053 | 0 | 0 | 8.6347
| Total |  |  | 124.2733 | 127.6585 | 46.3755 | 0 | 5.2951 | 3.2647 | 44.9392 | 0.65376 | 352.4601
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431637295.4565 |  | Hydro | 529510.4
|  |  |  | Coal | 918596905.9269 |  | Solar | 51203087.508
|  |  |  | HFO | 958727129.696 |  | Import | 278817151.11
|  |  |  | HSD | 0 |  | Wind | 9701798.4
[5 empty] | Total: | 264,92,12,878 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4495 | Peak Hr Flow | 774.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43122363.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.4655 | Peak Hr Flow | 1313.05 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2051 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0243 | Peak Hr Flow | 74.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2440 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.9392 | Peak Hr Flow | 2161.05 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 68 |  | 5978
|  |  |  | Chattogram |  | 0 |  | 1424
|  |  |  | Cumilla |  | 0 |  | 1442
|  |  |  | Mymensingh |  | 357 |  | 1542
|  |  |  | Sylhet |  | 145 |  | 784
|  |  |  | Khulna |  | 0 |  | 1618
|  |  |  | Barishal |  | 0 |  | 465
|  |  |  | Rajshahi |  | 0 |  | 1500
|  |  |  | Rangpur |  | 0 |  | 936
|  |  |  | Total |  | 570 |  | 15689
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[5 empty] | Total | 300 |  |  |  | Total | 143.5
|  |  |  | Total Unavailable Capacity |  |  |  | 443.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:23 | 18:59 | Ishurdi 230/132kV S/S 230 kV Bus 2 Scheduled S/D Due to Jack bus upgradation work by GtoG
|  | 08:44 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 08:45 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
|  | 08:48 | Bhulta 132/33kV S/S GT2 HT is restored.
| 09:09 | 18:07 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to SAS & DFDR work witness
| 09:09 | 18:07 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to SAS & DFDR work witness
| 09:35 | 11:17 | Araihazar 132/33kV S/S T-1 HT Project Work S/D Due to Red hot showing at incomer-01 CT | [7 empty] | 40.0MW load
|  |  | R-Phase. | [7 empty] | interrup.
| 09:35 | 17:56 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Fire fighter (CAF)
| 09:36 | 17:55 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Fire fighter (CAF)
| 09:47 | 11:40 | Bheramara(GK) 132/33kV S/S TR-2 LT Scheduled S/D Due to Insulator replacement
| 09:48 | 11:35 | Bheramara(GK) 132/33kV S/S TR-2 HT Scheduled S/D Due to Insulator replacement
|  | 10:32 | Barishal 230/132kV S/S T-5 HT is restored.
| 10:33 | 12:25 | Bogura-Mahasthangarh 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Meter
replace. and from Mahasthangarh 132/33kV end Due to Due to Energy meter change at Bogura
132 kv grid SS.
|  | 10:33 | Barishal 230/132kV S/S T-5 LT is restored.
| 10:55 | 13:02 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Meter Replace.
| 10:55 | 11:28 | Feni 132/33kV S/S T-1(405T) LT Tripped showing O/C,E/F relays Due to For sultanpur 33KV | [7 empty] | 24.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 11:18 |  | At Manirampur SS,T-2(132/33)kv Transformer is SD due to 33 kv side Project work. Approved
by EMD.
| 11:28 | 18:17 | Mirsorai 400/230/33kV S/S Bus-1 (400kV) Project Work S/D Due to Project Work
| 12:00 |  | Day Peak Generation: 14592 MW.
| 12:05 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- ST
| 12:06 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT running
| 12:28 | 13:23 | Bogura-Mahasthangarh 132 kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due to
Due to Energy meter change at Bogura 132 kv grid SS. and from Bogura 132/33kV end Due to
Meter replace
| 12:53 |  | Sylhet 225 MW CCPP Synchronized with remarks:- GT
| 13:36 |  | At Manirampur SS,T-1(132/33)kv Transformer is charged.
| 13:44 |  | At Manirampur SS,T-2(132/33)kv Transformer SD is Withdrawn.
| 14:19 | 15:56 | Daudkandi 132/33kV S/S Transformer-1 LT Forced S/D Due to 132/33 kv Transformer-1 | [7 empty] | 50.0MW load
|  |  | Shutdown for red hot maintenance at 33 kV switchyard by Palli Bidyut Samity-3 | [7 empty] | interrup.
| 14:21 | 15:54 | Daudkandi 132/33kV S/S Transformer-1 HT Forced S/D Due to 132/33 kv Transformer-1 | [7 empty] | 50.0MW load
|  |  | Shutdown for red hot maintenance at 33 kV switchyard by Palli Bidyut Samity-3 | [7 empty] | interrup.
| 14:51 | 15:07 | Savar 132/33kV S/S T-1 LT Tripped showing OVER CURRENT RELAY relays Due to OC/EF
|  | 15:07 | Savar 132/33kV S/S T-1 LT is restored.
| 15:30 | 17:40 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Red hot maintenance at 33kv | [7 empty] | 20.0MW load
|  |  | PBS feeder. | [7 empty] | interrup.
| 15:30 | 17:40 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Red hot maintenance at 33kv | [7 empty] | 20.0MW load
|  |  | PBS feeder. | [7 empty] | interrup.
| 16:02 | 17:45 | Bhulta 132/33kV S/S GT1 LT Scheduled S/D Due to নারায়ণগঞ্জ পিবিএস-২ জিটি-০১
ট্রান্সফর্মারের ৩৩ কেভি জিআইএস বাসবারে হরিপুর-২ ফিডারের ব্রেকার প্রতিস্থাপন করার জন্য
শাটডাউন নেয়।
| 17:05 | 18:17 | Chowmuhani 230/132/33kV S/S TR3 Forced S/D Due to 33 kv Bus loop maintenance work and | [7 empty] | 40.0MW load
|  |  | Auxiliary Transformer 1 fuse change. | [7 empty] | interrup.
| 18:47 |  | Chandraghona-Madunaghat 132 kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL-670
relays Due to General trip zone 01: 4.9 km B-phase fault
| 18:47 | 18:49 | Savar 132/33kV S/S T-1 LT Tripped showing Over current realy relays Due to dpbs-3 L-42
feeder fault
| 18:47 | 18:59 | Savar 132/33kV S/S T-2 LT Tripped showing Over current relay relays Due to DPBS-3 L-42
feeder fault
| 20:00 |  | Evening peak generation is 15660 MW.
| 03:30 |  | Bogura 230/132kV S/S T-01 LT Tripped showing N/A relays Due to None
| 03:30 |  | Bogura 230/132kV S/S T-01 HT Tripped showing backup relay trip lock out relay . relays
Due to None
| 06:33 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to Maintenance work at CT-8005 due
to excessive temperature.
| 06:33 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to Maintenance work at CT-8005 due
to excessive temperature.
| 07:17 | 07:52 | Barishal 230/132kV S/S T-5 LT Tripped showing Micom P142 relays Due to Banaripara 33 kV | [7 empty] | 28.0MW load
|  |  | feeder R-phase CT blast. | [7 empty] | interrup.
| 07:17 | 07:52 | Barishal 230/132kV S/S T-4 LT Tripped showing Micom P142 relays Due to Banaripara 33 kV | [7 empty] | 28.0MW load
|  |  | feeder R-phase CT blast. | [7 empty] | interrup.
| 07:46 |  | Chowmuhani 230/132/33kV S/S TR2 Scheduled S/D Due to 33kv L bus ds to 33kv bus connecting | [7 empty] | 50.0MW load
|  |  | loop red-hot maintaence | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 354 | 8640000 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 299 | 7178676 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 543052 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 307 | 7330521 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 811440 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 31 | 729600 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 771055 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 847784 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 311400 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 445320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 653760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 130 | 3952069 | Bad Weather
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 1824336 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 1006080 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2292480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 111501 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 376920 | Bad Weather
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 10879545.45 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 68 | 913200 | Machine Problem
Dhaka Area Total |  |  |  |  | 6204.914 | 2276 | 49618739.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 200851.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112995 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 158400 | Fuel Shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5295104 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5509785 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 104545 | Fuel Shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 889662 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 670946 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 491520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 359040 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 24 | 485760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 51 | 1194327 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 650737 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 200726 | Fuel Shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2043840 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 843055 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 17 | 1614182 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28314543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 27 | 653760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1050 | 25250909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3153.36 | 75068687.29
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 203 | 5027000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 335 | 8361400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 310 | 6716000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8089500 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 918288 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 107040 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1756364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1045136 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 102 | 557018 | Fuel Shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 189616 | Fuel Shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 107 | 2535746 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 2002560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 74 | 1024320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 428112 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 371960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 607620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 1241520 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1658880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 543845 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1904 | 43181925
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 124747 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2683200 | ps availability is less
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1592400 | ps availability is less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 333380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293280 | Fuel Shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 414360 | Fuel Shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 279 | 5452067
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 78612 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 556000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 715680 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2003520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1551110 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 381168 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7067000 | Gas Shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 274 | 6479000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9485100 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1227 | 28317190
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 774 | 20449455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 225600 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 297728 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 374400 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 728928 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 295920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1015 | 24450912 | Machine Problem
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1901 | 46822943
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 23367273 | Coal Shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 1586688 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2586000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 580 | 14155636.36 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5157010 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 442800 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7113000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1578 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2371 | 54409985.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 185704 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 568937 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 68826 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 139 | 3510636 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9198327 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 292474 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 595152 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1042368 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1354848 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 22080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1313.05 | 23465454 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 248416 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 400647 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2204.05 | 40953869
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 44 | 1174254 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3832000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1409836 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 13658.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 1448050 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 75028 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 681840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 345 | 8634666.4
Eastern Grid Total |  |  |  |  | 16961.086 | 8839.36 | 201638608.74
Western Grid Total |  |  |  |  | 11731.125 | 6821.05 | 150821463.76
National Grid Total |  |  |  |  | 28692.211 | 15660.41 | 352460072.5
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-09-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10600.33 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4518.3 | MW
i) Dhaka area |  |  | 5909.93 |  | MW | i) Khulna area |  |  |  | 1618 | MW
ii) Chattogram area |  |  | 1424.4 |  | MW | ii) Barishal area |  |  |  | 464.7 | MW
iii) Cumilla area |  |  | 1442 |  | MW | iii) Rajshahi area |  |  |  | 1499.6 | MW
iv) Mymensingh area |  |  | 1185 |  | MW | iv) Rangpur area |  |  |  | 936 | MW
v) Sylhet area |  |  | 639 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15118.63 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 18:00 | 72 | Hatirjheel | 87 | 13:00 | 143 | Pabna | 105 | 19:00
2 | AKSML | 137.9 | 01:00 | 73 | Ishurdi | 89 | 18:30 | 144 | Palashbari | 132 | 18:30
3 | Aftabnagar | 44 | 12:00 | 74 | Jaldhaka | 80 | 18:30 | 145 | Panchagarh | 56 | 00:00
4 | Agargaon | 142 | 13:00 | 75 | Jamalpur | 131 | 23:00 | 146 | Patiya | 28 | 00:00
5 | Agrabad | 82 | 15:00 | 76 | Jashore | 145 | 00:00 | 147 | Patnitala | 31 | 22:00
6 | Amnura | 29 | 00:00 | 77 | Jhenaidah | 96 | 19:30 | 148 | Patuakhali | 72 | 02:00
7 | Araihazar | 103 | 19:30 | 78 | Joydebpur | 177 | 18:30 | 149 | Payra | 38 | 22:00
8 | Ashuganj | N/A | N/A | 79 | Joypurhat | 60 | 00:00 | 150 | Postogola | 66 | 13:00
9 | Ashuganj-230 | 97 | 00:00 | 80 | Juldah | 19 | 18:00 | 151 | Pubail | 50 | 18:30
10 | BSRM | 200 | 17:00 | 81 | KSRM | 25 | 19:30 | 152 | Purbachal | 31 | 00:00
11 | Bagerhat | 88 | 02:00 | 82 | Kabirpur | 286 | 18:00 | 153 | Purbasadipur | 123 | 19:00
12 | Bajitpur | 116 | 18:00 | 83 | Kachua | 100 | 19:00 | 154 | Rahanpur | 42 | 02:00
13 | Bakerganj | 13.6 | 22:00 | 84 | Kaliganj | 40 | 00:00 | 155 | Rahim | 25 | 15:00
14 | Bakulia | 107 | 18:30 | 85 | Kallyanpur | 120 | 00:00 | 156 | Rajbari | 87 | 19:00
15 | Banani | 70.6 | 13:00 | 86 | Kalurghat | 44 | 15:00 | 157 | Rajendrapur | 128 | 18:30
16 | Bangabhaban | 17 | 11:00 | 87 | Kamrangirchar | 86 | 12:00 | 158 | Rajshahi | 124 | 00:00
17 | Barapukuria | 63 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi-230 | 106 | 13:00
18 | Barguna | 20 | 20:00 | 89 | Kasba | 37 | 20:00 | 160 | Ramganj | 116 | 18:00
19 | Barishal | 106 | 13:00 | 90 | Kazla | 135 | 12:00 | 161 | Rampur | 46 | 00:00
20 | Barishal-230 | 98 | 02:00 | 91 | Keranigonj | 94 | 20:00 | 162 | Rangamati | 17 | 18:00
21 | Baroaulia | 48 | 08:00 | 92 | Khagrachori | 38 | 23:00 | 163 | Rangpur | 136 | 18:30
22 | Baroirhat | 65 | 18:30 | 93 | Khulna | 63 | 13:00 | 164 | Ruppur | 4.2 | 09:00
23 | Bashundhara | 213 | 12:00 | 94 | Khulshi | 200 | 18:30 | 165 | SSM | 0 | 00:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 138 | 23:00 | 166 | Saidpur | 102 | 19:00
25 | Beanibazar | 70 | 23:00 | 96 | Kodda | 329 | 10:00 | 167 | Santhia | 36 | 18:30
26 | Benapole | 67 | 00:00 | 97 | Kulaura | 56 | 14:00 | 168 | Satkhira | 136 | 00:00
27 | Bhaluka | 163 | 23:00 | 98 | Kurigram | 72 | 18:30 | 169 | Satmasjid | 114 | 13:00
28 | Bhandaria | 57 | 23:00 | 99 | Kushtia | 148 | 19:00 | 170 | Savar | 230 | 12:00
29 | Bhangura | 39 | 18:30 | 100 | Laksam | 39 | 22:00 | 171 | SevenRings | 20.94 | 23:00
30 | Bheramara(GK) | 66 | 02:00 | 101 | Lakshmipur | 52 | 00:00 | 172 | ShahCement | 29 | 18:00
31 | Bhulta | 198 | 01:00 | 102 | Lalbag | 82 | 13:00 | 173 | Shahjadpur | 90 | 19:00
32 | Bog-Sherpur | 72 | 02:00 | 103 | Lalmonirhat | 54 | 01:00 | 174 | Shahjibazar | 151 | 00:00
33 | Bogura | 203 | 00:00 | 104 | MI_Cement | 11.8 | 02:00 | 175 | Shahmirpur | 62 | 18:00
34 | Borhanuddin | 80 | 23:00 | 105 | Madanganj | 56 | 18:00 | 176 | Shariatpur | 99 | 20:00
35 | Brahmanbaria | 145 | 00:00 | 106 | Madaripur | 112 | 02:00 | 177 | Sherpur | 164 | 22:00
36 | Cantonment | 140 | 13:00 | 107 | Madartek | 86 | 00:00 | 178 | Shikalbaha | 24 | 02:00
37 | Chandina | 34 | 09:00 | 108 | Madunaghat | 57 | 18:00 | 179 | Shitalakhya | 85.5 | 13:00
38 | Chandpur | 90 | 19:00 | 109 | Magura | 60 | 18:00 | 180 | Sholosohor | 47 | 15:00
39 | Chandraghona | 38 | 00:00 | 110 | Mahasthangarh | 78 | 02:00 | 181 | Shomvuganj | 54 | 18:00
40 | Chapai | 68 | 01:00 | 111 | Maijdee | 42 | 22:00 | 182 | Shyampur | 138 | 15:00
41 | Charfasson | 35 | 21:00 | 112 | Manikganj | 148 | 23:00 | 183 | Siddhirganj | 136 | 12:00
42 | Charsaidpur | 41 | 00:00 | 113 | Maniknagar | 72 | 13:00 | 184 | Sirajganj | 124 | 20:00
43 | Chauddagram | 80 | 18:30 | 114 | Matarbari | 58 | 19:00 | 185 | Sitakunda | 35 | 18:00
44 | Chhatak | 40 | 00:00 | 115 | Matuail | 82 | 12:00 | 186 | Sonargaon | 122 | 10:00
45 | Chowmuhani | 169 | 18:30 | 116 | Metrorail_Motijheel | 20 | 09:00 | 187 | Sreemongol | 96 | 18:30
46 | Chuadanga | 120 | 18:30 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreepur | 136 | 18:30
47 | Coxsbazar | 147 | 13:00 | 118 | Millgate | 108 | 11:00 | 189 | Srinagar | 51 | 22:00
48 | Cumilla(N) | 157 | 18:00 | 119 | Mirpur | 165 | 18:30 | 190 | Sunamganj | 62 | 01:00
49 | Cumilla(S) | 155 | 14:00 | 120 | Mirsorai | 56 | 09:00 | 191 | Sylhet | 121 | 00:00
50 | Daganbhuiyan | 37 | 02:00 | 121 | Mirzapur | 50 | 12:00 | 192 | Sylhet_(South) | 59 | 02:00
51 | Daudkandi | 136 | 23:00 | 122 | Mithapukur | 74 | 18:30 | 193 | TK | 0 | 00:00
52 | DhakaUniversity | 108 | 13:00 | 123 | Modern | N/A | N/A | 194 | Tangail | 192 | 19:30
53 | Dhamrai | 96 | 14:00 | 124 | Mogbazar | 68.6 | 10:00 | 195 | Taraganj | 34 | 19:00
54 | Dhanmondi | 130 | 13:00 | 125 | Mongla | 42 | 02:00 | 196 | Tasnim | 44 | 01:00
55 | Dohazari | 118 | 22:00 | 126 | Motijheel | 58 | 13:00 | 197 | Thakurgaon | 101 | 18:30
56 | Faridpur | 178 | 21:00 | 127 | Muktagacha | 41 | 00:00 | 198 | Tongi | 158 | 19:30
57 | Fatullah | 115 | 12:00 | 128 | Munshiganj | 114 | 22:00 | 199 | Ullahpara | 41 | 20:00
58 | Fenchuganj | 48 | 20:00 | 129 | Muradnagar | 58 | 11:00 | 200 | Ullon | 47 | 00:00
59 | Feni | 112 | 19:00 | 130 | Mymensingh | 140 | 22:00 | 201 | Uttara | 101 | 12:00
60 | GPH | 4 | 11:00 | 131 | Nabinagar | 110 | 10:00 | 202 | UttaraNew | 57 | 13:00
61 | Ghatail | 101 | 23:00 | 132 | Naogaon | 132 | 00:00 | 203 | Zigatola | 99 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Narail | 56 | 02:00
63 | Ghorashal-230 | 96 | 12:00 | 134 | Narinda | 81 | 13:00
64 | Goalpara | 33 | 00:00 | 135 | Narshingdi | 200 | 18:30
65 | Gollamari | 104 | 00:00 | 136 | Natore | 149 | 18:00
66 | Gopalganj | 117 | 19:00 | 137 | Nawabganj | 49.7 | 00:00
67 | Gulshan | 126 | 12:00 | 138 | Netrakona | 114 | 19:00
68 | Halishahar | 107 | 16:00 | 139 | New | 87.5 | 12:00
69 | HaripurSBU | 140 | 23:00 | 140 | Niamatpur | 79 | 00:00
70 | Hasnabad | 105 | 19:30 | 141 | Noapara | 48 | 18:30
71 | Hathazari | 108 | 18:30 | 142 | PHP | 13 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15832.85 | 854 |  | 16725.28
1:00 | 14877.91 | 1237 |  | 16170.58
2:00 | 14811.86 | 472 |  | 15304.86
3:00 | 14582.63 | 422 |  | 15023.63
4:00 | 14063.92 | 394 |  | 14475.92
5:00 | 13655.04 | 346 |  | 14017.04
6:00 | 13532.07 | 292 |  | 13837.07
7:00 | 13315.31 | 304 |  | 13633.31
8:00 | 13150.99 | 249 |  | 13410.99
9:00 | 13316.92 | 200 |  | 13525.92
10:00 | 13776.26 | 185 |  | 13969.26
11:00 | 14041.19 | 230 |  | 14281.19
12:00 | 14592.51 | 320 |  | 14926.51
13:00 | 14642.22 | 438 |  | 15100.22
14:00 | 14597.3 | 340 |  | 14952.6
15:00 | 14659.3 | 419 |  | 15097.3
16:00 | 14292.4 | 383 |  | 14692.4
17:00 | 14269.56 | 373 |  | 14659.56
18:00 | 14830.57 | 442 |  | 15292.57
19:00 | 15580.21 | 433 |  | 16032.7
19:30 | 15621.05 | 433 |  | 16073.54
20:00 | 15660.41 | 570 |  | 16256.41
21:00 | 15345.22 | 390 |  | 15753.22
22:00 | 15320.85 | 362 |  | 15698.85
23:00 | 15388.26 | 236 |  | 15635.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 23-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 97 | 45 | 322 | 174 | 1302 | 630 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 75 | 34 | 270 | 164 | 1256 | 638
2:00 | 44 | 23 | 196 | 162 | 1068 | 566 |  | Import | 0
3:00 | 52 | 21 | 230 | 174 | 1148 | 568
4:00 | 58 | 22 | 250 | 172 | 1164 | 532 | Ishurdi-Ghorashal Ckt-2 | Export | 2952363.64
5:00 | 91 | 24 | 300 | 170 | 1304 | 570
6:00 | 102 | 28 | 310 | 154 | 1348 | 582 |  | Import | 0
7:00 | 101 | 32 | 300 | 150 | 1342 | 590
8:00 | 113 | 41 | 292 | 166 | 1466 | 672 | Sirajganj-Sreepur Ckt-1 | Export | 2231000
9:00 | 160 | 65 | 384 | 182 | 1674 | 746
10:00 | 164 | 71 | 430 | 204 | 1710 | 802 |  | Import | 0
11:00 | 161 | 67 | 210 | 212 | 1700 | 868
12:00 | 151 | 56 | 420 | 220 | 1596 | 826 | Sirajganj-Sreepur Ckt-2 | Export | 2239000
13:00 | 132 | 53 | 390 | 224 | 1538 | 844
14:00 | 151 | 54 | 440 | 220 | 1634 | 824 |  | Import | 0
15:00 | 173 | 73 | 480 | 244 | 1744 | 876
16:00 | 174 | 66 | 470 | 220 | 1796 | 802 | Gopalganj-Aminbazar Ckt-1 | Export | 17830000
17:00 | 170 | 65 | 420 | 208 | 1758 | 816
18:00 | 156 | 61 | 460 | 216 | 1676 | 808 |  | Import | 0
18:30 | 107 | 33 | 380 | 204 | 1492 | 704
19:00 | 120 | 41 | 380 | 196 | 1444 | 706 | Gopalganj-Aminbazar Ckt-2 | Export | 17870000
19:30 | 133 | 42 | 420 | 196 | 1552 | 714
20:00 | 133 | 41 | 410 | 184 | 1508 | 674 |  | Import | 0
21:00 | 126 | 37 | 390 | 185 | 1418 | 622
22:00 | 128 | 31 | 410 | 180 | 1440 | 624 |  | Total Export | 43122363.64
23:00 | 123 | 26 | 420 | 186 | 1434 | 600 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8995.5 | 6837.35 | 15832.85 | DAILY GENERATION CURVE
00:30 | 8824.35 | 6531.03 | 15355.38
01:00 | 8653.2 | 6224.71 | 14877.91 | 23-09-2026
01:30 | 8685.45 | 6159.435 | 14844.885
02:00 | 8717.7 | 6094.16 | 14811.86
02:30 | 8601.6 | 6095.645 | 14697.245
03:00 | 8485.5 | 6097.13 | 14582.63
03:30 | 8328.5 | 5994.775 | 14323.275
04:00 | 8171.5 | 5892.42 | 14063.92
04:30 | 7956.5 | 5902.98 | 13859.48
05:00 | 7741.5 | 5913.54 | 13655.04
05:30 | 7697.055 | 5896.5 | 13593.555
06:00 | 7652.61 | 5879.46 | 13532.07
06:30 | 7565.96 | 5857.73 | 13423.69
07:00 | 7479.31 | 5836 | 13315.31
07:30 | 7457.85 | 5775.3 | 13233.15
08:00 | 7436.39 | 5714.6 | 13150.99
08:30 | 7452.36 | 5781.595 | 13233.955
09:00 | 7468.33 | 5848.59 | 13316.92
09:30 | 7647.88 | 5898.71 | 13546.59
10:00 | 7827.43 | 5948.83 | 13776.26
10:30 | 7940.565 | 5968.16 | 13908.725
11:00 | 8053.7 | 5987.49 | 14041.19
11:30 | 8221.54 | 6095.31 | 14316.85
12:00 | 8389.38 | 6203.13 | 14592.51
12:30 | 8436.415 | 6180.95 | 14617.365
13:00 | 8483.45 | 6158.77 | 14642.22
13:30 | 8450.885 | 6168.875 | 14619.76
14:00 | 8418.32 | 6178.98 | 14597.3
14:30 | 8421.495 | 6206.805 | 14628.3
15:00 | 8424.67 | 6234.63 | 14659.3
15:30 | 8289.08 | 6186.77 | 14475.85
16:00 | 8153.49 | 6138.91 | 14292.4
16:30 | 8128.5 | 6152.48 | 14280.98
17:00 | 8103.51 | 6166.05 | 14269.56
17:30 | 8326.685 | 6223.38 | 14550.065
18:00 | 8549.86 | 6280.71 | 14830.57
18:30 | 8664.71 | 6540.68 | 15205.39
19:00 | 8779.56 | 6800.65 | 15580.21
19:30 | 8769.36 | 6851.69 | 15621.05
20:00 | 8839.36 | 6821.05 | 15660.41
20:30 | 8696.11 | 6806.705 | 15502.815 |  | Executive Engineer
21:00 | 8552.86 | 6792.36 | 15345.22 |  | Network Operation Division
21:30 | 8543.86 | 6789.175 | 15333.035
22:00 | 8534.86 | 6785.99 | 15320.85
22:30 | 8539.61 | 6814.945 | 15354.555
23:00 | 8544.36 | 6843.9 | 15388.26

## En-Curve
QF-LDC-12
Date | 23-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3560 | 1441 | 726 | 0 | 38 | 1409.35 | 218 | 5288 | 0 | 584 | 2536.5 | 0 | 0 | 32 | 854 | DAILY ENERGY CURVE
00:30 | 3573.5 | 1467.5 | 745.5 | 0 | 37 | 1284.03 | 218 | 5224.5 | 0 | 511.5 | 2263.35 | 0 | 0 | 30.5 | 1045.5 | 23-09-2026
01:00 | 3587 | 1494 | 765 | 0 | 36 | 1158.71 | 218 | 5161 | 0 | 439 | 1990.2 | 0 | 0 | 29 | 1237
01:30 | 3665.5 | 1515.25 | 765 | 0 | 36 | 1037.435 | 218 | 5150 | 0 | 438.5 | 1988.2 | 0 | 0 | 31 | 854.5 | Energy Generated | 352.4601 |  | MKWHr
02:00 | 3744 | 1536.5 | 765 | 0 | 36 | 916.16 | 218 | 5139 | 0 | 438 | 1986.2 | 0 | 0 | 33 | 472 | Energy not Served | 9.891 |  | MKWHr
02:30 | 3760 | 1524 | 788 | 0 | 35 | 873.645 | 219 | 5147 | 0 | 435 | 1875.1 | 0 | 0 | 40.5 | 447 | Total Energy Requirement | 362.3511 |  | MKWHr
03:00 | 3776 | 1511.5 | 811 | 0 | 34 | 831.13 | 220 | 5155 | 0 | 432 | 1764 | 0 | 0 | 48 | 422
03:30 | 3763 | 1524 | 811.5 | 0 | 33 | 827.775 | 220 | 5167.5 | 0 | 356 | 1582.5 | 0 | 0 | 38 | 408
04:00 | 3750 | 1536.5 | 812 | 0 | 32 | 824.42 | 220 | 5180 | 0 | 280 | 1401 | 0 | 0 | 28 | 394
04:30 | 3695.5 | 1561.5 | 859.5 | 0 | 32 | 822.48 | 220 | 5205 | 0 | 276 | 1161 | 0 | 0 | 26.5 | 370
05:00 | 3641 | 1586.5 | 907 | 0 | 32 | 820.54 | 220 | 5230 | 0 | 272 | 921 | 0 | 0 | 25 | 346
05:30 | 3636.5 | 1560 | 907.5 | 0 | 32 | 823.49 | 220 | 5246 | 2.065 | 268.5 | 872 | 0 | 0 | 25.5 | 319
06:00 | 3632 | 1533.5 | 908 | 0 | 32 | 826.44 | 220 | 5262 | 4.13 | 265 | 823 | 0 | 0 | 26 | 292
06:30 | 3613 | 1512 | 907.5 | 0 | 28 | 823.755 | 220 | 5233 | 38.435 | 265 | 757.5 | 0 | 0 | 25.5 | 298
07:00 | 3594 | 1490.5 | 907 | 0 | 24 | 821.07 | 220 | 5204 | 72.74 | 265 | 692 | 0 | 0 | 25 | 304
07:30 | 3507.5 | 1471.5 | 907 | 0 | 24 | 827.32 | 220 | 5200.5 | 128.33 | 227.5 | 695 | 0 | 0 | 24.5 | 276.5
08:00 | 3421 | 1452.5 | 907 | 0 | 24 | 833.57 | 220 | 5197 | 183.92 | 190 | 698 | 0 | 0 | 24 | 249
08:30 | 3450.5 | 1455.5 | 907 | 0 | 24 | 825.535 | 220 | 5218 | 271.42 | 189 | 647.5 | 0 | 0 | 25.5 | 224.5
09:00 | 3480 | 1458.5 | 907 | 0 | 24 | 817.5 | 220 | 5239 | 358.92 | 188 | 597 | 0 | 0 | 27 | 200
09:30 | 3555 | 1501 | 907 | 0 | 27 | 818.255 | 219.5 | 5259 | 370.835 | 176.5 | 684.5 | 0 | 0 | 28 | 192.5
10:00 | 3630 | 1543.5 | 907 | 0 | 30 | 819.01 | 219 | 5279 | 382.75 | 165 | 772 | 0 | 0 | 29 | 185
10:30 | 3608.5 | 1594.85 | 907 | 0 | 32 | 816.135 | 218.5 | 5300 | 397.74 | 173.5 | 833 | 0 | 0 | 27.5 | 207.5
11:00 | 3587 | 1646.2 | 907 | 0 | 34 | 813.26 | 218 | 5321 | 412.73 | 182 | 894 | 0 | 0 | 26 | 230
11:30 | 3497.5 | 1625.2 | 907 | 0 | 33 | 815.67 | 217.5 | 5294.5 | 386.48 | 215 | 1301 | 0 | 0 | 24 | 275
12:00 | 3408 | 1604.2 | 907 | 0 | 32 | 818.08 | 217 | 5268 | 360.23 | 248 | 1708 | 0 | 0 | 22 | 320
12:30 | 3377.5 | 1544.7 | 907.5 | 0 | 35 | 816.82 | 217 | 5232 | 351.845 | 223 | 1893 | 0 | 0 | 19 | 379
13:00 | 3347 | 1485.2 | 908 | 0 | 38 | 815.56 | 217 | 5196 | 343.46 | 198 | 2078 | 0 | 0 | 16 | 438
13:30 | 3381 | 1467.35 | 907.5 | 0 | 37 | 816.56 | 217 | 5209 | 382.35 | 190 | 1997 | 0 | 0 | 15 | 389
14:00 | 3415 | 1449.5 | 907 | 0 | 36 | 817.56 | 217 | 5222 | 421.24 | 182 | 1916 | 0 | 0 | 14 | 340
14:30 | 3480 | 1472.35 | 907 | 0 | 36 | 818.98 | 217 | 5248 | 373.97 | 182 | 1881 | 0 | 0 | 12 | 379.5
15:00 | 3545 | 1495.2 | 907 | 0 | 36 | 820.4 | 217 | 5274 | 326.7 | 182 | 1846 | 0 | 0 | 10 | 419
15:30 | 3514.5 | 1532.1 | 907.5 | 0 | 37 | 819.545 | 218 | 5267 | 259.205 | 160 | 1751.5 | 0 | 0 | 9.5 | 401
16:00 | 3484 | 1569 | 908 | 0 | 38 | 818.69 | 219 | 5260 | 191.71 | 138 | 1657 | 0 | 0 | 9 | 383
16:30 | 3460 | 1528.25 | 907.5 | 0 | 37 | 860.79 | 219 | 5313 | 123.76 | 146.5 | 1671.18 | 0 | 0 | 14 | 378
17:00 | 3436 | 1487.5 | 907 | 0 | 36 | 902.89 | 219 | 5366 | 55.81 | 155 | 1685.36 | 0 | 0 | 19 | 373
17:30 | 3440.5 | 1529.5 | 840.5 | 0 | 58 | 1002.8 | 219 | 5372 | 27.905 | 214 | 1820.86 | 0 | 0 | 25 | 407.5
18:00 | 3445 | 1571.5 | 774 | 0 | 80 | 1102.71 | 219 | 5378 | 0 | 273 | 1956.36 | 0 | 0 | 31 | 442
18:30 | 3456.5 | 1497.25 | 773.5 | 0 | 77 | 1206.18 | 219.5 | 5422.5 | 0 | 433 | 2080.96 | 0 | 0 | 39 | 437.5
19:00 | 3468 | 1423 | 773 | 0 | 74 | 1309.65 | 220 | 5467 | 0 | 593 | 2205.56 | 0 | 0 | 47 | 433
19:30 | 3692 | 1459 | 773 | 0 | 76 | 1313.69 | 221 | 5480 | 0 | 559 | 2026.36 | 0 | 0 | 21 | 433
20:00 | 3767 | 1493 | 774 | 0 | 74 | 1313.05 | 220 | 5473 | 0 | 543 | 1976.36 | 0 | 0 | 27 | 570
20:30 | 3781.5 | 1480.25 | 773.5 | 0 | 64 | 1314.705 | 220.5 | 5476 | 0 | 545.5 | 1817.36 | 0 | 0 | 29.5 | 480
21:00 | 3796 | 1467.5 | 773 | 0 | 54 | 1316.36 | 221 | 5479 | 0 | 548 | 1658.36 | 0 | 0 | 32 | 390
21:30 | 3718 | 1545 | 772.5 | 0 | 63 | 1321.675 | 221 | 5478.5 | 0 | 528.5 | 1644.36 | 0 | 0 | 40.5 | 376
22:00 | 3640 | 1622.5 | 772 | 0 | 72 | 1326.99 | 221 | 5478 | 0 | 509 | 1630.36 | 0 | 0 | 49 | 362
22:30 | 3555 | 1583.25 | 772.5 | 0 | 71 | 1323.445 | 219.5 | 5479 | 0 | 539.5 | 1778.86 | 0 | 0 | 32.5 | 299
23:00 | 3470 | 1544 | 773 | 0 | 70 | 1319.9 | 218 | 5480 | 0 | 570 | 1927.36 | 0 | 0 | 16 | 236
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 03:00 | 358 | 10:00 | Madunaghat | 398 | 02:00 | 388 | 11:00
Amtali | 413 | 01:00 | 408 | 11:00 | Meghnaghat | 384 | 03:00 | 366 | 11:00
Ashuganj | 392 | 03:00 | 380 | 11:00 | Mirsorai | 395 | 01:00 | 381 | 11:00
Bhulta | 393 | 07:00 | 369 | 13:00 | Payra | 414 | 01:00 | 410 | 00:00
Bibiana | 380 | 03:00 | 371 | 10:00 | Rahanpur | 411 | 17:00 | 400 | 21:00
BIPTC | 403 | 01:00 | 395 | 10:00 | Rampal | 396 | 08:00 | 387 | 23:00
Bogura | 396 | 17:00 | 384 | 21:00
Gopalganj | 392 | 03:00 | 380 | 11:00
Kaliakoir | 370 | 03:00 | 352 | 13:00
Korerhat | 394 | 02:00 | 380 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 214 | 11:00 | Hasnabad | 224 | 05:00 | 211 | 11:00
AKSML | 236 | 00:00 | 224 | 11:00 | Hathazari | 233 | 00:00 | 213 | 18:00
Aminbazar | 230 | 03:00 | 214 | 11:00 | Ishurdi | 235 | 00:00 | 223 | 22:00
Ashuganj | 225 | 03:00 | 215 | 11:00 | Jhenaidah | 226 | 09:00 | 214 | 22:00
Ashuganj-400 | 225 | 03:00 | 215 | 11:00 | Kachua | 228 | 01:00 | 218 | 11:00
Baghabari | 231 | 03:00 | 225 | 18:30 | Kaliakoir | 230 | 03:00 | 214 | 11:00
Barapukuria | 228 | 14:00 | 221 | 23:00 | Keranigonj | 226 | 03:00 | 211 | 11:00
Barapukuria-230 | 228 | 14:00 | 221 | 23:00 | Khulna(S) | 227 | 01:00 | 219 | 22:00
Barapukuria(N) | 230 | 13:00 | 224 | 20:00 | Korerhat | 226 | 03:00 | 217 | 11:00
Barishal | 227 | 06:00 | 220 | 22:00 | Madunaghat | 236 | 00:00 | 229 | 10:00
Bheramara | 235 | 00:00 | 221 | 22:00 | Madunaghat-400 | 238 | 02:00 | 231 | 11:00
Bhulta | 224 | 04:00 | 208 | 11:00 | Maniknagar | 223 | 04:00 | 207 | 11:00
Bibiana | 216 | 01:00 | 207 | 10:00 | Meghnaghat | 229 | 03:00 | 215 | 14:00
BIPTC | 236 | 00:00 | 221 | 22:00 | Meghnaghat-400 | 225 | 03:00 | 212 | 11:00
Birulia | 230 | 04:00 | 214 | 11:00 | Mirsorai | 229 | 01:00 | 221 | 11:00
Bogura | 239 | 16:00 | 232 | 21:00 | Naogaon | 228 | 17:00 | 213 | 00:00
Bogura-400 | 239 | 17:00 | 232 | 21:00 | Purbasadipur | 226 | 17:00 | 218 | 08:00
Borhanuddin | 230 | 02:00 | 224 | 22:00 | Rajshahi | 233 | 17:00 | 221 | 18:30
BSRM | 226 | 01:00 | 217 | 11:00 | Rampal | 226 | 09:00 | 218 | 22:00
Charfasson | 230 | 12:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 01:00 | 218 | 11:00 | Rampura | 223 | 04:00 | 204 | 13:00
Cumilla(N) | 221 | 04:00 | 210 | 11:00 | Shikalbaha | 236 | 00:00 | 227 | 10:00
Faridpur | 222 | 01:00 | 215 | 21:00 | Shyampur | 225 | 03:00 | 210 | 11:00
Fenchuganj | 215 | 01:00 | 202 | 11:00 | Siddhirganj | 225 | 06:00 | 209 | 12:00
Feni | 224 | 01:00 | 214 | 11:00 | Sirajgonj | 236 | 17:00 | 23 | 17:00
Ghorashal | 220 | 00:00 | 215 | 11:00 | Sreepur | 221 | 06:00 | 213 | 15:00
Ghorashal-230 | 218 | 03:00 | 198 | 11:00 | Tongi | 217 | 04:00 | 205 | 11:00
Gopalganj | 223 | 01:00 | 216 | 22:00
GPH | 232 | 01:00 | 224 | 11:00
Haripur | 223 | 03:00 | 208 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 03:00 | 125 | 13:00 | Madanganj | 135 | 07:00 | 125 | 12:00
Agargaon | 136 | 03:00 | 125 | 11:00 | Madaripur | 130 | 07:00 | 127 | 22:00
Agrabad | 135 | 00:00 | 130 | 10:00 | Madartek | 138 | 04:00 | 124 | 13:00
AKS | 133 | 00:00 | 128 | 08:00 | Madunaghat | 137 | 02:00 | 132 | 11:00
Aminbazar | 132 | 03:00 | 122 | 11:00 | Magura | 135 | 09:00 | 126 | 22:00
Amnura | 134 | 17:00 | 129 | 11:00 | Mahasthangarh | 137 | 17:00 | 131 | 00:00
Araihazar | 125 | 07:00 | 113 | 15:00 | Maijdee | 128 | 01:00 | 122 | 11:00
Ashuganj | 132 | 08:00 | 125 | 11:00 | Manikganj | 125 | 00:00 | 120 | 11:00
Ashuganj-230 | 135 | 01:00 | 130 | 15:00 | Maniknagar | 139 | 05:00 | 126 | 11:00
Bagerhat | 128 | 01:00 | 121 | 22:00 | Matarbari | 121 | 18:00 | 112 | 05:00
Bajitpur | 126 | 06:00 | 120 | 19:00 | Matuail | 136 | 06:00 | 125 | 13:00
Bakerganj | 133 | 01:00 | 128 | 22:00 | Metrorail_Motijheel | 139 | 05:00 | 126 | 11:00
Bakulia | 135 | 00:00 | 128 | 10:00 | Metrorail_Uttara | 133 | 03:00 | 116 | 11:00
Banani | 138 | 04:00 | 124 | 13:00 | Millgate | 135 | 03:00 | 118 | 10:00
Bangabhaban | 138 | 04:00 | 124 | 13:00 | Mirpur | 130 | 03:00 | 121 | 11:00
Barapukuria | 139 | 14:00 | 130 | 08:00 | Mirzapur | 129 | 00:00 | 122 | 20:00
Barguna | 133 | 01:00 | 127 | 22:00 | Mithapukur | 135 | 15:00 | 127 | 02:00
Barishal | 133 | 01:00 | 127 | 21:00 | MI_Cement | 133 | 04:00 | 120 | 11:00
Barishal-230 | 133 | 03:00 | 127 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 134 | 00:00 | 130 | 11:00 | Mogbazar | 140 | 04:00 | 125 | 13:00
Baroirhat | 131 | 01:00 | 125 | 11:00 | Mongla | 127 | 01:00 | 120 | 23:00
Bashundhara | 138 | 04:00 | 118 | 11:00 | Motijheel | 138 | 04:00 | 124 | 13:00
BashundharaCement | 135 | 07:00 | 125 | 12:00 | Muktagacha | 126 | 00:00 | 118 | 20:00
Beanibazar | 122 | 00:00 | 109 | 11:00 | Munshiganj | 135 | 06:00 | 124 | 11:00
Benapole | 134 | 09:00 | 118 | 22:00 | Muradnagar | 127 | 01:00 | 118 | 11:00
Bhaluka | 130 | 04:00 | 123 | 12:00 | Mymensingh | 128 | 10:00 | 114 | 01:00
Bhandaria | 132 | 07:00 | 120 | 23:00 | Nabinagar | 132 | 01:00 | 122 | 11:00
Bhangura | 133 | 00:00 | 127 | 19:00 | Naogaon | 137 | 17:00 | 128 | 00:00
Bheramara | 137 | 00:00 | 130 | 22:00 | Narail | 133 | 06:00 | 126 | 22:00
Bheramara(GK) | 137 | 00:00 | 130 | 19:00 | Narinda | 139 | 05:00 | 126 | 11:00
Bhulta | 125 | 07:00 | 114 | 13:00 | Narshingdi | 128 | 01:00 | 110 | 13:00
Bhulta-400 | 126 | 07:00 | 114 | 13:00 | Natore | 133 | 09:00 | 127 | 22:00
Birulia | 134 | 02:00 | 125 | 13:00 | Nawabganj | 136 | 03:00 | 126 | 13:00
Bog-Sherpur | 136 | 17:00 | 131 | 21:00 | Netrakona | 122 | 01:00 | 112 | 19:00
Bogura | 139 | 17:00 | 133 | 21:00 | New | 134 | 01:00 | 120 | 10:00
Bogura-230 | 139 | 17:00 | 134 | 21:00 | Niamatpur | 136 | 16:00 | 128 | 00:00
Brahmanbaria | 128 | 05:00 | 122 | 12:00 | Noapara | 130 | 01:00 | 123 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 03:00 | 125 | 11:00 | Pabna | 133 | 00:00 | 127 | 22:00
Chandina | 128 | 01:00 | 121 | 11:00 | Palashbari | 133 | 17:00 | 126 | 23:00
Chandpur | 133 | 01:00 | 125 | 11:00 | Panchagarh | 137 | 13:00 | 128 | 11:00
Chandraghona | 137 | 00:00 | 133 | 10:00 | Patiya | 134 | 01:00 | 128 | 11:00
Chapai | 134 | 16:00 | 128 | 00:00 | Patnitala | 135 | 16:00 | 128 | 21:00
Charsaidpur | 135 | 02:00 | 125 | 11:00 | Patuakhali | 132 | 00:00 | 127 | 22:00
Chauddagram | 129 | 01:00 | 121 | 11:00 | Payra | 135 | 01:00 | 132 | 19:30
Chhatak | 120 | 13:00 | 105 | 11:00 | PHP | 131 | 01:00 | 125 | 11:00
Chowmuhani | 128 | 01:00 | 123 | 11:00 | Postogola | 134 | 04:00 | 124 | 11:00
Chuadanga | 134 | 17:00 | 125 | 22:00 | Pubail | 127 | 01:00 | 119 | 11:00
Coxsbazar | 126 | 06:00 | 116 | 00:00 | Purbachal | 138 | 06:00 | 125 | 13:00
Cumilla(N) | 128 | 00:00 | 120 | 11:00 | Purbasadipur | 137 | 15:00 | 131 | 08:00
Cumilla(S) | 134 | 02:00 | 121 | 11:00 | Rahanpur | 138 | 17:00 | 133 | 21:00
Daganbhuiyan | 129 | 01:00 | 123 | 11:00 | Rahanpur-400 | 138 | 17:00 | 134 | 18:30
Daudkandi | 127 | 01:00 | 116 | 13:00 | Rahim | 136 | 06:00 | 126 | 11:00
DhakaUniversity | 139 | 06:00 | 125 | 13:00 | Rajbari | 126 | 01:00 | 121 | 19:00
Dhamrai | 133 | 04:00 | 123 | 11:00 | Rajendrapur | 131 | 00:00 | 126 | 18:30
Dhanmondi | 138 | 06:00 | 125 | 12:00 | Rajshahi | 132 | 17:00 | 126 | 18:30
Dohazari | 129 | 02:00 | 124 | 11:00 | Rajshahi-230 | 134 | 17:00 | 127 | 18:30
Faridpur | 128 | 01:00 | 124 | 21:00 | Ramganj | 129 | 01:00 | 122 | 10:00
Fatullah | 134 | 04:00 | 122 | 11:00 | Rampur | 135 | 00:00 | 129 | 11:00
Fenchuganj | 127 | 01:00 | 117 | 11:00 | Rampura | 138 | 03:00 | 124 | 13:00
Feni | 130 | 00:00 | 122 | 11:00 | Rangamati | 134 | 00:00 | 132 | 10:00
Feni-230 | 130 | 01:00 | 123 | 11:00 | Rangpur | 134 | 15:00 | 127 | 00:00
Ghatail | 126 | 00:00 | 115 | 21:00 | Ruppur | 136 | 00:00 | 130 | 19:00
Ghorashal | 129 | 03:00 | 121 | 12:00 | Saidpur | 136 | 13:00 | 130 | 23:00
Goalpara | 132 | 01:00 | 126 | 22:00 | Santhia | 134 | 00:00 | 129 | 18:30
Gollamari | 132 | 01:00 | 126 | 21:00 | Satkhira | 128 | 14:00 | 118 | 22:00
Gopalganj | 133 | 01:00 | 124 | 18:00 | Satmasjid | 135 | 03:00 | 125 | 11:00
Gopalganj-400 | 132 | 00:00 | 128 | 11:00 | Savar | 130 | 00:00 | 121 | 11:00
Gulshan | 137 | 05:00 | 125 | 13:00 | SevenRings | 130 | 03:00 | 121 | 11:00
Halishahar | 136 | 00:00 | 129 | 11:00 | ShahCement | 132 | 23:00 | 126 | 15:00
Haripur | 136 | 03:00 | 126 | 13:00 | Shahjadpur | 135 | 01:00 | 130 | 00:00
HaripurSBU | 136 | 03:00 | 126 | 13:00 | Shahjibazar | 128 | 06:00 | 121 | 11:00
Hasnabad | 134 | 05:00 | 125 | 11:00 | Shahmirpur | 137 | 02:00 | 131 | 10:00
Hathazari | 136 | 00:00 | 131 | 11:00 | Shariatpur | 131 | 01:00 | 124 | 20:00
Hatirjheel | 139 | 06:00 | 124 | 13:00 | Sherpur | 127 | 12:00 | 110 | 01:00
Ishurdi | 137 | 00:00 | 130 | 22:00 | Shikalbaha | 126 | 02:00 | 119 | 11:00
Jaldhaka | 133 | 13:00 | 127 | 08:00 | Shikalbaha-230 | 137 | 01:00 | 130 | 10:00
Jamalpur | 130 | 00:00 | 114 | 01:00 | Shitalakhya | 133 | 04:00 | 120 | 11:00
Jashore | 136 | 09:00 | 119 | 22:00 | Sholosohor | 136 | 01:00 | 130 | 15:00
Jhenaidah | 138 | 17:00 | 129 | 19:30 | Shomvuganj | 120 | 08:00 | 114 | 00:00
Jhenaidah-230 | 137 | 09:00 | 130 | 18:30 | Shyampur | 132 | 02:00 | 124 | 12:00
Joydebpur | 125 | 00:00 | 117 | 15:00 | Shyampur-230 | 135 | 03:00 | 126 | 11:00
Joypurhat | 135 | 17:00 | 127 | 21:00 | Siddhirganj | 137 | 04:00 | 126 | 11:00
Juldah | 137 | 01:00 | 131 | 10:00 | Sirajganj | 131 | 17:00 | 125 | 21:00
Kabirpur | 130 | 02:00 | 113 | 11:00 | Sitakunda | 135 | 00:00 | 131 | 10:00
Kachua | 130 | 01:00 | 124 | 11:00 | Sonargaon | 133 | 07:00 | 122 | 11:00
Kaliakoir | 134 | 00:00 | 127 | 11:00 | Sreemongol | 126 | 08:00 | 119 | 11:00
Kaliganj | 137 | 09:00 | 129 | 22:00 | Sreepur | 134 | 06:00 | 129 | 15:00
Kallyanpur | 131 | 04:00 | 120 | 11:00 | Srinagar | 136 | 04:00 | 127 | 11:00
Kalurghat | 137 | 01:00 | 132 | 11:00 | SSM | 140 | 00:00 | 138 | 07:00
Kamrangirchar | 136 | 02:00 | 117 | 13:00 | Sunamganj | 117 | 12:00 | 104 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 122 | 13:00 | 111 | 11:00
Kasba | 126 | 01:00 | 117 | 11:00 | Sylhet_(South) | 122 | 01:00 | 113 | 11:00
Kazla | 138 | 04:00 | 125 | 13:00 | Tangail | 127 | 00:00 | 117 | 21:00
Keranigonj | 137 | 03:00 | 127 | 11:00 | Taraganj | 134 | 13:00 | 33 | 12:00
Khagrachori | 135 | 00:00 | 130 | 11:00 | Tasnim | 133 | 06:00 | 122 | 11:00
Khulna | 130 | 09:00 | 124 | 22:00 | Thakurgaon | 139 | 13:00 | 129 | 09:00
Khulna(S) | 131 | 01:00 | 126 | 11:00 | TK | 136 | 01:00 | 133 | 09:00
Khulshi | 134 | 01:00 | 127 | 11:00 | Tongi | 134 | 04:00 | 124 | 13:00
Kishoreganj | 125 | 08:00 | 119 | 18:30 | Ullahpara | 133 | 17:00 | 128 | 18:30
Kodda | 128 | 00:00 | 118 | 09:00 | Ullon | 138 | 03:00 | 12 | 12:00
Korerhat | 133 | 00:00 | 127 | 11:00 | Uttara | 134 | 03:00 | 118 | 10:00
KSRM | 136 | 00:00 | 130 | 11:00 | UttaraNew | 133 | 03:00 | 116 | 11:00
Kulaura | 127 | 00:00 | 119 | 11:00 | Zigatola | 137 | 04:00 | 126 | 13:00
Kurigram | 132 | 14:00 | 122 | 07:00
Kushtia | 136 | 00:00 | 129 | 22:00
Laksam | 129 | 01:00 | 123 | 13:00
Lakshmipur | 126 | 01:00 | 121 | 19:30
Lalbag | 136 | 04:00 | 127 | 12:00
Lalmonirhat | 131 | 14:00 | 123 | 08:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division