## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-09-2026 | during | 25-09-2026 | during | 25-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 412 | 312 | 412 | 412 | 375 | 375 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 277 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 25 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 314 | 333 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 31 | 15 | 149.36 | 149.36 | 31 | 31 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 25 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 0 | 33 | 33 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 17 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 52 | 80 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 74 | 125 | 149 | 149 | 52 | 133 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 12 | 0 | 12 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 350 | 584 | 584 | 526 | 526 | AGC, Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 34 | 34 | 143.42 | 143.42 | 51 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2125 | 2047 | 5565.16 | 5553.16 | 2098.5 | 2646.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 6 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 5 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 5 | 50 | 50 | 6 | 6 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 216 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 17 | 17 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 52 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 13 | 42 | 42 | 25 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 2 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.81 | 0 | 3.54 | 0 | 3.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 98 | 300 | 300 | 68 | 68 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 93 | 163 | 163 | 65 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1178 | 1160 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 46 | 31 | 30 | 20 | 30 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1050 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2822.81 | 3221.36 | 4145.5 | 4192.96 | 3312.54 | 3514.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 204 | 221 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 335 | 275 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 280 | 240 | 342.01 | 342.01 | 307 | 307 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 390 | 320 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 36 | 41.65 | 41.65 | 20 | 20.01 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 46 | 8 | 195 | 195 | 25 | 25 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 35 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 50 | 150 | 150 | 13 | 100 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 107 | 109 | 163 | 163 | 140 | 140 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 136 | 34 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 66 | 84 | 76 | 84 | 76 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 0 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 66 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 60 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 77 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1636 | 1553 | 2732.44 | 2654.44 | 1953.26 | 2006.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-09-2026 | during | 25-09-2026 | during | 25-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 1.51 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 162 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9.32 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 210.83 | 278 | 538.2 | 546.5 | 280.7 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 30 | 30 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 29 | 30 | 30 | 40 | 40 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 96 | 97 | 140 | 140 | 95 | 95 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 30 | 30 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 0 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 307 | 341 | 341 | 295 | 295 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 260 | 274 | 280 | 280 | 350 | 380 | Plant availability less
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 381 | 394 | 383 | 383 | 383 | 383 | ps availability is less
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1273 | 1223 | 1406 | 1406 | 1424 | 1454
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 907 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 1.01 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1015 | 1000 | 1234.2 | 1234.2 | 950 | 950 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1923.01 | 1975 | 3389.2 | 3304.2 | 2462 | 2409
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 969 | 1100 | 1000 | 1100 | 1000 | 1100 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 77 | 110 | 110 | 48 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 115 | 120 | 120 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 580 | 575 | 580 | 580 | 570 | 570 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 280 | 307 | 307 | 200 | 200 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.04 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2193.04 | 2421 | 2488 | 2587 | 2126 | 2287
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 37.46 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 17 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 146 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 378 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 58 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 57 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.1 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 852.96 | 1314.8 | 900 | 1300 | 800 | 1300 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 8.32 | 0 | 62 | 0 | 62 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1630.84 | 2144.8 | 2708.91 | 2889.99 | 1799.71 | 2301.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 156 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 112 | 0 | 161.67 | 0 | 161.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 334.6 | 354 | 654.67 | 458 | 564.67 | 447
System Total |  |  |  |  | 28843.2 | 28692.211 | 14149.13 | 15217.16 | 23628.08 | 23592.25 | 16021.38 | 17355.59
Forecast Scenario (25-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15300 |  | 500 |  | 15800
|  |  |  | 1:00 | 14920 |  | 420 |  | 15340
|  |  |  | 2:00 | 14490 |  | 400 |  | 14890
|  |  |  | 3:00 | 14110 |  | 390 |  | 14500
|  |  |  | 4:00 | 13700 |  | 370 |  | 14070
|  |  |  | 5:00 | 13500 |  | 350 |  | 13850
|  |  |  | 6:00 | 12960 |  | 310 |  | 13270
|  |  |  | 7:00 | 13270 |  | 280 |  | 13550
|  |  |  | 8:00 | 13200 |  | 250 |  | 13450
|  |  |  | 9:00 | 13340 |  | 0 |  | 12540
|  |  |  | 10:00 | 13560 |  | 0 |  | 12530
|  |  |  | 11:00 | 13860 |  | 0 |  | 13010
|  |  |  | 12:00 | 14150 |  | 0 |  | 13670
|  |  |  | 13:00 | 13820 |  | 582.55 |  | 14430
|  |  |  | 14:00 | 13620 |  | 191 |  | 13820
|  |  |  | 15:00 | 13390 |  | 429.75 |  | 13840
|  |  |  | 16:00 | 13210 |  | 238.75 |  | 13460
|  |  |  | 17:00 | 13320 |  | 0 |  | 13070
|  |  |  | 18:00 | 14110 |  | 0 |  | 13420
|  |  |  | 18:30 | 14660 |  | 0 |  | 14500
|  |  |  | 19:00 | 15220 |  | 410.65 |  | 15650
|  |  |  | 19:30 | 15090 |  | 525.25 |  | 15640
|  |  |  | 20:00 | 15660 |  | 191 |  | 15860
|  |  |  | 21:00 | 15350 |  | 420.2 |  | 15790
|  |  |  | 22:00 | 15320 |  | 611.2 |  | 15960
|  |  |  | 23:00 | 15390 |  | 792.65 |  | 16220
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13670.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 191
Probable Maximum Demand at Evening Peak: |  |  | 15860.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15660.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.77 MKWHr. |  | 0 | 0 | 0 | 100 | 91 | 0 | 0 | 0 | 0 | 191
*** This report is generated digitally from Operation Information System (OIS) at 08:08 hrs on 25-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-09-2026 | [28 empty] | Date: | 24-09-2026 | [28 empty] | Date: | 24-09-2026 | [28 empty] | Date: | 24-09-2026 | [28 empty] | Date: | 24-09-2026 | [16 empty] | Date: | 24-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 54 | 17 | 60 | 31 | 278 | 55 | 55 | 162 | 0 | 281 | 0 | 0 | 55 | 293 | 0 | 0 | 0 | 68 | 13 | 22 | 0 | 390 | 17 | 51 | 12 | 0 | 25 | 51 | 30 | 35 | 12 | 100 | 0 | 218 | 0 | 17 | 1050 | 162 | 0 | 6 | 8 | 17 | 221 | 0 | 0 | 0 | 1180 | 0 | 13 | 55 | 360 | 290 | 260 | 44 | 5 | 222 | 40 | 108 | 107 | 168 | 69 | 19 | 17 | 68 | 25 | 0 | 0 | 341 | 400 | 58 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 96 | 0 | 183 | 0 | 0 | 0 | 12 | 8795 | 821 | 0 | 23 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1316.96 | 0 | 39 | 0 | 95 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 580 | 17 | 6829.96 | 15624.96 | 105.89
01:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 54 | 17 | 52 | 31 | 278 | 55 | 35 | 72 | 0 | 285 | 0 | 0 | 35 | 294 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 470 | 21 | 51 | 12 | 0 | 30 | 51 | 30 | 0 | 12 | 100 | 0 | 217 | 0 | 18 | 1050 | 160 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 1160 | 0 | 13 | 55 | 350 | 290 | 260 | 44 | 5 | 223 | 40 | 108 | 107 | 170 | 68 | 19 | 17 | 66 | 25 | 0 | 0 | 338 | 400 | 192 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 5 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8545 | 912 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1015 | 17 | 0 | 0 | 1109.12 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 117 | 220 | 0 | 1000 | 580 | 17 | 6379.12 | 14924.12 | 105.9
02:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 17 | 52 | 31 | 278 | 55 | 35 | 72 | 0 | 282 | 0 | 0 | 35 | 284 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 380 | 102 | 51 | 11 | 0 | 28 | 51 | 30 | 0 | 0 | 100 | 0 | 217 | 0 | 18 | 1050 | 30 | 0 | 6 | 0 | 17 | 221 | 0 | 0 | 0 | 1170 | 0 | 13 | 55 | 370 | 280 | 250 | 44 | 5 | 223 | 40 | 109 | 107 | 170 | 68 | 19 | 0 | 64 | 0 | 0 | 0 | 307 | 400 | 272 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 5 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8367 | 908 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1015 | 17 | 0 | 0 | 896.4 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 151 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 117 | 220 | 0 | 1000 | 580 | 17 | 6121.4 | 14488.4 | 105.91
03:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 54 | 17 | 52 | 31 | 195 | 15 | 35 | 72 | 0 | 287 | 0 | 0 | 35 | 296 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 435 | 109 | 51 | 0 | 0 | 27 | 51 | 30 | 0 | 0 | 100 | 0 | 218 | 0 | 27 | 1050 | 16 | 0 | 6 | 0 | 17 | 221 | 0 | 0 | 0 | 1160 | 0 | 13 | 55 | 360 | 300 | 270 | 44 | 5 | 223 | 40 | 108 | 107 | 100 | 0 | 19 | 0 | 64 | 0 | 0 | 0 | 290 | 400 | 272 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 10 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8188 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 0 | 0 | 0 | 821.65 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1000 | 580 | 17 | 5923.65 | 14111.65 | 105.92
04:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35 | 17 | 52 | 31 | 45 | 0 | 17 | 72 | 0 | 288 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 490 | 0 | 51 | 0 | 0 | 26 | 17 | 30 | 0 | 0 | 100 | 0 | 219 | 0 | 32 | 1050 | 0 | 0 | 6 | 0 | 17 | 221 | 0 | 0 | 0 | 1160 | 0 | 13 | 55 | 340 | 305 | 275 | 44 | 5 | 218 | 36 | 108 | 108 | 0 | 0 | 19 | 0 | 62 | 0 | 0 | 0 | 290 | 400 | 272 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 95 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7840 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 0 | 0 | 0 | 822.11 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 152 | 51 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1000 | 580 | 17 | 5859.11 | 13699.11 | 105.92
05:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 35 | 17 | 52 | 31 | 45 | 0 | 17 | 72 | 0 | 289 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 390 | 0 | 51 | 0 | 0 | 15 | 17 | 30 | 0 | 0 | 100 | 0 | 219 | 0 | 36 | 1050 | 0 | 0 | 6 | 0 | 17 | 221 | 0 | 0 | 0 | 1160 | 0 | 13 | 55 | 340 | 305 | 275 | 44 | 5 | 223 | 36 | 76 | 107 | 0 | 0 | 14 | 0 | 62 | 0 | 0 | 0 | 290 | 400 | 272 | 28 | 30 | 0 | 0 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7691 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 0 | 0 | 0 | 825.98 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 152 | 51 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 117 | 220 | 0 | 1000 | 580 | 17 | 5810.98 | 13501.98 | 105.94
06:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 42 | 31 | 0 | 0 | 17 | 17 | 0 | 281 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 34 | 13 | 22 | 0 | 395 | 0 | 15 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 12 | 0.05 | 219 | 0 | 36 | 1050 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1130 | 0 | 13 | 55 | 350 | 300 | 270 | 44 | 5 | 223 | 36 | 16 | 107 | 0 | 0 | 14 | 0 | 58 | 0 | 1 | 0 | 291 | 400 | 272 | 28 | 30 | 0 | 0 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 58 | 0.18 | 67 | 0 | 0 | 0 | 12 | 7250.23 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 0 | 0 | 0 | 832.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 307 | 117 | 220 | 0 | 1000 | 580 | 17 | 5713.81 | 12964.04 | 105.95
07:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17 | 17 | 35 | 31 | 0 | 0 | 17 | 17 | 0 | 304 | 0 | 0 | 0 | 313 | 0 | 0 | 3 | 34 | 13 | 22 | 0 | 530 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 0.34 | 219 | 0 | 36 | 1050 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1120 | 2 | 13 | 55 | 335 | 330 | 290 | 44 | 5 | 202 | 39 | 16 | 107 | 0 | 0 | 14 | 0 | 56 | 0 | 19 | 0 | 291 | 400 | 272 | 28 | 30 | 0 | 1 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 58 | 4.11 | 67 | 0 | 0.3 | 11.21 | 8 | 7474.96 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1015 | 0 | 0 | 0 | 841.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3 | 0 | 0 | 2.97 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.27 | 153 | 51 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 8 | 0.01 | 0 | 307 | 117 | 220 | 0 | 1000 | 580 | 0 | 5792.37 | 13267.33 | 105.96
08:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 35 | 31 | 45 | 12 | 17 | 72 | 0 | 288 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 34 | 12 | 22 | 0 | 420 | 0 | 15 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 12 | 1.91 | 220 | 0 | 14 | 1050 | 0 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 | 1075 | 6 | 13 | 55 | 280 | 300 | 265 | 44 | 5 | 222 | 36 | 16 | 107 | 0 | 0 | 14 | 0 | 60 | 0 | 40 | 0 | 295 | 400 | 272 | 28 | 29 | 0 | 7 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 58 | 13.84 | 67 | 0 | 0.7 | 27.19 | 12 | 7351.64 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1015 | 0 | 0 | 0 | 825.92 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 42.55 | 37 | 0 | 0 | 9.73 | 150 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1.49 | 155 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0.9 | 31 | 0.02 | 0 | 307 | 117 | 180 | 0 | 1000 | 580 | 0 | 5849.61 | 13201.25 | 105.97
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 17 | 35 | 31 | 45 | 15 | 17 | 72 | 0 | 281 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 34 | 11 | 19 | 0 | 420 | 0 | 15 | 0 | 0 | 19 | 0 | 0 | 17 | 0 | 12 | 2.87 | 221 | 0 | 8 | 1050 | 0 | 0 | 0 | 0 | 17 | 217 | 0 | 0 | 0 | 1005 | 7 | 13 | 55 | 280 | 305 | 235 | 44 | 5 | 191 | 33 | 16 | 107 | 0 | 0 | 19 | 0 | 62 | 0 | 52 | 0 | 290 | 398 | 274 | 28 | 29 | 0 | 8 | 8 | 0 | 80 | 0 | 95 | 0 | 100 | 17 | 58 | 10.48 | 67 | 0 | 0.7 | 45.4 | 12 | 7306.45 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1015 | 0 | 0 | 0 | 836.24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 19.86 | 69 | 0 | 0 | 17.36 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.54 | 155 | 50 | 0 | 20 | 0 | 0 | 0 | 0 | 1.2 | 96 | 0.04 | 0 | 307 | 115 | 180 | 0 | 989 | 580 | 0 | 6031.24 | 13337.69 | 105.97
10:00 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 38 | 31 | 45 | 15 | 35 | 90 | 0 | 285 | 0 | 0 | 0 | 297 | 0 | 0 | 5 | 34 | 11 | 19 | 0 | 400 | 0 | 15 | 0 | 0 | 28 | 0 | 0 | 35 | 0 | 12 | 3.43 | 221 | 0 | 8 | 1050 | 0 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 | 1080 | 14 | 10 | 55 | 300 | 325 | 260 | 44 | 5 | 180 | 36 | 16 | 107 | 0 | 0 | 19 | 0 | 62 | 0 | 69 | 0 | 285 | 393 | 274 | 28 | 29 | 0 | 11 | 8 | 0 | 79 | 0 | 96 | 0 | 100 | 17 | 58 | 13 | 115 | 0 | 1.6 | 53.1 | 12 | 7596.13 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1015 | 0 | 0 | 0 | 829.55 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 21.38 | 47 | 0 | 0 | 25.12 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.44 | 153 | 50 | 0 | 18 | 0 | 0 | 0 | 0 | 2.7 | 62 | 0.17 | 0 | 307 | 115 | 180 | 0 | 948 | 580 | 0 | 5968.36 | 13564.49 | 106
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 17 | 17 | 53 | 31 | 45 | 15 | 0 | 90 | 0 | 287 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 34 | 0 | 14 | 0 | 420 | 0 | 15 | 0 | 0 | 26 | 0 | 0 | 35 | 0 | 12 | 4.07 | 219 | 0 | 5 | 1050 | 0 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 | 1080 | 17 | 6 | 55 | 330 | 325 | 260 | 44 | 5 | 198 | 35 | 16 | 107 | 0 | 0 | 8 | 0 | 68 | 0 | 78 | 0 | 260 | 383 | 270 | 28 | 28 | 0 | 12 | 8 | 0 | 81 | 0 | 96 | 0 | 100 | 17 | 58 | 9.02 | 115 | 0 | 1 | 33.65 | 12 | 7629.74 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1015 | 0 | 0 | 0 | 826.68 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 31.91 | 113 | 0 | 0 | 21.81 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.77 | 155 | 49 | 0 | 24 | 0 | 0 | 0 | 0 | 2.6 | 205 | 0.17 | 0 | 307 | 115 | 220 | 0 | 951 | 580 | 0 | 6234.94 | 13864.68 | 105.98
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 74 | 31 | 52 | 15 | 25 | 108 | 0 | 300 | 0 | 0 | 0 | 314 | 0 | 0 | 13 | 34 | 10 | 18 | 0 | 530 | 0 | 15 | 0 | 0 | 46 | 0 | 0 | 35 | 0 | 36 | 3.81 | 218 | 0 | 8 | 1050 | 0 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 | 1178 | 5 | 13 | 46 | 390 | 335 | 280 | 44 | 5 | 204 | 35 | 16 | 107 | 0 | 0 | 14 | 0 | 70 | 0 | 77 | 0 | 280 | 381 | 260 | 28 | 28 | 0 | 12 | 8 | 0 | 80 | 0 | 96 | 0 | 100 | 17 | 58 | 1.51 | 115 | 0 | 0 | 9.32 | 10 | 8067.64 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 1015 | 0 | 0 | 0 | 852.96 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 37.46 | 105 | 0 | 0 | 8.32 | 156 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.1 | 157 | 48 | 0 | 14 | 0 | 0 | 0 | 0 | 3.6 | 112 | 0.04 | 0 | 307 | 117 | 220 | 0 | 969 | 580 | 0 | 6081.49 | 14149.13 | 105.98
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 17 | 17 | 65 | 15 | 140 | 15 | 24 | 108 | 0 | 277 | 0 | 0 | 17 | 327 | 0 | 0 | 18 | 34 | 10 | 18 | 0 | 380 | 0 | 45 | 0 | 0 | 53 | 0 | 1 | 35 | 0 | 90 | 3.58 | 217 | 0 | 9 | 1050 | 26 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 | 1224 | 17 | 13 | 8 | 330 | 285 | 245 | 44 | 5 | 198 | 34 | 32 | 107 | 12 | 2 | 19 | 0 | 64 | 0 | 42 | 0 | 281 | 386 | 270 | 28 | 27 | 0 | 12 | 8 | 0 | 79 | 0 | 94 | 0 | 100 | 17 | 45 | 1.2 | 75 | 0 | 0 | 12.13 | 2 | 7818.91 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.31 | 1015 | 0 | 0 | 0 | 919.4 | 0 | 0 | 0 | 57 | 20 | 0 | 0 | 0 | 0 | 35.07 | 72 | 0 | 0 | 11.96 | 156 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.41 | 156 | 50 | 0 | 12 | 70 | 0 | 0 | 0 | 3.2 | 19 | 0.22 | 16 | 307 | 117 | 180 | 0 | 966 | 580 | 10 | 6000.57 | 13819.48 | 105.98
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 55 | 15 | 145 | 15 | 32 | 108 | 0 | 274 | 0 | 0 | 55 | 330 | 0 | 0 | 22 | 34 | 10 | 18 | 0 | 380 | 0 | 15 | 0 | 0 | 41 | 0 | 14 | 35 | 0 | 90 | 3.23 | 217 | 0 | 3 | 1050 | 0 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 | 1130 | 18 | 13 | 8 | 360 | 280 | 240 | 44 | 5 | 187 | 35 | 40 | 107 | 0 | 17 | 19 | 0 | 68 | 0 | 66 | 0 | 283 | 386 | 270 | 28 | 28 | 0 | 8 | 8 | 0 | 81 | 0 | 95 | 0 | 100 | 17 | 45 | 5 | 45 | 0 | 0.3 | 3.42 | 0 | 7724.95 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1015 | 0 | 0 | 0 | 912.03 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 38.22 | 43 | 0 | 0 | 45.66 | 146 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5.23 | 158 | 48 | 0 | 5 | 70 | 0 | 0 | 0 | 1.2 | 10 | 0.23 | 16 | 307 | 117 | 180 | 0 | 927 | 580 | 17 | 5896.57 | 13621.52 | 105.98
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 17 | 0 | 52 | 15 | 95 | 15 | 0 | 108 | 0 | 291 | 0 | 0 | 55 | 333 | 0 | 0 | 7 | 34 | 10.5 | 18 | 0 | 440 | 0 | 15 | 0 | 0 | 45 | 0 | 7 | 35 | 0 | 50 | 2.19 | 217 | 0 | 3 | 1050 | 0 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 | 1100 | 12 | 13 | 8 | 360 | 315 | 280 | 44 | 5 | 204 | 36 | 15 | 107 | 0 | 17 | 8 | 0 | 68 | 0 | 20 | 0 | 280 | 381 | 270 | 26 | 28 | 0 | 4 | 8 | 0 | 81 | 0 | 96 | 0 | 100 | 17 | 45 | 5.45 | 45 | 0 | 0.1 | 2.63 | 0 | 7604.87 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 982 | 0 | 0 | 0 | 914.98 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 16.91 | 30 | 0 | 0 | 36.13 | 154 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.66 | 155 | 49 | 0 | 6 | 34 | 0 | 0 | 0 | 0.6 | 7 | 0.43 | 0 | 307 | 117 | 180 | 0 | 921 | 580 | 17 | 5784.71 | 13389.58 | 105.99
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 2 | 52 | 15 | 95 | 0 | 0 | 126 | 0 | 284 | 0 | 0 | 17 | 330 | 0 | 0 | 7 | 34 | 10 | 18 | 0 | 470 | 0 | 15 | 0 | 0 | 49 | 0 | 7 | 35 | 0 | 0 | 1.35 | 218 | 0 | 2 | 1050 | 0 | 0 | 0 | 0 | 17 | 213 | 0 | 0 | 0 | 1160 | 8 | 11 | 8 | 393 | 300 | 265 | 44 | 5 | 202 | 36 | 0 | 109 | 0 | 17 | 8 | 0 | 64 | 0 | 24 | 0 | 285 | 386 | 272 | 26 | 27 | 0 | 2 | 8 | 0 | 85 | 0 | 96 | 0 | 0 | 17 | 45 | 2.2 | 45 | 0 | 0.5 | 7.59 | 0 | 7451.64 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 950 | 0 | 0 | 0 | 913.77 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 6.96 | 2 | 0 | 0 | 5.73 | 154 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.42 | 155 | 49 | 0 | 2 | 34 | 0 | 0 | 0 | 0.6 | 12 | 0.11 | 0 | 200 | 117 | 220 | 0 | 965 | 580 | 17 | 5758.59 | 13210.23 | 105.99
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 52 | 15 | 95 | 0 | 55 | 126 | 0 | 293 | 0 | 0 | 17 | 328 | 0 | 0 | 1 | 34 | 10 | 18 | 0 | 500 | 0 | 15 | 0 | 0 | 39 | 0 | 7 | 35 | 0 | 0 | 0.12 | 218 | 0 | 10 | 1050 | 2 | 0 | 0 | 0 | 23 | 213 | 0 | 0 | 0 | 1160 | 2 | 13 | 8 | 385 | 305 | 270 | 44 | 5 | 192 | 36 | 0 | 109 | 0 | 17 | 8 | 0 | 66 | 0 | 4 | 0 | 290 | 390 | 270 | 27 | 27 | 0 | 1 | 8 | 0 | 85 | 0 | 95 | 0 | 0 | 17 | 45 | 0.11 | 55 | 0 | 0 | 0 | 9 | 7542.23 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 974 | 0 | 0 | 0 | 916.96 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 2.65 | 3 | 0 | 0 | 1.25 | 151 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.11 | 154 | 49 | 0 | 0 | 34 | 0 | 0 | 0 | 0.1 | 12 | 0.07 | 0 | 200 | 117 | 220 | 0 | 980 | 580 | 17 | 5775.14 | 13317.37 | 105.99
18:00 | 0 | 37 | 50 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 17 | 17 | 80 | 15 | 105 | 10 | 55 | 162 | 0 | 301 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 34 | 10 | 18 | 0 | 530 | 12 | 15 | 0 | 0 | 19 | 0 | 42 | 54.36 | 0 | 56 | 0 | 219 | 0 | 13 | 1050 | 18 | 0 | 0 | 0 | 50 | 215 | 0 | 0 | 0 | 1180 | 0 | 13 | 8 | 365 | 325 | 285 | 35 | 5 | 202 | 36 | 11 | 110 | 9 | 25 | 19 | 0 | 72 | 0 | 0 | 0 | 295 | 385 | 264 | 27 | 27 | 0 | 0 | 8 | 0 | 85 | 0 | 94 | 0 | 0 | 17 | 52 | 0 | 84 | 0 | 0 | 0 | 12 | 8005.36 | 907 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1001 | 0 | 0 | 0 | 1015.86 | 0 | 12 | 0 | 90 | 13 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 156 | 50 | 45 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 116 | 220 | 0 | 970 | 575 | 54 | 6101.86 | 14107.22 | 106
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 35 | 17 | 125 | 15 | 80 | 25 | 55 | 162 | 0 | 277 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 350 | 17 | 98 | 2 | 0 | 31 | 34 | 52 | 54.36 | 0 | 100 | 0 | 220 | 0 | 13 | 1050 | 93 | 0 | 5 | 6 | 70 | 216 | 0 | 0 | 0 | 1160 | 0 | 50 | 8 | 320 | 275 | 240 | 35 | 5 | 221 | 36 | 60 | 109 | 34 | 66 | 19 | 0 | 66 | 8 | 0 | 1 | 307 | 394 | 274 | 28 | 29 | 0 | 0 | 8 | 0 | 86 | 0 | 97 | 0 | 0 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 12 | 8322.36 | 907 | 0 | 33 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1000 | 0 | 0 | 0 | 1314.8 | 0 | 38 | 0 | 113 | 58 | 0 | 52 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 156 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 280 | 115 | 220 | 0 | 1100 | 575 | 54 | 6894.8 | 15217.16 | 106.01
19:30 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 17 | 133 | 0 | 15 | 15 | 35 | 162 | 0 | 294 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 400 | 17 | 98 | 10 | 0 | 35 | 34 | 52 | 54.36 | 0 | 100 | 0 | 220 | 0 | 17 | 1050 | 34 | 0 | 6 | 8 | 70 | 216 | 0 | 0 | 0 | 1160 | 0 | 102 | 8 | 320 | 305 | 270 | 35 | 5 | 202 | 36 | 68 | 110 | 17 | 74 | 19 | 0 | 74 | 8 | 0 | 10 | 305 | 392 | 274 | 28 | 30 | 0 | 0 | 8 | 0 | 86 | 0 | 93 | 0 | 0 | 17 | 87 | 0 | 153 | 0 | 0 | 0 | 12 | 8316.36 | 907 | 0 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 978 | 10 | 0 | 0 | 1319.99 | 0 | 38 | 0 | 113 | 35 | 0 | 52 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 156 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 116 | 180 | 0 | 1100 | 575 | 54 | 6768.99 | 15085.35
20:00 | 0 | 71 | 50 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 54 | 17 | 134 | 0 | 15 | 15 | 35 | 162 | 0 | 289 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 34 | 10.5 | 17 | 0 | 385 | 17 | 98 | 10 | 0 | 23 | 34 | 52 | 54.36 | 0 | 100 | 0 | 221 | 0 | 21 | 1050 | 16 | 0 | 6 | 8 | 70 | 216 | 0 | 0 | 0 | 1160 | 0 | 102 | 8 | 320 | 305 | 270 | 35 | 5 | 202 | 36 | 68 | 110 | 17 | 74 | 11 | 0 | 74 | 0 | 0 | 8 | 297 | 393 | 274 | 28 | 30 | 0 | 0 | 8 | 0 | 86 | 0 | 94 | 0 | 0 | 17 | 87 | 0 | 161 | 0 | 0 | 0 | 12 | 8279.86 | 907 | 0 | 29 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982 | 16 | 0 | 0 | 1321 | 0 | 38 | 0 | 113 | 35 | 0 | 52 | 37 | 0 | 0 | 0 | 30 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 155 | 51 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 117 | 220 | 0 | 1100 | 575 | 54 | 6873 | 15152.86 | 106.01
21:00 | 0 | 52 | 50 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 54 | 17 | 134 | 0 | 15 | 0 | 35 | 53 | 0 | 300 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 34 | 10.5 | 17 | 0 | 390 | 17 | 102 | 10 | 0 | 34 | 34 | 52 | 54.36 | 0 | 100 | 0 | 221 | 0 | 23 | 1050 | 16 | 0 | 6 | 8 | 70 | 220 | 0 | 0 | 0 | 1224 | 0 | 102 | 8 | 320 | 300 | 270 | 44 | 5 | 205 | 35 | 34 | 110 | 16 | 53 | 16 | 0 | 70 | 0 | 0 | 8 | 304 | 392 | 274 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 96 | 0 | 0 | 17 | 87 | 0 | 161 | 0 | 0 | 0 | 12 | 8165.86 | 907 | 0 | 29 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 17 | 0 | 0 | 1318.07 | 0 | 39 | 0 | 113 | 35 | 0 | 52 | 37 | 0 | 0 | 0 | 32 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 154 | 51 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 117 | 220 | 0 | 1100 | 575 | 54 | 6818.07 | 14983.93 | 106.02
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 54 | 17 | 133 | 0 | 15 | 0 | 35 | 52 | 0 | 300 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 34 | 10.5 | 16 | 0 | 530 | 17 | 104 | 11 | 0 | 16 | 34 | 52 | 54.36 | 0 | 100 | 0 | 221 | 0 | 22 | 1050 | 16 | 0 | 7 | 8 | 70 | 220 | 0 | 0 | 0 | 1224 | 0 | 48 | 8 | 320 | 305 | 270 | 44 | 5 | 199 | 36 | 34 | 109 | 16 | 53 | 19 | 0 | 70 | 0 | 0 | 8 | 290 | 393 | 274 | 28 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 96 | 0 | 0 | 17 | 88 | 0 | 191 | 0 | 0 | 0 | 0 | 8239.86 | 907 | 0 | 27 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 17 | 0 | 0 | 1296.42 | 0 | 39 | 0 | 113 | 35 | 0 | 52 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 154 | 51 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 116 | 220 | 0 | 1100 | 575 | 54 | 6743.42 | 14983.28 | 160.02
23:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 17 | 125 | 3 | 15 | 4 | 55 | 162 | 0 | 291 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 34 | 10.5 | 16 | 0 | 360 | 17 | 104 | 12 | 0 | 45 | 34 | 52 | 35 | 7 | 100 | 0 | 220 | 0 | 25 | 1000 | 21 | 0 | 6 | 8 | 80 | 219 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 300 | 270 | 230 | 44 | 0 | 180 | 36 | 45 | 110 | 16 | 65 | 19 | 5 | 72 | 0 | 0 | 8 | 285 | 395 | 220 | 29 | 30 | 0 | 0 | 16 | 0 | 86 | 0 | 95 | 0 | 0 | 17 | 87 | 0 | 193 | 0 | 0 | 0 | 0 | 7928.5 | 917 | 0 | 26 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1067 | 17 | 0 | 0 | 1307.16 | 0 | 38 | 0 | 113 | 45 | 0 | 52 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 153 | 51 | 32 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 116 | 220 | 0 | 1100 | 575 | 54 | 6803.16 | 14731.66 | 106.03
Total KWH | 0 | 1144320 | 613920 | 0 | 0 | 0 | 0 | 0 | 8956800 | 0 | 0 | 712800 | 407160 | 1764000 | 504480 | 2169360 | 359709 | 711010 | 2298240 | 0 | 7005382 | 0 | 0 | 676212 | 7450540 | 0 | 0 | 92046 | 842400 | 256200 | 452880 | 0 | 10793181.82 | 425291 | 1078909 | 84480 | 0 | 672000 | 404689 | 505926 | 651649 | 33600 | 1497600 | 25559 | 5236215 | 0 | 414720 | 25163636.36 | 600509 | 0 | 73440 | 63261 | 809599 | 5096917 | 0 | 0 | 0 | 27550906 | 104240 | 555345 | 786182 | 8145000 | 7735900 | 6494000 | 981552 | 127680 | 5050000 | 873432 | 1177920 | 2612450 | 659040 | 662760 | 372100 | 50160 | 1584000 | 66629 | 496382 | 42416 | 6990000 | 9399500 | 6444000 | 666000 | 690000 | 0 | 80893 | 266520 | 0 | 2015040 | 0 | 1912500 | 0 | 1520590 | 430200 | 1507200 | 62712 | 2368800 | 0 | 5900 | 202000 | 216240 | 190954830.18 | 21879273 | 0 | 155040 | 183424 | 0 | 0 | 0 | 0 | 0 | 75456 | 350640 | 23978178 | 104640 | 0 | 0 | 23845020 | 0 | 445205 | 0 | 1180800 | 482496 | 0 | 367344 | 73482 | 0 | 240168 | 459900 | 304526 | 0 | 193504 | 3707182 | 0 | 0 | 0 | 0 | 0 | 9236800 | 0 | 18240 | 3813000 | 1204364 | 245979 | 102183 | 1256534 | 0 | 0 | 0 | 15609.84 | 566640 | 1428 | 774048 | 6895000 | 2791000 | 5174680 | 0 | 24181818 | 14177454.55 | 565200 | 149046256.39 | 340001086.57

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14149.13 | MW | 12:00 Hr. | Energy Generated |  |  | 340.0011 |  | MKWHr.
| Day Peak Demand |  |  | 14340.13 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.607 |  | MKWHr.
| Evening Peak Generation |  |  | 15217.16 | MW | 19:00 Hr. | Energy Demand |  |  | 346.6081 |  | MKWHr.
| Evening Peak Demand |  |  | 15820.16 | MW | 19:00 Hr. | Maximum Temperature |  |  | 31.3 |  | °C
| Minimum Generation of the Day |  |  | 12964.04 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 856.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 15624.96 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.8787 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.915 | 0 | 12.2036 | 0 | 0 | 0.092046 | 0 | 0 | 47.2106 | Gas | 124.4187 | Gas | 432765996.4394
| Chattogram Zone |  |  | 5.5116 | 52.7145 | 6.229 | 0 | 5.2362 | 0.1298 | 0 | 0.672 | 70.4931 | Coal | 126.9644 | Coal | 914204201.2643
| Cumilla Zone |  |  | 33.1783 | 0 | 3.2143 | 0 | 0 | 0.49638 | 1.584 | 0 | 38.4729 | HFO | 32.3834 | HFO | 642060697.35
| Mymensingh Zone |  |  | 0 | 0 | 4.5224 | 0 | 0 | 0.27061 | 0 | 0 | 4.7931 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.9042 | 0 | 0 | 0 | 0 | 0.080893 | 0 | 0 | 29.985 | Hydro | 5.2362 | Hydro | 523621.5
| Khulna Zone |  |  | 0 | 23.9782 | 0.51856 | 0 | 0 | 0.35064 | 21.8793 | 0 | 46.7267 | Solar | 3.018 | Solar | 46821450.0388
| Barishal Zone |  |  | 7.9657 | 45.2543 | 1.3392 | 0 | 0 | 0.001428 | 0 | 0 | 54.5606 | Import | 47.3083 | Import | 292409209.23
| Rajshahi Zone |  |  | 12.944 | 0 | 2.8539 | 0 | 0 | 0.91181 | 23.845 | 0 | 40.5547 | Wind | 0.672 | Wind | 9972480
| Rangpur Zone |  |  | 0 | 5.0174 | 1.5025 | 0 | 0 | 0.68443 | 0 | 0 | 7.2043
| Total |  |  | 124.4187 | 126.9644 | 32.3834 | 0 | 5.2362 | 3.018 | 47.3083 | 0.672 | 340.0011
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 432765996.4394 |  | Hydro | 523621.5
|  |  |  | Coal | 914204201.2643 |  | Solar | 46821450.0388
|  |  |  | HFO | 642060697.35 |  | Import | 292409209.23
|  |  |  | HSD | 0 |  | Wind | 9972480
[5 empty] | Total: | 233,87,57,655 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8793 | Peak Hr Flow | 907.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48804127.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.845 | Peak Hr Flow | 1314.80 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2392 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.584 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2584 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.3083 | Peak Hr Flow | 2287.80 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 88 |  | 5986
|  |  |  | Chattogram |  | 0 |  | 1630
|  |  |  | Cumilla |  | 0 |  | 1465
|  |  |  | Mymensingh |  | 206 |  | 1220
|  |  |  | Sylhet |  | 276 |  | 788
|  |  |  | Khulna |  | 5 |  | 1630
|  |  |  | Barishal |  | 0 |  | 389
|  |  |  | Rajshahi |  | 2 |  | 1367
|  |  |  | Rangpur |  | 0 |  | 841
|  |  |  | Total |  | 577 |  | 15316
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 374.5
|  |  |  | Total Unavailable Capacity |  |  |  | 674.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:45 | 11:43 | Bheramara 230/132kV S/S Transformer-2 HT Forced S/D Due to Bushing & Clamp Maintenance .
| 08:45 | 11:44 | Bheramara 230/132kV S/S Transformer-2 LT Forced S/D Due to Bushing & Clamp Maintenance.
|  | 09:12 | Chowmuhani 230/132/33kV S/S TR2 is restored.
| 09:30 | 16:44 | Ishurdi 230/132kV S/S 230 kV Bus 1 Project Work S/D Due to Jack bus upgradation work
|  | 09:33 | Bogura 230/132kV S/S T-01 LT is restored.
|  | 09:33 | Bogura 230/132kV S/S T-01 HT is restored.
| 09:45 | 12:19 | Dohazari 132/33kV S/S 100 MW PPP Scheduled S/D Due to High Temperature Maintenance
|  | 09:47 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 09:47 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
| 09:49 |  | Mirsorai 400/230/33kV S/S ATR-2 LT Project Work S/D Due to project work
| 09:50 | 10:07 | Keranigonj 230/132/33kV S/S TR-2 LT Tripped showing 86.1 relays Due to PBS 33kv feeder
fault.
|  | 10:07 | Keranigonj 230/132/33kV S/S TR-2 LT is restored.
| 10:17 |  | Mirsorai 400/230/33kV S/S ATR-2 HT Project Work S/D Due to project work
| 10:25 | 13:31 | Pubail 132/33kV S/S TRX-1 HT Scheduled S/D Due to Red hot Maintenance.
| 10:25 | 13:31 | Pubail 132/33kV S/S TRX-1 LT Scheduled S/D Due to Red Hot Maintenance.
| 10:27 | 16:15 | Feni 230/132kV S/S Bus-A (230kV) Project Work S/D Due to SAS & DFDR works
| 10:53 | 18:10 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Fire work
| 10:54 | 18:08 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Fire work
| 12:00 |  | Day Peak Generation: 14149 MW.
| 13:27 | 00:14 | Bagerhat-Mongla 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance relay | [7 empty] | and 11.0MW load
|  |  | z-2 relays. and from Mongla 132/33kV end Due to Y-Phase Conductor has snapped and fallen | [7 empty] | interrup. Mongla
|  |  | on structure. | [7 empty] | 132/33kV end
| 13:33 | 14:01 | Barishal 230/132kV S/S T-4 LT Tripped showing O/C E/F Realy relays Due to For | [7 empty] | 23.0MW load
|  |  | Sarupkathi-2 feeder fault. | [7 empty] | interrup.
| 13:33 | 14:01 | Barishal 230/132kV S/S T-5 LT Tripped showing O/C E/F relay relays Due to For | [7 empty] | 23.0MW load
|  |  | Sarupkathi-2 feeder fault. | [7 empty] | interrup.
| 14:28 | 18:36 | Pubail 132/33kV S/S TRX-2 LT Scheduled S/D Due to Red hot maintenance.
| 14:28 | 18:36 | Pubail 132/33kV S/S TRX-2 HT Scheduled S/D Due to Red hot maintenance.
| 14:34 | 15:46 | Khulna (C) S/S Tr-2 415 T LT Tripped showing O/C & E/F TRIP relays Due to For 33KV Khulna | [7 empty] | 5.0MW load
|  |  | PBS feeder fault | [7 empty] | interrup.
| 14:34 | 15:03 | Khulna (C) S/S TR-1 425T LT Tripped showing O/C AND E/F TRIP A PHASE. relays Due to For | [7 empty] | 12.0MW load
|  |  | 33kv PbS Khulna feeder fault. | [7 empty] | interrup.
| 14:34 | 15:46 | Khulna (C) S/S Tr-2 415 T HT Tripped showing 96D(pressure release device) relays Due to | [7 empty] | 5.0MW load
|  |  | FOR 33KV Khulna PBS feeder fault. | [7 empty] | interrup.
| 15:11 |  | Sylhet 225 MW CCPP Tripped with remarks:- GT
| 15:11 |  | Sylhet 225 MW CCPP ST Tripped with remarks:- None
| 15:11 |  | Sylhet 225 MW CCPP GT Tripped with remarks:- GT Trip Due To Flame Failure.
| 15:42 | 17:12 | Nabinagar 132/33kV S/S T-2 LT Scheduled S/D Due to PRD canopy installation work
| 15:43 | 17:11 | Nabinagar 132/33kV S/S T-1 HT Scheduled S/D Due to PRD canopy installation work.
| 16:15 | 00:13 | Bagerhat-Mongla 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end.
| 19:00 |  | Evening Peak Generation: 15217 MW.
| 21:07 | 22:33 | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33kv bus maintenance | [7 empty] | 100.0MW load
interrup.
| 21:07 | 22:33 | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33kv bus maintenance | [7 empty] | 100.0MW load
interrup.
| 06:34 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230/132kV end. and from Haripur
230/132kV end Due to High temperature maintenance
| 06:53 |  | Payra 1320 MW Shutdown with remarks:- unit-2
| 06:58 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Project Work S/D from Joydebpur 132/33kV end.
| 06:58 |  | Ghorasal-Joydeb-B 132kV Ckt-1 Project Work S/D from Joydebpur 132/33kV end.
| 07:00 |  | Minimum Generation: 12380 MW.
| 07:05 |  | Payra 1320 MW Synchronized
| 07:05 |  | Payra 1320 MW Synchronized with remarks:- Unit-1 Running & Unit-2 SD
| 07:12 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Source DS maintenance of Banaripara 33 | [7 empty] | 45.0MW load
|  |  | kV feeder | [7 empty] | interrup.
| 07:13 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Source DS maintenance of Banaripara 33 | [7 empty] | 45.0MW load
|  |  | kV feeder | [7 empty] | interrup.
| 07:15 |  | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to 33 kv Bus section 1 Red hot maintenance | [7 empty] | 19.0MW load
interrup.
| 07:16 |  | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to 33 kv Bus section 1 Red hot maintenance | [7 empty] | 19.0MW load
interrup.
| 07:38 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D
| 07:38 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 312 | 8956800 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 277 | 7005382 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 25 | 359709 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7450540 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 712800 | Fuel Shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 504480 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 711010 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 676212 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 256200 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 452880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 613920 | Fuel Shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 80 | 2169360 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 125 | 1764000 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1144320 | Fuel Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2298240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 92046 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 407160 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 10793181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 34 | 842400 | Fuel Shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2047 | 47210640.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 6 | 63261 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104240 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 5 | 73440 | Fuel Shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5236215 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5096917 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 70 | 809599 | Fuel Shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 505926 | plant availability zero
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 404689 | Fuel Shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 33600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 414720 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 2 | 84480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 98 | 1078909 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 651649 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Fuel Shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1497600 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 425291 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 93 | 600509 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 27550906 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 31 | 672000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1050 | 25163636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3221.36 | 70493146.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 221 | 5050000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 275 | 7735900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 6494000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 8145000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 873432 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 127680 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 786182 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 35 | 981552 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 555345 | Fuel Shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 1 | 42416 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 109 | 2612450 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 659040 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1584000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 66629 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 372100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 50160 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 66 | 662760 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 60 | 1177920 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 496382 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1553 | 38472948
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 62712 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2368800 | ps availability is less
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1507200 | ps availability is less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 202000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 216240 | Fuel Shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 430200 | Fuel Shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 278 | 4793052
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 80893 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 666000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 690000 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 97 | 1912500 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2015040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1520590 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 266520 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 307 | 6990000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 274 | 6444000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 394 | 9399500 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1223 | 29985043
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 907 | 21879273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 155040 | Fuel Shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 183424 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 104640 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 75456 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 350640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1000 | 23978178 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1975 | 46726651
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24181818 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 77 | 774048 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2791000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 575 | 14177454.55 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5174680 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 565200 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 6895000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1428 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2421 | 54560628.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 240168 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 445205 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 73482 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 146 | 3707182 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 378 | 9236800 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 304526 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Fuel Shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 52 | 367344 | Fuel Shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 58 | 482496 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1180800 | Fuel Shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 18240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1314.8 | 23845020 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 193504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 459900 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2144.8 | 40554667
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1204364 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3813000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1256534 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 15609.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 245979 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 102183 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 566640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 354 | 7204309.84
Eastern Grid Total |  |  |  |  | 16961.086 | 8322.36 | 190954830.18
Western Grid Total |  |  |  |  | 11731.125 | 6894.8 | 149046256.39
National Grid Total |  |  |  |  | 28692.211 | 15217.16 | 340001086.57
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-09-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10518.86 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4220.5 | MW
i) Dhaka area |  |  | 5897.76 |  | MW | i) Khulna area |  |  |  | 1625 | MW
ii) Chattogram area |  |  | 1630.1 |  | MW | ii) Barishal area |  |  |  | 389.1 | MW
iii) Cumilla area |  |  | 1465 |  | MW | iii) Rajshahi area |  |  |  | 1365.4 | MW
iv) Mymensingh area |  |  | 1014 |  | MW | iv) Rangpur area |  |  |  | 841 | MW
v) Sylhet area |  |  | 512 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14739.36 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 12:00 | 72 | Hatirjheel | 80 | 12:00 | 143 | Pabna | 97 | 18:30
2 | AKSML | 146.8 | 01:00 | 73 | Ishurdi | 78 | 19:30 | 144 | Palashbari | 120 | 00:00
3 | Aftabnagar | 42 | 15:00 | 74 | Jaldhaka | 66 | 00:00 | 145 | Panchagarh | 39 | 00:00
4 | Agargaon | 143 | 19:00 | 75 | Jamalpur | 149 | 00:00 | 146 | Patiya | 30.2 | 18:30
5 | Agrabad | 78 | 13:00 | 76 | Jashore | 117 | 13:00 | 147 | Patnitala | 31 | 00:00
6 | Amnura | 26 | 00:00 | 77 | Jhenaidah | 86 | 18:30 | 148 | Patuakhali | 69.5 | 00:00
7 | Araihazar | 106 | 23:00 | 78 | Joydebpur | 174 | 11:00 | 149 | Payra | 38 | 22:00
8 | Ashuganj | N/A | N/A | 79 | Joypurhat | 57 | 00:00 | 150 | Postogola | 64 | 13:00
9 | Ashuganj-230 | 90 | 23:00 | 80 | Juldah | 18 | 00:00 | 151 | Pubail | 49 | 12:00
10 | BSRM | 191 | 07:00 | 81 | KSRM | 23 | 15:00 | 152 | Purbachal | 29 | 00:00
11 | Bagerhat | 98.5 | 19:30 | 82 | Kabirpur | 277 | 18:30 | 153 | Purbasadipur | 115 | 00:00
12 | Bajitpur | 105 | 00:00 | 83 | Kachua | 98 | 00:00 | 154 | Rahanpur | 33 | 22:00
13 | Bakerganj | 13 | 00:00 | 84 | Kaliganj | 36 | 18:30 | 155 | Rahim | 43 | 22:00
14 | Bakulia | 102 | 15:00 | 85 | Kallyanpur | 105 | 12:00 | 156 | Rajbari | 81 | 00:00
15 | Banani | 68 | 11:00 | 86 | Kalurghat | 42 | 14:00 | 157 | Rajendrapur | 121 | 00:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 86 | 13:00 | 158 | Rajshahi | 92 | 00:00
17 | Barapukuria | 52 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi-230 | 96 | 13:00
18 | Barguna | 22 | 19:30 | 89 | Kasba | 38 | 20:00 | 160 | Ramganj | 112 | 21:00
19 | Barishal | 99 | 14:00 | 90 | Kazla | 133 | 13:00 | 161 | Rampur | 46 | 00:00
20 | Barishal-230 | 96 | 00:00 | 91 | Keranigonj | 88 | 13:00 | 162 | Rangamati | 17 | 18:30
21 | Baroaulia | 40 | 10:00 | 92 | Khagrachori | 36 | 18:00 | 163 | Rangpur | 120 | 13:00
22 | Baroirhat | 63 | 19:30 | 93 | Khulna | 58 | 12:00 | 164 | Ruppur | 4 | 09:00
23 | Bashundhara | 207 | 12:00 | 94 | Khulshi | 200 | 15:00 | 165 | SSM | 0 | 00:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 134 | 00:00 | 166 | Saidpur | 96 | 08:00
25 | Beanibazar | 80 | 03:00 | 96 | Kodda | 327 | 18:30 | 167 | Santhia | 32 | 00:00
26 | Benapole | 58 | 00:00 | 97 | Kulaura | 51 | 01:00 | 168 | Satkhira | 120 | 00:00
27 | Bhaluka | 156 | 00:00 | 98 | Kurigram | 56 | 00:00 | 169 | Satmasjid | 104 | 13:00
28 | Bhandaria | 54 | 01:00 | 99 | Kushtia | 144 | 18:30 | 170 | Savar | 205 | 18:30
29 | Bhangura | 50 | 16:00 | 100 | Laksam | 36 | 00:00 | 171 | SevenRings | 23.08 | 12:00
30 | Bheramara(GK) | 61 | 20:00 | 101 | Lakshmipur | 53 | 23:00 | 172 | ShahCement | 32 | 11:00
31 | Bhulta | 210 | 18:30 | 102 | Lalbag | 85 | 13:00 | 173 | Shahjadpur | 78 | 19:00
32 | Bog-Sherpur | 68 | 00:00 | 103 | Lalmonirhat | 52 | 00:00 | 174 | Shahjibazar | 143 | 00:00
33 | Bogura | 188 | 00:00 | 104 | MI_Cement | 11.7 | 10:00 | 175 | Shahmirpur | 60 | 23:00
34 | Borhanuddin | 76 | 23:00 | 105 | Madanganj | 48 | 00:00 | 176 | Shariatpur | 91 | 01:00
35 | Brahmanbaria | 146 | 20:00 | 106 | Madaripur | 103 | 00:00 | 177 | Sherpur | 138 | 22:00
36 | Cantonment | 130 | 14:00 | 107 | Madartek | 82 | 01:00 | 178 | Shikalbaha | 18 | 00:00
37 | Chandina | 19 | 11:00 | 108 | Madunaghat | 53 | 19:00 | 179 | Shitalakhya | 83.1 | 13:00
38 | Chandpur | 86 | 00:00 | 109 | Magura | 61 | 18:30 | 180 | Sholosohor | 48 | 14:00
39 | Chandraghona | 33 | 18:00 | 110 | Mahasthangarh | 79 | 00:00 | 181 | Shomvuganj | 40 | 01:00
40 | Chapai | 61 | 00:00 | 111 | Maijdee | 40 | 22:00 | 182 | Shyampur | 154 | 12:00
41 | Charfasson | 35 | 21:00 | 112 | Manikganj | 148 | 00:00 | 183 | Siddhirganj | 143 | 09:00
42 | Charsaidpur | 38 | 13:00 | 113 | Maniknagar | 66 | 14:00 | 184 | Sirajganj | 108 | 00:00
43 | Chauddagram | 78 | 23:00 | 114 | Matarbari | 58 | 23:00 | 185 | Sitakunda | 36 | 19:00
44 | Chhatak | 41 | 06:00 | 115 | Matuail | 80 | 10:00 | 186 | Sonargaon | 125 | 17:00
45 | Chowmuhani | 157 | 18:30 | 116 | Metrorail_Motijheel | 37 | 20:00 | 187 | Sreemongol | 91 | 00:00
46 | Chuadanga | 113 | 00:00 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreepur | 124 | 06:00
47 | Coxsbazar | 150 | 18:30 | 118 | Millgate | 104 | 10:00 | 189 | Srinagar | 47.7 | 00:00
48 | Cumilla(N) | 157 | 23:00 | 119 | Mirpur | 148 | 13:00 | 190 | Sunamganj | 56 | 08:00
49 | Cumilla(S) | 150 | 19:30 | 120 | Mirsorai | 53 | 14:00 | 191 | Sylhet | 137 | 13:00
50 | Daganbhuiyan | 35 | 01:00 | 121 | Mirzapur | 46 | 18:00 | 192 | Sylhet_(South) | 56 | 00:00
51 | Daudkandi | 131 | 07:00 | 122 | Mithapukur | 64 | 18:30 | 193 | TK | 0 | 00:00
52 | DhakaUniversity | 98 | 13:00 | 123 | Modern | N/A | N/A | 194 | Tangail | 170 | 23:00
53 | Dhamrai | 100 | 16:00 | 124 | Mogbazar | 67.2 | 00:00 | 195 | Taraganj | 30 | 08:00
54 | Dhanmondi | 116 | 13:00 | 125 | Mongla | 40 | 09:00 | 196 | Tasnim | 44 | 21:00
55 | Dohazari | 123 | 20:00 | 126 | Motijheel | 51 | 13:00 | 197 | Thakurgaon | 88 | 19:00
56 | Faridpur | 168 | 00:00 | 127 | Muktagacha | 38 | 11:00 | 198 | Tongi | 167 | 11:00
57 | Fatullah | 116 | 09:00 | 128 | Munshiganj | 114 | 00:00 | 199 | Ullahpara | 37 | 00:00
58 | Fenchuganj | 42 | 05:00 | 129 | Muradnagar | 56 | 19:00 | 200 | Ullon | 46 | 00:00
59 | Feni | 112 | 20:00 | 130 | Mymensingh | 148 | 00:00 | 201 | Uttara | 99 | 13:00
60 | GPH | 75 | 19:30 | 131 | Nabinagar | 110 | 08:00 | 202 | UttaraNew | 55 | 13:00
61 | Ghatail | 102 | 00:00 | 132 | Naogaon | 114 | 00:00 | 203 | Zigatola | 92 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Narail | 54 | 21:00
63 | Ghorashal-230 | 84 | 10:00 | 134 | Narinda | 77.5 | 13:00
64 | Goalpara | 36 | 18:30 | 135 | Narshingdi | 192 | 00:00
65 | Gollamari | 102 | 19:30 | 136 | Natore | 140 | 21:00
66 | Gopalganj | 102 | 00:00 | 137 | Nawabganj | 54.1 | 23:00
67 | Gulshan | 118 | 11:00 | 138 | Netrakona | 122 | 17:00
68 | Halishahar | 104 | 11:00 | 139 | New | 84 | 12:00
69 | HaripurSBU | 140 | 00:00 | 140 | Niamatpur | 52 | 21:00
70 | Hasnabad | 103 | 00:00 | 141 | Noapara | 44 | 20:00
71 | Hathazari | 99 | 18:30 | 142 | PHP | 12 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15624.96 | 260 |  | 15896.96
1:00 | 14924.12 | 293 |  | 15230.12
2:00 | 14488.4 | 315 |  | 14817.4
3:00 | 14111.65 | 308 |  | 14433.65
4:00 | 13699.11 | 283 |  | 13995.11
5:00 | 13501.98 | 193 |  | 13703.98
6:00 | 12964.04 | 183 |  | 13155.28
7:00 | 13267.33 | 232 |  | 13509.33
8:00 | 13201.25 | 229 |  | 13440.25
9:00 | 13337.69 | 235 |  | 13583.69
10:00 | 13564.49 | 257 |  | 13833.49
11:00 | 13864.68 | 175 |  | 14047.68
12:00 | 14149.13 | 183 |  | 14340.13
13:00 | 13819.48 | 157 |  | 13983.48
14:00 | 13621.52 | 137 |  | 13764.52
15:00 | 13389.58 | 191 |  | 13589.58
16:00 | 13210.23 | 224 |  | 13444.23
17:00 | 13317.37 | 192 |  | 13518.37
18:00 | 14107.22 | 302 |  | 14423.22
19:00 | 15217.16 | 577 |  | 15820.16
19:30 | 15085.35 | 393 |  | 15496.35
20:00 | 15152.86 | 399 |  | 15569.86
21:00 | 14983.93 | 409 |  | 15410.93
22:00 | 14983.28 | 430 |  | 15432.28
23:00 | 14731.66 | 443 |  | 15194.66
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8795 | 6829.96 | 15624.96 | DAILY GENERATION CURVE
00:30 | 8670 | 6604.54 | 15274.54
01:00 | 8545 | 6379.12 | 14924.12 | 24-09-2026
01:30 | 8456 | 6250.26 | 14706.26
02:00 | 8367 | 6121.4 | 14488.4
02:30 | 8277.5 | 6022.525 | 14300.025
03:00 | 8188 | 5923.65 | 14111.65
03:30 | 8014 | 5891.38 | 13905.38
04:00 | 7840 | 5859.11 | 13699.11
04:30 | 7765.5 | 5835.045 | 13600.545
05:00 | 7691 | 5810.98 | 13501.98
05:30 | 7470.615 | 5762.395 | 13233.01
06:00 | 7250.23 | 5713.81 | 12964.04
06:30 | 7362.595 | 5753.09 | 13115.685
07:00 | 7474.96 | 5792.37 | 13267.33
07:30 | 7413.3 | 5820.99 | 13234.29
08:00 | 7351.64 | 5849.61 | 13201.25
08:30 | 7329.045 | 5940.425 | 13269.47
09:00 | 7306.45 | 6031.24 | 13337.69
09:30 | 7451.29 | 5999.8 | 13451.09
10:00 | 7596.13 | 5968.36 | 13564.49
10:30 | 7612.935 | 6101.65 | 13714.585
11:00 | 7629.74 | 6234.94 | 13864.68
11:30 | 7848.69 | 6158.215 | 14006.905
12:00 | 8067.64 | 6081.49 | 14149.13
12:30 | 7943.275 | 6041.03 | 13984.305
13:00 | 7818.91 | 6000.57 | 13819.48
13:30 | 7771.93 | 5948.57 | 13720.5
14:00 | 7724.95 | 5896.57 | 13621.52
14:30 | 7664.91 | 5840.64 | 13505.55
15:00 | 7604.87 | 5784.71 | 13389.58
15:30 | 7528.255 | 5771.65 | 13299.905
16:00 | 7451.64 | 5758.59 | 13210.23
16:30 | 7496.935 | 5766.865 | 13263.8
17:00 | 7542.23 | 5775.14 | 13317.37
17:30 | 7773.795 | 5938.5 | 13712.295
18:00 | 8005.36 | 6101.86 | 14107.22
18:30 | 8163.86 | 6498.33 | 14662.19
19:00 | 8322.36 | 6894.8 | 15217.16
19:30 | 8316.36 | 6768.99 | 15085.35
20:00 | 8279.86 | 6873 | 15152.86
20:30 | 8222.86 | 6845.535 | 15068.395 |  | Executive Engineer
21:00 | 8165.86 | 6818.07 | 14983.93 |  | Network Operation Division
21:30 | 8202.86 | 6780.745 | 14983.605
22:00 | 8239.86 | 6743.42 | 14983.28
22:30 | 8084.18 | 6773.29 | 14857.47
23:00 | 7928.5 | 6803.16 | 14731.66

## En-Curve
QF-LDC-12
Date | 24-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3451 | 1509 | 821 | 0 | 68 | 1316.96 | 218 | 5332 | 0 | 563 | 2321 | 0 | 0 | 25 | 260 | DAILY ENERGY CURVE
00:30 | 3525.5 | 1550 | 866.5 | 0 | 67 | 1213.04 | 217.5 | 5322 | 0 | 430.5 | 2055 | 0 | 0 | 27.5 | 276.5 | 24-09-2026
01:00 | 3600 | 1591 | 912 | 0 | 66 | 1109.12 | 217 | 5312 | 0 | 298 | 1789 | 0 | 0 | 30 | 293
01:30 | 3625.5 | 1529 | 910 | 0 | 65 | 1002.76 | 217 | 5317.5 | 0 | 294.5 | 1716 | 0 | 0 | 29 | 304 | Energy Generated | 340.0011 |  | MKWHr
02:00 | 3651 | 1467 | 908 | 0 | 64 | 896.4 | 217 | 5323 | 0 | 291 | 1643 | 0 | 0 | 28 | 315 | Energy not Served | 6.607 |  | MKWHr
02:30 | 3680 | 1493 | 908 | 0 | 64 | 859.025 | 217.5 | 5279.5 | 0 | 277 | 1494.5 | 0 | 0 | 27.5 | 311.5 | Total Energy Requirement | 346.6081 |  | MKWHr
03:00 | 3709 | 1519 | 908 | 0 | 64 | 821.65 | 218 | 5236 | 0 | 263 | 1346 | 0 | 0 | 27 | 308
03:30 | 3737 | 1549.5 | 908 | 0 | 63 | 821.88 | 218.5 | 5251 | 0 | 246 | 1084 | 0 | 0 | 26.5 | 295.5
04:00 | 3765 | 1580 | 908 | 0 | 62 | 822.11 | 219 | 5266 | 0 | 229 | 822 | 0 | 0 | 26 | 283
04:30 | 3767.5 | 1526 | 906 | 0 | 62 | 824.045 | 219 | 5240.5 | 0 | 229 | 806 | 0 | 0 | 20.5 | 238
05:00 | 3770 | 1472 | 904 | 0 | 62 | 825.98 | 219 | 5215 | 0 | 229 | 790 | 0 | 0 | 15 | 193
05:30 | 3767 | 1471 | 904.5 | 0 | 60 | 829.205 | 219 | 5219 | 1.305 | 173 | 572 | 0 | 0 | 17 | 188
06:00 | 3764 | 1470 | 905 | 0 | 58 | 832.43 | 219 | 5223 | 2.61 | 117 | 354 | 0 | 0 | 19 | 183
06:30 | 3796 | 1549 | 904.5 | 0 | 57 | 837.19 | 219 | 5249.5 | 33.495 | 117 | 340 | 0 | 0 | 13 | 207.5
07:00 | 3828 | 1628 | 904 | 0 | 56 | 841.95 | 219 | 5276 | 64.38 | 117 | 326 | 0 | 0 | 7 | 232
07:30 | 3746 | 1535.5 | 904.5 | 0 | 58 | 833.935 | 219.5 | 5254 | 164.355 | 108 | 401.5 | 0 | 0 | 9 | 230.5
08:00 | 3664 | 1443 | 905 | 0 | 60 | 825.92 | 220 | 5232 | 264.33 | 99 | 477 | 0 | 0 | 11 | 229
08:30 | 3672.5 | 1431.5 | 905.5 | 0 | 61 | 831.08 | 220.5 | 5191.5 | 335.89 | 108 | 497 | 0 | 0 | 15 | 232
09:00 | 3681 | 1420 | 906 | 0 | 62 | 836.24 | 221 | 5151 | 407.45 | 117 | 517 | 0 | 0 | 19 | 235
09:30 | 3706.5 | 1409 | 906 | 0 | 62 | 832.895 | 221 | 5167 | 420.695 | 133.5 | 569 | 0 | 0 | 23.5 | 246
10:00 | 3732 | 1398 | 906 | 0 | 62 | 829.55 | 221 | 5183 | 433.94 | 150 | 621 | 0 | 0 | 28 | 257
10:30 | 3746.5 | 1402.5 | 906.5 | 0 | 65 | 828.115 | 220 | 5185 | 539.97 | 185 | 609 | 0 | 0 | 27 | 216
11:00 | 3761 | 1407 | 907 | 0 | 68 | 826.68 | 219 | 5187 | 646 | 220 | 597 | 0 | 0 | 26 | 175
11:30 | 3814.5 | 1485 | 907 | 0 | 69 | 839.82 | 218.5 | 5245.5 | 524.585 | 220 | 647 | 0 | 0 | 36 | 179
12:00 | 3868 | 1563 | 907 | 0 | 70 | 852.96 | 218 | 5304 | 403.17 | 220 | 697 | 0 | 0 | 46 | 183
12:30 | 3746.5 | 1440.5 | 906.5 | 0 | 67 | 886.18 | 217.5 | 5326 | 342.125 | 160.5 | 842 | 0 | 0 | 49.5 | 170
13:00 | 3625 | 1318 | 906 | 0 | 64 | 919.4 | 217 | 5348 | 281.08 | 101 | 987 | 0 | 0 | 53 | 157
13:30 | 3628 | 1315.5 | 906.5 | 0 | 66 | 915.715 | 217 | 5281.5 | 284.285 | 107.5 | 951.5 | 0 | 0 | 47 | 147
14:00 | 3631 | 1313 | 907 | 0 | 68 | 912.03 | 217 | 5215 | 287.49 | 114 | 916 | 0 | 0 | 41 | 137
14:30 | 3679.5 | 1344.75 | 906.5 | 0 | 68 | 913.505 | 217 | 5179.5 | 236.795 | 110.5 | 806.5 | 0 | 0 | 43 | 164
15:00 | 3728 | 1376.5 | 906 | 0 | 68 | 914.98 | 217 | 5144 | 186.1 | 107 | 697 | 0 | 0 | 45 | 191
15:30 | 3721.5 | 1411.75 | 906.5 | 0 | 66 | 914.375 | 217.5 | 5126.5 | 143.28 | 107 | 638.5 | 0 | 0 | 47 | 207.5
16:00 | 3715 | 1447 | 907 | 0 | 64 | 913.77 | 218 | 5109 | 100.46 | 107 | 580 | 0 | 0 | 49 | 224
16:30 | 3709.5 | 1473 | 907 | 0 | 65 | 915.365 | 218 | 5128 | 67.435 | 107 | 629.5 | 0 | 0 | 44 | 208
17:00 | 3704 | 1499 | 907 | 0 | 66 | 916.96 | 218 | 5147 | 34.41 | 107 | 679 | 0 | 0 | 39 | 192
17:30 | 3707 | 1523 | 907 | 0 | 69 | 966.41 | 218.5 | 5164.5 | 17.205 | 167.5 | 943.18 | 0 | 0 | 29 | 247
18:00 | 3710 | 1547 | 907 | 0 | 72 | 1015.86 | 219 | 5182 | 0 | 228 | 1207.36 | 0 | 0 | 19 | 302
18:30 | 3616.5 | 1446 | 907 | 0 | 69 | 1165.33 | 219.5 | 5276.5 | 0 | 361 | 1576.36 | 0 | 0 | 25 | 439.5
19:00 | 3523 | 1345 | 907 | 0 | 66 | 1314.8 | 220 | 5371 | 0 | 494 | 1945.36 | 0 | 0 | 31 | 577
19:30 | 3512 | 1374 | 907 | 0 | 74 | 1319.99 | 220 | 5349 | 0 | 484 | 1810.36 | 0 | 0 | 35 | 393
20:00 | 3559 | 1392.5 | 907 | 0 | 74 | 1321 | 221 | 5353 | 0 | 484 | 1818.36 | 0 | 0 | 23 | 399
20:30 | 3557.5 | 1416 | 907 | 0 | 72 | 1319.535 | 221 | 5401 | 0 | 469 | 1676.86 | 0 | 0 | 28.5 | 404
21:00 | 3556 | 1439.5 | 907 | 0 | 70 | 1318.07 | 221 | 5449 | 0 | 454 | 1535.36 | 0 | 0 | 34 | 409
21:30 | 3563.5 | 1503 | 907 | 0 | 70 | 1307.245 | 221 | 5449 | 0 | 417.5 | 1520.36 | 0 | 0 | 25 | 419.5
22:00 | 3571 | 1566.5 | 907 | 0 | 70 | 1296.42 | 221 | 5449 | 0 | 381 | 1505.36 | 0 | 0 | 16 | 430
22:30 | 3407.5 | 1473.5 | 912 | 0 | 71 | 1301.79 | 220.5 | 5449.5 | 0 | 384.5 | 1606.68 | 0 | 0 | 30.5 | 436.5
23:00 | 3244 | 1380.5 | 917 | 0 | 72 | 1307.16 | 220 | 5450 | 0 | 388 | 1708 | 0 | 0 | 45 | 443
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 24-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 115 | 12 | 450 | 192 | 1486 | 558 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 102 | 10 | 360 | 166 | 1352 | 544
2:00 | 102 | 16 | 364 | 180 | 1390 | 566 |  | Import | 0
3:00 | 106 | 21 | 370 | 184 | 1366 | 562
4:00 | 118 | 29 | 380 | 182 | 1376 | 596 | Ishurdi-Ghorashal Ckt-2 | Export | 3807127.27
5:00 | 127 | 34 | 410 | 186 | 1478 | 612
6:00 | 140 | 41 | 410 | 176 | 1600 | 652 |  | Import | 0
7:00 | 120 | 34 | 340 | 182 | 1498 | 648
8:00 | 147 | 45 | 390 | 198 | 1640 | 660 | Sirajganj-Sreepur Ckt-1 | Export | 2754000
9:00 | 187 | 68 | 490 | 214 | 1772 | 772
10:00 | 198 | 78 | 500 | 212 | 1856 | 818 |  | Import | 0
11:00 | 205 | 76 | 540 | 218 | 1814 | 768
12:00 | 173 | 66 | 460 | 224 | 1636 | 776 | Sirajganj-Sreepur Ckt-2 | Export | 2763000
13:00 | 167 | 57 | 470 | 226 | 1612 | 772
14:00 | 183 | 64 | 490 | 206 | 1814 | 806 |  | Import | 0
15:00 | 192 | 66 | 500 | 206 | 1854 | 812
16:00 | 202 | 71 | 520 | 210 | 1862 | 840 | Gopalganj-Aminbazar Ckt-1 | Export | 19720000
17:00 | 186 | 65 | 510 | 240 | 1724 | 770
18:00 | 172 | 54 | 520 | 216 | 1638 | 734 |  | Import | 0
18:30 | 157 | 40 | 490 | 208 | 1636 | 678
19:00 | 166 | 41 | 520 | 198 | 1706 | 678 | Gopalganj-Aminbazar Ckt-2 | Export | 19760000
19:30 | 169 | 45 | 500 | 200 | 1670 | 692
20:00 | 165 | 38 | 510 | 196 | 1672 | 650 |  | Import | 0
21:00 | 168 | 42 | 500 | 190 | 1658 | 696
22:00 | 170 | 58 | 510 | 216 | 1602 | 674 |  | Total Export | 48804127.27
23:00 | 177 | 57 | 530 | 216 | 1732 | 644 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 374 | 03:00 | 362 | 12:00 | Madunaghat | 395 | 02:00 | 387 | 13:00
Amtali | 412 | 04:00 | 408 | 12:00 | Meghnaghat | 381 | 02:00 | 369 | 12:00
Ashuganj | 400 | 5:00 | 380 | 13:00 | Mirsorai | 394 | 01:00 | 381 | 12:00
Bhulta | 390 | 03:00 | 371 | 12:00 | Payra | 413 | 03:00 | 410 | 12:00
Bibiana | 377 | 02:00 | 370 | 12:00 | Rahanpur | 411 | 06:00 | 401 | 01:00
BIPTC | 402 | 03:00 | 393 | 12:00 | Rampal | 395 | 05:00 | 386 | 22:00
Bogura | 396 | 05:00 | 385 | 01:00
Gopalganj | 390 | 03:00 | 381 | 21:00
Kaliakoir | 368 | 03:00 | 350 | 12:00
Korerhat | 391 | 00:00 | 381 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 02:00 | 217 | 12:00 | Hasnabad | 223 | 05:00 | 213 | 12:00
AKSML | 236 | 00:00 | 224 | 12:00 | Hathazari | 230 | 00:00 | 225 | 12:00
Aminbazar | 228 | 08:00 | 218 | 10:00 | Ishurdi | 234 | 05:00 | 223 | 21:00
Ashuganj | 223 | 04:00 | 214 | 12:00 | Jhenaidah | 228 | 09:00 | 213 | 20:00
Ashuganj-400 | 223 | 04:00 | 214 | 12:00 | Kachua | 225 | 01:00 | 216 | 16:00
Baghabari | 231 | 05:00 | 225 | 00:00 | Kaliakoir | 229 | 03:00 | 215 | 12:00
Barapukuria | 228 | 16:00 | 222 | 00:00 | Keranigonj | 225 | 03:00 | 215 | 10:00
Barapukuria-230 | 228 | 16:00 | 222 | 00:00 | Khulna(S) | 228 | 14:00 | 218 | 20:00
Barapukuria(N) | 230 | 16:00 | 224 | 00:00 | Korerhat | 222 | 00:00 | 216 | 12:00
Barishal | 226 | 14:00 | 220 | 22:00 | Madunaghat | 233 | 00:00 | 227 | 16:00
Bheramara | 233 | 09:00 | 220 | 21:00 | Madunaghat-400 | 235 | 01:00 | 229 | 16:00
Bhulta | 222 | 05:00 | 209 | 12:00 | Maniknagar | 220 | 04:00 | 208 | 13:00
Bibiana | 213 | 02:00 | 207 | 18:00 | Meghnaghat | 228 | 10:00 | 218 | 12:00
BIPTC | 236 | 09:00 | 221 | 21:00 | Meghnaghat-400 | 223 | 02:00 | 213 | 12:00
Birulia | 228 | 03:00 | 217 | 12:00 | Mirsorai | 230 | 01:00 | 221 | 12:00
Bogura | 239 | 05:00 | 232 | 01:00 | Naogaon | 227 | 14:00 | 213 | 00:00
Bogura-400 | 239 | 05:00 | 232 | 01:00 | Purbasadipur | 226 | 23:00 | 219 | 00:00
Borhanuddin | 229 | 08:00 | 225 | 21:00 | Rajshahi | 233 | 09:00 | 220 | 21:00
BSRM | 224 | 01:00 | 217 | 12:00 | Rampal | 226 | 08:00 | 218 | 20:00
Charfasson | 230 | 06:00 | 224 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 223 | 00:00 | 215 | 22:00 | Rampura | 222 | 03:00 | 207 | 13:00
Cumilla(N) | 218 | 01:00 | 210 | 12:00 | Shikalbaha | 234 | 02:00 | 225 | 16:00
Faridpur | 222 | 08:00 | 215 | 21:00 | Shyampur | 223 | 03:00 | 212 | 12:00
Fenchuganj | 214 | 06:00 | 207 | 18:00 | Siddhirganj | 222 | 03:00 | 211 | 12:00
Feni | 221 | 01:00 | 213 | 12:00 | Sirajgonj | 236 | 04:00 | 232 | 00:00
Ghorashal | 222 | 02:00 | 215 | 11:00 | Sreepur | 221 | 06:00 | 214 | 12:00
Ghorashal-230 | 217 | 03:00 | 201 | 12:00 | Tongi | 215 | 04:00 | 202 | 11:00
Gopalganj | 222 | 05:00 | 216 | 21:00
GPH | 230 | 01:00 | 224 | 11:00
Haripur | 222 | 06:00 | 209 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 01:00 | 125 | 11:00 | Madanganj | 133 | 00:00 | 126 | 13:00
Agargaon | 136 | 03:00 | 128 | 10:00 | Madaripur | 131 | 07:00 | 126 | 22:00
Agrabad | 132 | 01:00 | 126 | 12:00 | Madartek | 137 | 03:00 | 126 | 12:00
AKS | 131 | 01:00 | 126 | 12:00 | Madunaghat | 135 | 03:00 | 130 | 16:00
Aminbazar | 132 | 04:00 | 125 | 10:00 | Magura | 136 | 06:00 | 126 | 19:30
Amnura | 135 | 08:00 | 129 | 01:00 | Mahasthangarh | 136 | 14:00 | 131 | 00:00
Araihazar | 119 | 05:00 | 112 | 13:00 | Maijdee | 125 | 01:00 | 120 | 16:00
Ashuganj | 130 | 03:00 | 125 | 13:00 | Manikganj | 124 | 02:00 | 120 | 15:00
Ashuganj-230 | 135 | 06:00 | 130 | 12:00 | Maniknagar | 137 | 04:00 | 126 | 13:00
Bagerhat | 130 | 14:00 | 120 | 19:30 | Matarbari | 118 | 10:00 | 107 | 18:30
Bajitpur | 127 | 14:00 | 121 | 12:00 | Matuail | 134 | 03:00 | 126 | 12:00
Bakerganj | 133 | 14:00 | 129 | 00:00 | Metrorail_Motijheel | 137 | 04:00 | 126 | 13:00
Bakulia | 133 | 01:00 | 128 | 10:00 | Metrorail_Uttara | 131 | 04:00 | 119 | 11:00
Banani | 137 | 03:00 | 126 | 13:00 | Millgate | 134 | 14:00 | 123 | 11:00
Bangabhaban | 137 | 03:00 | 127 | 12:00 | Mirpur | 132 | 06:00 | 123 | 21:00
Barapukuria | 139 | 16:00 | 130 | 00:00 | Mirzapur | 129 | 00:00 | 121 | 15:00
Barguna | 133 | 08:00 | 129 | 21:00 | Mithapukur | 136 | 15:00 | 128 | 00:00
Barishal | 132 | 04:00 | 128 | 21:00 | MI_Cement | 132.3 | 05:00 | 122 | 12:00
Barishal-230 | 132 | 05:00 | 128 | 21:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 132 | 00:00 | 128 | 16:00 | Mogbazar | 139 | 04:00 | 128 | 13:00
Baroirhat | 130 | 08:00 | 125 | 12:00 | Mongla | 128 | 14:00 | 119 | 19:30
Bashundhara | 138 | 05:00 | 120 | 11:00 | Motijheel | 137 | 03:00 | 127 | 12:00
BashundharaCement | 133 | 00:00 | 126 | 13:00 | Muktagacha | 131 | 00:00 | 118 | 15:00
Beanibazar | 117 | 02:00 | 110 | 18:00 | Munshiganj | 133 | 01:00 | 125 | 12:00
Benapole | 137 | 06:00 | 119 | 00:00 | Muradnagar | 125 | 06:00 | 119 | 12:00
Bhaluka | 129 | 06:00 | 123 | 17:00 | Mymensingh | 132 | 13:00 | 115 | 17:00
Bhandaria | 130 | 13:00 | 120 | 01:00 | Nabinagar | 132 | 03:00 | 124 | 10:00
Bhangura | 133 | 02:00 | 127 | 00:00 | Naogaon | 137 | 14:00 | 128 | 19:30
Bheramara | 137 | 05:00 | 130 | 20:00 | Narail | 136 | 15:00 | 124 | 19:30
Bheramara(GK) | 136 | 06:00 | 130 | 20:00 | Narinda | 137 | 04:00 | 126 | 13:00
Bhulta | 119 | 05:00 | 113 | 12:00 | Narshingdi | 128 | 00:00 | 111 | 13:00
Bhulta-400 | 123 | 05:00 | 114 | 13:00 | Natore | 134 | 09:00 | 128 | 01:00
Birulia | 134 | 03:00 | 127 | 12:00 | Nawabganj | 136 | 03:00 | 128 | 13:00
Bog-Sherpur | 136 | 13:00 | 131 | 01:00 | Netrakona | 122 | 14:00 | 112 | 12:00
Bogura | 137 | 09:00 | 132 | 01:00 | New | 133 | 03:00 | 122 | 11:00
Bogura-230 | 138 | 05:00 | 133 | 01:00 | Niamatpur | 136 | 05:00 | 130 | 00:00
Brahmanbaria | 127 | 05:00 | 121 | 22:00 | Noapara | 132 | 15:00 | 123 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 03:00 | 127 | 12:00 | Pabna | 134 | 05:00 | 128 | 19:30
Chandina | 127 | 06:00 | 122 | 12:00 | Palashbari | 134 | 15:00 | 125 | 00:00
Chandpur | 133 | 02:00 | 123 | 12:00 | Panchagarh | 137 | 23:00 | 130 | 12:00
Chandraghona | 135 | 00:00 | 131 | 16:00 | Patiya | 131 | 01:00 | 126 | 16:00
Chapai | 135 | 09:00 | 129 | 01:00 | Patnitala | 135 | 07:00 | 129 | 00:00
Charsaidpur | 134 | 02:00 | 126 | 13:00 | Patuakhali | 133 | 14:00 | 129 | 00:00
Chauddagram | 126 | 02:00 | 121 | 21:00 | Payra | 134 | 00:00 | 133 | 01:00
Chhatak | 116 | 06:00 | 109 | 13:00 | PHP | 129 | 02:00 | 124 | 12:00
Chowmuhani | 125 | 00:00 | 119 | 10:00 | Postogola | 132 | 01:00 | 122 | 12:00
Chuadanga | 137 | 09:00 | 123 | 20:00 | Pubail | 129 | 07:00 | 120 | 13:00
Coxsbazar | 123 | 05:00 | 110 | 20:00 | Purbachal | 137 | 03:00 | 125 | 13:00
Cumilla(N) | 126 | 01:00 | 122 | 11:00 | Purbasadipur | 136 | 03:00 | 126 | 21:00
Cumilla(S) | 132 | 05:00 | 122 | 12:00 | Rahanpur | 138 | 07:00 | 134 | 00:00
Daganbhuiyan | 127 | 00:00 | 122 | 12:00 | Rahanpur-400 | 138 | 06:00 | 134 | 00:00
Daudkandi | 125 | 05:00 | 119 | 10:00 | Rahim | 134 | 03:00 | 126 | 13:00
DhakaUniversity | 137 | 03:00 | 127 | 12:00 | Rajbari | 126 | 05:00 | 121 | 22:00
Dhamrai | 132 | 00:00 | 126 | 10:00 | Rajendrapur | 132 | 06:00 | 127 | 11:00
Dhanmondi | 137.5 | 04:00 | 127 | 12:00 | Rajshahi | 132 | 05:00 | 126 | 01:00
Dohazari | 126 | 09:00 | 122 | 15:00 | Rajshahi-230 | 134 | 09:00 | 128 | 00:00
Faridpur | 128 | 04:00 | 124 | 00:00 | Ramganj | 126 | 00:00 | 119 | 22:00
Fatullah | 133 | 03:00 | 122 | 12:00 | Rampur | 134 | 05:00 | 126 | 16:00
Fenchuganj | 126 | 04:00 | 120 | 18:00 | Rampura | 137 | 03:00 | 126 | 13:00
Feni | 126 | 00:00 | 123 | 11:00 | Rangamati | 134 | 02:00 | 131 | 12:00
Feni-230 | 128 | 01:00 | 123 | 12:00 | Rangpur | 134 | 15:00 | 127 | 00:00
Ghatail | 128 | 13:00 | 115 | 07:00 | Ruppur | 137 | 07:00 | 130 | 21:00
Ghorashal | 134 | 22:00 | 123 | 17:00 | Saidpur | 136 | 23:00 | 131 | 12:00
Goalpara | 133 | 14:00 | 125 | 19:30 | Santhia | 134 | 08:00 | 129 | 21:00
Gollamari | 132 | 14:00 | 125 | 19:00 | Satkhira | 129 | 14:00 | 118 | 19:30
Gopalganj | 130 | 14:00 | 125 | 18:30 | Satmasjid | 135 | 02:00 | 126 | 13:00
Gopalganj-400 | 131 | 03:00 | 127 | 21:00 | Savar | 131 | 03:00 | 123 | 21:00
Gulshan | 137 | 04:00 | 126 | 13:00 | SevenRings | 131 | 03:00 | 123 | 10:00
Halishahar | 134 | 01:00 | 126 | 16:00 | ShahCement | 134 | 02:00 | 126 | 12:00
Haripur | 134 | 02:00 | 126 | 13:00 | Shahjadpur | 136 | 07:00 | 134 | 00:00
HaripurSBU | 134 | 04:00 | 127 | 12:00 | Shahjibazar | 126 | 06:00 | 121 | 13:00
Hasnabad | 134 | 04:00 | 124 | 12:00 | Shahmirpur | 134 | 02:00 | 127 | 16:00
Hathazari | 134 | 00:00 | 132 | 15:00 | Shariatpur | 130 | 06:00 | 123 | 22:00
Hatirjheel | 137 | 03:00 | 126 | 13:00 | Sherpur | 137 | 00:00 | 116 | 07:00
Ishurdi | 138 | 09:00 | 131 | 19:30 | Shikalbaha | 123 | 00:00 | 118 | 15:00
Jaldhaka | 134 | 16:00 | 128 | 00:00 | Shikalbaha-230 | 135 | 01:00 | 129 | 12:00
Jamalpur | 139 | 00:00 | 117 | 07:00 | Shitalakhya | 132.3 | 05:00 | 122 | 12:00
Jashore | 139 | 09:00 | 120 | 19:30 | Sholosohor | 134 | 01:00 | 127 | 16:00
Jhenaidah | 139 | 09:00 | 129 | 19:30 | Shomvuganj | 123 | 16:00 | 114 | 02:00
Jhenaidah-230 | 138 | 05:00 | 128 | 19:30 | Shyampur | 131 | 08:00 | 125 | 12:00
Joydebpur | 126 | 00:00 | 116 | 13:00 | Shyampur-230 | 134 | 03:00 | 124 | 12:00
Joypurhat | 135 | 10:00 | 129 | 00:00 | Siddhirganj | 134 | 02:00 | 127 | 12:00
Juldah | 134 | 01:00 | 127 | 16:00 | Sirajganj | 132 | 05:00 | 127 | 01:00
Kabirpur | 131 | 03:00 | 116 | 12:00 | Sitakunda | 134 | 02:00 | 129 | 12:00
Kachua | 128 | 01:00 | 123 | 12:00 | Sonargaon | 130 | 03:00 | 124 | 13:00
Kaliakoir | 133 | 00:00 | 126 | 15:00 | Sreemongol | 124 | 07:00 | 119 | 12:00
Kaliganj | 138 | 09:00 | 128 | 20:00 | Sreepur | 134 | 04:00 | 129 | 00:00
Kallyanpur | 130 | 00:00 | 124 | 15:00 | Srinagar | 135 | 03:00 | 129 | 10:00
Kalurghat | 135 | 01:00 | 130 | 14:00 | SSM | 140 | 01:00 | 134 | 00:00
Kamrangirchar | 136 | 02:00 | 122 | 12:00 | Sunamganj | 113 | 02:00 | 106 | 13:00
Kaptai | 138 | 5:00 | 135 | 12:00 | Sylhet | 120 | 06:00 | 111 | 18:00
Kasba | 125 | 06:00 | 118 | 12:00 | Sylhet_(South) | 120 | 06:00 | 112 | 18:00
Kazla | 136 | 04:00 | 126 | 13:00 | Tangail | 127 | 00:00 | 119 | 15:00
Keranigonj | 136 | 02:00 | 130 | 10:00 | Taraganj | 135 | 16:00 | 130 | 00:00
Khagrachori | 133 | 03:00 | 129 | 12:00 | Tasnim | 131 | 05:00 | 124 | 13:00
Khulna | 132 | 14:00 | 124 | 18:00 | Thakurgaon | 137 | 18:30 | 130 | 12:00
Khulna(S) | 133 | 14:00 | 125 | 19:30 | TK | 134 | 01:00 | 132 | 11:00
Khulshi | 132 | 03:00 | 126 | 12:00 | Tongi | 132 | 04:00 | 123 | 11:00
Kishoreganj | 128 | 15:00 | 120 | 00:00 | Ullahpara | 134 | 04:00 | 130 | 00:00
Kodda | 127 | 07:00 | 119 | 16:00 | Ullon | 137 | 03:00 | 126 | 12:00
Korerhat | 131 | 01:00 | 127 | 12:00 | Uttara | 133 | 02:00 | 118 | 12:00
KSRM | 134 | 23:00 | 128 | 16:00 | UttaraNew | 132 | 03:00 | 119 | 11:00
Kulaura | 124 | 05:00 | 120 | 13:00 | Zigatola | 136 | 02:00 | 128 | 13:00
Kurigram | 133 | 16:00 | 124 | 00:00
Kushtia | 137 | 05:00 | 129 | 19:30
Laksam | 128 | 02:00 | 121 | 22:00
Lakshmipur | 124 | 01:00 | 119 | 22:00
Lalbag | 135 | 08:00 | 129 | 12:00
Lalmonirhat | 132 | 16:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division