## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-09-2026 | during | 27-09-2026 | during | 27-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 349 | 333 | 412 | 412 | 375 | 375 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 292 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 295 | 285 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 105 | 149.36 | 149.36 | 31 | 31 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 14 | 33 | 33 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 34 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 260 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 25 | 133 | 149 | 149 | 52 | 133 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 88 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 435 | 395 | 584 | 584 | 400 | 450 | AGC, Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 88 | 88 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 1686.42 | 2502.42 | 5585.16 | 5553.16 | 2047.5 | 2495.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 216 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 111 | 111 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 49 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 34 | 34 | 55 | 55 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 9 | 42 | 42 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 65 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.71 | 0 | 4.84 | 0 | 4.84 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 278 | 300 | 300 | 111 | 111 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 85 | 110 | 110 | 111 | 111 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 60 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 144 | 163 | 163 | 55 | 55 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1170 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1050 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2664.71 | 3729.86 | 4153.8 | 4155.96 | 3623.84 | 3687.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 206 | 192 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 340 | 310 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 270 | 290 | 342.01 | 342.01 | 307 | 307 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 385 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 40 | 41.65 | 41.65 | 20 | 20.01 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 10 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 35 | 195 | 195 | 36 | 36 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 100 | 150 | 150 | 13 | 100 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 15 | 24 | 24 | 55 | 55 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 110 | 83 | 163 | 163 | 140 | 140 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 134 | 200 | 200 | 136 | 17 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 84 | 94 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 55 | 55 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 74 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 115 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1574 | 2014 | 2756.44 | 2680.44 | 2074.26 | 2060.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-09-2026 | during | 27-09-2026 | during | 27-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 188 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 86 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 57.33 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 18 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 264.53 | 309 | 538.4 | 546.5 | 280.9 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 40 | 30 | 30 | 29 | 29 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 40 | 40 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 138 | 139 | 140 | 140 | 95 | 95 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 25 | 30 | 30 | 30 | 30 | machine problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 84 | 84 | 86 | 86 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 273 | 310 | 341 | 341 | 295 | 295 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 270 | 126 | 0 | 0 | 280 | 280 | ST Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 382 | 392 | 383 | 383 | 383 | 383
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1262 | 1159 | 1064 | 1064 | 1254 | 1254
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 912 | 911 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 26 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 77 | 105 | 105 | 55 | 55 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 87 | 0 | 87 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1046 | 958 | 750 | 750 | 750 | 750 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2056 | 2022 | 3137 | 3050 | 2549 | 2462
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 979 | 1100 | 1000 | 1100 | 1000 | 1100 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 99 | 110 | 110 | 48 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 115 | 120 | 120 | 70 | 70 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 221 | 280 | 307 | 307 | 280 | 280 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.74 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1834.74 | 2214 | 2208 | 2307 | 1936 | 2097
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 63.6 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 152 | 163 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 375 | 375 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 55 | 55 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 50 | 113 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 55 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.64 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1220.33 | 1308.87 | 900 | 1300 | 900 | 1300 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.95 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2027.52 | 2243.87 | 2707.91 | 2889.99 | 1934.92 | 2338
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 48 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 110 | 160 | 160 | 110 | 110 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 180.67 | 0 | 180.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 446.3 | 366 | 671.67 | 458 | 481.67 | 347
System Total |  |  |  |  | 28843.2 | 28692.211 | 13816.22 | 16560.15 | 22822.38 | 22705.05 | 16182.09 | 17030.6
Forecast Scenario (27-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15200 |  | 500 |  | 15700
|  |  |  | 1:00 | 14580 |  | 650 |  | 15230
|  |  |  | 2:00 | 14150 |  | 700 |  | 14850
|  |  |  | 3:00 | 13760 |  | 600 |  | 14360
|  |  |  | 4:00 | 13250 |  | 550 |  | 13800
|  |  |  | 5:00 | 13080 |  | 500 |  | 13580
|  |  |  | 6:00 | 12770 |  | 350 |  | 13120
|  |  |  | 7:00 | 12680 |  | 420 |  | 13100
|  |  |  | 8:00 | 12830 |  | 450 |  | 13280
|  |  |  | 9:00 | 12650 |  | 500 |  | 13150
|  |  |  | 10:00 | 12680 |  | 550 |  | 13230
|  |  |  | 11:00 | 13180 |  | 570 |  | 13750
|  |  |  | 12:00 | 13820 |  | 750 |  | 14570
|  |  |  | 13:00 | 13970 |  | 450 |  | 14420
|  |  |  | 14:00 | 14340 |  | 460 |  | 14800
|  |  |  | 15:00 | 14460 |  | 440 |  | 14900
|  |  |  | 16:00 | 14250 |  | 480 |  | 14730
|  |  |  | 17:00 | 14370 |  | 490 |  | 14860
|  |  |  | 18:00 | 14280 |  | 510 |  | 14790
|  |  |  | 18:30 | 15180 |  | 520 |  | 15700
|  |  |  | 19:00 | 16050 |  | 525 |  | 16575
|  |  |  | 19:30 | 16000 |  | 480 |  | 16480
|  |  |  | 20:00 | 16000 |  | 430 |  | 16430
|  |  |  | 21:00 | 16240 |  | 400 |  | 16640
|  |  |  | 22:00 | 15900 |  | 500 |  | 16400
|  |  |  | 23:00 | 15900 |  | 470 |  | 16370
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 14570.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16640.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16240.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 340.39 MKWHr. |  | 40 | 30 | 80 | 70 | 30 | 70 | 20 | 35 | 25 | 400
*** This report is generated digitally from Operation Information System (OIS) at 09:03 hrs on 27-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-09-2026 | [28 empty] | Date: | 26-09-2026 | [28 empty] | Date: | 26-09-2026 | [28 empty] | Date: | 26-09-2026 | [28 empty] | Date: | 26-09-2026 | [16 empty] | Date: | 26-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 50.6 | 17 | 71 | 13 | 115 | 0 | 55 | 155 | 0 | 284 | 0 | 0 | 55 | 281 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 350 | 0 | 115 | 0 | 0 | 10 | 17 | 52 | 54.36 | 0 | 100 | 0 | 221 | 0 | 42 | 1050 | 83 | 0 | 19 | 0 | 68 | 220 | 0 | 0 | 0 | 1224 | 0 | 13 | 16 | 270 | 325 | 305 | 44 | 0 | 199 | 0 | 107 | 110 | 88 | 74 | 19 | 0 | 80 | 0 | 0 | 23 | 286 | 400 | 280 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 88 | 0 | 164 | 0 | 0 | 0 | 18 | 8508.88 | 923 | 0 | 31 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1283.75 | 0 | 38 | 0 | 113 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 156 | 0 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 280 | 117 | 220 | 0 | 1000 | 300 | 90 | 6644.95 | 15153.83 | 106.19
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 17 | 17 | 70 | 13 | 145 | 0 | 35 | 72 | 0 | 293 | 0 | 0 | 55 | 287 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 380 | 0 | 115 | 0 | 0 | 3 | 17 | 30 | 0 | 0 | 100 | 0 | 218 | 7 | 42 | 1050 | 83 | 0 | 19 | 0 | 72 | 220 | 0 | 0 | 0 | 1224 | 0 | 11 | 35 | 270 | 330 | 275 | 44 | 0 | 201 | 0 | 110 | 109 | 112 | 74 | 19 | 0 | 76 | 0 | 0 | 23 | 280 | 398 | 284 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8249.92 | 912 | 0 | 31 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1086.58 | 0 | 38 | 0 | 113 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 155 | 49 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 280 | 117 | 220 | 0 | 932 | 300 | 54 | 6328.78 | 14578.7 | 106.24
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 70 | 13 | 145 | 0 | 35 | 72 | 0 | 284 | 0 | 0 | 55 | 285 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 350 | 0 | 115 | 0 | 0 | 2 | 17 | 30 | 0 | 0 | 100 | 0 | 217 | 19 | 42 | 1050 | 80 | 0 | 19 | 0 | 85 | 220 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 270 | 320 | 265 | 44 | 0 | 199 | 0 | 108 | 109 | 130 | 74 | 19 | 0 | 74 | 0 | 0 | 23 | 273 | 400 | 284 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8149.92 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 940.01 | 0 | 38 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 156 | 49 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 280 | 117 | 220 | 0 | 907 | 300 | 54 | 6001.21 | 14151.13 | 106.23
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 17 | 17 | 70 | 13 | 15 | 0 | 35 | 72 | 0 | 283 | 0 | 0 | 35 | 287 | 0 | 0 | 0 | 143.42 | 12.7 | 22 | 0 | 375 | 0 | 115 | 0 | 0 | 9 | 17 | 30 | 0 | 0 | 100 | 0 | 213 | 37 | 42 | 1050 | 34 | 0 | 6 | 0 | 85 | 220 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 270 | 330 | 275 | 44 | 0 | 201 | 0 | 107 | 109 | 51 | 16 | 19 | 0 | 72 | 0 | 0 | 23 | 272 | 398 | 284 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 139 | 0 | 0 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7872.12 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 905.94 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 155 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 117 | 220 | 0 | 886 | 300 | 54 | 5888.14 | 13760.26 | 106.22
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 17 | 17 | 60 | 13 | 0 | 0 | 0 | 72 | 0 | 284 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 12.7 | 22 | 0 | 345 | 0 | 115 | 0 | 0 | 9 | 6 | 0 | 0 | 0 | 50 | 0 | 214 | 52 | 42 | 1050 | 0 | 0 | 0 | 0 | 85 | 220 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 270 | 325 | 265 | 44 | 0 | 197 | 0 | 50 | 109 | 0 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 271 | 399 | 284 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 138 | 0 | 0 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7473.12 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 912.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 154 | 51 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 117 | 220 | 0 | 898 | 300 | 54 | 5773.41 | 13246.53 | 106.21
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 72 | 0 | 293 | 0 | 0 | 17 | 287 | 0 | 0 | 0 | 123 | 12.7 | 22 | 0 | 390 | 0 | 45 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 0 | 214 | 51 | 42 | 1050 | 0 | 0 | 0 | 0 | 85 | 220 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 270 | 340 | 285 | 44 | 0 | 203 | 0 | 16 | 109 | 0 | 0 | 19 | 0 | 68 | 0 | 0 | 0 | 263 | 399 | 284 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 138 | 0 | 0 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7327.7 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 916.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 117 | 220 | 0 | 898 | 300 | 54 | 5753.86 | 13081.56 | 106.2
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 0 | 47 | 0 | 0 | 0 | 0 | 35 | 0 | 287 | 0 | 0 | 17 | 287 | 0 | 0 | 0 | 105 | 14 | 22 | 0 | 395 | 0 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 0.06 | 215 | 17 | 42 | 1050 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 1160 | 1 | 11 | 35 | 270 | 335 | 280 | 44 | 0 | 204 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 64 | 0 | 2 | 0 | 259 | 395 | 279 | 29 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 138 | 0 | 0 | 0 | 58 | 0.34 | 67 | 0 | 0 | 0.56 | 12 | 7111.96 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 1208 | 0 | 0 | 0 | 908.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0 | 0 | 0 | 0.16 | 136 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.04 | 154 | 49 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 280 | 117 | 220 | 0 | 911 | 300 | 17 | 5661.07 | 12773.03 | 106.19
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 0 | 24 | 0 | 0 | 0 | 0 | 35 | 0 | 282 | 0 | 0 | 17 | 281 | 0 | 0 | 6 | 105 | 14 | 22 | 0 | 345 | 0 | 15 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 0 | 220 | 17 | 34 | 1050 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1160 | 5 | 13 | 35 | 270 | 320 | 260 | 44 | 0 | 195 | 0 | 0 | 109 | 0 | 0 | 19 | 0 | 64 | 0 | 18 | 0 | 259 | 400 | 282 | 29 | 30 | 0 | 4 | 8 | 0 | 81 | 30 | 138 | 0 | 0 | 0 | 58 | 4.7 | 67 | 0 | 0.3 | 5.68 | 8 | 6986.68 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 1155 | 0 | 0 | 0 | 907.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.68 | 9 | 0 | 0 | 10.62 | 146 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.05 | 154 | 51 | 0 | 1 | 34 | 0 | 0 | 0 | 0.2 | 22 | 0.1 | 0 | 280 | 117 | 220 | 0 | 921 | 300 | 17 | 5691.41 | 12678.09 | 106.18
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 0 | 284 | 0 | 0 | 0 | 285 | 0 | 0 | 14 | 86 | 13 | 22 | 0 | 350 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12 | 1.75 | 220 | 17 | 15 | 1050 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1160 | 10 | 13 | 35 | 270 | 325 | 270 | 44 | 0 | 198 | 0 | 0 | 109 | 0 | 5 | 19 | 0 | 68 | 0 | 40 | 0 | 257 | 393 | 282 | 10 | 30 | 0 | 8 | 8 | 0 | 81 | 30 | 139 | 0 | 0 | 0 | 59 | 7 | 67 | 0 | 1.1 | 22.81 | 12 | 6989.66 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1152 | 0 | 0 | 0 | 916.93 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 26.62 | 30 | 0 | 0 | 29.82 | 153 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.79 | 156 | 50 | 0 | 14 | 34 | 0 | 0 | 0 | 1.4 | 41 | 0.27 | 0 | 280 | 116 | 220 | 0 | 910 | 300 | 0 | 5836.83 | 12826.49 | 106.17
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 0 | 285 | 0 | 0 | 0 | 290 | 0 | 0 | 23 | 51 | 12.5 | 22 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.75 | 221 | 0 | 8 | 1050 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 15 | 13 | 35 | 230 | 305 | 270 | 44 | 0 | 206 | 0 | 0 | 110 | 0 | 0 | 19 | 0 | 66 | 0 | 57 | 0 | 266 | 390 | 278 | 14 | 30 | 0 | 9 | 16 | 0 | 81 | 30 | 139 | 0 | 0 | 0 | 59 | 17 | 95 | 0 | 1.6 | 37.55 | 12 | 6843.4 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.69 | 1104 | 0 | 0 | 0 | 926.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.45 | 76 | 0 | 0 | 51.22 | 140 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 4.34 | 157 | 50 | 0 | 21 | 0 | 0 | 0 | 0 | 4 | 146 | 0.14 | 0 | 220 | 115 | 180 | 0 | 943 | 300 | 0 | 5802.36 | 12645.76 | 106.16
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 8 | 17 | 0 | 290 | 0 | 0 | 0 | 294 | 0 | 0 | 24 | 51 | 12.5 | 22 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.31 | 220 | 0 | 7 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1000 | 19 | 13 | 35 | 230 | 305 | 270 | 44 | 0 | 204 | 0 | 0 | 110 | 0 | 0 | 14 | 0 | 74 | 0 | 67 | 0 | 271 | 385 | 276 | 15 | 30 | 0 | 11 | 16 | 0 | 80 | 28 | 138 | 0 | 0 | 0 | 59 | 17.7 | 115 | 0 | 1.8 | 38.92 | 12 | 6860.23 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1052 | 0 | 0 | 0 | 928.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.09 | 74 | 0 | 0 | 33.04 | 140 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 3.21 | 157 | 50 | 0 | 37 | 0 | 0 | 0 | 0 | 4.2 | 182 | 0.21 | 0 | 218 | 115 | 180 | 0 | 968 | 300 | 0 | 5823.72 | 12683.95 | 106.2
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 0 | 293 | 0 | 0 | 0 | 290 | 0 | 0 | 33 | 86 | 12 | 22 | 0 | 405 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3.73 | 220 | 0 | 9 | 1050 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1000 | 11 | 11 | 35 | 350 | 305 | 270 | 44 | 0 | 204 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 72 | 0 | 73 | 0 | 275 | 387 | 276 | 15 | 30 | 0 | 12 | 16 | 0 | 80 | 25 | 138 | 0 | 0 | 0 | 58 | 22.27 | 115 | 0 | 2.3 | 56.5 | 12 | 7071.8 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1058 | 0 | 0 | 0 | 1120.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.35 | 62 | 0 | 0 | 63.5 | 140 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 5.57 | 158 | 50 | 0 | 28 | 0 | 0 | 0 | 0 | 6.2 | 178 | 0.55 | 0 | 218 | 115 | 220 | 0 | 971 | 300 | 0 | 6103.9 | 13175.7 | 106.14
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 17 | 0 | 25 | 0 | 0 | 0 | 35 | 17 | 0 | 302 | 0 | 0 | 0 | 295 | 0 | 0 | 34 | 143.42 | 12 | 22 | 0 | 435 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.71 | 220 | 0 | 5 | 1050 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 1160 | 12 | 13 | 35 | 385 | 340 | 270 | 44 | 0 | 206 | 0 | 0 | 110 | 0 | 0 | 13 | 0 | 84 | 0 | 74 | 0 | 273 | 382 | 270 | 39 | 30 | 0 | 12 | 16 | 0 | 77 | 25 | 138 | 0 | 0 | 0 | 58 | 20 | 115 | 0 | 2.2 | 57.33 | 12 | 7451.66 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 1046 | 0 | 0 | 0 | 1220.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.6 | 112 | 0 | 0 | 59.95 | 152 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.64 | 156 | 49 | 0 | 35 | 0 | 0 | 0 | 0 | 2.3 | 204 | 0.74 | 0 | 221 | 114 | 220 | 0 | 979 | 300 | 0 | 6364.56 | 13816.22 | 106.14
13:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 0 | 33 | 15 | 90 | 0 | 35 | 108 | 0 | 288 | 0 | 0 | 0 | 288 | 0 | 0 | 8 | 143.42 | 12 | 22 | 0 | 360 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 17 | 0 | 50 | 2.29 | 217 | 0 | 3 | 1050 | 0 | 0 | 0 | 0 | 10 | 213 | 0 | 0 | 0 | 1160 | 0 | 13 | 72 | 390 | 325 | 305 | 44 | 0 | 200 | 27 | 0 | 110 | 0 | 0 | 13 | 0 | 82 | 0 | 72 | 0 | 285 | 381 | 0 | 36 | 29 | 0 | 12 | 16 | 0 | 77 | 25 | 138 | 0 | 0 | 5 | 58 | 21.5 | 114 | 0 | 2.1 | 55.28 | 12 | 7412.59 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 1166 | 0 | 0 | 0 | 1215.25 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 14.7 | 109 | 0 | 0 | 60.74 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.37 | 155 | 50 | 0 | 35 | 45 | 0 | 0 | 0 | 7.6 | 196 | 0.68 | 0 | 280 | 115 | 220 | 0 | 985 | 300 | 0 | 6555.34 | 13967.93 | 106.14
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 0 | 94 | 15 | 95 | 0 | 35 | 108 | 0 | 299 | 0 | 0 | 35 | 294 | 0 | 0 | 29 | 143.42 | 12 | 22 | 0 | 350 | 0 | 65 | 0 | 0 | 3 | 0 | 0 | 35 | 0 | 100 | 3.18 | 217 | 0 | 2 | 1050 | 0 | 0 | 0 | 0 | 77 | 213 | 0 | 0 | 0 | 1160 | 17 | 13 | 90 | 389 | 315 | 295 | 44 | 9 | 204 | 39 | 0 | 85 | 0 | 43 | 13 | 0 | 86 | 0 | 31 | 0 | 334 | 381 | 0 | 41 | 29 | 0 | 10 | 16 | 0 | 76 | 25 | 138 | 0 | 0 | 17 | 58 | 22 | 113 | 0 | 1.6 | 27.29 | 12 | 7806.49 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1234.2 | 0 | 0 | 0 | 1208.56 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 54.93 | 53 | 0 | 0 | 54.71 | 160 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 4.41 | 156 | 49 | 0 | 30 | 72 | 0 | 0 | 0 | 5 | 176 | 0.62 | 0 | 280 | 114 | 180 | 0 | 910 | 300 | 35 | 6533.43 | 14339.92 | 106.13
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 97 | 15 | 95 | 13 | 55 | 162 | 0 | 297 | 0 | 0 | 55 | 311 | 0 | 0 | 22 | 143.42 | 12 | 22 | 0 | 430 | 0 | 65 | 0 | 0 | 5 | 0 | 0 | 54.36 | 0 | 100 | 2.45 | 217 | 0 | 0 | 1050 | 3 | 0 | 0 | 0 | 85 | 211 | 0 | 0 | 0 | 1185 | 13 | 13 | 90 | 383 | 350 | 315 | 44 | 10 | 211 | 38 | 0 | 83 | 0 | 72 | 13 | 0 | 88 | 0 | 49 | 0 | 336 | 377 | 0 | 40 | 29 | 0 | 4 | 16 | 0 | 76 | 25 | 139 | 0 | 0 | 17 | 57 | 15.15 | 112 | 0 | 1.4 | 31.89 | 12 | 8163.67 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 1193 | 0 | 0 | 0 | 1029.79 | 0 | 0 | 0 | 113 | 1 | 0 | 0 | 0 | 0 | 38.95 | 23 | 0 | 0 | 14.73 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.59 | 156 | 50 | 0 | 22 | 86 | 0 | 0 | 0 | 5 | 114 | 0.66 | 0 | 280 | 113 | 220 | 0 | 961 | 300 | 54 | 6297.72 | 14461.39 | 106.13
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 97 | 15 | 145 | 24 | 55 | 162 | 0 | 156 | 0 | 0 | 55 | 303 | 0 | 0 | 13 | 143.42 | 13 | 22 | 0 | 415 | 20 | 150 | 0 | 0 | 2 | 0 | 0 | 54.36 | 0 | 100 | 1.38 | 217 | 26 | 0 | 1050 | 48 | 0 | 3 | 0 | 85 | 213 | 0 | 0 | 0 | 1160 | 8 | 13 | 46 | 350 | 340 | 315 | 51 | 10 | 208 | 38 | 34 | 83 | 47 | 73 | 19 | 0 | 84 | 0 | 30 | 0 | 331 | 380 | 0 | 40 | 29 | 0 | 5 | 16 | 0 | 76 | 25 | 139 | 0 | 0 | 17 | 58 | 8.64 | 113 | 0 | 0.7 | 18.15 | 12 | 8177.65 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 972 | 0 | 0 | 0 | 1006.5 | 0 | 0 | 0 | 113 | 54 | 0 | 0 | 0 | 0 | 19.69 | 8 | 0 | 0 | 19.4 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 48 | 50 | 6 | 35 | 0 | 0 | 0 | 1.3 | 84 | 0.27 | 40 | 280 | 114 | 220 | 0 | 983 | 300 | 54 | 6075.16 | 14252.81 | 106.13
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 97 | 15 | 165 | 30 | 55 | 162 | 0 | 148 | 0 | 0 | 55 | 296 | 0 | 0 | 1 | 143.42 | 12 | 22 | 0 | 440 | 50 | 173 | 2 | 0 | 1 | 17 | 26 | 54.36 | 0 | 100 | 0.51 | 218 | 68 | 4 | 1050 | 75 | 0 | 16 | 1 | 85 | 212 | 0 | 0 | 0 | 1160 | 2 | 13 | 35 | 340 | 320 | 300 | 51 | 10 | 214 | 39 | 68 | 83 | 100 | 73 | 19 | 17 | 82 | 0 | 8 | 2 | 330 | 385 | 0 | 40 | 29 | 0 | 2 | 16 | 0 | 77 | 25 | 139 | 0 | 0 | 17 | 58 | 2.33 | 113 | 0 | 0.2 | 5.7 | 12 | 8395.52 | 912 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 800 | 0 | 0 | 0 | 1037.8 | 0 | 38 | 0 | 113 | 70 | 0 | 0 | 0 | 0 | 0.7 | 2 | 0 | 0 | 5.04 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 50 | 61 | 5 | 35 | 0 | 0 | 0 | 0.4 | 23 | 0.08 | 64 | 280 | 115 | 220 | 0 | 998 | 300 | 54 | 5973.02 | 14368.54 | 106.12
18:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 17 | 97 | 25 | 195 | 30 | 35 | 162 | 0 | 190 | 0 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 500 | 72 | 190 | 24 | 0 | 0 | 51 | 50 | 54.36 | 20 | 100 | 0 | 219 | 81 | 4 | 1050 | 91 | 0 | 28 | 10 | 85 | 214 | 0 | 0 | 0 | 1190 | 0 | 15 | 35 | 375 | 347 | 342 | 51 | 10 | 212 | 39 | 69 | 83 | 101 | 74 | 19 | 23 | 94 | 10 | 0 | 15 | 330 | 380 | 0 | 40 | 29 | 0 | 0 | 16 | 0 | 80 | 28 | 140 | 0 | 0 | 17 | 58 | 0 | 113 | 0 | 0 | 0 | 12 | 8919.78 | 911 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 770 | 2 | 0 | 0 | 1132.42 | 0 | 38 | 0 | 113 | 76 | 0 | 0 | 0 | 9 | 0 | 0 | 26 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 128 | 48 | 79 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 114 | 220 | 0 | 886 | 300 | 100 | 5964.42 | 14884.2 | 106.12
19:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 54 | 17 | 119 | 124 | 260 | 55 | 55 | 162 | 0 | 285 | 0 | 0 | 55 | 284 | 0 | 0 | 0 | 143.42 | 14 | 22 | 0 | 363 | 72 | 278 | 49 | 0 | 0 | 51 | 49 | 54.36 | 62 | 100 | 0 | 220 | 85 | 18 | 1050 | 145 | 0 | 39 | 25.5 | 85 | 216 | 0 | 0 | 0 | 1180 | 0 | 45 | 35 | 393 | 305 | 280 | 51 | 10 | 185 | 40 | 100 | 83 | 131 | 74 | 19 | 70 | 92 | 35 | 0 | 15 | 320 | 392 | 110 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 139 | 0 | 0 | 17 | 86 | 0 | 179 | 0 | 0 | 0 | 18 | 9701.28 | 911 | 0 | 37 | 21 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 840 | 17 | 0 | 0 | 1297.8 | 0 | 38 | 0 | 113 | 110 | 0 | 50 | 24 | 38 | 0 | 0 | 34 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 111 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 280 | 116 | 220 | 0 | 1100 | 300 | 100 | 6779.8 | 16481.08 | 106.12
19:30 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 133 | 105 | 260 | 55 | 55 | 162 | 0 | 292 | 0 | 0 | 55 | 285 | 0 | 0 | 0 | 143.42 | 14 | 22 | 0 | 395 | 60 | 278 | 65 | 0 | 0 | 51 | 49 | 54.36 | 24 | 100 | 0 | 220 | 85 | 9 | 1050 | 144 | 0 | 44 | 25.5 | 85 | 216 | 0 | 0 | 0 | 1170 | 0 | 100 | 35 | 393 | 310 | 290 | 51 | 10 | 192 | 40 | 115 | 83 | 134 | 74 | 19 | 34 | 94 | 25 | 0 | 15 | 310 | 392 | 126 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 86 | 0 | 188 | 0 | 0 | 0 | 18 | 9714.28 | 911 | 0 | 33 | 26 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 958 | 17 | 0 | 0 | 1308.87 | 0 | 38 | 0 | 113 | 70 | 0 | 50 | 28 | 25 | 0 | 0 | 34 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 110 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 280 | 115 | 220 | 0 | 1100 | 300 | 100 | 6845.87 | 16560.15
20:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 133 | 90 | 230 | 40 | 55 | 162 | 0 | 288 | 0 | 0 | 55 | 288 | 0 | 0 | 0 | 143.42 | 16 | 22 | 0 | 395 | 30 | 278 | 66 | 0 | 0 | 51 | 49 | 54.36 | 24 | 100 | 0 | 221 | 88 | 15 | 1050 | 114 | 0 | 46 | 25.5 | 85 | 217 | 0 | 0 | 0 | 1146 | 0 | 100 | 35 | 393 | 300 | 280 | 51 | 10 | 188 | 40 | 115 | 83 | 127 | 74 | 19 | 34 | 88 | 25 | 0 | 15 | 312 | 393 | 141 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 141 | 0 | 0 | 17 | 86 | 0 | 190 | 0 | 0 | 0 | 18 | 9565.28 | 911 | 0 | 33 | 36 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1053 | 17 | 0 | 0 | 1319.81 | 0 | 38 | 0 | 113 | 70 | 0 | 51 | 36 | 25 | 0 | 0 | 34 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 112 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 280 | 115 | 220 | 0 | 1100 | 300 | 100 | 6909.81 | 16475.09 | 106.11
21:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 133 | 90 | 195 | 40 | 55 | 162 | 0 | 301 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 143.42 | 16 | 22 | 0 | 480 | 28 | 278 | 42 | 0 | 0 | 51 | 50 | 54.36 | 12 | 70 | 0 | 221 | 103 | 23 | 1050 | 65 | 0 | 36 | 8 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 102 | 35 | 393 | 330 | 310 | 51 | 10 | 202 | 40 | 68 | 108 | 119 | 75 | 19 | 17 | 84 | 25 | 0 | 15 | 286 | 391 | 276 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 140 | 0 | 0 | 17 | 86 | 0 | 181 | 0 | 0 | 0 | 18 | 9373.78 | 912 | 0 | 33 | 53 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1117 | 17 | 0 | 0 | 1285.24 | 0 | 38 | 0 | 113 | 70 | 0 | 51 | 35 | 25 | 0 | 0 | 34 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 49 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 280 | 116 | 220 | 0 | 1100 | 300 | 100 | 6915.24 | 16289.02 | 106.11
22:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 54 | 17 | 128 | 90 | 195 | 55 | 55 | 162 | 0 | 301 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 143.42 | 15 | 22 | 0 | 480 | 30 | 245 | 38 | 0 | 0 | 51 | 50 | 54.36 | 12 | 70 | 0 | 221 | 105 | 26 | 1050 | 63 | 0 | 34 | 8 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 58 | 35 | 393 | 325 | 305 | 51 | 10 | 200 | 40 | 68 | 108 | 144 | 74 | 19 | 17 | 88 | 25 | 0 | 15 | 257 | 389 | 280 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 20 | 140 | 0 | 0 | 17 | 86 | 0 | 181 | 0 | 0 | 0 | 18 | 9339.78 | 912 | 0 | 32 | 45 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1197 | 17 | 0 | 0 | 1318.98 | 0 | 38 | 0 | 113 | 70 | 0 | 51 | 0 | 25 | 0 | 0 | 34 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 280 | 117 | 220 | 0 | 1100 | 300 | 100 | 6984.98 | 16324.76 | 106.11
23:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 17 | 116 | 90 | 195 | 55 | 55 | 162 | 0 | 301 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 143.42 | 15 | 22 | 0 | 500 | 30 | 245 | 38 | 0 | 0 | 51 | 50 | 54.36 | 12 | 100 | 0 | 221 | 93 | 30 | 1050 | 65 | 0 | 33 | 8 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 11 | 35 | 393 | 331 | 305 | 51 | 10 | 202 | 40 | 68 | 108 | 152 | 75 | 19 | 17 | 88 | 25 | 0 | 15 | 265 | 389 | 279 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 20 | 140 | 0 | 0 | 17 | 86 | 0 | 182 | 0 | 0 | 0 | 18 | 9327.78 | 912 | 0 | 32 | 45 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 1311.13 | 0 | 38 | 0 | 113 | 70 | 0 | 51 | 0 | 25 | 0 | 0 | 34 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 109 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 280 | 117 | 220 | 0 | 1100 | 300 | 100 | 6922.33 | 16250.11 | 106.11
Total KWH | 0 | 697920 | 270912 | 0 | 0 | 0 | 0 | 0 | 8506800 | 0 | 0 | 625320 | 242640 | 1785168 | 692640 | 2381127 | 415943 | 788312 | 2347200 | 0 | 6680873 | 0 | 0 | 798862 | 5978121 | 0 | 0 | 221914 | 3060000 | 320400 | 527400 | 0 | 9758181.82 | 392673 | 2732651 | 302400 | 0 | 51840 | 396970 | 456807 | 652171 | 144960 | 1531200 | 22921 | 5273789 | 1000300 | 467040 | 25338181.82 | 1032073 | 0 | 329280 | 91263.6 | 1571527 | 5117062 | 0 | 0 | 0 | 27594543 | 133515 | 568727 | 1003636 | 7980500 | 8203300 | 7020000 | 1090452 | 115200 | 4941000 | 435816 | 1181760 | 2430456 | 1417920 | 972720 | 420960 | 198360 | 1894080 | 176410 | 547609 | 175024 | 6864000 | 9387900 | 4864000 | 754000 | 704160 | 0 | 82488 | 374784 | 0 | 1910400 | 622944 | 3130000 | 0 | 0 | 261720 | 1543200 | 143910 | 2719200 | 0 | 14100 | 358440 | 324000 | 195566077.24 | 22052364 | 0 | 226560 | 239232 | 0 | 0 | 0 | 0 | 0 | 358848 | 539280 | 26785460 | 99360 | 0 | 0 | 26246481 | 0 | 405820 | 0 | 1384224 | 959424 | 0 | 304752 | 62450 | 160478 | 335504 | 626139 | 292800 | 0 | 410992 | 3677909 | 0 | 0 | 0 | 0 | 0 | 9454254 | 0 | 33240 | 3600000 | 1093963 | 837833 | 230456 | 1566355 | 0 | 0 | 0 | 43205.88 | 1343520 | 4509 | 723456 | 6981800 | 2752000 | 5304920 | 0 | 23461818 | 7317818.18 | 1216800 | 151134025.06 | 346700102.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13816.22 | MW | 12:00 Hr. | Energy Generated |  |  | 346.7001 |  | MKWHr.
| Day Peak Demand |  |  | 14125.22 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.382 |  | MKWHr.
| Evening Peak Generation |  |  | 16560.15 | MW | 19:30 Hr. | Energy Demand |  |  | 353.0821 |  | MKWHr.
| Evening Peak Demand |  |  | 17027.15 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 12645.76 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 855.01 |  | MMCFD
| Maximum Generation of the Day |  |  | 16560.15 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.403 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.7718 | 0 | 14.106 | 0 | 0 | 0.22191 | 0 | 0 | 46.0997 | Gas | 120.7985 | Gas | 421628000.8594
| Chattogram Zone |  |  | 5.5841 | 52.9327 | 10.6343 | 0 | 5.2738 | 0.15644 | 0 | 0.05184 | 74.6332 | Coal | 122.1736 | Coal | 882020703.1392
| Cumilla Zone |  |  | 33.6413 | 0 | 4.6909 | 0 | 0 | 0.54761 | 1.8941 | 0 | 40.7739 | HFO | 43.1178 | HFO | 864531296.358
| Mymensingh Zone |  |  | 0 | 0 | 4.8481 | 0 | 0 | 0.51645 | 0 | 0 | 5.3646 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6122 | 0 | 0 | 0 | 0 | 0.082488 | 0 | 0 | 28.6947 | Hydro | 5.2738 | Hydro | 527378.9
| Khulna Zone |  |  | 0 | 26.7855 | 0.924 | 0 | 0 | 0.53928 | 22.0524 | 0 | 50.3011 | Solar | 5.0917 | Solar | 81915245.4216
| Barishal Zone |  |  | 8.0569 | 37.7614 | 1.9403 | 0 | 0 | 0.004509 | 0 | 0 | 47.7631 | Import | 50.1929 | Import | 315245619.33
| Rajshahi Zone |  |  | 13.1322 | 0 | 3.5699 | 0 | 0 | 1.4059 | 26.2465 | 0 | 44.3545 | Wind | 0.05184 | Wind | 769305.6
| Rangpur Zone |  |  | 0 | 4.694 | 2.4042 | 0 | 0 | 1.6172 | 0 | 0 | 8.7153
| Total |  |  | 120.7985 | 122.1736 | 43.1178 | 0 | 5.2738 | 5.0917 | 50.1929 | 0.05184 | 346.7001
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 421628000.8594 |  | Hydro | 527378.9
|  |  |  | Coal | 882020703.1392 |  | Solar | 81915245.4216
|  |  |  | HFO | 864531296.358 |  | Import | 315245619.33
|  |  |  | HSD | 0 |  | Wind | 769305.6
[5 empty] | Total: | 256,66,37,549 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0524 | Peak Hr Flow | 911.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43514018.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.2465 | Peak Hr Flow | 1308.87 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1727 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.8941 | Peak Hr Flow | 94.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2570 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.1929 | Peak Hr Flow | 2313.87 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 66 |  | 6061
|  |  |  | Chattogram |  | 0 |  | 1552
|  |  |  | Cumilla |  | 4 |  | 1563
|  |  |  | Mymensingh |  | 132 |  | 1435
|  |  |  | Sylhet |  | 231 |  | 818
|  |  |  | Khulna |  | 0 |  | 1799
|  |  |  | Barishal |  | 6 |  | 517
|  |  |  | Rajshahi |  | 8 |  | 1564
|  |  |  | Rangpur |  | 0 |  | 1060
|  |  |  | Total |  | 447 |  | 16369
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 374.5
|  |  |  | Total Unavailable Capacity |  |  |  | 674.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 11:09 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Sharupkathi-2 33kv breaker Change | [7 empty] | 48.0MW load
interrup.
| 08:22 | 11:06 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Sharupkathi-2 33 kv Breaker Change | [7 empty] | 48.0MW load
interrup.
| 08:47 |  | Jaldhaka-Saidpur 132kV Ckt-1 Project Work S/D from Jaldhaka 132/33kV end Due to
Saidpur-Jaldhaka 132kV ckt-1 cable connection, relay configuration and commissioning work
at Saidpur grid S/S end by PGNS project. and from Saidpur 132/33kV end Due to Bay
shifting to new control building.
| 09:09 | 10:54 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Red hot
maintenance work. and from Feni 230/132kV end Due to Chuaddagram works
| 09:22 | 15:44 | Ishurdi 230/132kV S/S 230 kV Bus 1 Project Work S/D Due to jack bus upgradation work
| 09:23 | 12:34 | Gopalganj(132)-Gopalganj(N) 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to
Hot spot maintenance and from Gopalganj 400/230/132kV end Due to Ct Maintenance
| 09:43 | 17:24 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to CAF work
| 09:44 | 17:23 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to CAF work
| 09:46 | 14:45 | Khulna (S)-Satkhira 132kV Ckt-1 Forced S/D from Khulna(S) 230/132kV end. and from
Satkhira 132/33kV end Due to Old and new bus loop connection.
| 09:54 |  | Satkhira 132/33kV S/S 132 KV BUS-A (main) Scheduled S/D Due to Old and new bus loop
connection.
|  | 09:56 | Haripur 230/132kV S/S 132KV Bhulta-2 is restored.
|  | 09:57 | Bhulta-Haripur 132 kV Ckt-2 is restored.
|  | 09:58 | Bhulta-Haripur 132 kV Ckt-1 is restored.
|  | 09:59 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) is restored.
| 10:25 | 17:09 | Patiya 132/33kV S/S TRAFO-02 LT Scheduled S/D Due to For line maintenance work | [7 empty] | 18.0MW load
interrup.
| 10:41 | 17:08 | Patiya 132/33kV S/S TRAFO-02 HT Scheduled S/D Due to For line maintenance work | [7 empty] | 18.0MW load
interrup.
| 10:41 | 17:08 | Patiya 132/33kV S/S TRAFO-02 HT Scheduled S/D Due to For line maintenance work | [7 empty] | 18.0MW load
interrup.
| 10:53 | 12:01 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to 33 kv incomer CB R-phase red hot
maintenance
| 10:54 | 12:01 | Mithapukur 132/33kV S/S TR-2 (414T) HT Forced S/D Due to 33 kv incomer CB R-phase red hot
maintenance
| 11:59 | 13:20 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 230/132kV end Due to work
Chauddagram End and from Chauddagram 132/33kV end Due to Red hot maintenance work.
| 12:00 |  | Day Peak Generation: 13815 MW.
|  | 12:01 | Mithapukur 132/33kV S/S TR-2 (414T) HT is restored.
|  | 12:01 | Mithapukur 132/33kV S/S TR-2 (414T) HT is restored.
|  | 12:03 | Mirzapur 132/33kV S/S Mirzapur-Kaliakair-ckt-2A(E08) is restored.
|  | 12:21 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
|  | 12:22 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 is restored.
| 12:38 |  | Bibiyana-III 400 MW CCPP Tripped
| 12:41 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 15:22 | 18:25 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Oil filling at Main tank of ATR-01
| 15:53 | 16:47 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Instt.O/C, Definite O/C, Instt.E/F | [7 empty] | 40.0MW load
|  |  | relays Due to WZPDCL Auxiliary transformer's LA blast and loop short with structure | [7 empty] | interrup.
| 15:57 | 16:47 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to WZPDCL Auxiliary transformer's | [7 empty] | 20.0MW load
|  |  | LA Changing work | [7 empty] | interrup.
| 16:45 | 16:47 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to WZPDCL Auxiliary transformer's | [7 empty] | 20.0MW load
|  |  | LA Changing work | [7 empty] | interrup.
| 16:45 | 16:47 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to WZPDCL Auxiliary transformer's | [7 empty] | 20.0MW load
|  |  | LA Changing work | [7 empty] | interrup.
| 17:25 | 17:40 | Savar 132/33kV S/S T-3 LT Tripped showing Over current Relay relays Due to DPBS-3 feeder
fault
| 17:25 | 17:40 | Savar 132/33kV S/S T-4 LT Tripped showing Over current relay relays Due to DPBS-3 feeder
fault.
| 17:30 | 18:23 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D
| 17:30 | 17:57 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Hasnabad 132/33kV end showing Distance Relay | [7 empty] | 88.0MW load
|  |  | relays Due to None | [7 empty] | interrup. Hasnabad
132/33kV end
| 18:21 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 20:30 | 21:50 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Tripped showing No relay operated. relays Due to | [7 empty] | 190.0MW load
|  |  | unknown | [7 empty] | interrup.
| 22:25 |  | Barapukuria TPP Unit-1 Shutdown
| 06:00 |  | Minimum generation: 13991 MW
| 06:40 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to
Temperature high at line D/S
| 06:59 |  | Hasnabad 132/33kV S/S 132kV Main Bus Scheduled S/D Due to 132kV Shitalakhya Main Bus D/S
maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 333 | 8506800 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 292 | 6680873 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 415943 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 285 | 5978121 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 625320 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 105 | 692640 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 788312 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 798862 | Fuel Shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 320400 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 270912 | Fuel Shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 2381127 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1785168 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 697920 | Fuel Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2347200 | Fuel Shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 221914 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 242640 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 395 | 9758181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3060000 | Fuel Shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2502.42 | 46099733.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 91263.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 329280 | Machine Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5273789 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5117062 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 1571527 | Fuel Shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 456807 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 396970 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 144960 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 467040 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 65 | 302400 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22921 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 278 | 2732651 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 652171 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 85 | 1000300 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1531200 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 60 | 392673 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 144 | 1032073 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1170 | 27594543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 51840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1050 | 25338181.82 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3729.86 | 74633167.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 192 | 4941000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 310 | 8203300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 7020000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 7980500 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 435816 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 10 | 115200 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 35 | 1003636 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1090452 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 568727 | Fuel Shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 175024 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 83 | 2430456 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 134 | 1417920 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 94 | 1894080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 176410 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 420960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 198360 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 972720 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1181760 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 547609 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2014 | 40773930
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 143910 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 188 | 2719200 | ps availability is less
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1543200 | ps availability is less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 358440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 324000 | Fuel Shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 261720 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 309 | 5364570
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 82488 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 754000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 704160 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3130000 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 622944 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1910400 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | ps availability is less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 374784 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 6864000 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 126 | 4864000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 392 | 9387900 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1159 | 28694676
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 911 | 22052364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 226560 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 26 | 239232 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 99360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 77 | 358848 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 539280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 958 | 26785460 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2022 | 50301104
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 23461818 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 99 | 723456 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2752000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7317818.18 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5304920 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1216800 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 6981800 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4509 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2214 | 47763121.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 335504 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 405820 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 62450 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 163 | 3677909 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9454254 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 292800 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 160478 | Fuel Shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 304752 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 959424 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1384224 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 33240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1308.87 | 26246481 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 410992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 626139 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2243.87 | 44354467
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1093963 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 110 | 3600000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1566355 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43205.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 837833 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230456 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1343520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 366 | 8715332.88
Eastern Grid Total |  |  |  |  | 16961.086 | 9714.28 | 195566077.24
Western Grid Total |  |  |  |  | 11731.125 | 6845.87 | 151134025.06
National Grid Total |  |  |  |  | 28692.211 | 16560.15 | 346700102.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-09-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10995.77 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4925.8 | MW
i) Dhaka area |  |  | 5994.77 |  | MW | i) Khulna area |  |  |  | 1799 | MW
ii) Chattogram area |  |  | 1552 |  | MW | ii) Barishal area |  |  |  | 511 | MW
iii) Cumilla area |  |  | 1559 |  | MW | iii) Rajshahi area |  |  |  | 1555.8 | MW
iv) Mymensingh area |  |  | 1303 |  | MW | iv) Rangpur area |  |  |  | 1060 | MW
v) Sylhet area |  |  | 587 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15921.57 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 19:30 | 72 | Hatirjheel | 73 | 13:00 | 143 | Pabna | 98 | 19:00
2 | AKSML | 139 | 01:00 | 73 | Ishurdi | 85 | 19:00 | 144 | Palashbari | 138 | 19:30
3 | Aftabnagar | 42 | 13:00 | 74 | Jaldhaka | 86 | 18:30 | 145 | Panchagarh | 63 | 18:30
4 | Agargaon | 129 | 13:00 | 75 | Jamalpur | 146 | 18:30 | 146 | Patiya | 31 | 18:00
5 | Agrabad | 76 | 18:00 | 76 | Jashore | 120 | 19:00 | 147 | Patnitala | 33 | 22:00
6 | Amnura | 27 | 00:00 | 77 | Jhenaidah | 94 | 19:00 | 148 | Patuakhali | 75 | 21:00
7 | Araihazar | 110 | 23:00 | 78 | Joydebpur | 182 | 18:30 | 149 | Payra | 38 | 00:00
8 | Ashuganj | 0 | 23:00 | 79 | Joypurhat | 63 | 21:00 | 150 | Postogola | 62 | 12:00
9 | Ashuganj-230 | 99 | 03:00 | 80 | Juldah | 24 | 11:00 | 151 | Pubail | 48 | 12:00
10 | BSRM | 196 | 06:00 | 81 | KSRM | 37 | 23:00 | 152 | Purbachal | 32 | 18:30
11 | Bagerhat | 96 | 20:00 | 82 | Kabirpur | 289 | 19:00 | 153 | Purbasadipur | 130 | 19:00
12 | Bajitpur | 115 | 18:30 | 83 | Kachua | 100 | 22:00 | 154 | Rahanpur | 38 | 21:00
13 | Bakerganj | 15 | 19:30 | 84 | Kaliganj | 41 | 18:30 | 155 | Rahim | 27 | 10:00
14 | Bakulia | 109 | 19:00 | 85 | Kallyanpur | 120 | 18:00 | 156 | Rajbari | 84 | 19:00
15 | Banani | 58 | 13:00 | 86 | Kalurghat | 41 | 16:00 | 157 | Rajendrapur | 131 | 15:00
16 | Bangabhaban | 7 | 14:00 | 87 | Kamrangirchar | 81 | 13:00 | 158 | Rajshahi | 104 | 23:00
17 | Barapukuria | 65 | 19:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi-230 | 98 | 13:00
18 | Barguna | 24 | 22:00 | 89 | Kasba | 46 | 20:00 | 160 | Ramganj | 124 | 18:00
19 | Barishal | 106 | 19:00 | 90 | Kazla | 132 | 13:00 | 161 | Rampur | 46 | 18:00
20 | Barishal-230 | 110 | 22:00 | 91 | Keranigonj | 92 | 15:00 | 162 | Rangamati | 19 | 18:30
21 | Baroaulia | 43 | 11:00 | 92 | Khagrachori | 36 | 18:30 | 163 | Rangpur | 150 | 19:00
22 | Baroirhat | 69 | 19:30 | 93 | Khulna | 60 | 13:00 | 164 | Ruppur | 2.6 | 09:00
23 | Bashundhara | 210 | 18:00 | 94 | Khulshi | 172 | 22:00 | 165 | SSM | 0 | 00:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 142 | 20:00 | 166 | Saidpur | 114 | 18:30
25 | Beanibazar | 62 | 09:00 | 96 | Kodda | 306 | 21:00 | 167 | Santhia | 36 | 18:30
26 | Benapole | 63 | 00:00 | 97 | Kulaura | 47 | 18:00 | 168 | Satkhira | 139 | 19:00
27 | Bhaluka | 163 | 18:00 | 98 | Kurigram | 75 | 19:00 | 169 | Satmasjid | 109 | 13:00
28 | Bhandaria | 62 | 21:00 | 99 | Kushtia | 152 | 18:30 | 170 | Savar | 225 | 15:00
29 | Bhangura | 40 | 19:30 | 100 | Laksam | 25 | 18:30 | 171 | SevenRings | 20.18 | 18:00
30 | Bheramara(GK) | 64 | 18:00 | 101 | Lakshmipur | 54 | 22:00 | 172 | ShahCement | 29 | 00:00
31 | Bhulta | 205 | 19:30 | 102 | Lalbag | 82 | 13:00 | 173 | Shahjadpur | 87 | 20:00
32 | Bog-Sherpur | 72 | 21:00 | 103 | Lalmonirhat | 70 | 18:30 | 174 | Shahjibazar | 127 | 22:00
33 | Bogura | 207 | 22:00 | 104 | MI_Cement | 16.2 | 00:00 | 175 | Shahmirpur | 57 | 19:00
34 | Borhanuddin | 78 | 22:00 | 105 | Madanganj | 41 | 19:30 | 176 | Shariatpur | 105 | 22:00
35 | Brahmanbaria | 156 | 23:00 | 106 | Madaripur | 124 | 22:00 | 177 | Sherpur | 166 | 19:30
36 | Cantonment | 136 | 13:00 | 107 | Madartek | 88 | 23:00 | 178 | Shikalbaha | 29 | 15:00
37 | Chandina | 19 | 18:30 | 108 | Madunaghat | 57 | 19:30 | 179 | Shitalakhya | 77.3 | 16:00
38 | Chandpur | 88 | 19:00 | 109 | Magura | 72 | 18:30 | 180 | Sholosohor | 49 | 16:00
39 | Chandraghona | 35 | 18:30 | 110 | Mahasthangarh | 81 | 20:00 | 181 | Shomvuganj | 58 | 20:00
40 | Chapai | 68 | 21:00 | 111 | Maijdee | 42 | 01:00 | 182 | Shyampur | 152 | 15:00
41 | Charfasson | 35 | 21:00 | 112 | Manikganj | 151 | 20:00 | 183 | Siddhirganj | 136 | 12:00
42 | Charsaidpur | 44 | 00:00 | 113 | Maniknagar | 64 | 13:00 | 184 | Sirajganj | 120 | 19:30
43 | Chauddagram | 79 | 20:00 | 114 | Matarbari | 56 | 19:30 | 185 | Sitakunda | 36 | 19:30
44 | Chhatak | 30 | 18:30 | 115 | Matuail | 78 | 16:00 | 186 | Sonargaon | 122 | 18:30
45 | Chowmuhani | 164 | 18:30 | 116 | Metrorail_Motijheel | 18 | 09:00 | 187 | Sreemongol | 70 | 23:00
46 | Chuadanga | 116 | 19:00 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreepur | 121 | 21:00
47 | Coxsbazar | 151 | 22:00 | 118 | Millgate | 103 | 15:00 | 189 | Srinagar | 51.4 | 22:00
48 | Cumilla(N) | 169 | 18:30 | 119 | Mirpur | 160 | 18:30 | 190 | Sunamganj | 44 | 18:30
49 | Cumilla(S) | 173 | 19:30 | 120 | Mirsorai | 47 | 23:00 | 191 | Sylhet | 130 | 20:00
50 | Daganbhuiyan | 39 | 14:00 | 121 | Mirzapur | 54 | 13:00 | 192 | Sylhet_(South) | 63 | 17:00
51 | Daudkandi | 132 | 05:00 | 122 | Mithapukur | 76 | 18:30 | 193 | TK | 0 | 00:00
52 | DhakaUniversity | 84 | 13:00 | 123 | Modern | N/A | N/A | 194 | Tangail | 196 | 20:00
53 | Dhamrai | 100 | 00:00 | 124 | Mogbazar | 66.1 | 18:30 | 195 | Taraganj | 34 | 22:00
54 | Dhanmondi | 111.5 | 13:00 | 125 | Mongla | 33 | 15:00 | 196 | Tasnim | 44 | 09:00
55 | Dohazari | 132 | 19:00 | 126 | Motijheel | 50 | 13:00 | 197 | Thakurgaon | 111 | 18:30
56 | Faridpur | 181 | 20:00 | 127 | Muktagacha | 46 | 19:30 | 198 | Tongi | 156 | 11:00
57 | Fatullah | 125 | 15:00 | 128 | Munshiganj | 118 | 20:00 | 199 | Ullahpara | 40 | 18:30
58 | Fenchuganj | 40 | 01:00 | 129 | Muradnagar | 60 | 19:00 | 200 | Ullon | 47 | 23:00
59 | Feni | 120 | 18:30 | 130 | Mymensingh | 160 | 18:30 | 201 | Uttara | 102 | 13:00
60 | GPH | 71 | 03:00 | 131 | Nabinagar | 110 | 08:00 | 202 | UttaraNew | 57 | 23:00
61 | Ghatail | 100 | 23:00 | 132 | Naogaon | 115 | 19:00 | 203 | Zigatola | 95 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Narail | 60 | 18:30
63 | Ghorashal-230 | 93 | 17:00 | 134 | Narinda | 76 | 13:00
64 | Goalpara | 39 | 18:30 | 135 | Narshingdi | 198 | 20:00
65 | Gollamari | 108 | 13:00 | 136 | Natore | 162 | 18:30
66 | Gopalganj | 115 | 18:30 | 137 | Nawabganj | 51.9 | 22:00
67 | Gulshan | 104 | 12:00 | 138 | Netrakona | 136 | 00:00
68 | Halishahar | 112 | 15:00 | 139 | New | 86 | 15:00
69 | HaripurSBU | 128 | 00:00 | 140 | Niamatpur | 60 | 21:00
70 | Hasnabad | 102 | 20:00 | 141 | Noapara | 48 | 13:00
71 | Hathazari | 98 | 18:30 | 142 | PHP | 11 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15153.83 | 262 |  | 15427.62
1:00 | 14578.7 | 312 |  | 14904.7
2:00 | 14151.13 | 309 |  | 14474.13
3:00 | 13760.26 | 300 |  | 14074.26
4:00 | 13246.53 | 285 |  | 13544.53
5:00 | 13081.56 | 283 |  | 13377.56
6:00 | 12773.03 | 267 |  | 13052.05
7:00 | 12678.09 | 406 |  | 13102.09
8:00 | 12826.49 | 333 |  | 13174.49
9:00 | 12645.76 | 285 |  | 12943.76
10:00 | 12683.95 | 233 |  | 12926.95
11:00 | 13175.7 | 188 |  | 13371.7
12:00 | 13816.22 | 296 |  | 14125.22
13:00 | 13967.93 | 184 |  | 14159.93
14:00 | 14339.92 | 130 |  | 14475.77
15:00 | 14461.39 | 140 |  | 14607.39
16:00 | 14252.81 | 152 |  | 14411.81
17:00 | 14368.54 | 145 |  | 14520.54
18:00 | 14884.2 | 308 |  | 15206.2
19:00 | 16481.08 | 364 |  | 16861.08
19:30 | 16560.15 | 447 |  | 17027.15
20:00 | 16475.09 | 299 |  | 16787.09
21:00 | 16289.02 | 298 |  | 16600.02
22:00 | 16324.76 | 304 |  | 16642.76
23:00 | 16250.11 | 299 |  | 16562.11
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8508.88 | 6644.95 | 15153.83 | DAILY GENERATION CURVE
00:30 | 8379.4 | 6486.865 | 14866.265
01:00 | 8249.92 | 6328.78 | 14578.7 | 26-09-2026
01:30 | 8199.92 | 6164.995 | 14364.915
02:00 | 8149.92 | 6001.21 | 14151.13
02:30 | 8011.02 | 5944.675 | 13955.695
03:00 | 7872.12 | 5888.14 | 13760.26
03:30 | 7672.62 | 5830.775 | 13503.395
04:00 | 7473.12 | 5773.41 | 13246.53
04:30 | 7400.41 | 5763.635 | 13164.045
05:00 | 7327.7 | 5753.86 | 13081.56
05:30 | 7219.83 | 5707.465 | 12927.295
06:00 | 7111.96 | 5661.07 | 12773.03
06:30 | 7049.32 | 5676.24 | 12725.56
07:00 | 6986.68 | 5691.41 | 12678.09
07:30 | 6988.17 | 5764.12 | 12752.29
08:00 | 6989.66 | 5836.83 | 12826.49
08:30 | 6916.53 | 5819.595 | 12736.125
09:00 | 6843.4 | 5802.36 | 12645.76
09:30 | 6851.815 | 5813.04 | 12664.855
10:00 | 6860.23 | 5823.72 | 12683.95
10:30 | 6966.015 | 5963.81 | 12929.825
11:00 | 7071.8 | 6103.9 | 13175.7
11:30 | 7261.73 | 6234.23 | 13495.96
12:00 | 7451.66 | 6364.56 | 13816.22
12:30 | 7432.125 | 6459.95 | 13892.075
13:00 | 7412.59 | 6555.34 | 13967.93
13:30 | 7609.54 | 6544.385 | 14153.925
14:00 | 7806.49 | 6533.43 | 14339.92
14:30 | 7985.08 | 6415.575 | 14400.655
15:00 | 8163.67 | 6297.72 | 14461.39
15:30 | 8170.66 | 6186.44 | 14357.1
16:00 | 8177.65 | 6075.16 | 14252.81
16:30 | 8286.585 | 6024.09 | 14310.675
17:00 | 8395.52 | 5973.02 | 14368.54
17:30 | 8657.65 | 5968.72 | 14626.37
18:00 | 8919.78 | 5964.42 | 14884.2
18:30 | 9310.53 | 6372.11 | 15682.64
19:00 | 9701.28 | 6779.8 | 16481.08
19:30 | 9714.28 | 6845.87 | 16560.15
20:00 | 9565.28 | 6909.81 | 16475.09
20:30 | 9469.53 | 6912.525 | 16382.055 |  | Executive Engineer
21:00 | 9373.78 | 6915.24 | 16289.02 |  | Network Operation Division
21:30 | 9356.78 | 6950.11 | 16306.89
22:00 | 9339.78 | 6984.98 | 16324.76
22:30 | 9333.78 | 6953.655 | 16287.435
23:00 | 9327.78 | 6922.33 | 16250.11

## En-Curve
QF-LDC-12
Date | 26-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3538 | 1390.5 | 923 | 0 | 80 | 1283.75 | 221 | 5244.2 | 0 | 456.42 | 2006.96 | 0 | 0 | 10 | 262 | DAILY ENERGY CURVE
00:30 | 3527.5 | 1417.5 | 917.5 | 0 | 78 | 1185.165 | 219.5 | 5234.2 | 0 | 420.92 | 1859.48 | 0 | 0 | 6.5 | 287 | 26-09-2026
01:00 | 3517 | 1444.5 | 912 | 0 | 76 | 1086.58 | 218 | 5224.2 | 0 | 385.42 | 1712 | 0 | 0 | 3 | 312
01:30 | 3513.5 | 1421.5 | 912 | 0 | 75 | 1013.295 | 217.5 | 5180.2 | 0 | 354.42 | 1675 | 0 | 0 | 2.5 | 310.5 | Energy Generated | 346.7001 |  | MKWHr
02:00 | 3510 | 1398.5 | 912 | 0 | 74 | 940.01 | 217 | 5136.2 | 0 | 323.42 | 1638 | 0 | 0 | 2 | 309 | Energy not Served | 6.382 |  | MKWHr
02:30 | 3533 | 1410.1 | 912 | 0 | 73 | 922.975 | 215 | 5125.7 | 0 | 323.42 | 1435 | 0 | 0 | 5.5 | 304.5 | Total Energy Requirement | 353.0821 |  | MKWHr
03:00 | 3556 | 1421.7 | 912 | 0 | 72 | 905.94 | 213 | 5115.2 | 0 | 323.42 | 1232 | 0 | 0 | 9 | 300
03:30 | 3556 | 1406.7 | 911.5 | 0 | 70 | 909.075 | 213.5 | 5121.2 | 0 | 255.42 | 1051 | 0 | 0 | 9 | 292.5
04:00 | 3556 | 1391.7 | 911 | 0 | 68 | 912.21 | 214 | 5127.2 | 0 | 187.42 | 870 | 0 | 0 | 9 | 285
04:30 | 3589 | 1414.7 | 911.5 | 0 | 68 | 914.435 | 214 | 5126.2 | 0 | 163.71 | 754.5 | 0 | 0 | 8 | 284
05:00 | 3622 | 1437.7 | 912 | 0 | 68 | 916.66 | 214 | 5125.2 | 0 | 140 | 639 | 0 | 0 | 7 | 283
05:30 | 3613 | 1435.85 | 912 | 0 | 66 | 912.385 | 214.5 | 5118.6 | 2.46 | 122.5 | 524.5 | 0 | 0 | 5.5 | 275
06:00 | 3604 | 1434 | 912 | 0 | 64 | 908.11 | 215 | 5112 | 4.92 | 105 | 410 | 0 | 0 | 4 | 267
06:30 | 3590 | 1398.5 | 911.5 | 0 | 64 | 907.86 | 217.5 | 5091.5 | 56.2 | 105 | 380.5 | 0 | 0 | 3 | 336.5
07:00 | 3576 | 1363 | 911 | 0 | 64 | 907.61 | 220 | 5071 | 107.48 | 105 | 351 | 0 | 0 | 2 | 406
07:30 | 3572 | 1355.5 | 911.5 | 0 | 66 | 912.27 | 220 | 5064.5 | 200.02 | 95.5 | 354 | 0 | 0 | 1 | 369.5
08:00 | 3568 | 1348 | 912 | 0 | 68 | 916.93 | 220 | 5058 | 292.56 | 86 | 357 | 0 | 0 | 0 | 333
08:30 | 3508.5 | 1363.25 | 912 | 0 | 67 | 921.725 | 220.5 | 4941 | 425.15 | 68.5 | 308.5 | 0 | 0 | 0 | 309
09:00 | 3449 | 1378.5 | 912 | 0 | 66 | 926.52 | 221 | 4824 | 557.74 | 51 | 260 | 0 | 0 | 0 | 285
09:30 | 3453.5 | 1370 | 911.5 | 0 | 70 | 927.745 | 220.5 | 4809.5 | 592.11 | 51 | 259 | 0 | 0 | 0 | 259
10:00 | 3458 | 1361.5 | 911 | 0 | 74 | 928.97 | 220 | 4795 | 626.48 | 51 | 258 | 0 | 0 | 0 | 233
10:30 | 3516 | 1392.75 | 911 | 0 | 73 | 1024.85 | 220 | 4800 | 661.225 | 68.5 | 261 | 0 | 0 | 1.5 | 210.5
11:00 | 3574 | 1424 | 911 | 0 | 72 | 1120.73 | 220 | 4805 | 695.97 | 86 | 264 | 0 | 0 | 3 | 188
11:30 | 3653 | 1439 | 911.5 | 0 | 78 | 1170.53 | 220 | 4883 | 746.22 | 114.71 | 278 | 0 | 0 | 2 | 242
12:00 | 3732 | 1454 | 912 | 0 | 84 | 1220.33 | 220 | 4961 | 796.47 | 143.42 | 292 | 0 | 0 | 1 | 296
12:30 | 3617 | 1433 | 912 | 0 | 83 | 1217.79 | 218.5 | 5053.5 | 718.865 | 151.92 | 485.5 | 0 | 0 | 1 | 240
13:00 | 3502 | 1412 | 912 | 0 | 82 | 1215.25 | 217 | 5146 | 641.26 | 160.42 | 679 | 0 | 0 | 1 | 184
13:30 | 3464 | 1429.5 | 912 | 0 | 84 | 1211.905 | 217 | 5142.6 | 620 | 171.92 | 899 | 0 | 0 | 2 | 157
14:00 | 3426 | 1447 | 912 | 0 | 86 | 1208.56 | 217 | 5139.2 | 598.74 | 183.42 | 1119 | 0 | 0 | 3 | 130
14:30 | 3490.5 | 1506.5 | 911.5 | 0 | 87 | 1119.175 | 217 | 5157.1 | 495.78 | 183.42 | 1228.68 | 0 | 0 | 4 | 135
15:00 | 3555 | 1566 | 911 | 0 | 88 | 1029.79 | 217 | 5175 | 392.82 | 183.42 | 1338.36 | 0 | 0 | 5 | 140
15:30 | 3530.5 | 1470.5 | 911 | 0 | 86 | 1018.145 | 217 | 5062.5 | 309.675 | 193.42 | 1554.86 | 0 | 0 | 3.5 | 146
16:00 | 3506 | 1375 | 911 | 0 | 84 | 1006.5 | 217 | 4950 | 226.53 | 203.42 | 1771.36 | 0 | 0 | 2 | 152
16:30 | 3487 | 1379.5 | 911.5 | 0 | 83 | 1022.15 | 217.5 | 4872 | 144.745 | 260.92 | 1930.86 | 0 | 0 | 1.5 | 148.5
17:00 | 3468 | 1384 | 912 | 0 | 82 | 1037.8 | 218 | 4794 | 62.96 | 318.42 | 2090.36 | 0 | 0 | 1 | 145
17:30 | 3518.5 | 1434.5 | 911.5 | 0 | 88 | 1085.11 | 218.5 | 4723 | 31.48 | 403.42 | 2211.86 | 0 | 0 | 0.5 | 226.5
18:00 | 3569 | 1485 | 911 | 0 | 94 | 1132.42 | 219 | 4652 | 0 | 488.42 | 2333.36 | 0 | 0 | 0 | 308
18:30 | 3569 | 1469.5 | 911 | 0 | 93 | 1215.11 | 219.5 | 4780.5 | 0 | 649.42 | 2775.61 | 0 | 0 | 0 | 336
19:00 | 3569 | 1454 | 911 | 0 | 92 | 1297.8 | 220 | 4909 | 0 | 810.42 | 3217.86 | 0 | 0 | 0 | 364
19:30 | 3586 | 1474 | 911 | 0 | 94 | 1308.87 | 220 | 5016 | 0 | 771.42 | 3178.86 | 0 | 0 | 0 | 447
20:00 | 3580 | 1480 | 911 | 0 | 88 | 1319.81 | 221 | 5089 | 0 | 748.42 | 3037.86 | 0 | 0 | 0 | 299
20:30 | 3570.5 | 1520 | 911.5 | 0 | 86 | 1302.525 | 221 | 5129 | 0 | 738.92 | 2902.61 | 0 | 0 | 0 | 298.5
21:00 | 3561 | 1560 | 912 | 0 | 84 | 1285.24 | 221 | 5169 | 0 | 729.42 | 2767.36 | 0 | 0 | 0 | 298
21:30 | 3580 | 1546.5 | 912 | 0 | 86 | 1302.11 | 221 | 5208.5 | 0 | 707.42 | 2743.36 | 0 | 0 | 0 | 301
22:00 | 3599 | 1533 | 912 | 0 | 88 | 1318.98 | 221 | 5248 | 0 | 685.42 | 2719.36 | 0 | 0 | 0 | 304
22:30 | 3602.5 | 1549 | 912 | 0 | 88 | 1315.055 | 221 | 5240.6 | 0 | 685.42 | 2673.86 | 0 | 0 | 0 | 301.5
23:00 | 3606 | 1565 | 912 | 0 | 88 | 1311.13 | 221 | 5233.2 | 0 | 685.42 | 2628.36 | 0 | 0 | 0 | 299
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 26-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 146 | 21 | 474 | 183 | 1416 | 532 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 128 | 24 | 420 | 182 | 1312 | 552
2:00 | 116 | 25 | 370 | 172 | 1214 | 504 |  | Import | 0
3:00 | 132 | 34 | 390 | 172 | 1302 | 434
4:00 | 138 | 37 | 398 | 164 | 1376 | 546 | Ishurdi-Ghorashal Ckt-2 | Export | 3685018.18
5:00 | 140 | 38 | 402 | 162 | 1414 | 570
6:00 | 147 | 42 | 412 | 160 | 1398 | 584 |  | Import | 0
7:00 | 134 | 38 | 304 | 168 | 1274 | 548
8:00 | 150 | 47 | 412 | 176 | 1540 | 668 | Sirajganj-Sreepur Ckt-1 | Export | 2594000
9:00 | 192 | 72 | 486 | 190 | 1566 | 722
10:00 | 203 | 72 | 516 | 198 | 1640 | 746 |  | Import | 0
11:00 | 214 | 73 | 560 | 192 | 1796 | 786
12:00 | 212 | 70 | 560 | 200 | 1666 | 816 | Sirajganj-Sreepur Ckt-2 | Export | 2605000
13:00 | 201 | 75 | 530 | 184 | 1684 | 774
14:00 | 205 | 77 | 546 | 232 | 1702 | 768 |  | Import | 0
15:00 | 197 | 85 | 488 | 226 | 1590 | 784
16:00 | 189 | 75 | 488 | 234 | 1554 | 810 | Gopalganj-Aminbazar Ckt-1 | Export | 17290000
17:00 | 168 | 67 | 462 | 230 | 1376 | 780
18:00 | 152 | 57 | 420 | 190 | 1258 | 744 |  | Import | 0
18:30 | 89 | 18 | 300 | 178 | 1038 | 596
19:00 | 107 | 23 | 322 | 169 | 1180 | 600 | Gopalganj-Aminbazar Ckt-2 | Export | 17340000
19:30 | 113 | 24 | 360 | 170 | 1254 | 618
20:00 | 115 | 22 | 362 | 176 | 1272 | 592 |  | Import | 0
21:00 | 115 | 25 | 384 | 200 | 1236 | 594
22:00 | 116 | 24 | 384 | 200 | 1360 | 600 |  | Total Export | 43514018.18
23:00 | 115 | 24 | 384 | 214 | 1342 | 606 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 03:00 | 358 | 11:00 | Madunaghat | 396 | 03:00 | 386 | 13:00
Amtali | 412 | 04:00 | 406 | 12:00 | Meghnaghat | 384 | 02:00 | 367 | 12:00
Ashuganj | 399 | 5:00 | 382 | 12:00 | Mirsorai | 395 | 02:00 | 381 | 12:00
Bhulta | 390 | 04:00 | 369 | 12:00 | Payra | 413 | 03:00 | 408 | 12:00
Bibiana | 380 | 02:00 | 373 | 12:00 | Rahanpur | 410 | 03:00 | 396 | 23:00
BIPTC | 402 | 04:00 | 392 | 12:00 | Rampal | 397 | 05:00 | 384 | 12:00
Bogura | 397 | 03:00 | 380 | 23:00
Gopalganj | 391 | 04:00 | 379 | 12:00
Kaliakoir | 371 | 02:00 | 353 | 13:00
Korerhat | 394 | 02:00 | 381 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 02:00 | 214 | 12:00 | Hasnabad | 226 | 05:00 | 214 | 11:00
AKSML | 235 | 12:00 | 223 | 12:00 | Hathazari | 232 | 17:00 | 223 | 12:00
Aminbazar | 231 | 03:00 | 215 | 11:00 | Ishurdi | 235 | 04:00 | 223 | 21:00
Ashuganj | 224 | 03:00 | 214 | 12:00 | Jhenaidah | 227 | 05:00 | 212 | 21:00
Ashuganj-400 | 224 | 03:00 | 214 | 12:00 | Kachua | 224 | 03:00 | 216 | 13:00
Baghabari | 232 | 05:00 | 223 | 23:00 | Kaliakoir | 230 | 02:00 | 213 | 12:00
Barapukuria | 227 | 04:00 | 216 | 02:00 | Keranigonj | 226 | 02:00 | 211 | 12:00
Barapukuria-230 | 227 | 04:00 | 216 | 02:00 | Khulna(S) | 227 | 06:00 | 217 | 00:00
Barapukuria(N) | 230 | 02:00 | 221 | 18:30 | Korerhat | 224 | 02:00 | 215 | 12:00
Barishal | 226 | 17:00 | 220 | 12:00 | Madunaghat | 235 | 03:00 | 220 | 10:00
Bheramara | 233 | 04:00 | 221 | 12:00 | Madunaghat-400 | 238 | 18:00 | 229 | 13:00
Bhulta | 223 | 04:00 | 209 | 12:00 | Maniknagar | 222 | 04:00 | 207 | 13:00
Bibiana | 214 | 02:00 | 209 | 15:00 | Meghnaghat | 225 | 05:00 | 216 | 14:00
BIPTC | 236 | 04:00 | 220 | 21:00 | Meghnaghat-400 | 224 | 02:00 | 212 | 13:00
Birulia | 229 | 02:00 | 213 | 12:00 | Mirsorai | 230 | 02:00 | 221 | 12:00
Bogura | 239 | 02:00 | 229 | 23:00 | Naogaon | 226 | 03:00 | 205 | 22:00
Bogura-400 | 240 | 03:00 | 229 | 23:00 | Purbasadipur | 226 | 03:00 | 214 | 22:00
Borhanuddin | 229 | 09:00 | 224 | 22:00 | Rajshahi | 233 | 05:00 | 219 | 23:00
BSRM | 225 | 02:00 | 216 | 12:00 | Rampal | 227 | 06:00 | 217 | 12:00
Charfasson | 230 | 08:00 | 225 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 01:00 | 215 | 13:00 | Rampura | 222 | 03:00 | 208 | 13:00
Cumilla(N) | 219 | 06:00 | 211 | 13:00 | Shikalbaha | 237 | 18:00 | 223 | 12:00
Faridpur | 221 | 04:00 | 214 | 22:00 | Shyampur | 224 | 02:00 | 210 | 12:00
Fenchuganj | 216 | 03:00 | 207 | 22:00 | Siddhirganj | 223 | 04:00 | 211 | 12:00
Feni | 221 | 02:00 | 213 | 12:00 | Sirajgonj | 237 | 04:00 | 230 | 12:00
Ghorashal | 225 | 00:00 | 215 | 16:00 | Sreepur | 222 | 04:00 | 212 | 23:00
Ghorashal-230 | 216 | 02:00 | 197 | 12:00 | Tongi | 217 | 04:00 | 200 | 11:00
Gopalganj | 222 | 05:00 | 216 | 12:00
GPH | 233 | 13:00 | 222 | 12:00
Haripur | 223 | 05:00 | 209 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 02:00 | 127 | 12:00 | Madanganj | 135 | 04:00 | 124 | 13:00
Agargaon | 137 | 03:00 | 125 | 12:00 | Madaripur | 130 | 01:00 | 125 | 22:00
Agrabad | 134 | 17:00 | 127 | 12:00 | Madartek | 138 | 05:00 | 127 | 13:00
AKS | 131 | 05:00 | 126 | 12:00 | Madunaghat | 136 | 17:00 | 130 | 12:00
Aminbazar | 132 | 02:00 | 122 | 11:00 | Magura | 135 | 06:00 | 125 | 18:30
Amnura | 134 | 03:00 | 127 | 23:00 | Mahasthangarh | 136 | 02:00 | 128 | 23:00
Araihazar | 125 | 10:00 | 119 | 00:00 | Maijdee | 125 | 02:00 | 121 | 12:00
Ashuganj | 131 | 05:00 | 124 | 15:00 | Manikganj | 127 | 07:00 | 121 | 12:00
Ashuganj-230 | 134 | 03:00 | 130 | 12:00 | Maniknagar | 138 | 02:00 | 127 | 13:00
Bagerhat | 128 | 09:00 | 119 | 21:00 | Matarbari | 119 | 17:00 | 109 | 01:00
Bajitpur | 126 | 05:00 | 118 | 22:00 | Matuail | 135 | 05:00 | 124 | 13:00
Bakerganj | 133 | 17:00 | 128 | 04:00 | Metrorail_Motijheel | 138 | 03:00 | 127 | 13:00
Bakulia | 136 | 18:00 | 127 | 12:00 | Metrorail_Uttara | 132 | 02:00 | 116 | 12:00
Banani | 138 | 03:00 | 127 | 12:00 | Millgate | 134 | 04:00 | 117 | 12:00
Bangabhaban | 138 | 03:00 | 126 | 13:00 | Mirpur | 130 | 00:00 | 118 | 12:00
Barapukuria | 138 | 03:00 | 127 | 23:00 | Mirzapur | 129 | 05:00 | 124 | 18:00
Barguna | 133 | 18:00 | 127 | 12:00 | Mithapukur | 135 | 03:00 | 124 | 23:00
Barishal | 133 | 18:00 | 126 | 12:00 | MI_Cement | 133.5 | 05:00 | 118 | 12:00
Barishal-230 | 131 | 05:00 | 126 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 135 | 18:00 | 128 | 12:00 | Mogbazar | 140 | 03:00 | 129 | 13:00
Baroirhat | 129 | 01:00 | 125 | 12:00 | Mongla | 127 | 09:00 | 119 | 00:00
Bashundhara | 138 | 02:00 | 115 | 12:00 | Motijheel | 138 | 03:00 | 126 | 13:00
BashundharaCement | 135 | 04:00 | 124 | 13:00 | Muktagacha | 131 | 07:00 | 116 | 18:00
Beanibazar | 117 | 03:00 | 112 | 23:00 | Munshiganj | 133 | 03:00 | 123 | 13:00
Benapole | 137 | 04:00 | 116 | 22:00 | Muradnagar | 126 | 19:00 | 118 | 15:00
Bhaluka | 131 | 03:00 | 122 | 23:00 | Mymensingh | 132 | 07:00 | 119 | 12:00
Bhandaria | 132 | 18:00 | 120 | 23:00 | Nabinagar | 134 | 03:00 | 117 | 12:00
Bhangura | 134 | 03:00 | 128 | 12:00 | Naogaon | 136 | 02:00 | 123 | 22:00
Bheramara | 138 | 05:00 | 130 | 19:00 | Narail | 135 | 05:00 | 123 | 19:00
Bheramara(GK) | 137 | 04:00 | 129 | 21:00 | Narinda | 138 | 02:00 | 127 | 13:00
Bhulta | 126 | 10:00 | 118 | 00:00 | Narshingdi | 128 | 04:00 | 116 | 00:00
Bhulta-400 | 125 | 10:00 | 119 | 00:00 | Natore | 134 | 05:00 | 127 | 21:00
Birulia | 134 | 02:00 | 125 | 12:00 | Nawabganj | 137 | 03:00 | 126 | 13:00
Bog-Sherpur | 136 | 01:00 | 130 | 12:00 | Netrakona | 118 | 08:00 | 110 | 23:00
Bogura | 138 | 16:00 | 132 | 12:00 | New | 133 | 01:00 | 118 | 12:00
Bogura-230 | 139 | 16:00 | 132 | 23:00 | Niamatpur | 135 | 01:00 | 128 | 21:00
Brahmanbaria | 127 | 05:00 | 121 | 23:00 | Noapara | 129 | 05:00 | 121 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 02:00 | 123 | 12:00 | Pabna | 135 | 05:00 | 128 | 18:30
Chandina | 128 | 06:00 | 122 | 12:00 | Palashbari | 132 | 06:00 | 121 | 23:00
Chandpur | 130 | 01:00 | 121 | 15:00 | Panchagarh | 136 | 02:00 | 128 | 12:00
Chandraghona | 136 | 03:00 | 132 | 12:00 | Patiya | 132 | 17:00 | 125 | 12:00
Chapai | 134 | 05:00 | 128 | 21:00 | Patnitala | 134 | 06:00 | 126 | 22:00
Charsaidpur | 135 | 04:00 | 124 | 13:00 | Patuakhali | 133 | 17:00 | 127 | 12:00
Chauddagram | 126 | 02:00 | 120 | 12:00 | Payra | 135 | 18:00 | 132 | 12:00
Chhatak | 116 | 05:00 | 107 | 22:00 | PHP | 129 | 03:00 | 124 | 13:00
Chowmuhani | 126 | 01:00 | 120 | 13:00 | Postogola | 134 | 01:00 | 121 | 12:00
Chuadanga | 135 | 09:00 | 122 | 23:00 | Pubail | 132 | 00:00 | 116 | 12:00
Coxsbazar | 125 | 18:30 | 112 | 00:00 | Purbachal | 138 | 03:00 | 127 | 13:00
Cumilla(N) | 127 | 06:00 | 121 | 13:00 | Purbasadipur | 137 | 03:00 | 129 | 18:30
Cumilla(S) | 130 | 01:00 | 121 | 12:00 | Rahanpur | 137 | 05:00 | 132 | 22:00
Daganbhuiyan | 127 | 02:00 | 122 | 12:00 | Rahanpur-400 | 137 | 02:00 | 132 | 21:00
Daudkandi | 126 | 05:00 | 117 | 13:00 | Rahim | 136 | 05:00 | 124 | 13:00
DhakaUniversity | 138 | 02:00 | 127 | 13:00 | Rajbari | 126 | 05:00 | 120 | 22:00
Dhamrai | 134 | 05:00 | 123 | 12:00 | Rajendrapur | 133 | 03:00 | 127 | 21:00
Dhanmondi | 139 | 05:00 | 127 | 13:00 | Rajshahi | 133 | 05:00 | 125 | 18:30
Dohazari | 128 | 17:00 | 121 | 12:00 | Rajshahi-230 | 134 | 04:00 | 126 | 12:00
Faridpur | 129 | 09:00 | 124 | 20:00 | Ramganj | 126 | 02:00 | 119 | 15:00
Fatullah | 134 | 03:00 | 121 | 12:00 | Rampur | 135 | 18:00 | 127 | 12:00
Fenchuganj | 126 | 04:00 | 121 | 22:00 | Rampura | 138 | 03:00 | 127 | 13:00
Feni | 129 | 03:00 | 122 | 15:00 | Rangamati | 135 | 17:00 | 130 | 12:00
Feni-230 | 128 | 02:00 | 123 | 12:00 | Rangpur | 134 | 03:00 | 124 | 18:30
Ghatail | 129 | 07:00 | 118 | 01:00 | Ruppur | 137 | 03:00 | 130 | 18:30
Ghorashal | 130 | 18:30 | 120 | 12:00 | Saidpur | 137 | 04:00 | 128 | 18:30
Goalpara | 131 | 04:00 | 123 | 21:00 | Santhia | 135 | 01:00 | 128 | 21:00
Gollamari | 131 | 06:00 | 124 | 21:00 | Satkhira | 127 | 15:00 | 115 | 18:30
Gopalganj | 129 | 17:00 | 122 | 12:00 | Satmasjid | 136 | 03:00 | 124 | 13:00
Gopalganj-400 | 131 | 05:00 | 127 | 12:00 | Savar | 131 | 00:00 | 119 | 12:00
Gulshan | 138 | 05:00 | 127 | 13:00 | SevenRings | 129 | 02:00 | 119 | 12:00
Halishahar | 135 | 18:30 | 127 | 12:00 | ShahCement | 135 | 04:00 | 124 | 13:00
Haripur | 135 | 02:00 | 125 | 13:00 | Shahjadpur | 136 | 02:00 | 132 | 19:00
HaripurSBU | 135 | 05:00 | 125 | 13:00 | Shahjibazar | 126 | 04:00 | 120 | 23:00
Hasnabad | 135 | 03:00 | 123 | 12:00 | Shahmirpur | 137 | 18:00 | 128 | 12:00
Hathazari | 136 | 17:00 | 131 | 12:00 | Shariatpur | 128 | 06:00 | 122 | 22:00
Hatirjheel | 138 | 02:00 | 127 | 13:00 | Sherpur | 132 | 07:00 | 116 | 01:00
Ishurdi | 137 | 03:00 | 130 | 21:00 | Shikalbaha | 126 | 18:30 | 117 | 12:00
Jaldhaka | 134 | 03:00 | 122 | 18:30 | Shikalbaha-230 | 137 | 18:00 | 128 | 12:00
Jamalpur | 135 | 07:00 | 122 | 01:00 | Shitalakhya | 133.7 | 05:00 | 118 | 12:00
Jashore | 139 | 06:00 | 118 | 21:00 | Sholosohor | 135 | 02:00 | 129 | 13:00
Jhenaidah | 138 | 06:00 | 128 | 19:00 | Shomvuganj | 121 | 05:00 | 110 | 23:00
Jhenaidah-230 | 139 | 06:00 | 127 | 21:00 | Shyampur | 133 | 01:00 | 124 | 12:00
Joydebpur | 126 | 04:00 | 113 | 12:00 | Shyampur-230 | 135 | 02:00 | 126 | 12:00
Joypurhat | 134 | 04:00 | 126 | 23:00 | Siddhirganj | 135 | 01:00 | 124 | 12:00
Juldah | 137 | 18:00 | 128 | 12:00 | Sirajganj | 132 | 02:00 | 125 | 21:00
Kabirpur | 131 | 02:00 | 115 | 12:00 | Sitakunda | 135 | 18:30 | 128 | 12:00
Kachua | 127 | 01:00 | 122 | 12:00 | Sonargaon | 132 | 04:00 | 122 | 12:00
Kaliakoir | 135 | 02:00 | 129 | 12:00 | Sreemongol | 124 | 06:00 | 119 | 22:00
Kaliganj | 139 | 04:00 | 128 | 18:30 | Sreepur | 135 | 04:00 | 128 | 23:00
Kallyanpur | 130 | 00:00 | 124 | 10:00 | Srinagar | 137 | 05:00 | 127 | 12:00
Kalurghat | 136 | 17:00 | 130 | 12:00 | SSM | 138 | 00:00 | 132 | 12:00
Kamrangirchar | 138 | 02:00 | 116 | 12:00 | Sunamganj | 114 | 06:00 | 110 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 118 | 01:00 | 113 | 23:00
Kasba | 125 | 06:00 | 117 | 13:00 | Sylhet_(South) | 120 | 06:00 | 113 | 23:00
Kazla | 137 | 04:00 | 125 | 13:00 | Tangail | 128 | 07:00 | 119 | 18:00
Keranigonj | 137 | 02:00 | 127 | 12:00 | Taraganj | 134 | 04:00 | 126 | 18:30
Khagrachori | 133 | 00:00 | 129 | 12:00 | Tasnim | 132 | 03:00 | 122 | 12:00
Khulna | 130 | 06:00 | 122 | 21:00 | Thakurgaon | 137 | 17:00 | 129 | 12:00
Khulna(S) | 131 | 06:00 | 124 | 00:00 | TK | 135 | 01:00 | 132 | 11:00
Khulshi | 133 | 19:00 | 125 | 12:00 | Tongi | 134 | 04:00 | 121 | 11:00
Kishoreganj | 124 | 05:00 | 112 | 23:00 | Ullahpara | 134 | 05:00 | 127 | 21:00
Kodda | 130 | 18:30 | 115 | 12:00 | Ullon | 138 | 05:00 | 128 | 12:00
Korerhat | 132 | 02:00 | 126 | 12:00 | Uttara | 132 | 01:00 | 115 | 12:00
KSRM | 135 | 05:00 | 128 | 12:00 | UttaraNew | 132 | 02:00 | 116 | 12:00
Kulaura | 124 | 02:00 | 120 | 22:00 | Zigatola | 138 | 05:00 | 126 | 13:00
Kurigram | 131 | 06:00 | 116 | 18:30
Kushtia | 136 | 07:00 | 128 | 00:00
Laksam | 128 | 02:00 | 122 | 12:00
Lakshmipur | 124 | 02:00 | 120 | 12:00
Lalbag | 137 | 04:00 | 128 | 14:00
Lalmonirhat | 130 | 04:00 | 121 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division