## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-09-2026 | during | 28-09-2026 | during | 28-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 389 | 409 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 306 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 326 | 335 | 335 | 323 | 323 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 140 | 149.36 | 149.36 | 31 | 123 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 12 | 33 | 33 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 0 | 0 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 8 | 52.19 | 52.19 | 8 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 225 | 295 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 97 | 149 | 149 | 149 | 52 | 133 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 70 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 400 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2267.42 | 2625.42 | 5563.16 | 5531.16 | 2300.92 | 2807.89
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 214 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 85 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 35 | 48 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 0 | 51 | 34 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 28 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 81 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.78 | 0 | 3.71 | 0 | 3.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 246 | 300 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 56 | 91 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 118 | 16 | 163 | 163 | 55 | 55 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 2 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1050 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3368.78 | 3822.36 | 4113.67 | 4172.96 | 3794.71 | 3857.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 207 | 215 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 340 | 330 | 350.01 | 350.01 | 314.01 | 314.01 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 305 | 342.01 | 342.01 | 306.01 | 306.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 355 | 330 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 41.65 | 41.65 | 40 | 40 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 19 | 0 | 0 | 0 | 20 | 20 | plant availability zero
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 157 | 45 | 0 | 0 | 160 | 160 | plant availability zero
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 36 | 51 | 51 | 51 | 36 | 36 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 11 | 150 | 150 | 150 | 13 | 100 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 23 | 14 | 14 | 14 | 14 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 109 | 108 | 163 | 163 | 108 | 108 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 151 | 200 | 200 | 136 | 136 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 84 | 86 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 0 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 14 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 86 | 114 | 114 | 34 | 88 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 68 | 75 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 33 | 107 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 75 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1928 | 2168.2 | 2498.62 | 2422.62 | 2065.27 | 2222.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-09-2026 | during | 28-09-2026 | during | 28-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.58 | 0 | 12 | 0 | 12 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 180 | 176 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 104 | 105 | 105 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 54.28 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 374.06 | 309 | 655.5 | 591.5 | 273 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 41 | 41 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 40 | 40 | 20 | 20 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 138 | 139 | 140 | 140 | 140 | 140 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 25 | 25 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 81 | 81 | 81 | 81 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 240 | 341 | 341 | 280 | 280 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 276 | 276 | 280 | 280 | 280 | 280 | STG Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 383 | 388 | 383 | 383 | 383 | 383 | ps availability is less
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1235 | 1240 | 1372 | 1372 | 1265 | 1265
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 48 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 15 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 55 | 55 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 750 | 750 | 750 | 750 | 750 | 750 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1767 | 1828 | 3148 | 3050 | 2560 | 2462
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 1100 | 1000 | 1100 | 970 | 1100 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 116 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 119 | 54 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 280 | 307 | 307 | 280 | 280 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.26 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2144.26 | 2180 | 2208 | 2307 | 2039 | 2168
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 42.51 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 30 | 29 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 194 | 188 | 214 | 214 | 197 | 197 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 50 | 50 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 90 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.33 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 916.52 | 1323.06 | 800 | 1000 | 900 | 1300 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.87 | 0 | 0 | 0 | 0 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 109 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1851.23 | 2249.06 | 2498.91 | 2541.99 | 1938.91 | 2352.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 100 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 107 | 116 | 120 | 120 | 110 | 110 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 5 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 183 | 0 | 183 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 330.9 | 444 | 598 | 382 | 498 | 361
System Total |  |  |  |  | 28843.2 | 28692.211 | 15266.65 | 16866.04 | 22655.86 | 22371.23 | 16734.81 | 17786.21
Forecast Scenario (28-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16100 |  | 1594.85 |  | 17770
|  |  |  | 1:00 | 15640 |  | 1337 |  | 17040
|  |  |  | 2:00 | 15140 |  | 1575.75 |  | 16790
|  |  |  | 3:00 | 14810 |  | 1652.15 |  | 16540
|  |  |  | 4:00 | 14380 |  | 1785.85 |  | 16250
|  |  |  | 5:00 | 14300 |  | 1470.7 |  | 15840
|  |  |  | 6:00 | 13990 |  | 1356.1 |  | 15410
|  |  |  | 7:00 | 14080 |  | 1155.55 |  | 15290
|  |  |  | 8:00 | 14090 |  | 1021.85 |  | 15160
|  |  |  | 9:00 | 14220 |  | 1031.4 |  | 15300
|  |  |  | 10:00 | 14620 |  | 869.05 |  | 15530
|  |  |  | 11:00 | 14880 |  | 945.45 |  | 15870
|  |  |  | 12:00 | 15270 |  | 1270.15 |  | 16600
|  |  |  | 13:00 | 15430 |  | 1098.25 |  | 16580
|  |  |  | 14:00 | 15440 |  | 974.1 |  | 16460
|  |  |  | 15:00 | 15780 |  | 1260.6 |  | 17100
|  |  |  | 16:00 | 15590 |  | 945.45 |  | 16580
|  |  |  | 17:00 | 15290 |  | 1031.4 |  | 16370
|  |  |  | 18:00 | 15790 |  | 611.2 |  | 16430
|  |  |  | 18:30 | 16210 |  | 892.925 |  | 17145
|  |  |  | 19:00 | 16640 |  | 1165.1 |  | 17860
|  |  |  | 19:30 | 16820 |  | 1165.1 |  | 18040
|  |  |  | 20:00 | 16760 |  | 964.55 |  | 17770
|  |  |  | 21:00 | 16290 |  | 1757.2 |  | 18130
|  |  |  | 22:00 | 16320 |  | 1337 |  | 17720
|  |  |  | 23:00 | 16250 |  | 1518.45 |  | 17840
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 16600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1165
Probable Maximum Demand at Evening Peak: |  |  | 18130.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16820.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 367.10 MKWHr. |  | 200 | 100 | 130 | 230 | 100 | 115 | 80 | 110 | 100 | 1165
*** This report is generated digitally from Operation Information System (OIS) at 08:46 hrs on 28-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-09-2026 | [28 empty] | Date: | 27-09-2026 | [28 empty] | Date: | 27-09-2026 | [28 empty] | Date: | 27-09-2026 | [28 empty] | Date: | 27-09-2026 | [16 empty] | Date: | 27-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 17 | 133 | 101 | 195 | 55 | 55 | 162 | 0 | 310 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 68 | 16.5 | 22 | 0 | 500 | 32 | 278 | 39 | 0 | 0 | 51 | 50 | 36 | 12 | 100 | 0 | 221 | 94 | 28 | 1050 | 68 | 0 | 33 | 9 | 85 | 218 | 0 | 0 | 0 | 1180 | 0 | 13 | 35 | 393 | 338 | 310 | 51 | 10 | 205 | 40 | 93 | 110 | 155 | 75 | 19 | 17 | 82 | 25 | 0 | 15 | 272 | 390 | 280 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 140 | 0 | 0 | 17 | 86 | 0 | 182 | 0 | 0 | 0 | 18 | 9333.5 | 912 | 0 | 32 | 37 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 1289.12 | 0 | 38 | 0 | 113 | 70 | 0 | 50 | 0 | 25 | 0 | 0 | 34 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 110 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 280 | 117 | 220 | 0 | 1000 | 300 | 100 | 6766.32 | 16099.82 | 106.11
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 17 | 149 | 123 | 294 | 55 | 35 | 35 | 0 | 310 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 51 | 15 | 22 | 0 | 540 | 66 | 282 | 48 | 0 | 0 | 51 | 36 | 0 | 88 | 100 | 0 | 218 | 106 | 28 | 1050 | 152 | 0 | 46 | 25.5 | 85 | 218 | 0 | 0 | 0 | 1224 | 0 | 13 | 53 | 375 | 315 | 275 | 51 | 0 | 195 | 40 | 108 | 81 | 151 | 75 | 19 | 86 | 84 | 52.2 | 0 | 15 | 280 | 392 | 278 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 57 | 0 | 67 | 0 | 0 | 0 | 12 | 9378.7 | 913 | 0 | 23 | 12 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1039 | 17 | 0 | 0 | 1071.39 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 52.2 | 0 | 0 | 34 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 109 | 0 | 113 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 116 | 220 | 0 | 1000 | 300 | 54 | 6259.59 | 15638.29 | 106.1
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 149 | 123 | 294 | 15 | 35 | 35 | 0 | 305 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 51 | 15 | 22 | 0 | 520 | 98 | 280 | 50 | 0 | 0 | 51 | 50 | 0 | 100 | 100 | 0 | 217 | 108 | 7 | 1050 | 156 | 0 | 0 | 25.5 | 85 | 218 | 0 | 0 | 0 | 1224 | 0 | 13 | 53 | 393 | 305 | 265 | 44 | 0 | 193 | 37 | 107 | 81 | 153 | 75 | 19 | 86 | 80 | 52.2 | 0 | 15 | 275 | 394 | 270 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 57 | 0 | 67 | 0 | 0 | 0 | 12 | 9283.7 | 913 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 770 | 17 | 0 | 0 | 933.52 | 0 | 38 | 0 | 0 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 34 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 109 | 0 | 114 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 116 | 220 | 0 | 1000 | 300 | 54 | 5857.72 | 15141.42 | 106.1
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 149 | 124 | 294 | 0 | 35 | 35 | 0 | 306 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 51 | 15 | 22 | 0 | 480 | 89 | 282 | 50 | 0 | 0 | 51 | 36 | 0 | 60 | 100 | 0 | 217 | 105 | 18 | 1050 | 142 | 0 | 25 | 1 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 393 | 305 | 265 | 44 | 0 | 191 | 37 | 103 | 81 | 153 | 17 | 19 | 86 | 80 | 52.2 | 0 | 15 | 265 | 394 | 280 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 57 | 0 | 66 | 0 | 0 | 0 | 12 | 9017.2 | 913 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 755 | 17 | 0 | 0 | 932.89 | 0 | 39 | 0 | 0 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 34 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 110 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 117 | 220 | 0 | 1000 | 300 | 54 | 5788.09 | 14805.29 | 106.1
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 149 | 30 | 294 | 0 | 35 | 35 | 0 | 301 | 0 | 0 | 35 | 11 | 0 | 0 | 0 | 51 | 16.5 | 22 | 0 | 520 | 60 | 282 | 50 | 0 | 0 | 51 | 36 | 0 | 0 | 100 | 0 | 217 | 107 | 30 | 1050 | 146 | 0 | 25 | 8 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 335 | 305 | 265 | 44 | 0 | 202 | 37 | 104 | 81 | 154 | 0 | 19 | 0 | 78 | 8 | 0 | 15 | 267 | 394 | 280 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 57 | 0 | 66 | 0 | 0 | 0 | 12 | 8714.5 | 906 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 750 | 17 | 0 | 0 | 931.4 | 0 | 39 | 0 | 0 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 34 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 110 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 117 | 220 | 0 | 1000 | 300 | 54 | 5669.4 | 14383.9 | 106.1
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 149 | 15 | 294 | 0 | 0 | 35 | 0 | 307 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 51 | 16.5 | 22 | 0 | 490 | 61 | 282 | 50 | 0 | 0 | 34 | 36 | 0 | 0 | 100 | 0 | 218 | 106 | 30 | 1050 | 146 | 0 | 26 | 8 | 85 | 218 | 0 | 0 | 0 | 1160 | 0 | 13 | 35 | 338 | 305 | 265 | 44 | 0 | 203 | 37 | 94 | 81 | 153 | 0 | 19 | 0 | 76 | 8 | 0 | 15 | 268 | 396 | 281 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 140 | 0 | 0 | 17 | 57 | 0 | 66 | 0 | 0 | 0 | 12 | 8634.5 | 907 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 750 | 17 | 0 | 0 | 934.65 | 0 | 39 | 0 | 0 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 34 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 107 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 117 | 220 | 0 | 994 | 300 | 54 | 5662.65 | 14297.15 | 106.09
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 17 | 130 | 15 | 145 | 0 | 0 | 35 | 0 | 309 | 0 | 0 | 17 | 232 | 0 | 0 | 0 | 51 | 16.5 | 22 | 0 | 480 | 0 | 282 | 26 | 0 | 0 | 34 | 36 | 0 | 0 | 100 | 0.05 | 219 | 106 | 36 | 1050 | 150 | 0 | 26 | 0 | 85 | 221 | 0 | 0 | 0 | 1162 | 1 | 13 | 35 | 335 | 305 | 265 | 36 | 0 | 201 | 37 | 70 | 107 | 100 | 0 | 19 | 0 | 70 | 0 | 1 | 15 | 270 | 397 | 281 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 28 | 139 | 0 | 0 | 17 | 57 | 0.4 | 66 | 0 | 0 | 0.57 | 12 | 8526.52 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 17 | 0 | 0 | 947.2 | 0 | 39 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0.37 | 0 | 34 | 0 | 0.4 | 192 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.07 | 108 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 1 | 0.01 | 64 | 280 | 117 | 220 | 0 | 959 | 300 | 54 | 5464.05 | 13990.57 | 106.09
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 54 | 17 | 97 | 15 | 145 | 0 | 0 | 17 | 0 | 294 | 0 | 0 | 17 | 230 | 0 | 0 | 7 | 51 | 16.5 | 22 | 0 | 445 | 0 | 282 | 0 | 0 | 0 | 34 | 36 | 0 | 0 | 100 | 0.84 | 219 | 107 | 35 | 1050 | 144 | 0 | 26 | 0 | 85 | 221 | 0 | 0 | 0 | 1160 | 5 | 11 | 70 | 338 | 335 | 305 | 36 | 0 | 204 | 40 | 37 | 107 | 98 | 0 | 19 | 0 | 70 | 0 | 19 | 15 | 272 | 394 | 281 | 40 | 30 | 0 | 3 | 16 | 0 | 81 | 29 | 139 | 0 | 0 | 17 | 58 | 4.1 | 66 | 0 | 0.4 | 9.84 | 12 | 8493.68 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 750 | 17 | 0 | 0 | 922.16 | 0 | 39 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 9.08 | 14 | 34 | 0 | 5.36 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1 | 103 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1.1 | 29 | 0.13 | 64 | 280 | 117 | 220 | 0 | 988 | 300 | 54 | 5585.83 | 14079.51 | 106.09
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 17 | 97 | 15 | 145 | 0 | 0 | 17 | 0 | 283 | 0 | 0 | 17 | 260 | 0 | 0 | 8 | 34 | 16.5 | 22 | 0 | 350 | 0 | 282 | 0 | 0 | 0 | 17 | 36 | 0 | 0 | 90 | 2.1 | 220 | 99 | 15 | 1050 | 145 | 0 | 26 | 0 | 85 | 221 | 0 | 0 | 0 | 1160 | 7 | 13 | 73 | 319 | 315 | 300 | 36 | 0 | 197 | 40 | 59 | 107 | 96 | 4 | 19 | 0 | 72 | 0 | 43 | 15 | 265 | 394 | 281 | 40 | 30 | 0 | 3 | 16 | 0 | 78 | 28 | 140 | 0 | 0 | 17 | 58 | 10.5 | 66 | 0 | 0.6 | 21.43 | 12 | 8359.13 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 750 | 17 | 0 | 0 | 919.05 | 0 | 39 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 22.74 | 35 | 0 | 0 | 11.71 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.9 | 106 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 2.8 | 84 | 0.14 | 64 | 280 | 116 | 220 | 0 | 978 | 300 | 54 | 5730.34 | 14089.47 | 106.08
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 97 | 45 | 145 | 0 | 0 | 17 | 0 | 278 | 0 | 0 | 17 | 270 | 0 | 0 | 12 | 34 | 16.5 | 22 | 0 | 325 | 0 | 282 | 0 | 0 | 0 | 17 | 36 | 2 | 0 | 90 | 2.39 | 221 | 92 | 6 | 1050 | 143 | 0 | 26 | 0 | 85 | 218 | 0 | 0 | 0 | 1160 | 17 | 13 | 73 | 305 | 305 | 285 | 36 | 3 | 192 | 40 | 34 | 107 | 96 | 52 | 19 | 0 | 70 | 0 | 26 | 15 | 263 | 392 | 281 | 40 | 30 | 0 | 10 | 16 | 0 | 78 | 28 | 139 | 0 | 0 | 17 | 58 | 9.18 | 112 | 0 | 0.5 | 37.49 | 12 | 8378.06 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 750 | 17 | 0 | 0 | 907.64 | 0 | 39 | 0 | 54 | 70 | 0 | 0 | 0 | 0 | 42.79 | 72 | 0 | 0 | 21.66 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.94 | 108 | 0 | 0 | 24 | 34 | 0 | 0 | 0 | 4.6 | 129 | 0.23 | 75 | 280 | 116 | 220 | 0 | 963 | 300 | 54 | 5845.86 | 14223.92 | 106.08
10:00 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 17 | 97 | 45 | 195 | 0 | 17 | 17 | 0 | 290 | 0 | 0 | 17 | 277 | 0 | 0 | 30 | 143.42 | 13 | 22 | 0 | 340 | 0 | 210 | 0 | 0 | 6 | 17 | 35 | 35 | 0 | 89 | 3.54 | 221 | 74 | 4 | 1050 | 105 | 0 | 26 | 0 | 85 | 215 | 0 | 0 | 0 | 1150 | 13 | 13 | 73 | 335 | 295 | 285 | 36 | 10 | 196 | 37 | 34 | 107 | 51 | 59 | 19 | 0 | 74 | 0 | 71 | 15 | 262 | 388 | 278 | 40 | 20 | 0 | 11 | 8 | 0 | 78 | 28 | 139 | 0 | 0 | 17 | 87 | 21.21 | 155 | 0 | 1.7 | 44.09 | 12 | 8626.96 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 750 | 17 | 0 | 0 | 912.92 | 0 | 39 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 49.07 | 91 | 0 | 0 | 46.63 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.38 | 107 | 0 | 0 | 31 | 33 | 0 | 0 | 0 | 2.4 | 161 | 0.57 | 80 | 280 | 116 | 220 | 0 | 966 | 300 | 103 | 5988.97 | 14615.93 | 106.08
11:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 17 | 97 | 45 | 195 | 4 | 35 | 60 | 0 | 291 | 0 | 0 | 17 | 284 | 0 | 0 | 33 | 143.42 | 12 | 22 | 0 | 400 | 0 | 210 | 0 | 0 | 7 | 17 | 35 | 35 | 0 | 88 | 3.74 | 220 | 55 | 5 | 1050 | 104 | 0 | 0 | 0 | 85 | 213 | 0 | 0 | 0 | 1160 | 6 | 13 | 100 | 330 | 300 | 265 | 36 | 10 | 201 | 40 | 34 | 108 | 46 | 76 | 19 | 0 | 80 | 0 | 74 | 15 | 268 | 386 | 271 | 40 | 20 | 0 | 12 | 8 | 0 | 77 | 25 | 139 | 0 | 0 | 17 | 65 | 17.77 | 170 | 0 | 2.4 | 51.61 | 12 | 8792.94 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 750 | 17 | 0 | 0 | 918.33 | 0 | 39 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 59.57 | 104 | 0 | 0 | 29.2 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.76 | 105 | 0 | 0 | 36 | 32 | 0 | 0 | 0 | 2.7 | 184 | 0.64 | 110 | 280 | 115 | 220 | 0 | 967 | 300 | 119 | 6082.2 | 14875.14 | 106.07
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 54 | 17 | 97 | 45 | 225 | 15 | 35 | 108 | 0 | 301 | 0 | 0 | 17 | 308 | 0 | 0 | 34 | 143.42 | 12 | 22 | 0 | 420 | 0 | 246 | 0 | 0 | 5 | 17 | 35 | 35 | 0 | 100 | 3.78 | 221 | 56 | 7 | 1050 | 118 | 0 | 0 | 0 | 85 | 211 | 0 | 0 | 0 | 1160 | 19 | 11 | 157 | 355 | 340 | 320 | 36 | 19 | 207 | 40 | 33 | 109 | 51 | 68 | 8 | 0 | 84 | 0 | 75 | 15 | 265 | 383 | 276 | 40 | 20 | 0 | 8 | 8 | 0 | 77 | 20 | 138 | 0 | 0 | 17 | 87 | 21.58 | 180 | 0 | 2.2 | 54.28 | 12 | 9173.26 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 750 | 15 | 0 | 0 | 916.52 | 0 | 30 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 42.51 | 109 | 0 | 0 | 53.87 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.33 | 107 | 0 | 5 | 32 | 34 | 0 | 0 | 0 | 7.9 | 145 | 0.26 | 110 | 280 | 115 | 220 | 0 | 1000 | 300 | 119 | 6093.39 | 15266.65 | 106.1
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 17 | 128 | 142 | 245 | 15 | 35 | 162 | 0 | 296 | 0 | 0 | 17 | 323 | 0 | 0 | 32 | 143.42 | 12 | 22 | 0 | 325 | 85 | 282 | 0 | 0 | 6 | 17 | 27 | 35 | 88 | 100 | 3.57 | 218 | 73 | 7 | 1050 | 157 | 0 | 0 | 7 | 85 | 210 | 0 | 0 | 0 | 1100 | 18 | 13 | 73 | 320 | 280 | 240 | 51 | 13 | 189 | 40 | 34 | 109 | 65 | 75 | 8 | 86 | 84 | 43 | 71 | 7 | 249 | 387 | 276 | 40 | 30 | 0 | 11 | 8 | 0 | 77 | 25 | 139 | 0 | 0 | 17 | 77 | 21.01 | 152 | 0 | 2.1 | 53.15 | 12 | 9285.25 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 90 | 750 | 17 | 0 | 0 | 916.73 | 0 | 36 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 57.96 | 104 | 0 | 0 | 23.18 | 191 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 5.05 | 107 | 0 | 91 | 35 | 34 | 0 | 0 | 0 | 3 | 183 | 0.7 | 110 | 280 | 114 | 180 | 0 | 995 | 300 | 119 | 6148.62 | 15433.87 | 106.06
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 149 | 142 | 295 | 15 | 35 | 162 | 0 | 297 | 0 | 0 | 35 | 320 | 0 | 0 | 28 | 143.42 | 12 | 22 | 0 | 355 | 107 | 282 | 10 | 0 | 8 | 16 | 27 | 35 | 88 | 88 | 3.06 | 217 | 70 | 0 | 1050 | 160 | 0 | 6 | 8 | 85 | 210 | 0 | 0 | 0 | 1050 | 0 | 13 | 45 | 350 | 325 | 305 | 51 | 0 | 203 | 40 | 34 | 109 | 68 | 73 | 8 | 86 | 86 | 43 | 62 | 10 | 244 | 385 | 272 | 40 | 30 | 0 | 8 | 8 | 0 | 77 | 25 | 138 | 0 | 0 | 17 | 77 | 19.33 | 152 | 0 | 1.8 | 47.49 | 12 | 9458.1 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 81 | 750 | 17 | 0 | 0 | 924.2 | 0 | 36 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 50.83 | 91 | 0 | 0 | 52.74 | 150 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 1.33 | 107 | 0 | 95 | 30 | 34 | 0 | 0 | 0 | 6.4 | 174 | 0.62 | 110 | 280 | 114 | 180 | 0 | 959 | 300 | 54 | 5981.12 | 15439.22 | 106.05
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 131 | 138 | 295 | 15 | 35 | 162 | 0 | 298 | 0 | 0 | 35 | 316 | 0 | 0 | 21 | 143.42 | 12 | 22 | 0 | 415 | 109 | 300 | 44 | 0 | 10 | 17 | 23 | 36 | 100 | 88 | 2.39 | 217 | 90 | 0 | 1050 | 158 | 0 | 39 | 8 | 85 | 211 | 0 | 0 | 0 | 1180 | 0 | 13 | 45 | 365 | 340 | 315 | 51 | 0 | 202 | 40 | 34 | 108 | 68 | 75 | 5 | 86 | 86 | 43 | 48 | 14 | 238 | 380 | 272 | 40 | 29 | 0 | 7 | 16 | 0 | 76 | 25 | 141 | 0 | 0 | 17 | 77 | 15.18 | 152 | 0 | 1.4 | 34.62 | 12 | 9740.01 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 59 | 750 | 17 | 0 | 0 | 924.88 | 0 | 35 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 32.11 | 71 | 0 | 0 | 41.14 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.12 | 105 | 0 | 115 | 24 | 34 | 0 | 0 | 0 | 4.8 | 126 | 0.44 | 110 | 280 | 114 | 220 | 0 | 973 | 300 | 54 | 6042.49 | 15782.5 | 106.05
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 95 | 136 | 295 | 15 | 55 | 162 | 0 | 296 | 0 | 0 | 35 | 315 | 0 | 0 | 13 | 143.42 | 12 | 22 | 0 | 370 | 107 | 300 | 72 | 0 | 14 | 17 | 40 | 36 | 100 | 88 | 1.01 | 217 | 93 | 2 | 1050 | 160 | 0 | 50 | 8 | 72 | 212 | 0 | 0 | 0 | 1162 | 7 | 13 | 45 | 350 | 335 | 305 | 51 | 0 | 192 | 39 | 34 | 108 | 68 | 74 | 19 | 85 | 86 | 52.2 | 28 | 17 | 242 | 380 | 274 | 40 | 29 | 0 | 4 | 16 | 0 | 76 | 25 | 139 | 0 | 0 | 17 | 76 | 7.99 | 152 | 0 | 0.8 | 5.92 | 16 | 9636.34 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 33 | 750 | 24 | 0 | 0 | 920.73 | 0 | 35 | 0 | 80 | 35 | 0 | 0 | 0 | 0 | 20.88 | 42 | 0 | 0 | 23.87 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.99 | 106 | 0 | 115 | 13 | 32 | 0 | 0 | 0 | 2.6 | 70 | 0.28 | 110 | 280 | 114 | 220 | 0 | 998 | 300 | 54 | 5957.35 | 15593.69 | 106.04
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 97 | 136 | 295 | 50 | 55 | 162 | 0 | 295 | 0 | 0 | 35 | 318 | 0 | 0 | 3 | 143.42 | 12 | 22 | 0 | 330 | 107 | 300 | 80 | 0 | 9 | 17 | 40 | 36 | 24 | 88 | 0.62 | 218 | 92 | 9 | 1050 | 43 | 0 | 50 | 8 | 78 | 211 | 0 | 0 | 0 | 1160 | 2 | 13 | 45 | 325 | 315 | 290 | 51 | 0 | 213 | 39 | 49 | 108 | 67 | 74 | 19 | 34 | 82 | 8 | 8 | 22 | 240 | 385 | 274 | 40 | 29 | 0 | 1 | 16 | 0 | 76 | 28 | 141 | 0 | 0 | 17 | 76 | 2.24 | 152 | 0 | 0.2 | 5.65 | 12 | 9295.13 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | 750 | 30 | 0 | 0 | 1131.56 | 0 | 35 | 0 | 113 | 35 | 0 | 0 | 0 | 0 | 5.97 | 13 | 0 | 0 | 6.77 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.54 | 105 | 0 | 115 | 4 | 48 | 0 | 0 | 0 | 0.8 | 22 | 0.08 | 110 | 280 | 50 | 220 | 0 | 982 | 300 | 54 | 5999.72 | 15294.85 | 106.04
18:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 97 | 137 | 295 | 55 | 55 | 162 | 0 | 303 | 0 | 0 | 55 | 323 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 395 | 109 | 300 | 81 | 0 | 7 | 21 | 34 | 54.36 | 50 | 88 | 0 | 219 | 91 | 15 | 1050 | 16 | 0 | 50 | 17 | 85 | 211 | 0 | 0 | 0 | 1115 | 0 | 17 | 45 | 380 | 305 | 270 | 51 | 0 | 207 | 39 | 59 | 108 | 84 | 74 | 19 | 43 | 94 | 8 | 0 | 22 | 243 | 380 | 272 | 40 | 29 | 0 | 0 | 16 | 0 | 77 | 25 | 139 | 0 | 0 | 17 | 76 | 0 | 153 | 0 | 0 | 0 | 12 | 9461.78 | 906 | 0 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 750 | 17 | 0 | 0 | 1319.84 | 0 | 29 | 0 | 113 | 39 | 0 | 40 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 105 | 0 | 115 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 114 | 220 | 0 | 1010 | 300 | 72 | 6325.84 | 15787.62 | 106.03
19:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 17 | 124 | 139 | 295 | 55 | 55 | 162 | 0 | 302 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 143.42 | 11.5 | 22 | 0 | 410 | 107 | 300 | 81 | 0 | 10 | 34 | 46 | 54.36 | 100 | 100 | 0 | 220 | 94 | 15 | 1050 | 17 | 0 | 50 | 25.5 | 85 | 212 | 0 | 0 | 0 | 1137 | 0 | 87 | 45 | 350 | 340 | 315 | 51 | 0 | 198 | 40 | 115 | 108 | 143 | 74 | 19 | 86 | 90 | 52.2 | 0 | 23 | 240 | 383 | 274 | 40 | 29 | 0 | 0 | 16 | 0 | 81 | 30 | 139 | 0 | 0 | 17 | 104 | 0 | 171 | 0 | 0 | 0 | 12 | 10053.98 | 907 | 0 | 33 | 26 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 750 | 17 | 0 | 0 | 1351.54 | 0 | 29 | 0 | 113 | 90 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 105 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 115 | 220 | 0 | 1100 | 300 | 54 | 6582.54 | 16636.52 | 106.03
19:30 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 17 | 133 | 139 | 295 | 55 | 55 | 162 | 0 | 306 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 143.42 | 11.5 | 22 | 0 | 424 | 107 | 300 | 81 | 0 | 4 | 34 | 48 | 54.36 | 100 | 100 | 0 | 220 | 92 | 12 | 1050 | 17 | 0 | 50 | 25.5 | 85 | 213 | 0 | 0 | 0 | 1157 | 0 | 110 | 45 | 330 | 345 | 330 | 51 | 0 | 204 | 40 | 115 | 108 | 151 | 74 | 19 | 86 | 94 | 52.2 | 0 | 23 | 242 | 383 | 274 | 40 | 29 | 0 | 0 | 16 | 0 | 81 | 30 | 139 | 0 | 0 | 17 | 104 | 0 | 172 | 0 | 0 | 0 | 12 | 10109.98 | 903 | 0 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 750 | 17 | 0 | 0 | 1339.24 | 0 | 29 | 0 | 113 | 90 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 108 | 0 | 115 | 0 | 113 | 0 | 140 | 0 | 0 | 0 | 0 | 110 | 280 | 115 | 220 | 0 | 1100 | 300 | 54 | 6711.24 | 16821.22 | 106.03
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 17 | 140 | 139 | 295 | 55 | 55 | 162 | 0 | 290 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 375 | 109 | 300 | 82 | 0 | 2 | 34 | 48 | 54.36 | 100 | 100 | 0 | 220 | 92 | 18 | 1050 | 16 | 0 | 50 | 25.5 | 85 | 214 | 0 | 0 | 0 | 1172 | 0 | 150 | 45 | 300 | 320 | 300 | 51 | 0 | 205 | 40 | 115 | 108 | 153 | 74 | 19 | 86 | 92 | 52.2 | 0 | 23 | 242 | 388 | 276 | 40 | 29 | 0 | 0 | 16 | 0 | 81 | 30 | 139 | 0 | 0 | 17 | 104 | 0 | 171 | 0 | 0 | 0 | 12 | 10022.48 | 903 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 750 | 17 | 0 | 0 | 1341.04 | 0 | 29 | 0 | 113 | 90 | 0 | 50 | 0 | 1 | 0 | 0 | 34 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 109 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 280 | 116 | 220 | 0 | 1100 | 300 | 54 | 6735.04 | 16757.52 | 106.03
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 54 | 17 | 149 | 140 | 295 | 55 | 55 | 162 | 0 | 306 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 400 | 107 | 300 | 81 | 0 | 2 | 34 | 48 | 54.36 | 100 | 100 | 0 | 221 | 91 | 28 | 1050 | 16 | 0 | 50 | 17 | 85 | 214 | 0 | 0 | 0 | 1224 | 0 | 150 | 45 | 330 | 330 | 305 | 51 | 0 | 215 | 40 | 107 | 108 | 151 | 75 | 14 | 86 | 86 | 52.2 | 0 | 23 | 240 | 388 | 276 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 30 | 139 | 0 | 0 | 17 | 104 | 0 | 176 | 0 | 0 | 0 | 12 | 10164.98 | 904 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 750 | 17 | 0 | 0 | 1323.06 | 0 | 29 | 0 | 113 | 90 | 0 | 50 | 0 | 8 | 0 | 0 | 34 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 116 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 280 | 116 | 220 | 0 | 1100 | 300 | 54 | 6701.06 | 16866.04 | 106.02
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 54 | 17 | 149 | 141 | 295 | 55 | 55 | 162 | 0 | 306 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 480 | 107 | 300 | 82 | 0 | 0 | 34 | 48 | 54.36 | 100 | 100 | 0 | 221 | 92 | 18 | 1050 | 16 | 0 | 50 | 25.5 | 85 | 214 | 0 | 0 | 0 | 1224 | 0 | 150 | 45 | 310 | 350 | 330 | 51 | 0 | 216 | 40 | 108 | 108 | 152 | 76 | 19 | 86 | 90 | 52.2 | 0 | 23 | 244 | 384 | 274 | 40 | 31 | 0 | 0 | 16 | 0 | 81 | 27 | 140 | 0 | 0 | 17 | 105 | 0 | 176 | 0 | 0 | 0 | 12 | 10277.48 | 904 | 0 | 24 | 39 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 750 | 17 | 0 | 0 | 1355.88 | 0 | 29 | 0 | 113 | 90 | 0 | 50 | 0 | 8 | 0 | 0 | 34 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 148 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 280 | 115 | 220 | 0 | 1100 | 300 | 54 | 6654.88 | 16932.36 | 106.02
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 17 | 17 | 149 | 142 | 295 | 55 | 55 | 162 | 0 | 285 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 390 | 107 | 300 | 83 | 0 | 0 | 34 | 48 | 36 | 100 | 100 | 0 | 221 | 93 | 27 | 1050 | 16 | 0 | 50 | 25.5 | 85 | 215 | 0 | 0 | 0 | 1160 | 0 | 150 | 45 | 370 | 280 | 240 | 51 | 0 | 191 | 37 | 90 | 108 | 152 | 75 | 19 | 86 | 90 | 52.2 | 0 | 23 | 242 | 390 | 277 | 40 | 30 | 0 | 0 | 16 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 105 | 0 | 173 | 0 | 0 | 0 | 12 | 9841.12 | 904 | 0 | 24 | 43 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 750 | 17 | 0 | 0 | 1355.54 | 0 | 29 | 0 | 113 | 90 | 0 | 51 | 0 | 8 | 0 | 0 | 34 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 153 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 235 | 116 | 180 | 0 | 1100 | 300 | 54 | 6386.54 | 16227.66 | 106.01
Total KWH | 0 | 553920 | 261600 | 0 | 0 | 0 | 0 | 0 | 9554400 | 0 | 0 | 783000 | 431640 | 3052368 | 2300160 | 6151036 | 621724 | 801241 | 2352960 | 0 | 7169978 | 0 | 0 | 798733 | 5639812 | 0 | 0 | 224318 | 2568000 | 334800 | 525600 | 0 | 10077727.27 | 1732527 | 6741927 | 1065600 | 0 | 75840 | 698016 | 882622 | 657123 | 1254720 | 2280000 | 25076 | 5300493 | 2213900 | 404160 | 25309090.91 | 2480655 | 0 | 761760 | 249827.4 | 2099272 | 4966855 | 0 | 0 | 0 | 27823634 | 128925 | 1082254 | 1388364 | 8415000 | 8072300 | 7094000 | 1074336 | 57120 | 4931000 | 939744 | 1678080 | 2445554 | 2667360 | 1330560 | 397550 | 1158240 | 1927680 | 668894 | 531927 | 397632 | 6143000 | 9292400 | 6724000 | 947000 | 632280 | 0 | 75032 | 357888 | 0 | 1891200 | 625728 | 3170000 | 0 | 0 | 429480 | 1809600 | 143208 | 3074400 | 0 | 12450 | 361630 | 298320 | 223600251.58 | 21923636 | 0 | 246240 | 228096 | 0 | 0 | 0 | 0 | 0 | 1228320 | 642960 | 18327273 | 373440 | 0 | 0 | 25410874 | 0 | 835609 | 0 | 1355712 | 1749120 | 0 | 337040 | 0 | 213821 | 381680 | 747670 | 427400 | 0 | 321008 | 4487091 | 0 | 0 | 0 | 0 | 0 | 9566327 | 0 | 30360 | 2802000 | 0 | 1796081 | 232006 | 1213728 | 0 | 275625 | 0 | 37846.44 | 1246320 | 4080 | 2239584 | 6589000 | 2747000 | 5285890 | 0 | 24363636 | 7192727.27 | 1548000 | 146407200.71 | 370007452.29

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15266.65 | MW | 12:00 Hr. | Energy Generated |  |  | 370.0075 |  | MKWHr.
| Day Peak Demand |  |  | 15404.65 | MW | 12:00 Hr. | Energy Unserverd |  |  | 9.516 |  | MKWHr.
| Evening Peak Generation |  |  | 16866.04 | MW | 21:00 Hr. | Energy Demand |  |  | 379.5235 |  | MKWHr.
| Evening Peak Demand |  |  | 17495.52 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13990.57 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 897.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 16932.36 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 8.493 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.3023 | 0 | 20.6764 | 0 | 0 | 0.22432 | 0 | 0 | 54.203 | Gas | 125.3581 | Gas | 437372100.3459
| Chattogram Zone |  |  | 5.371 | 53.1327 | 23.1179 | 0 | 5.3005 | 0.154 | 0 | 0.07584 | 87.152 | Coal | 112.4074 | Coal | 804450958.5042
| Cumilla Zone |  |  | 34.815 | 0 | 8.983 | 0 | 0 | 0.53193 | 1.9277 | 0 | 46.2576 | HFO | 72.1813 | HFO | 1499417504.932
| Mymensingh Zone |  |  | 0 | 0 | 5.6118 | 0 | 0 | 0.51729 | 0 | 0 | 6.1291 | HSD | 0.27563 | HSD | 8511300
| Sylhet Zone |  |  | 29.7835 | 0 | 0 | 0 | 0 | 0.075032 | 0 | 0 | 29.8585 | Hydro | 5.3005 | Hydro | 530049.3
| Khulna Zone |  |  | 0 | 18.3273 | 2.0761 | 0 | 0 | 0.64296 | 21.9236 | 0 | 42.97 | Solar | 5.1465 | Solar | 82788048.7008
| Barishal Zone |  |  | 8.0329 | 38.1454 | 3.7876 | 0 | 0 | 0.00408 | 0 | 0 | 49.9699 | Import | 49.2622 | Import | 308278248.22
| Rajshahi Zone |  |  | 14.0534 | 0 | 4.9187 | 0 | 0 | 1.4807 | 25.4109 | 0 | 45.8637 | Wind | 0.07584 | Wind | 1125465.6
| Rangpur Zone |  |  | 0 | 2.802 | 3.0098 | 0.27563 | 0 | 1.5162 | 0 | 0 | 7.6036
| Total |  |  | 125.3581 | 112.4074 | 72.1813 | 0.27563 | 5.3005 | 5.1465 | 49.2622 | 0.07584 | 370.0075
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 437372100.3459 |  | Hydro | 530049.3
|  |  |  | Coal | 804450958.5042 |  | Solar | 82788048.7008
|  |  |  | HFO | 1499417504.932 |  | Import | 308278248.22
|  |  |  | HSD | 8511300 |  | Wind | 1125465.6
[5 empty] | Total: | 314,24,73,675 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9236 | Peak Hr Flow | 904.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 28016800 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.4109 | Peak Hr Flow | 1323.06 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1219 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.9277 | Peak Hr Flow | 86.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2009 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.2622 | Peak Hr Flow | 2313.06 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 79 |  | 6060
|  |  |  | Chattogram |  | 0 |  | 1546
|  |  |  | Cumilla |  | 32 |  | 1660
|  |  |  | Mymensingh |  | 108 |  | 1409
|  |  |  | Sylhet |  | 254 |  | 793
|  |  |  | Khulna |  | 0 |  | 1954
|  |  |  | Barishal |  | 0 |  | 551
|  |  |  | Rajshahi |  | 0 |  | 1631
|  |  |  | Rangpur |  | 3 |  | 1064
|  |  |  | Total |  | 476 |  | 16668
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 374.5
|  |  |  | Total Unavailable Capacity |  |  |  | 674.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:21 | 17:22 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to Fire fighter
(CAF)
| 09:22 | 17:21 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to Fire fight
(CAF)
| 09:37 | 11:43 | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to maintenance work of 132 kv
substation
| 09:37 | 11:43 | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to maintenance work of 132 kv ss
| 10:08 |  | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 230/132/33kV end Due to Tower
Erection & line Stringing.
| 11:50 | 13:14 | Mithapukur 132/33kV S/S BUS-1 (132KV) Scheduled S/D Due to For oil leakage maintenance at
132kV Bus-01 CVT Y-ph
| 12:00 |  | Day peak generation is 15267 MW.
|  | 12:22 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
| 12:33 | 15:56 | Bhulta-Haripur 132 kV Ckt-2 Scheduled S/D from Bhulta 400/230/132kV end.
| 12:34 | 15:59 | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Bhulta 400/230/132kV end.
| 12:34 | 15:54 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to From Bhulta end.
| 12:52 | 15:36 | Bhulta 400/230/132kV S/S 132kV Bus-1 Scheduled S/D
| 13:23 | 22:01 | Feni 230/132kV S/S Bus-A (230kV) Project Work S/D Due to SAS & DFDR works
| 14:46 |  | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to Due to project work on SAS and DFDR
testing
| 14:46 |  | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to Due to project work on SAS and DFDR
testing
| 15:01 | 21:57 | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to Due to
project work on SAS and DFDR testing
|  | 15:47 | Hasnabad 132/33kV S/S 132kV Main Bus is restored.
| 15:52 | 16:54 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33 KV Feeder Langolbondh DS B phase | [7 empty] | 40.0MW load
|  |  | burn due to Earth Fault | [7 empty] | interrup.
| 15:52 | 16:54 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 KV Feeder Langolbondh incoming DS | [7 empty] | 40.0MW load
|  |  | burn due to Earth Fault | [7 empty] | interrup.
| 19:37 |  | Bagerhat-Goalpara 132 kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to Order by NLDC
| 19:41 | 20:50 | Patiya 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Red hot corrective maintenance | [7 empty] | 12.0MW load
interrup.
| 19:43 | 20:51 | Patiya 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Red hot corrective maintenance | [7 empty] | 12.0MW load
interrup.
| 21:00 |  | Evening Peak Generation: 16866 MW.
| 07:11 |  | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to
Cross arm replacement of Tower No. 839 on Chandraghona Line-2 was carried out by the
contractor. and from Chandraghona 132/33kV end Due to Maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9554400 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 7169978 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 621724 | Fuel Shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 5639812 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 783000 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 2300160 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 801241 | Fuel Shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 798733 | Fuel Shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 334800 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 525600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 261600 | Fuel Shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 6151036 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3052368 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 553920 | Fuel Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2352960 | Fuel Shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 224318 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 431640 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10077727.27 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Machine Ready & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2568000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2625.42 | 54203017.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 249827.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128925 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 761760 | Machine Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5300493 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 4966855 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 2099272 | Fuel Shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 882622 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 698016 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1254720 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 404160 | ps availability is less
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 81 | 1065600 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25076 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 6741927 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 657123 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 2213900 | Fuel Shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2280000 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1732527 | Machine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 2480655 | Fuel Shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27823634 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 75840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1050 | 25309090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3822.36 | 87152023.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 215 | 4931000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 330 | 8072300 | FGMO Available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 305 | 7094000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 330 | 8415000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 939744 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 57120 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 1388364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1074336 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1082254 | Fuel Shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 397632 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2445554 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 151 | 2667360 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 86 | 1927680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 668894 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 397550 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 1158240 | Fuel Shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 1330560 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 107 | 1678080 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 531927 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2168.2 | 46257595
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 143208 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 176 | 3074400 | Fuel Shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1809600 | ps availability is less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 361630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298320 | Fuel Shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 309 | 6129088
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 75032 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 947000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 632280 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3170000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 625728 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1891200 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 357888 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 240 | 6143000 | Gas Shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 276 | 6724000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 388 | 9292400 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1240 | 29858528
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21923636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 246240 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 48 | 228096 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 373440 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1228320 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 642960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 750 | 18327273 | Coal Shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1828 | 42969965
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24363636 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 2239584 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2747000 | Machine Problem
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7192727.27 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5285890 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 1548000 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 6589000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4080 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2180 | 49969917.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 381680 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 29 | 835609 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 188 | 4487091 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9566327 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 427400 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 213821 | Fuel Shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 337040 | Machine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 1749120 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1355712 | Fuel Shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 30360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1323.06 | 25410874 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 321008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 747670 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2249.06 | 45863712
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 100 | 275625 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 116 | 2802000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1213728 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37846.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1796081 | Machine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232006 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1246320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 444 | 7603606.44
Eastern Grid Total |  |  |  |  | 16961.086 | 10164.98 | 223600251.58
Western Grid Total |  |  |  |  | 11731.125 | 6701.06 | 146407200.71
National Grid Total |  |  |  |  | 28692.211 | 16866.04 | 370007452.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10995.01 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5196.8 | MW
i) Dhaka area |  |  | 5981.01 |  | MW | i) Khulna area |  |  |  | 1954 | MW
ii) Chattogram area |  |  | 1546 |  | MW | ii) Barishal area |  |  |  | 551.2 | MW
iii) Cumilla area |  |  | 1628 |  | MW | iii) Rajshahi area |  |  |  | 1630.6 | MW
iv) Mymensingh area |  |  | 1301 |  | MW | iv) Rangpur area |  |  |  | 1061 | MW
v) Sylhet area |  |  | 539 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16191.81 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 17 | 16:00 | 72 | Hatirjheel | 89 | 15:00 | 143 | Pabna | 108 | 19:00
2 | AKSML | 158.9 | 03:00 | 73 | Ishurdi | 90 | 19:00 | 144 | Palashbari | 142 | 21:00
3 | Aftabnagar | 44 | 21:00 | 74 | Jaldhaka | 88 | 20:00 | 145 | Panchagarh | 66 | 18:30
4 | Agargaon | 141 | 13:00 | 75 | Jamalpur | 152 | 23:00 | 146 | Patiya | 31 | 21:00
5 | Agrabad | 82 | 15:00 | 76 | Jashore | 133 | 18:30 | 147 | Patnitala | 35 | 21:00
6 | Amnura | 30 | 23:00 | 77 | Jhenaidah | 98 | 19:30 | 148 | Patuakhali | 82 | 22:00
7 | Araihazar | 110 | 17:00 | 78 | Joydebpur | 180 | 18:00 | 149 | Payra | 38 | 22:00
8 | Ashuganj | 0 | 00:00 | 79 | Joypurhat | 64 | 22:00 | 150 | Postogola | 64 | 23:00
9 | Ashuganj-230 | 93 | 01:00 | 80 | Juldah | 23 | 15:00 | 151 | Pubail | 48 | 02:00
10 | BSRM | 198 | 06:00 | 81 | KSRM | 33 | 08:00 | 152 | Purbachal | 33 | 22:00
11 | Bagerhat | 100 | 19:30 | 82 | Kabirpur | 273 | 09:00 | 153 | Purbasadipur | 134 | 19:00
12 | Bajitpur | 106 | 00:00 | 83 | Kachua | 108 | 21:00 | 154 | Rahanpur | 41 | 21:00
13 | Bakerganj | 15.6 | 23:00 | 84 | Kaliganj | 45 | 19:30 | 155 | Rahim | 30 | 18:00
14 | Bakulia | 108 | 18:30 | 85 | Kallyanpur | 120 | 18:00 | 156 | Rajbari | 92 | 20:00
15 | Banani | 74 | 13:00 | 86 | Kalurghat | 44 | 19:00 | 157 | Rajendrapur | 153 | 19:00
16 | Bangabhaban | 17 | 10:00 | 87 | Kamrangirchar | 85 | 13:00 | 158 | Rajshahi | 108 | 23:00
17 | Barapukuria | 62 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi-230 | 101 | 18:30
18 | Barguna | 24 | 20:00 | 89 | Kasba | 42 | 21:00 | 160 | Ramganj | 120 | 22:00
19 | Barishal | 110 | 13:00 | 90 | Kazla | 120 | 23:00 | 161 | Rampur | 50 | 08:00
20 | Barishal-230 | 114 | 19:30 | 91 | Keranigonj | 104 | 19:00 | 162 | Rangamati | 20 | 16:00
21 | Baroaulia | 46 | 11:00 | 92 | Khagrachori | 36 | 18:30 | 163 | Rangpur | 144 | 20:00
22 | Baroirhat | 68 | 18:00 | 93 | Khulna | 63 | 20:00 | 164 | Ruppur | 4.6 | 15:00
23 | Bashundhara | 223 | 18:30 | 94 | Khulshi | 198 | 19:30 | 165 | SSM | 0 | 00:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 149 | 22:00 | 166 | Saidpur | 120 | 19:00
25 | Beanibazar | 68 | 07:00 | 96 | Kodda | 303 | 18:30 | 167 | Santhia | 38 | 19:00
26 | Benapole | 72 | 23:00 | 97 | Kulaura | 58 | 03:00 | 168 | Satkhira | 139 | 21:00
27 | Bhaluka | 177 | 18:00 | 98 | Kurigram | 76 | 19:30 | 169 | Satmasjid | 113 | 14:00
28 | Bhandaria | 62 | 20:00 | 99 | Kushtia | 157 | 21:00 | 170 | Savar | 227 | 16:00
29 | Bhangura | 45 | 19:00 | 100 | Laksam | 25 | 22:00 | 171 | SevenRings | 18.24 | 15:00
30 | Bheramara(GK) | 70 | 20:00 | 101 | Lakshmipur | 55 | 18:30 | 172 | ShahCement | 31 | 14:00
31 | Bhulta | 207 | 22:00 | 102 | Lalbag | 83 | 13:00 | 173 | Shahjadpur | 91 | 19:00
32 | Bog-Sherpur | 74 | 21:00 | 103 | Lalmonirhat | 68 | 19:30 | 174 | Shahjibazar | 138 | 04:00
33 | Bogura | 208 | 20:00 | 104 | MI_Cement | 11.6 | 07:00 | 175 | Shahmirpur | 68 | 18:00
34 | Borhanuddin | 81 | 21:00 | 105 | Madanganj | 49 | 20:00 | 176 | Shariatpur | 107 | 22:00
35 | Brahmanbaria | 163 | 21:00 | 106 | Madaripur | 125 | 20:00 | 177 | Sherpur | 164 | 00:00
36 | Cantonment | 138 | 13:00 | 107 | Madartek | 93 | 23:00 | 178 | Shikalbaha | 23 | 08:00
37 | Chandina | 38 | 14:00 | 108 | Madunaghat | 63 | 18:00 | 179 | Shitalakhya | 86.1 | 12:00
38 | Chandpur | 92 | 21:00 | 109 | Magura | 74 | 19:30 | 180 | Sholosohor | 49 | 15:00
39 | Chandraghona | 35 | 18:30 | 110 | Mahasthangarh | 82 | 19:30 | 181 | Shomvuganj | 56 | 00:00
40 | Chapai | 73 | 19:30 | 111 | Maijdee | 45 | 22:00 | 182 | Shyampur | 144 | 10:00
41 | Charfasson | 36 | 00:00 | 112 | Manikganj | 152 | 18:30 | 183 | Siddhirganj | 139 | 13:00
42 | Charsaidpur | 44 | 15:00 | 113 | Maniknagar | 68 | 12:00 | 184 | Sirajganj | 130 | 19:30
43 | Chauddagram | 82 | 21:00 | 114 | Matarbari | 58 | 01:00 | 185 | Sitakunda | 37 | 19:00
44 | Chhatak | 35 | 07:00 | 115 | Matuail | 78 | 12:00 | 186 | Sonargaon | 135 | 18:00
45 | Chowmuhani | 167 | 21:00 | 116 | Metrorail_Motijheel | 18 | 17:00 | 187 | Sreemongol | 77 | 06:00
46 | Chuadanga | 126 | 19:30 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreepur | 134 | 19:00
47 | Coxsbazar | 154 | 19:00 | 118 | Millgate | 106 | 15:00 | 189 | Srinagar | 52.6 | 22:00
48 | Cumilla(N) | 168 | 18:30 | 119 | Mirpur | 162 | 15:00 | 190 | Sunamganj | 53 | 10:00
49 | Cumilla(S) | 174 | 18:00 | 120 | Mirsorai | 58 | 08:00 | 191 | Sylhet | 127 | 00:00
50 | Daganbhuiyan | 38 | 22:00 | 121 | Mirzapur | 52 | 19:00 | 192 | Sylhet_(South) | 68 | 03:00
51 | Daudkandi | 135 | 23:00 | 122 | Mithapukur | 78 | 19:00 | 193 | TK | 0 | 00:00
52 | DhakaUniversity | 108 | 13:00 | 123 | Modern | N/A | N/A | 194 | Tangail | 184 | 23:00
53 | Dhamrai | 94 | 01:00 | 124 | Mogbazar | 68 | 18:00 | 195 | Taraganj | 34 | 23:00
54 | Dhanmondi | 132 | 13:00 | 125 | Mongla | 48 | 18:30 | 196 | Tasnim | 37 | 02:00
55 | Dohazari | 122 | 18:30 | 126 | Motijheel | 56 | 12:00 | 197 | Thakurgaon | 114 | 19:30
56 | Faridpur | 189 | 21:00 | 127 | Muktagacha | 45 | 19:00 | 198 | Tongi | 172 | 18:30
57 | Fatullah | 119 | 09:00 | 128 | Munshiganj | 121 | 22:00 | 199 | Ullahpara | 42 | 19:00
58 | Fenchuganj | 38 | 12:00 | 129 | Muradnagar | 60 | 21:00 | 200 | Ullon | 50 | 23:00
59 | Feni | 114 | 21:00 | 130 | Mymensingh | 166 | 22:00 | 201 | Uttara | 107 | 18:30
60 | GPH | 75 | 23:00 | 131 | Nabinagar | 110 | 10:00 | 202 | UttaraNew | 59 | 23:00
61 | Ghatail | 101 | 20:00 | 132 | Naogaon | 120 | 22:00 | 203 | Zigatola | 98 | 12:00
62 | Ghorashal | 0 | 00:00 | 133 | Narail | 67 | 18:30
63 | Ghorashal-230 | 96 | 23:00 | 134 | Narinda | 80.5 | 13:00
64 | Goalpara | 45 | 23:00 | 135 | Narshingdi | 199 | 19:30
65 | Gollamari | 122 | 20:00 | 136 | Natore | 157 | 20:00
66 | Gopalganj | 121 | 22:00 | 137 | Nawabganj | 53.3 | 22:00
67 | Gulshan | 128 | 13:00 | 138 | Netrakona | 138 | 10:00
68 | Halishahar | 113 | 15:00 | 139 | New | 88 | 15:00
69 | HaripurSBU | 140 | 03:00 | 140 | Niamatpur | 63 | 22:00
70 | Hasnabad | 104 | 18:00 | 141 | Noapara | 48 | 19:30
71 | Hathazari | 99 | 19:30 | 142 | PHP | 9 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16099.82 | 568 |  | 16693.82
1:00 | 15638.29 | 614 |  | 16280.29
2:00 | 15141.42 | 599 |  | 15767.42
3:00 | 14805.29 | 433 |  | 15257.29
4:00 | 14383.9 | 380 |  | 14780.9
5:00 | 14297.15 | 365 |  | 14678.15
6:00 | 13990.57 | 279 |  | 14282.57
7:00 | 14079.51 | 250 |  | 14340.51
8:00 | 14089.47 | 250 |  | 14350.47
9:00 | 14223.92 | 245 |  | 14479.92
10:00 | 14615.93 | 122 |  | 14742.93
11:00 | 14875.14 | 72 |  | 14950.14
12:00 | 15266.65 | 132 |  | 15404.65
13:00 | 15433.87 | 198 |  | 15640.87
14:00 | 15439.22 | 174 |  | 15621.22
15:00 | 15782.5 | 288 |  | 16083.5
16:00 | 15593.69 | 218 |  | 15821.69
17:00 | 15294.85 | 223 |  | 15527.85
18:00 | 15787.62 | 637 |  | 16453.29
19:00 | 16636.52 | 822 |  | 17495.52
19:30 | 16821.22 | 627 |  | 17476.22
20:00 | 16757.52 | 661 |  | 17448.52
21:00 | 16866.04 | 476 |  | 17363.04
22:00 | 16932.36 | 404 |  | 17354.36
23:00 | 16227.66 | 1106 |  | 17383.66
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9333.5 | 6766.32 | 16099.82 | DAILY GENERATION CURVE
00:30 | 9356.1 | 6512.955 | 15869.055
01:00 | 9378.7 | 6259.59 | 15638.29 | 27-09-2026
01:30 | 9331.2 | 6058.655 | 15389.855
02:00 | 9283.7 | 5857.72 | 15141.42
02:30 | 9150.45 | 5822.905 | 14973.355
03:00 | 9017.2 | 5788.09 | 14805.29
03:30 | 8865.85 | 5728.745 | 14594.595
04:00 | 8714.5 | 5669.4 | 14383.9
04:30 | 8674.5 | 5666.025 | 14340.525
05:00 | 8634.5 | 5662.65 | 14297.15
05:30 | 8580.51 | 5563.35 | 14143.86
06:00 | 8526.52 | 5464.05 | 13990.57
06:30 | 8510.1 | 5524.94 | 14035.04
07:00 | 8493.68 | 5585.83 | 14079.51
07:30 | 8426.405 | 5658.085 | 14084.49
08:00 | 8359.13 | 5730.34 | 14089.47
08:30 | 8368.595 | 5788.1 | 14156.695
09:00 | 8378.06 | 5845.86 | 14223.92
09:30 | 8502.51 | 5917.415 | 14419.925
10:00 | 8626.96 | 5988.97 | 14615.93
10:30 | 8709.95 | 6035.585 | 14745.535
11:00 | 8792.94 | 6082.2 | 14875.14
11:30 | 8983.1 | 6087.795 | 15070.895
12:00 | 9173.26 | 6093.39 | 15266.65
12:30 | 9229.255 | 6121.005 | 15350.26
13:00 | 9285.25 | 6148.62 | 15433.87
13:30 | 9371.675 | 6064.87 | 15436.545
14:00 | 9458.1 | 5981.12 | 15439.22
14:30 | 9599.055 | 6011.805 | 15610.86
15:00 | 9740.01 | 6042.49 | 15782.5
15:30 | 9688.175 | 5999.92 | 15688.095
16:00 | 9636.34 | 5957.35 | 15593.69
16:30 | 9465.735 | 5978.535 | 15444.27
17:00 | 9295.13 | 5999.72 | 15294.85
17:30 | 9378.455 | 6162.78 | 15541.235
18:00 | 9461.78 | 6325.84 | 15787.62
18:30 | 9757.88 | 6454.19 | 16212.07
19:00 | 10053.98 | 6582.54 | 16636.52
19:30 | 10109.98 | 6711.24 | 16821.22
20:00 | 10022.48 | 6735.04 | 16757.52
20:30 | 10093.73 | 6718.05 | 16811.78 |  | Executive Engineer
21:00 | 10164.98 | 6701.06 | 16866.04 |  | Network Operation Division
21:30 | 10221.23 | 6677.97 | 16899.2
22:00 | 10277.48 | 6654.88 | 16932.36
22:30 | 10059.3 | 6520.71 | 16580.01
23:00 | 9841.12 | 6386.54 | 16227.66

## En-Curve
QF-LDC-12
Date | 27-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3630 | 1580.5 | 912 | 0 | 82 | 1289.12 | 221 | 5154.2 | 0 | 559 | 2672 | 0 | 0 | 0 | 568 | DAILY ENERGY CURVE
00:30 | 3571.5 | 1607.75 | 912.5 | 0 | 83 | 1180.255 | 219.5 | 5078.1 | 0 | 526 | 2690.45 | 0 | 0 | 0 | 591 | 27-09-2026
01:00 | 3513 | 1635 | 913 | 0 | 84 | 1071.39 | 218 | 5002 | 0 | 493 | 2708.9 | 0 | 0 | 0 | 614
01:30 | 3509 | 1606 | 913 | 0 | 82 | 1002.455 | 217.5 | 4867.5 | 0 | 494 | 2698.4 | 0 | 0 | 0 | 606.5 | Energy Generated | 370.0075 |  | MKWHr
02:00 | 3505 | 1577 | 913 | 0 | 80 | 933.52 | 217 | 4733 | 0 | 495 | 2687.9 | 0 | 0 | 0 | 599 | Energy not Served | 9.516 |  | MKWHr
02:30 | 3480.5 | 1549 | 913 | 0 | 80 | 933.205 | 217 | 4694 | 0 | 489 | 2617.65 | 0 | 0 | 0 | 516 | Total Energy Requirement | 379.5235 |  | MKWHr
03:00 | 3456 | 1521 | 913 | 0 | 80 | 932.89 | 217 | 4655 | 0 | 483 | 2547.4 | 0 | 0 | 0 | 433
03:30 | 3474 | 1546.25 | 909.5 | 0 | 79 | 932.145 | 217 | 4652.5 | 0 | 409.5 | 2374.7 | 0 | 0 | 0 | 406.5
04:00 | 3492 | 1571.5 | 906 | 0 | 78 | 931.4 | 217 | 4650 | 0 | 336 | 2202 | 0 | 0 | 0 | 380
04:30 | 3512.5 | 1560 | 906.5 | 0 | 77 | 933.025 | 217.5 | 4645.5 | 0 | 318 | 2170.5 | 0 | 0 | 0 | 372.5
05:00 | 3533 | 1548.5 | 907 | 0 | 76 | 934.65 | 218 | 4641 | 0 | 300 | 2139 | 0 | 0 | 0 | 365
05:30 | 3615 | 1544.5 | 906.5 | 0 | 73 | 940.925 | 218.5 | 4625 | 2.435 | 274.5 | 1943.5 | 0 | 0 | 0 | 322
06:00 | 3697 | 1540.5 | 906 | 0 | 70 | 947.2 | 219 | 4609 | 4.87 | 249 | 1748 | 0 | 0 | 0 | 279
06:30 | 3748.5 | 1533.5 | 906 | 0 | 70 | 934.68 | 219 | 4620 | 65.36 | 249 | 1689 | 0 | 0 | 0 | 264.5
07:00 | 3800 | 1526.5 | 906 | 0 | 70 | 922.16 | 219 | 4631 | 125.85 | 249 | 1630 | 0 | 0 | 0 | 250
07:30 | 3787 | 1460 | 906.5 | 0 | 71 | 920.605 | 219.5 | 4627.5 | 218.385 | 215 | 1659 | 0 | 0 | 0 | 250
08:00 | 3774 | 1393.5 | 907 | 0 | 72 | 919.05 | 220 | 4624 | 310.92 | 181 | 1688 | 0 | 0 | 0 | 250
08:30 | 3747.5 | 1374.5 | 907 | 0 | 71 | 913.345 | 220.5 | 4617.5 | 382.85 | 196 | 1726.5 | 0 | 0 | 0 | 247.5
09:00 | 3721 | 1355.5 | 907 | 0 | 70 | 907.64 | 221 | 4611 | 454.78 | 211 | 1765 | 0 | 0 | 0 | 245
09:30 | 3727 | 1365.25 | 906.5 | 0 | 72 | 910.28 | 221 | 4607 | 554.685 | 276.21 | 1777 | 0 | 0 | 3 | 183.5
10:00 | 3733 | 1375 | 906 | 0 | 74 | 912.92 | 221 | 4603 | 654.59 | 341.42 | 1789 | 0 | 0 | 6 | 122
10:30 | 3723.5 | 1421.5 | 906.5 | 0 | 77 | 915.625 | 220.5 | 4607.5 | 678.99 | 364.92 | 1823 | 0 | 0 | 6.5 | 97
11:00 | 3714 | 1468 | 907 | 0 | 80 | 918.33 | 220 | 4612 | 703.39 | 388.42 | 1857 | 0 | 0 | 7 | 72
11:30 | 3796.5 | 1510 | 907 | 0 | 82 | 917.425 | 220.5 | 4629.5 | 704.05 | 349.42 | 1948.5 | 0 | 0 | 6 | 102
12:00 | 3879 | 1552 | 907 | 0 | 84 | 916.52 | 221 | 4647 | 704.71 | 310.42 | 2040 | 0 | 0 | 5 | 132
12:30 | 3767.5 | 1436.5 | 906.5 | 0 | 84 | 916.625 | 219.5 | 4614.5 | 709.215 | 378.92 | 2311.5 | 0 | 0 | 5.5 | 165
13:00 | 3656 | 1321 | 906 | 0 | 84 | 916.73 | 218 | 4582 | 713.72 | 447.42 | 2583 | 0 | 0 | 6 | 198
13:30 | 3698 | 1310 | 906 | 0 | 85 | 920.465 | 217.5 | 4539 | 685.66 | 456.92 | 2611 | 0 | 0 | 7 | 186
14:00 | 3740 | 1299 | 906 | 0 | 86 | 924.2 | 217 | 4496 | 657.6 | 466.42 | 2639 | 0 | 0 | 8 | 174
14:30 | 3814 | 1348.5 | 906 | 0 | 86 | 924.54 | 217 | 4567 | 574.4 | 464.42 | 2700 | 0 | 0 | 9 | 231
15:00 | 3888 | 1398 | 906 | 0 | 86 | 924.88 | 217 | 4638 | 491.2 | 462.42 | 2761 | 0 | 0 | 10 | 288
15:30 | 3875 | 1384.5 | 906.5 | 0 | 86 | 922.805 | 217 | 4642 | 383.27 | 471.42 | 2787.6 | 0 | 0 | 12 | 253
16:00 | 3862 | 1371 | 907 | 0 | 86 | 920.73 | 217 | 4646 | 275.34 | 480.42 | 2814.2 | 0 | 0 | 14 | 218
16:30 | 3817 | 1353 | 906.5 | 0 | 84 | 1026.145 | 217.5 | 4636.5 | 181.605 | 482.92 | 2727.6 | 0 | 0 | 11.5 | 220.5
17:00 | 3772 | 1335 | 906 | 0 | 82 | 1131.56 | 218 | 4627 | 87.87 | 485.42 | 2641 | 0 | 0 | 9 | 223
17:30 | 3811 | 1376.5 | 906 | 0 | 88 | 1225.7 | 218.5 | 4618.5 | 43.935 | 535.42 | 2709.68 | 0 | 0 | 8 | 430
18:00 | 3850 | 1418 | 906 | 0 | 94 | 1319.84 | 219 | 4610 | 0 | 585.42 | 2778.36 | 0 | 0 | 7 | 637
18:30 | 3878 | 1425.25 | 906.5 | 0 | 92 | 1335.69 | 219.5 | 4666 | 0 | 639.42 | 3041.21 | 0 | 0 | 8.5 | 729.5
19:00 | 3906 | 1432.5 | 907 | 0 | 90 | 1351.54 | 220 | 4722 | 0 | 693.42 | 3304.06 | 0 | 0 | 10 | 822
19:30 | 3913 | 1449.5 | 903 | 0 | 94 | 1339.24 | 220 | 4745 | 0 | 670.42 | 3343.06 | 140 | 0 | 4 | 627
20:00 | 3840 | 1391 | 903 | 0 | 92 | 1341.04 | 220 | 4761 | 0 | 648.42 | 3394.06 | 165 | 0 | 2 | 661
20:30 | 3869 | 1413 | 903.5 | 0 | 89 | 1332.05 | 220.5 | 4790.5 | 0 | 665.92 | 3393.81 | 132.5 | 0 | 2 | 568.5
21:00 | 3898 | 1435 | 904 | 0 | 86 | 1323.06 | 221 | 4820 | 0 | 683.42 | 3393.56 | 100 | 0 | 2 | 476
21:30 | 3905 | 1474.5 | 904 | 0 | 88 | 1339.47 | 221 | 4836 | 0 | 679.42 | 3400.81 | 50 | 0 | 1 | 440
22:00 | 3912 | 1514 | 904 | 0 | 90 | 1355.88 | 221 | 4852 | 0 | 675.42 | 3408.06 | 0 | 0 | 0 | 404
22:30 | 3750 | 1442 | 904 | 0 | 90 | 1355.71 | 221 | 4800 | 0 | 678.42 | 3338.88 | 0 | 0 | 0 | 755
23:00 | 3588 | 1370 | 904 | 0 | 90 | 1355.54 | 221 | 4748 | 0 | 681.42 | 3269.7 | 0 | 0 | 0 | 1106
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 27-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 113 | 24 | 370 | 202 | 1296 | 622 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 78 | 28 | 270 | 210 | 798 | 598
2:00 | 75 | 32 | 270 | 210 | 768 | 580 |  | Import | 0
3:00 | 83 | 33 | 294 | 212 | 860 | 588
4:00 | 88 | 31 | 324 | 198 | 896 | 592 | Ishurdi-Ghorashal Ckt-2 | Export | 2796800
5:00 | 94 | 29 | 344 | 200 | 958 | 604
6:00 | 114 | 42 | 338 | 206 | 1002 | 662 |  | Import | 0
7:00 | 98 | 36 | 280 | 186 | 900 | 628
8:00 | 129 | 46 | 360 | 196 | 1154 | 698 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 173 | 69 | 444 | 208 | 1274 | 762
10:00 | 171 | 62 | 450 | 202 | 1374 | 774 |  | Import | 0
11:00 | 171 | 63 | 450 | 214 | 1388 | 790
12:00 | 164 | 62 | 432 | 230 | 1352 | 808 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 132 | 41 | 360 | 232 | 1156 | 750
14:00 | 126 | 42 | 354 | 232 | 1076 | 724 |  | Import | 0
15:00 | 130 | 47 | 364 | 230 | 1120 | 744
16:00 | 134 | 51 | 370 | 224 | 1084 | 754 | Gopalganj-Aminbazar Ckt-1 | Export | 12590000
17:00 | 141 | 48 | 408 | 204 | 1158 | 738
18:00 | 148 | 48 | 452 | 234 | 1246 | 734 |  | Import | 0
18:30 | 109 | 23 | 330 | 154 | 1052 | 644
19:00 | 92 | 29 | 280 | 176 | 970 | 644 | Gopalganj-Aminbazar Ckt-2 | Export | 12630000
19:30 | 92 | 25 | 284 | 168 | 864 | 592
20:00 | 91 | 19 | 302 | 166 | 880 | 588 |  | Import | 0
21:00 | 87 | 20 | 288 | 192 | 844 | 586
22:00 | 85 | 17 | 280 | 182 | 840 | 574 |  | Total Export | 28016800
23:00 | 120 | 50 | 318 | 196 | 1072 | 648 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 373 | 04:00 | 361 | 12:00 | Madunaghat | 398 | 04:00 | 392 | 00:00
Amtali | 412 | 08:00 | 407 | 19:00 | Meghnaghat | 381 | 05:00 | 368 | 12:00
Ashuganj | 394 | 5:00 | 379 | 15:00 | Mirsorai | 395 | 03:00 | 387 | 12:00
Bhulta | 385 | 05:00 | 368 | 15:00 | Payra | 413 | 05:00 | 408 | 22:00
Bibiana | 379 | 03:00 | 372 | 11:00 | Rahanpur | 409 | 08:00 | 395 | 19:00
BIPTC | 400 | 04:00 | 393 | 18:30 | Rampal | 397 | 03:00 | 385 | 00:00
Bogura | 395 | 09:00 | 378 | 19:00
Gopalganj | 391 | 03:00 | 381 | 00:00
Kaliakoir | 370 | 03:00 | 354 | 12:00
Korerhat | 394 | 05:00 | 386 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 05:00 | 216 | 12:00 | Hasnabad | 221 | 04:00 | 213 | 12:00
AKSML | 236 | 03:00 | 228 | 11:00 | Hathazari | 234 | 18:30 | 229 | 10:00
Aminbazar | 229 | 02:00 | 217 | 12:00 | Ishurdi | 235 | 03:00 | 218 | 21:00
Ashuganj | 222 | 05:00 | 214 | 13:00 | Jhenaidah | 227 | 04:00 | 208 | 22:00
Ashuganj-400 | 222 | 5:00 | 214 | 13:00 | Kachua | 225 | 23:00 | 220 | 18:00
Baghabari | 232 | 02:00 | 221 | 21:00 | Kaliakoir | 230 | 03:00 | 217 | 12:00
Barapukuria | 226 | 14:00 | 217 | 00:00 | Keranigonj | 224 | 03:00 | 213 | 12:00
Barapukuria-230 | 226 | 14:00 | 218 | 23:00 | Khulna(S) | 228 | 09:00 | 214 | 19:30
Barapukuria(N) | 229 | 23:00 | 218 | 00:00 | Korerhat | 224 | 03:00 | 219 | 12:00
Barishal | 226 | 03:00 | 220 | 22:00 | Madunaghat | 239 | 23:00 | 233 | 11:00
Bheramara | 233 | 03:00 | 217 | 22:00 | Madunaghat-400 | 240 | 21:00 | 234 | 12:00
Bhulta | 220 | 05:00 | 207 | 15:00 | Maniknagar | 222 | 22:00 | 206 | 13:00
Bibiana | 214 | 01:00 | 207 | 11:00 | Meghnaghat | 226 | 05:00 | 217 | 12:00
BIPTC | 235 | 03:00 | 216 | 21:00 | Meghnaghat-400 | 222 | 05:00 | 212 | 12:00
Birulia | 228 | 04:00 | 216 | 12:00 | Mirsorai | 231 | 02:00 | 225 | 21:00
Bogura | 239 | 09:00 | 229 | 00:00 | Naogaon | 226 | 09:00 | 205 | 21:00
Bogura-400 | 238 | 09:00 | 228 | 19:00 | Purbasadipur | 225 | 03:00 | 212 | 00:00
Borhanuddin | 228 | 04:00 | 224 | 22:00 | Rajshahi | 232 | 03:00 | 215 | 21:00
BSRM | 225 | 04:00 | 220 | 12:00 | Rampal | 227 | 05:00 | 214 | 21:00
Charfasson | 230 | 09:00 | 220 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 02:00 | 219 | 12:00 | Rampura | 219 | 05:00 | 206 | 12:00
Cumilla(N) | 218 | 04:00 | 212 | 12:00 | Shikalbaha | 240 | 19:00 | 233 | 11:00
Faridpur | 221 | 05:00 | 214 | 09:00 | Shyampur | 221 | 03:00 | 212 | 12:00
Fenchuganj | 212 | 17:00 | 206 | 12:00 | Siddhirganj | 220 | 05:00 | 210 | 15:00
Feni | 221 | 02:00 | 214 | 17:00 | Sirajgonj | 236 | 03:00 | 229 | 00:00
Ghorashal | 220 | 01:00 | 215 | 00:00 | Sreepur | 220 | 05:00 | 214 | 00:00
Ghorashal-230 | 218 | 04:00 | 202 | 12:00 | Tongi | 216 | 04:00 | 203 | 11:00
Gopalganj | 222 | 03:00 | 216 | 00:00
GPH | 232 | 18:30 | 227 | 12:00
Haripur | 219 | 05:00 | 208 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 125 | 12:00 | Madanganj | 129 | 04:00 | 122 | 12:00
Agargaon | 135 | 03:00 | 126 | 12:00 | Madaripur | 130 | 05:00 | 126 | 00:00
Agrabad | 136 | 02:00 | 131 | 11:00 | Madartek | 139 | 10:00 | 124 | 13:00
AKS | 134 | 18:30 | 130 | 11:00 | Madunaghat | 138 | 18:00 | 134 | 11:00
Aminbazar | 132 | 09:00 | 124 | 10:00 | Magura | 135 | 04:00 | 120 | 22:00
Amnura | 134 | 03:00 | 125 | 22:00 | Mahasthangarh | 135 | 09:00 | 127 | 00:00
Araihazar | 124 | 01:00 | 113 | 13:00 | Maijdee | 126 | 23:00 | 122 | 00:00
Ashuganj | 129 | 07:00 | 124 | 00:00 | Manikganj | 130 | 14:00 | 125 | 06:00
Ashuganj-230 | 133 | 04:00 | 130 | 00:00 | Maniknagar | 135 | 05:00 | 126 | 12:00
Bagerhat | 127 | 05:00 | 116 | 22:00 | Matarbari | 121 | 09:00 | 110 | 00:00
Bajitpur | 124 | 17:00 | 118 | 00:00 | Matuail | 130 | 05:00 | 123 | 12:00
Bakerganj | 134 | 10:00 | 128.5 | 21:00 | Metrorail_Motijheel | 135 | 05:00 | 126 | 12:00
Bakulia | 137 | 23:00 | 132 | 11:00 | Metrorail_Uttara | 133 | 03:00 | 120 | 12:00
Banani | 135 | 04:00 | 123 | 13:00 | Millgate | 134 | 02:00 | 121 | 12:00
Bangabhaban | 135 | 05:00 | 126 | 12:00 | Mirpur | 128 | 05:00 | 122 | 12:00
Barapukuria | 138 | 23:00 | 127 | 00:00 | Mirzapur | 130 | 02:00 | 126 | 06:00
Barguna | 134 | 10:00 | 127 | 22:00 | Mithapukur | 132 | 09:00 | 121 | 01:00
Barishal | 133 | 10:00 | 128 | 20:00 | MI_Cement | 130 | 02:00 | 121.7 | 12:00
Barishal-230 | 132 | 09:00 | 127 | 21:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 136 | 02:00 | 131 | 11:00 | Mogbazar | 138 | 05:00 | 125 | 13:00
Baroirhat | 131 | 03:00 | 126 | 12:00 | Mongla | 127 | 09:00 | 116 | 22:00
Bashundhara | 136 | 03:00 | 121 | 12:00 | Motijheel | 135 | 05:00 | 126 | 12:00
BashundharaCement | 129 | 04:00 | 122 | 12:00 | Muktagacha | 131 | 10:00 | 120 | 05:00
Beanibazar | 117 | 23:00 | 110 | 12:00 | Munshiganj | 128 | 01:00 | 121 | 12:00
Benapole | 137 | 09:00 | 113 | 21:00 | Muradnagar | 123 | 05:00 | 118 | 12:00
Bhaluka | 129 | 10:00 | 124 | 00:00 | Mymensingh | 134 | 10:00 | 113 | 18:00
Bhandaria | 130 | 09:00 | 120 | 00:00 | Nabinagar | 134 | 02:00 | 124 | 12:00
Bhangura | 134 | 05:00 | 126 | 21:00 | Naogaon | 136 | 09:00 | 123 | 00:00
Bheramara | 137 | 03:00 | 127 | 21:00 | Narail | 135 | 09:00 | 118 | 19:30
Bheramara(GK) | 137 | 05:00 | 126 | 21:00 | Narinda | 135 | 5:00 | 126 | 12:00
Bhulta | 124 | 07:00 | 115 | 15:00 | Narshingdi | 128 | 02:00 | 110 | 15:00
Bhulta-400 | 125 | 02:00 | 114 | 15:00 | Natore | 135 | 09:00 | 124 | 21:00
Birulia | 133 | 02:00 | 127 | 12:00 | Nawabganj | 135 | 04:00 | 127 | 13:00
Bog-Sherpur | 135 | 03:00 | 128 | 22:00 | Netrakona | 118 | 08:00 | 109 | 14:00
Bogura | 137 | 05:00 | 132 | 00:00 | New | 135 | 05:00 | 121 | 12:00
Bogura-230 | 138 | 08:00 | 132 | 00:00 | Niamatpur | 135 | 09:00 | 127 | 19:00
Brahmanbaria | 126 | 19:00 | 121 | 21:00 | Noapara | 129 | 04:00 | 118 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 135 | 03:00 | 126 | 12:00 | Pabna | 134 | 03:00 | 125 | 19:30
Chandina | 126 | 02:00 | 122 | 12:00 | Palashbari | 131 | 10:00 | 120 | 00:00
Chandpur | 132 | 18:30 | 127 | 11:00 | Panchagarh | 138 | 03:00 | 128 | 00:00
Chandraghona | 137 | 06:00 | 134 | 11:00 | Patiya | 135 | 14:00 | 130 | 00:00
Chapai | 134 | 03:00 | 128 | 00:00 | Patnitala | 134 | 09:00 | 125 | 22:00
Charsaidpur | 129 | 01:00 | 123 | 12:00 | Patuakhali | 134 | 15:00 | 129 | 20:00
Chauddagram | 126 | 04:00 | 122 | 00:00 | Payra | 135 | 10:00 | 133 | 00:00
Chhatak | 115 | 07:00 | 102 | 12:00 | PHP | 130 | 03:00 | 126 | 12:00
Chowmuhani | 126 | 02:00 | 123 | 00:00 | Postogola | 133 | 05:00 | 125 | 13:00
Chuadanga | 135 | 05:00 | 118 | 21:00 | Pubail | 125 | 01:00 | 118 | 11:00
Coxsbazar | 122 | 05:00 | 111 | 18:30 | Purbachal | 136 | 04:00 | 124 | 13:00
Cumilla(N) | 126 | 05:00 | 122 | 00:00 | Purbasadipur | 137 | 17:00 | 128 | 00:00
Cumilla(S) | 131 | 04:00 | 122 | 18:00 | Rahanpur | 137 | 07:00 | 131 | 21:00
Daganbhuiyan | 127 | 02:00 | 124 | 00:00 | Rahanpur-400 | 137 | 05:00 | 131 | 22:00
Daudkandi | 123 | 05:00 | 117 | 12:00 | Rahim | 130 | 06:00 | 123 | 12:00
DhakaUniversity | 136 | 04:00 | 125 | 12:00 | Rajbari | 126 | 05:00 | 119 | 21:00
Dhamrai | 134 | 04:00 | 125 | 12:00 | Rajendrapur | 131 | 02:00 | 126 | 14:00
Dhanmondi | 136 | 03:00 | 124.6 | 13:00 | Rajshahi | 133 | 09:00 | 122 | 22:00
Dohazari | 129 | 08:00 | 125 | 00:00 | Rajshahi-230 | 134 | 06:00 | 123 | 21:00
Faridpur | 127 | 04:00 | 124 | 00:00 | Ramganj | 127 | 19:00 | 122 | 00:00
Fatullah | 132 | 04:00 | 122 | 13:00 | Rampur | 137 | 23:00 | 131 | 12:00
Fenchuganj | 124 | 02:00 | 120 | 12:00 | Rampura | 137 | 06:00 | 125 | 15:00
Feni | 128 | 04:00 | 123 | 00:00 | Rangamati | 136 | 17:00 | 133 | 11:00
Feni-230 | 129 | 03:00 | 124 | 17:00 | Rangpur | 131 | 14:00 | 121 | 00:00
Ghatail | 126 | 09:00 | 118 | 07:00 | Ruppur | 137 | 03:00 | 127 | 21:00
Ghorashal | 130 | 01:00 | 122 | 12:00 | Saidpur | 134 | 16:00 | 126 | 19:00
Goalpara | 132 | 06:00 | 120 | 22:00 | Santhia | 135 | 04:00 | 126 | 19:30
Gollamari | 131 | 09:00 | 122 | 19:30 | Satkhira | 127 | 10:00 | 111 | 19:30
Gopalganj | 130 | 03:00 | 125 | 00:00 | Satmasjid | 135 | 03:00 | 126 | 12:00
Gopalganj-400 | 131 | 03:00 | 127 | 00:00 | Savar | 128 | 03:00 | 122 | 09:00
Gulshan | 135 | 04:00 | 125 | 12:00 | SevenRings | 131 | 04:00 | 121 | 12:00
Halishahar | 138 | 20:00 | 132 | 11:00 | ShahCement | 129 | 01:00 | 123 | 12:00
Haripur | 130 | 07:00 | 124 | 12:00 | Shahjadpur | 136 | 07:00 | 130 | 19:30
HaripurSBU | 130 | 02:00 | 124 | 12:00 | Shahjibazar | 125 | 17:00 | 121 | 00:00
Hasnabad | 132 | 03:00 | 123 | 13:00 | Shahmirpur | 139 | 20:00 | 132 | 11:00
Hathazari | 137 | 18:30 | 134 | 10:00 | Shariatpur | 128 | 05:00 | 122 | 21:00
Hatirjheel | 136 | 04:00 | 125 | 13:00 | Sherpur | 133 | 10:00 | 115 | 07:00
Ishurdi | 138 | 09:00 | 127 | 21:00 | Shikalbaha | 126 | 01:00 | 121 | 12:00
Jaldhaka | 132 | 02:00 | 119 | 19:00 | Shikalbaha-230 | 138 | 03:00 | 133 | 12:00
Jamalpur | 136 | 10:00 | 120 | 03:00 | Shitalakhya | 130 | 02:00 | 121.7 | 12:00
Jashore | 138 | 04:00 | 114 | 21:00 | Sholosohor | 137 | 20:00 | 132 | 11:00
Jhenaidah | 139 | 06:00 | 123 | 21:00 | Shomvuganj | 119 | 18:30 | 110 | 00:00
Jhenaidah-230 | 139 | 06:00 | 125 | 21:00 | Shyampur | 131 | 03:00 | 123 | 12:00
Joydebpur | 125 | 04:00 | 115 | 12:00 | Shyampur-230 | 133 | 05:00 | 123 | 12:00
Joypurhat | 134 | 08:00 | 126 | 19:00 | Siddhirganj | 130 | 01:00 | 124 | 12:00
Juldah | 138 | 20:00 | 132 | 12:00 | Sirajganj | 132 | 05:00 | 123 | 19:30
Kabirpur | 134 | 02:00 | 117 | 12:00 | Sitakunda | 136 | 23:00 | 132 | 11:00
Kachua | 128 | 02:00 | 125 | 00:00 | Sonargaon | 127 | 06:00 | 122 | 15:00
Kaliakoir | 136 | 02:00 | 130 | 12:00 | Sreemongol | 123 | 19:00 | 118 | 12:00
Kaliganj | 138 | 05:00 | 124 | 21:00 | Sreepur | 133 | 06:00 | 128 | 21:00
Kallyanpur | 129 | 08:00 | 123 | 11:00 | Srinagar | 135 | 04:00 | 127 | 12:00
Kalurghat | 138 | 23:00 | 134 | 11:00 | SSM | 140 | 10:00 | 138 | 00:00
Kamrangirchar | 137 | 06:00 | 121 | 10:00 | Sunamganj | 111 | 05:00 | 100 | 11:00
Kaptai | 139 | 4:00 | 137 | 1:00 | Sylhet | 117 | 03:00 | 110 | 12:00
Kasba | 122 | 03:00 | 118 | 00:00 | Sylhet_(South) | 117 | 03:00 | 112 | 10:00
Kazla | 135 | 05:00 | 125 | 13:00 | Tangail | 127 | 09:00 | 121 | 06:00
Keranigonj | 136 | 04:00 | 128 | 12:00 | Taraganj | 132 | 04:00 | 123 | 19:00
Khagrachori | 134 | 03:00 | 132 | 00:00 | Tasnim | 127 | 02:00 | 122 | 15:00
Khulna | 130 | 05:00 | 119 | 21:00 | Thakurgaon | 140 | 17:00 | 129 | 00:00
Khulna(S) | 131 | 01:00 | 121 | 21:00 | TK | 137 | 20:00 | 134 | 00:00
Khulshi | 136 | 23:00 | 130 | 11:00 | Tongi | 133 | 04:00 | 124 | 11:00
Kishoreganj | 123 | 18:30 | 114 | 00:00 | Ullahpara | 134 | 05:00 | 125 | 22:00
Kodda | 133 | 02:00 | 115 | 12:00 | Ullon | 135 | 03:00 | 125 | 13:00
Korerhat | 132 | 02:00 | 129 | 11:00 | Uttara | 134 | 04:00 | 119 | 12:00
KSRM | 138 | 23:00 | 132 | 11:00 | UttaraNew | 133 | 03:00 | 120 | 12:00
Kulaura | 123 | 05:00 | 119 | 12:00 | Zigatola | 136 | 04:00 | 127 | 13:00
Kurigram | 129 | 23:00 | 117 | 19:00
Kushtia | 136 | 06:00 | 124 | 21:00
Laksam | 128 | 19:00 | 124 | 00:00
Lakshmipur | 126 | 23:00 | 121 | 00:00
Lalbag | 135 | 03:00 | 127 | 12:00
Lalmonirhat | 127 | 10:00 | 121 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division