## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-10-2026 | [28 empty] | Date: | 03-10-2026 | [28 empty] | Date: | 03-10-2026 | [28 empty] | Date: | 03-10-2026 | [28 empty] | Date: | 03-10-2026 | [16 empty] | Date: | 03-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 0 | 61 | 15 | 279 | 55 | 55 | 162 | 0 | 0 | 365 | 0 | 35 | 308 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 505 | 36 | 104 | 46 | 0 | 0 | 51 | 42 | 35 | 100 | 100 | 0 | 220 | 110 | 42 | 1050 | 36 | 0 | 50 | 8 | 85 | 222 | 0 | 0 | 0 | 1160 | 0 | 150 | 177 | 0 | 335 | 0 | 44 | 22 | 201 | 37 | 69 | 108 | 21 | 68 | 19 | 86 | 66 | 8 | 0 | 0 | 266 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 139 | 0 | 100 | 0 | 86 | 0 | 193 | 0 | 0 | 0 | 0 | 8920.5 | 809 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1150 | 17 | 0 | 0 | 593.98 | 0 | 0 | 0 | 35 | 113 | 0 | 25 | 28 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5723.18 | 14643.68 | 106.41
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 35 | 0 | 97 | 15 | 279 | 55 | 35 | 54 | 0 | 0 | 340 | 0 | 35 | 316 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 480 | 35 | 67 | 45 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0 | 221 | 110 | 42 | 1050 | 35 | 0 | 50 | 8 | 85 | 222 | 0 | 0 | 0 | 1160 | 0 | 125 | 173 | 0 | 335 | 0 | 44 | 40 | 201 | 37 | 69 | 107 | 16 | 73 | 19 | 86 | 64 | 8 | 0 | 0 | 250 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8398.5 | 810 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 517.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5446.86 | 13845.36 | 106.42
02:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 0 | 109 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 190 | 0 | 35 | 312 | 0 | 0 | 0 | 17 | 13.5 | 22 | 0 | 530 | 36 | 68 | 42 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0 | 221 | 110 | 42 | 1050 | 35 | 0 | 50 | 8 | 97 | 222 | 0 | 0 | 0 | 1160 | 0 | 102 | 184 | 0 | 325 | 0 | 44 | 46 | 196 | 37 | 69 | 107 | 17 | 0 | 19 | 86 | 62 | 8 | 0 | 0 | 256 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8119.5 | 906 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 509.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 149 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1000 | 300 | 54 | 5499.57 | 13619.07 | 106.43
03:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35 | 0 | 130 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 175 | 0 | 35 | 304 | 0 | 0 | 0 | 17 | 13.8 | 22 | 0 | 520 | 36 | 68 | 45 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0 | 222 | 110 | 42 | 1050 | 36 | 0 | 50 | 0 | 95 | 221 | 0 | 0 | 0 | 1160 | 0 | 102 | 185 | 0 | 315 | 0 | 44 | 47 | 192 | 36 | 69 | 107 | 16 | 0 | 19 | 86 | 60 | 8 | 0 | 0 | 253 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 138 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8079.8 | 906 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 508.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 117 | 220 | 0 | 1000 | 300 | 54 | 5500.25 | 13580.05 | 106.44
04:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 35 | 0 | 133 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 190 | 0 | 35 | 317 | 0 | 0 | 0 | 17 | 13.8 | 22 | 0 | 540 | 36 | 68 | 45 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0 | 222 | 110 | 42 | 1050 | 35 | 0 | 50 | 0 | 105 | 222 | 0 | 0 | 0 | 1160 | 0 | 41 | 187 | 0 | 335 | 0 | 44 | 47 | 201 | 36 | 69 | 107 | 16 | 0 | 19 | 86 | 60 | 8 | 0 | 0 | 255 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 8093.8 | 899 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 512.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 240 | 117 | 220 | 0 | 1000 | 300 | 54 | 5436.11 | 13529.91 | 106.45
05:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 0 | 133 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 200 | 0 | 17 | 309 | 0 | 0 | 0 | 17 | 13.8 | 22 | 0 | 515 | 35 | 68 | 45 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0 | 220 | 95 | 27 | 1050 | 36 | 0 | 50 | 0 | 105 | 222 | 0 | 0 | 0 | 1140 | 0 | 26 | 187 | 0 | 325 | 0 | 44 | 47 | 199 | 36 | 69 | 107 | 17 | 0 | 19 | 86 | 60 | 8 | 0 | 0 | 251 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 5 | 0 | 0 | 0 | 7928.8 | 899 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 17 | 0 | 0 | 513.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 300 | 117 | 220 | 0 | 1000 | 300 | 54 | 5496.03 | 13424.83 | 106.46
06:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 35 | 0 | 127 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 220 | 0 | 17 | 304 | 0 | 0 | 0 | 17 | 13.8 | 22 | 0 | 505 | 36 | 68 | 46 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0.01 | 219 | 92 | 41 | 1050 | 35 | 0 | 50 | 0 | 105 | 223 | 0 | 0 | 0 | 1120 | 0 | 26 | 187 | 0 | 310 | 80 | 44 | 47 | 186 | 36 | 64 | 107 | 16 | 0 | 19 | 86 | 58 | 8 | 0 | 0 | 247 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 58 | 0.05 | 67 | 12 | 0 | 0.09 | 0 | 7947.95 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 1150 | 17 | 0 | 0 | 514.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0.19 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.01 | 155 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.02 | 110 | 307 | 95 | 180 | 0 | 1000 | 300 | 54 | 5305.98 | 13253.93 | 106.47
07:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 17 | 0 | 124 | 15 | 196 | 55 | 0 | 72 | 0 | 0 | 250 | 0 | 17 | 310 | 0 | 0 | 5 | 17 | 13 | 22 | 0 | 530 | 35 | 68 | 46 | 0 | 0 | 51 | 29 | 0 | 24 | 37 | 0.42 | 218 | 92 | 38 | 1050 | 35 | 0 | 50 | 0 | 105 | 223 | 0 | 0 | 0 | 1160 | 3 | 26 | 187 | 0 | 320 | 77 | 44 | 46 | 197 | 36 | 51 | 107 | 16 | 0 | 19 | 86 | 56 | 8 | 11 | 0 | 244 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 139 | 0 | 100 | 0 | 58 | 2.5 | 67 | 10 | 0.2 | 4.73 | 0 | 8052.85 | 805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1150 | 17 | 0 | 0 | 511.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 7.62 | 13 | 0 | 0 | 7.89 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.76 | 154 | 0 | 115 | 3 | 34 | 0 | 0 | 0 | 0.8 | 18 | 0.05 | 110 | 307 | 110 | 220 | 0 | 1000 | 300 | 54 | 5419.18 | 13472.03 | 106.48
08:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 0 | 127 | 15 | 160 | 30 | 0 | 72 | 0 | 0 | 305 | 0 | 17 | 300 | 0 | 0 | 13 | 17 | 12 | 22 | 0 | 480 | 36 | 68 | 39 | 0 | 0 | 51 | 27 | 30 | 24 | 37 | 1.53 | 218 | 94 | 15 | 1055 | 35 | 0 | 50 | 0 | 105 | 220 | 0 | 0 | 0 | 1160 | 10 | 26 | 187 | 0 | 304 | 73 | 44 | 44 | 185 | 36 | 51 | 107 | 17 | 1 | 19 | 34 | 60 | 0 | 23 | 0 | 242 | 400 | 276 | 40 | 40 | 0 | 2 | 16 | 0 | 80 | 30 | 139 | 0 | 100 | 0 | 58 | 7.8 | 67 | 10 | 0.6 | 18.36 | 0 | 7975.29 | 805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1150 | 17 | 0 | 0 | 551.81 | 0 | 0 | 0 | 35 | 11 | 0 | 0 | 0 | 25 | 21.62 | 36 | 0 | 0 | 21.41 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.88 | 160 | 0 | 70 | 12 | 34 | 0 | 0 | 0 | 2.1 | 60 | 0.22 | 80 | 307 | 116 | 180 | 0 | 1000 | 300 | 54 | 5502.04 | 13477.33 | 106.49
09:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 133 | 15 | 110 | 15 | 0 | 72 | 0 | 0 | 385 | 0 | 17 | 310 | 0 | 0 | 21 | 17 | 10.5 | 22 | 0 | 450 | 0 | 50 | 26 | 0 | 0 | 0 | 27 | 36 | 0 | 37 | 2.38 | 219 | 34 | 10 | 1055 | 35 | 0 | 50 | 0 | 68 | 218 | 0 | 0 | 0 | 1160 | 15 | 26 | 187 | 0 | 327 | 125 | 44 | 46 | 200 | 36 | 16 | 107 | 0 | 54 | 19 | 0 | 64 | 0 | 28 | 0 | 241 | 400 | 276 | 42 | 40 | 0 | 7 | 16 | 0 | 79 | 30 | 141 | 0 | 100 | 0 | 58 | 13.38 | 113 | 8 | 1.2 | 32.84 | 0 | 7961.3 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1150 | 0 | 0 | 0 | 553.27 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 36.91 | 65 | 0 | 0 | 36.64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 3.36 | 157 | 0 | 0 | 21 | 34 | 0 | 0 | 0 | 1.8 | 114 | 0.38 | 16 | 307 | 116 | 220 | 0 | 980 | 300 | 54 | 5543.36 | 13504.66 | 106.5
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 0 | 99 | 5 | 80 | 15 | 35 | 72 | 0 | 0 | 445 | 0 | 17 | 310 | 0 | 0 | 27 | 105 | 10.5 | 22 | 0 | 350 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 24 | 2.43 | 220 | 34 | 8 | 1055 | 0 | 0 | 6 | 8 | 34 | 218 | 0 | 0 | 0 | 1100 | 13 | 26 | 187 | 0 | 336 | 200 | 44 | 46 | 204 | 36 | 16 | 107 | 0 | 73 | 19 | 0 | 66 | 0 | 62 | 0 | 242 | 397 | 276 | 42 | 40 | 0 | 6 | 16 | 0 | 83 | 30 | 139 | 0 | 100 | 0 | 58 | 13 | 112 | 5 | 1.6 | 41.8 | 0 | 7833.33 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1150 | 0 | 0 | 0 | 564.55 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 47.39 | 86 | 0 | 0 | 48.31 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.37 | 156 | 0 | 0 | 26 | 34 | 0 | 0 | 0 | 5.2 | 144 | 0.31 | 16 | 307 | 115 | 220 | 0 | 947 | 300 | 17 | 5610.13 | 13443.46 | 106.5
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 0 | 70 | 15 | 80 | 15 | 35 | 72 | 0 | 0 | 575 | 0 | 17 | 308 | 0 | 0 | 31 | 105 | 10.5 | 22 | 0 | 350 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 38 | 3.91 | 220 | 34 | 7 | 1055 | 2 | 0 | 6 | 8 | 34 | 214 | 0 | 0 | 0 | 1160 | 0 | 26 | 187 | 0 | 333 | 230 | 35 | 45 | 208 | 37 | 22 | 108 | 0 | 73 | 19 | 0 | 70 | 0 | 52 | 0 | 242 | 400 | 276 | 42 | 40 | 0 | 10 | 16 | 0 | 80 | 30 | 141 | 0 | 100 | 0 | 58 | 20.22 | 115 | 0 | 0.8 | 37.02 | 0 | 8068.45 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1190 | 0 | 0 | 0 | 573.58 | 0 | 0 | 0 | 55 | 1 | 0 | 0 | 0 | 0 | 50.33 | 95 | 0 | 0 | 58.42 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.24 | 157 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 4.3 | 129 | 0.62 | 32 | 307 | 114 | 220 | 0 | 965 | 300 | 17 | 5736.49 | 13804.94 | 106.5
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 17 | 0 | 70 | 15 | 162 | 41 | 35 | 72 | 0 | 0 | 455 | 0 | 17 | 315 | 0 | 0 | 12 | 123 | 10.5 | 22 | 0 | 420 | 10 | 112 | 2 | 0 | 2 | 0 | 0 | 36 | 10 | 25 | 3.4 | 221 | 49 | 7 | 1055 | 92 | 0 | 13 | 8 | 62 | 214 | 0 | 0 | 0 | 1180 | 11 | 26 | 187 | 0 | 345 | 225 | 44 | 45 | 192 | 36 | 61 | 108 | 16 | 72 | 11 | 7 | 78 | 0 | 68 | 0 | 243 | 395 | 276 | 42 | 40 | 0 | 7 | 16 | 0 | 80 | 28 | 140 | 0 | 100 | 0 | 58 | 18.85 | 115 | 0 | 2 | 50.19 | 0 | 8487.94 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1234.2 | 0 | 0 | 0 | 578.5 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 56.42 | 100 | 0 | 0 | 57.09 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.54 | 158 | 0 | 40 | 34 | 34 | 0 | 0 | 0 | 4 | 164 | 0.64 | 73 | 307 | 114 | 220 | 0 | 966 | 300 | 54 | 6007.39 | 14495.33 | 106.51
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 17 | 0 | 108 | 15 | 261 | 55 | 35 | 72 | 0 | 0 | 400 | 0 | 17 | 310 | 0 | 0 | 29 | 123 | 10.5 | 21 | 0 | 350 | 48 | 151 | 24 | 0 | 6 | 0 | 0 | 36 | 24 | 25 | 0.74 | 221 | 75 | 8 | 1055 | 141 | 0 | 35 | 8 | 105 | 213 | 0 | 0 | 0 | 1190 | 18 | 26 | 187 | 0 | 331 | 230 | 44 | 45 | 168 | 36 | 72 | 107 | 17 | 72 | 11 | 71 | 76 | 0 | 63 | 0 | 249 | 400 | 276 | 40 | 40 | 0 | 10 | 16 | 0 | 83 | 25 | 140 | 0 | 100 | 0 | 58 | 19.39 | 113 | 0 | 1.9 | 46.09 | 0 | 8796.62 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1234.2 | 17 | 0 | 0 | 566.46 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 25 | 52.07 | 91 | 0 | 0 | 52.65 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.9 | 155 | 0 | 94 | 25 | 34 | 0 | 0 | 0 | 4.8 | 190 | 0.6 | 110 | 307 | 114 | 220 | 0 | 972 | 300 | 54 | 6118.68 | 14915.3 | 106.51
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 0 | 131 | 15 | 278 | 55 | 35 | 72 | 0 | 0 | 385 | 0 | 35 | 315 | 0 | 0 | 24 | 123 | 10.5 | 21 | 0 | 390 | 91 | 155 | 43 | 0 | 4 | 0 | 0 | 36 | 24 | 25 | 1.11 | 221 | 87 | 2 | 1060 | 141 | 0 | 40 | 0 | 105 | 213 | 0 | 0 | 0 | 1160 | 17 | 26 | 147 | 0 | 341 | 225 | 44 | 43 | 174 | 35 | 72 | 108 | 16 | 72 | 17 | 86 | 78 | 0 | 53 | 0 | 256 | 393 | 266 | 40 | 40 | 0 | 9 | 16 | 0 | 82 | 30 | 139 | 0 | 100 | 0 | 58 | 16.28 | 113 | 0 | 1.6 | 38.89 | 0 | 8897.38 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1234.2 | 17 | 0 | 0 | 577.87 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 34 | 44 | 88 | 0 | 0 | 35.27 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.26 | 157 | 0 | 115 | 26 | 34 | 0 | 0 | 0 | 3.2 | 150 | 0.46 | 110 | 307 | 134 | 220 | 0 | 966 | 300 | 54 | 6067.26 | 14964.64 | 106.51
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 0 | 133 | 15 | 278 | 55 | 35 | 72 | 0 | 0 | 385 | 0 | 35 | 315 | 0 | 0 | 16 | 123 | 10.5 | 21 | 0 | 360 | 95 | 158 | 43 | 0 | 2 | 0 | 0 | 36 | 24 | 25 | 1.83 | 120 | 92 | 2 | 1060 | 150 | 0 | 47 | 0 | 105 | 213 | 0 | 0 | 0 | 1224 | 12 | 26 | 128 | 0 | 335 | 224 | 44 | 20 | 205 | 35 | 69 | 108 | 16 | 70 | 18 | 85 | 78 | 0 | 37 | 0 | 250 | 393 | 275 | 40 | 38 | 0 | 6 | 16 | 0 | 82 | 30 | 140 | 0 | 100 | 0 | 58 | 12.32 | 113 | 0 | 1.1 | 27.13 | 0 | 8784.88 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1234.2 | 17 | 0 | 0 | 567.99 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 27.42 | 64 | 0 | 0 | 33.4 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.87 | 162 | 0 | 115 | 21 | 34 | 0 | 0 | 0 | 2.9 | 90 | 0.36 | 105 | 307 | 113 | 220 | 0 | 979 | 300 | 54 | 5938.14 | 14723.02 | 106.53
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 0 | 132 | 15 | 261 | 55 | 35 | 90 | 0 | 0 | 315 | 0 | 35 | 318 | 0 | 0 | 9 | 123 | 10.5 | 22 | 0 | 340 | 90 | 158 | 44 | 0 | 0 | 0 | 0 | 36 | 24 | 12 | 0.78 | 122 | 92 | 2 | 1060 | 155 | 0 | 46 | 0 | 105 | 213 | 0 | 0 | 0 | 1224 | 7 | 31 | 127 | 0 | 328 | 225 | 44 | 20 | 197 | 31 | 68 | 108 | 16 | 71 | 13 | 85 | 70 | 0 | 11 | 0 | 248 | 397 | 276 | 40 | 38 | 0 | 3 | 16 | 0 | 82 | 30 | 140 | 0 | 100 | 0 | 57 | 6.39 | 114 | 0 | 0.6 | 12.18 | 0 | 8569.45 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 1234.2 | 17 | 0 | 0 | 567.79 | 0 | 0 | 0 | 55 | 60 | 0 | 0 | 0 | 43 | 15.68 | 34 | 0 | 0 | 17.43 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.57 | 158 | 0 | 115 | 9 | 37 | 0 | 0 | 0 | 0.3 | 56 | 0.19 | 110 | 307 | 114 | 220 | 0 | 1000 | 300 | 54 | 5864.16 | 14433.61 | 106.53
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 0 | 133 | 4 | 261 | 55 | 55 | 162 | 0 | 0 | 410 | 0 | 35 | 320 | 0 | 0 | 2 | 143.42 | 10.5 | 22 | 0 | 330 | 108 | 209 | 45 | 0 | 0 | 0 | 0 | 36 | 24 | 12 | 0.15 | 80 | 92 | 10 | 1060 | 160 | 0 | 48 | 0 | 105 | 214 | 0 | 0 | 0 | 1224 | 1 | 107 | 147 | 0 | 311 | 230 | 44 | 20 | 194 | 36 | 69 | 108 | 17 | 70 | 18 | 85 | 66 | 0 | 4 | 0 | 248 | 398 | 276 | 40 | 38 | 0 | 1 | 16 | 0 | 82 | 30 | 140 | 0 | 100 | 0 | 57 | 1.7 | 114 | 0 | 0.1 | 3.26 | 0 | 8902.13 | 787 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 6 | 1234.2 | 17 | 0 | 0 | 561.67 | 0 | 0 | 0 | 112 | 90 | 0 | 0 | 5 | 43 | 3.95 | 9 | 0 | 0 | 4.13 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0.33 | 157 | 0 | 115 | 3 | 34 | 0 | 0 | 0 | 0 | 15 | 0.04 | 110 | 307 | 114 | 220 | 0 | 1000 | 300 | 54 | 5771.32 | 14673.45 | 106.54
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 14 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 315 | 0 | 55 | 318 | 0 | 0 | 0 | 143.42 | 10.5 | 22 | 0 | 400 | 107 | 209 | 38 | 0 | 0 | 0 | 0 | 36 | 24 | 12 | 0 | 220 | 92 | 3 | 1060 | 163 | 0 | 50 | 1 | 105 | 217 | 0 | 0 | 0 | 1160 | 0 | 128 | 147 | 0 | 311 | 230 | 44 | 20 | 206 | 30 | 69 | 108 | 49 | 70 | 18 | 85 | 80 | 0 | 0 | 0 | 250 | 398 | 276 | 40 | 38 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 57 | 0 | 118 | 0 | 0 | 0 | 2 | 9227.92 | 682 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 662.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 52.2 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 155 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1100 | 300 | 91 | 5693.06 | 14920.98 | 106.54
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 17 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 395 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 320 | 109 | 211 | 48 | 0 | 0 | 36 | 0 | 54.36 | 24 | 12 | 0 | 220 | 92 | 13 | 1060 | 160 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 133 | 147 | 0 | 275 | 230 | 44 | 20 | 183 | 36 | 83 | 108 | 51 | 72 | 18 | 85 | 64 | 9 | 0 | 0 | 245 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 77 | 0 | 198 | 0 | 0 | 0 | 12 | 9478.08 | 588 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 753.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 115 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1100 | 300 | 91 | 5737.88 | 0 | 106.54
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 17 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 475 | 0 | 55 | 318 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 470 | 108 | 211 | 52 | 0 | 0 | 51 | 0 | 54.36 | 24 | 12 | 0 | 220 | 92 | 11 | 1055 | 160 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 163 | 0 | 349 | 225 | 44 | 20 | 222 | 36 | 115 | 108 | 51 | 72 | 19 | 85 | 78 | 34 | 0 | 0 | 246 | 397 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 77 | 0 | 199 | 0 | 0 | 0 | 12 | 9924.08 | 588 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 748.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 0 | 115 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 91 | 5765.25 | 15215.96
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 17 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 455 | 0 | 55 | 321 | 0 | 0 | 0 | 143.42 | 11.2 | 22 | 0 | 370 | 107 | 212 | 52 | 0 | 0 | 51 | 1 | 54.36 | 24 | 12 | 0 | 220 | 92 | 13 | 1055 | 162 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 165 | 0 | 331 | 230 | 44 | 27 | 203 | 36 | 115 | 108 | 52 | 72 | 19 | 86 | 78 | 36 | 0 | 0 | 245 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 141 | 0 | 100 | 0 | 77 | 0 | 200 | 0 | 0 | 0 | 12 | 9801.48 | 588 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 737.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 115 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 91 | 5814.2 | 15689.33 | 106.55
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 17 | 133 | 5 | 278 | 55 | 55 | 162 | 0 | 0 | 450 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 360 | 107 | 212 | 52 | 0 | 0 | 51 | 9 | 54.36 | 24 | 12 | 0 | 221 | 92 | 29 | 1055 | 162 | 0 | 50 | 18 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 165 | 0 | 330 | 230 | 44 | 30 | 204 | 37 | 115 | 108 | 51 | 70 | 19 | 86 | 76 | 52.2 | 0 | 0 | 244 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 0 | 77 | 0 | 200 | 0 | 0 | 0 | 12 | 9787.98 | 806 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 709.47 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 30 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 0 | 115 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 91 | 6094.87 | 15615.68 | 106.59
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 30 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 405 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 470 | 109 | 212 | 52 | 0 | 0 | 51 | 29 | 36 | 24 | 12 | 0 | 222 | 93 | 26 | 1055 | 63 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 167 | 0 | 350 | 230 | 44 | 30 | 207 | 37 | 108 | 108 | 51 | 72 | 19 | 86 | 80 | 52.2 | 0 | 0 | 243 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 138 | 0 | 100 | 1 | 77 | 0 | 200 | 0 | 0 | 0 | 12 | 9693.92 | 806 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 690.41 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 91 | 6078.81 | 15882.85 | 106.59
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 133 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 410 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 465 | 107 | 212 | 48 | 0 | 0 | 51 | 29 | 36 | 24 | 12 | 0 | 222 | 92 | 34 | 1055 | 18 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 345 | 230 | 44 | 30 | 179 | 37 | 101 | 107 | 51 | 69 | 19 | 86 | 84 | 52.2 | 0 | 0 | 246 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 139 | 0 | 100 | 17 | 77 | 0 | 200 | 0 | 0 | 0 | 12 | 9652.92 | 807 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 694.73 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1000 | 300 | 91 | 5983.13 | 15772.73 | 106.59
Total KWH | 0 | 952320 | 368160 | 0 | 0 | 0 | 0 | 0 | 9223200 | 0 | 0 | 783000 | 170280 | 2929968 | 346560 | 5359920 | 1194530 | 799095 | 2350080 | 0 | 0 | 8545955 | 0 | 799772 | 7482740 | 0 | 0 | 199512 | 2085600 | 277200 | 524160 | 0 | 10633636.36 | 1505455 | 2998364 | 923520 | 0 | 13440 | 675799 | 359357 | 663838 | 552960 | 651480 | 18238 | 4906067 | 2113491 | 500160 | 25410909.09 | 1938691 | 0 | 1059360 | 166996.8 | 2332618 | 5295182 | 0 | 0 | 0 | 28352724 | 112995 | 1823272 | 4148364 | 0 | 8312300 | 3658000 | 921056 | 898080 | 4841000 | 860832 | 1667520 | 2580136 | 580320 | 1202040 | 427580 | 1666680 | 1635840 | 313930 | 436373 | 0 | 5932000 | 9591600 | 6672000 | 953000 | 951696 | 0 | 59196 | 465504 | 0 | 1962240 | 710784 | 3152000 | 0 | 2402060 | 37080 | 1492800 | 126000 | 2860800 | 38400 | 12150 | 291190 | 76800 | 209337956.25 | 20108364 | 0 | 225600 | 0 | 0 | 0 | 0 | 0 | 0 | 615456 | 506160 | 28763630 | 316320 | 0 | 0 | 14046006 | 0 | 0 | 0 | 840192 | 522624 | 0 | 0 | 137416 | 949579 | 352000 | 706056 | 314176 | 0 | 368357 | 0 | 0 | 0 | 0 | 0 | 0 | 9611490 | 0 | 31860 | 3884000 | 0 | 2278097 | 196998 | 1076985 | 0 | 0 | 0 | 32145.12 | 1100880 | 3952 | 2332608 | 7287000 | 2750000 | 5392640 | 0 | 24516363 | 7322181.82 | 1474800 | 138063935.94 | 347401892.19

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-10-2026 | during | 04-10-2026 | during | 04-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 381 | 412 | 412 | 412 | 412 | 412 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 41 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 300 | 335 | 335 | 305 | 305 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 5 | 149.36 | 149.36 | 15 | 15 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10.5 | 11 | 24.75 | 24.75 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 50 | 52.19 | 52.19 | 8 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 162 | 278 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 133 | 149 | 149 | 97 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 17 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 360 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 455 | 450 | 583 | 583 | 400 | 400 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2243.5 | 2667.42 | 5576.91 | 5544.91 | 2357.42 | 2743.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 18 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 62 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 9 | 0 | 0 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 24 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 7 | 29 | 30 | 42 | 30 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 2 | 52 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.4 | 0 | 3.82 | 0 | 3.82 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 112 | 212 | 300 | 300 | 230 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 49 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 10 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 92 | 162 | 163 | 163 | 35 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1180 | 1224 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1055 | 1055 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3112.4 | 3695.36 | 4080.78 | 4122.96 | 3631.82 | 3879.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 192 | 204 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 345 | 330 | 350.01 | 350.01 | 314.01 | 314.01 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 225 | 230 | 342.01 | 342.01 | 306.01 | 306.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 37 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 45 | 30 | 52.82 | 52.82 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 165 | 195 | 195 | 100 | 155 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 51 | 51 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 150 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 23 | 23 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 108 | 108 | 163 | 163 | 108 | 108 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 16 | 51 | 200 | 200 | 51 | 160 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 78 | 76 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 7 | 86 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 72 | 70 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 61 | 115 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 0 | 0 | 0 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1521 | 1767.2 | 2269.44 | 2263.44 | 1667.47 | 1962.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-10-2026 | during | 04-10-2026 | during | 04-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 18.85 | 0 | 18 | 0 | 18 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 200 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 77 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.19 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 22 | 18:00 to 24:00 hrs dispatch 12MW for fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 244.04 | 289 | 661.6 | 591.5 | 266.1 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 140 | 138 | 138 | 140 | 140 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 86 | 86 | 81 | 81 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 243 | 244 | 341 | 341 | 260 | 260 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 276 | 276 | 280 | 280 | 280 | 280 | STG Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 395 | 400 | 383 | 383 | 383 | 383 | ps availability is less
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1367 | 1369 | 1474 | 1474 | 1360 | 1360
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 806 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 25 | 25 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 750 | 750 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2222.2 | 2165.2 | 3577.2 | 3479.2 | 2552 | 2454
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 966 | 1100 | 1000 | 1100 | 934 | 1034 | FGMO
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 73 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 91 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 280 | 280 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2034.64 | 2243 | 2208 | 2307 | 2003 | 2102
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 56.42 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 410 | 410 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 0 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 90 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.54 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 578.5 | 709.47 | 650 | 680 | 500 | 600 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.09 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1316.55 | 1323.67 | 2320.11 | 2131.99 | 1339.12 | 1392
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 154 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 94 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 40 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 164 | 0 | 184.18 | 0 | 184.18 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 434 | 363 | 627.18 | 408 | 537.18 | 397
System Total |  |  |  |  | 28843.2 | 28692.211 | 14495.33 | 15882.85 | 22795.22 | 22323 | 15714.11 | 16594.72
Forecast Scenario (04-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14640 |  | 2664.45 |  | 17430
|  |  |  | 1:00 | 13850 |  | 2922.3 |  | 16910
|  |  |  | 2:00 | 13620 |  | 2721.75 |  | 16470
|  |  |  | 3:00 | 13580 |  | 2483 |  | 16180
|  |  |  | 4:00 | 13530 |  | 2234.7 |  | 15870
|  |  |  | 5:00 | 13420 |  | 2005.5 |  | 15520
|  |  |  | 6:00 | 13250 |  | 1556.65 |  | 14880
|  |  |  | 7:00 | 13470 |  | 1231.95 |  | 14760
|  |  |  | 8:00 | 13480 |  | 1222.4 |  | 14760
|  |  |  | 9:00 | 13500 |  | 1165.1 |  | 14720
|  |  |  | 10:00 | 13440 |  | 1174.65 |  | 14670
|  |  |  | 11:00 | 13800 |  | 1117.35 |  | 14970
|  |  |  | 12:00 | 14500 |  | 1098.25 |  | 15650
|  |  |  | 13:00 | 14920 |  | 1050.5 |  | 16020
|  |  |  | 14:00 | 14960 |  | 1040.95 |  | 16050
|  |  |  | 15:00 | 14720 |  | 1814.5 |  | 16620
|  |  |  | 16:00 | 14430 |  | 1852.7 |  | 16370
|  |  |  | 17:00 | 14670 |  | 1470.7 |  | 16210
|  |  |  | 18:00 | 14920 |  | 1088.7 |  | 16060
|  |  |  | 18:30 | 15070 |  | 1895.675 |  | 17055
|  |  |  | 19:00 | 15190 |  | 2731.3 |  | 18050
|  |  |  | 19:30 | 15430 |  | 2750.4 |  | 18310
|  |  |  | 20:00 | 15540 |  | 2683.55 |  | 18350
|  |  |  | 21:00 | 15570 |  | 2979.6 |  | 18690
|  |  |  | 22:00 | 15180 |  | 2960.5 |  | 18280
|  |  |  | 23:00 | 15150 |  | 2970.05 |  | 18260
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 15650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2980
Probable Maximum Demand at Evening Peak: |  |  | 18690.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15570.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.33 MKWHr. |  | 660 | 250 | 450 | 450 | 170 | 300 | 150 | 300 | 250 | 2980
*** This report is generated digitally from Operation Information System (OIS) at 10:16 hrs on 04-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14495.33 | MW | 12:00 Hr. | Energy Generated |  |  | 347.4019 |  | MKWHr.
| Day Peak Demand |  |  | 14517.33 | MW | 12:00 Hr. | Energy Unserverd |  |  | 27.042 |  | MKWHr.
| Evening Peak Generation |  |  | 15882.85 | MW | 21:00 Hr. | Energy Demand |  |  | 374.4439 |  | MKWHr.
| Evening Peak Demand |  |  | 18230.85 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 13253.93 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 885.97 |  | MMCFD
| Maximum Generation of the Day |  |  | 15882.85 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.9897 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.6869 | 0 | 18.1393 | 0 | 0 | 0.19951 | 0 | 0 | 55.0257 | Gas | 119.715 | Gas | 415220969.9212
| Chattogram Zone |  |  | 5.7953 | 53.7636 | 15.9419 | 0 | 4.9061 | 0.13123 | 0 | 0.01344 | 80.5516 | Coal | 125.5368 | Coal | 904769645.8731
| Cumilla Zone |  |  | 26.6473 | 0 | 7.2538 | 0 | 0 | 0.43637 | 1.6358 | 0 | 35.9733 | HFO | 56.8863 | HFO | 1175465736.154
| Mymensingh Zone |  |  | 0.0384 | 0 | 4.4675 | 0 | 0 | 0.42934 | 0 | 0 | 4.9352 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.7929 | 0 | 0 | 0 | 0 | 0.059196 | 0 | 0 | 32.8521 | Hydro | 4.9061 | Hydro | 490606.7
| Khulna Zone |  |  | 0 | 28.7636 | 1.1574 | 0 | 0 | 0.50616 | 20.1084 | 0 | 50.5355 | Solar | 4.5541 | Solar | 72840150.9584
| Barishal Zone |  |  | 8.1426 | 39.1255 | 3.8074 | 0 | 0 | 0.003952 | 0 | 0 | 51.0795 | Import | 35.7902 | Import | 206667642.18
| Rajshahi Zone |  |  | 9.6115 | 0 | 2.764 | 0 | 0 | 1.4583 | 14.046 | 0 | 27.8798 | Wind | 0.01344 | Wind | 199449.6
| Rangpur Zone |  |  | 0 | 3.884 | 3.3551 | 0 | 0 | 1.33 | 0 | 0 | 8.5691
| Total |  |  | 119.715 | 125.5368 | 56.8863 | 0 | 4.9061 | 4.5541 | 35.7902 | 0.01344 | 347.4019
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 415220969.9212 |  | Hydro | 490606.7
|  |  |  | Coal | 904769645.8731 |  | Solar | 72840150.9584
|  |  |  | HFO | 1175465736.154 |  | Import | 206667642.18
|  |  |  | HSD | 0 |  | Wind | 199449.6
[5 empty] | Total: | 277,56,54,201 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 21745.45 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1084 | Peak Hr Flow | 806.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31142818.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.046 | Peak Hr Flow | 709.47 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1057 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6358 | Peak Hr Flow | 76.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1960 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 35.7902 | Peak Hr Flow | 1591.47 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 540 |  | 6135
|  |  |  | Chattogram |  | 152 |  | 1608
|  |  |  | Cumilla |  | 307 |  | 1779
|  |  |  | Mymensingh |  | 232 |  | 1501
|  |  |  | Sylhet |  | 153 |  | 751
|  |  |  | Khulna |  | 290 |  | 2060
|  |  |  | Barishal |  | 140 |  | 598
|  |  |  | Rajshahi |  | 214 |  | 1775
|  |  |  | Rangpur |  | 219 |  | 1128
|  |  |  | Total |  | 2247 |  | 17335
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116 | 2 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 700 |  |  |  | Total | 197.5
|  |  |  | Total Unavailable Capacity |  |  |  | 897.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 15:35 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to For Annual Maintenance
| 08:20 | 15:35 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to For Annual Maintenance.
|  | 08:29 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 08:31 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 08:46 | 15:54 | Barapukuria-Rangpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
132KV CB maintenance
|  | 09:21 | Joydebpur-Kodda B 132 kV Ckt-2 is restored.
| 09:28 | 10:42 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to 132kV CT connector temperature reduce
work
| 09:28 | 10:42 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to 132kV CT connector temperature reduce
work
| 09:30 | 21:10 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to Project work
(CAF)
| 09:31 | 17:43 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to Project work
(CAF)
|  | 09:52 | Bhaluka-Mymensingh 132 kV Ckt-1 is restored.
|  | 09:52 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
|  | 11:11 | Aminbazar-Manikgonj PP 132kV Ckt-2 is restored.
| 12:00 |  | Day Peak Generation: 14495 MW.
| 12:05 | 14:25 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to Red hot maintenance
| 12:16 | 14:23 | Narshingdi 132/33kV S/S 132 kV Main Bus-1 Scheduled S/D Due to Red hot Maintenance
|  | 12:20 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
| 12:50 | 14:25 | Baghabari-Shahjadpur 132 kV Ckt-2 Forced S/D from Shahjadpur 132/33kV end Due to
Maintenance work
|  | 13:20 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
|  | 13:20 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
| 13:22 |  | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to Reserve
| 16:58 | 17:08 | Pabna 132/33kV S/S T-1 LT Tripped showing E/F, O/C relays Due to Pailanpur & SQUARE 33 KV | [7 empty] | 30.0MW load
|  |  | Feeder trip | [7 empty] | interrup.
| 17:25 | 18:04 | Bogura-Mahasthangarh 132 kV Ckt-1 Tripped from Mahasthangarh 132/33kV end showing No | [7 empty] | 120.0MW load
|  |  | relays Due to Grid power fail. | [7 empty] | interrup.
Mahasthangarh
132/33kV end
| 17:25 | 18:04 | Bogura-Mahasthangarh 132 kV Ckt-2 Tripped from Mahasthangarh 132/33kV end showing No | [7 empty] | 120.0MW load
|  |  | relays Due to Grid power fail. | [7 empty] | interrup.
Mahasthangarh
132/33kV end
| 17:25 | 18:49 | Bogura(New) South-Naogaon 132 kV Ckt-1 Tripped from Naogaon 230/132/33kV end showing | [7 empty] | and 34.0MW load
|  |  | Distance relay main 1 relays Due to Due to wire snapping. and from Bogura 230/132kV end | [7 empty] | interrup. Bogura
|  |  | showing no relays. | [7 empty] | 230/132kV end
| 17:26 |  | Full load interruption occurred under Bogura old, Mohasthangarh, Palashbari, Mithapukur,
Rangpur, Kurigram & Lalmonirhat from 17:26hr to 17:55hr due to tripping of Bogura south
230/132kV T1,T2,T3,T4, Bogura south-Bogura old ckt-1&2 and Barapukuria 230/132kV T1
transformers as Bogura south-Confidence unit-2 132kV ckt. got snapped and fall on the
Bogura south 132kV bus.
| 17:26 | 20:03 | Bogura South-Confidence 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing no relays | [7 empty] | 112.0MW load
|  |  | Due to due to cpbl 2 trip | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 |  | Bogura(New) South-Naogaon 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing no | [7 empty] | 34.0MW load
|  |  | relays. | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 | 00:19 | Bogura 230/132kV S/S 132KV Main 1 Tripped showing no relays Due to cpbl uperbus-2 cable
brused n full in bus
| 17:26 | 17:48 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 73.0MW load
interrup.
| 17:26 | 18:26 | Bogura 230/132kV S/S T-03 LT Tripped showing no relay relays Due to None | [7 empty] | 110.0MW load
interrup.
| 17:26 | 18:16 | Bogura 230/132kV S/S T-01 LT Tripped showing no relays Due to cpbl 2 upper bus conductor | [7 empty] | 82.0MW load
|  |  | out | [7 empty] | interrup.
| 17:26 | 18:22 | Bogura 230/132kV S/S T-02 LT Tripped showing no relays. | [7 empty] | 82.0MW load
interrup.
| 17:26 | 18:26 | Bogura 230/132kV S/S T-04 HT Tripped showing no relays. | [7 empty] | 110.0MW load
interrup.
| 17:26 | 18:19 | Bogura 230/132kV S/S T-04 LT Tripped showing no relays. | [7 empty] | 110.0MW load
interrup.
| 17:26 | 18:20 | Bogura-Bogura(New) South 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing no | [7 empty] | 215.0MW load
|  |  | relays. | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 | 18:24 | Bogura-Bogura(New) South 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing no | [7 empty] | 215.0MW load
|  |  | relays. | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 | 19:04 | Bogura(New) South-Bogura(Sherpur) 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing | [7 empty] | 41.0MW load
|  |  | no relays. | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 | 00:30 | Bogura South-Confidence 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing no relays | [7 empty] | 90.0MW load
|  |  | Due to upper bus cable brused | [7 empty] | interrup. Bogura
230/132kV end
| 17:26 | 18:50 | Bogura(New) South-Bogura(Sherpur) 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing | [7 empty] | 41.0MW load
|  |  | no relays. | [7 empty] | interrup. Bogura
230/132kV end
| 17:28 | 18:00 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing Siemens Siprotec | [7 empty] | 100.0MW load
|  |  | relays Due to Over current | [7 empty] | interrup.
| 17:28 | 17:58 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing Siemens Siprotec | [7 empty] | 100.0MW load
|  |  | relays Due to HV O/C Trip | [7 empty] | interrup.
| 17:30 | 18:37 | Sherpur(Bogura)-Sirajganj 132 kV Ckt-1 Tripped from Sirajganj 132/33kV end showing
QUADRAMHO SHPM- 101 (21) relays.
| 17:32 | 18:02 | Mahasthangar-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing NOT | [7 empty] | 110.0MW load
|  |  | OPERATED relays Due to BLACK OUT | [7 empty] | interrup.
Palashbari 132/33kV
end
| 17:32 | 18:02 | Mahasthangar-Palashbari 132kV Ckt-1 Tripped from Palashbari 132/33kV end showing NOT | [7 empty] | 110.0MW load
|  |  | OPERATED relays. | [7 empty] | interrup.
Palashbari 132/33kV
end
| 01:45 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 03:12 | 03:47 | Chattak-Sunamganj 132 kV Ckt-1 Tripped from Sunamganj 132/33kV end showing REL670(Main 1 | [7 empty] | 8.0MW load
|  |  | Protection-FN1) relays Due to Thunder strom | [7 empty] | interrup. Sunamganj
132/33kV end
| 03:48 |  | Chattak-Sunamganj 132 kV Ckt-2 Forced S/D from Sunamganj 132/33kV end Due to Chattak end
pole discrepancy
| 05:50 |  | Ashuganj (South) 360 MW CCPP ST was synchronized.
| 06:00 |  | Minimum generation is 14045 MW.
| 07:44 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Annual maintenance.
| 07:44 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Annual maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9223200 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1194530 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7482740 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 783000 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 5 | 346560 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 799095 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 799772 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 277200 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 524160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 368160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 5359920 | Machine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2929968 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 952320 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2350080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199512 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 170280 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 360 | 10633636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 450 | 8545955 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2085600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2667.42 | 55025688.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 18 | 166996.8 | Machine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112995 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1059360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 4906067 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5295182 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2332618 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 9 | 359357 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 675799 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 552960 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 500160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 52 | 923520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 212 | 2998364 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 663838 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2113491 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 651480 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1505455 | Machine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 162 | 1938691 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28352724 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 13440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1055 | 25410909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3695.36 | 80551644.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 204 | 4841000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 330 | 8312300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 3658000 | ST Ready
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 860832 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 30 | 898080 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 4148364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 921056 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1823272 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 108 | 2580136 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 580320 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1635840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 313930 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 427580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 1666680 | Machine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 1202040 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1667520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 436373 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1767.2 | 35973323
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 126000 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 38400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 2860800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1492800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 291190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 76800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 37080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 289 | 4935220
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 59196 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 953000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 951696 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3152000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 710784 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1962240 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2402060 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 465504 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 244 | 5932000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 276 | 6672000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9591600 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1369 | 32852080
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 806 | 20108364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 225600 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 316320 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 615456 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 506160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 28763630 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2165.2 | 50535530
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24516363 | FGMO
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 2332608 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2750000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7322181.82 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5392640 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 91 | 1474800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7287000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3952 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2243 | 51079544.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 352000 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 137416 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9611490 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 314176 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 949579 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 522624 | Line trip
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 90 | 840192 | Machine Problem
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 31860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 709.47 | 14046006 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 368357 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 706056 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1323.67 | 27879756
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3884000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 94 | 1076985 | Machine Problem
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32145.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2278097 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 196998 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1100880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 363 | 8569105.12
Eastern Grid Total |  |  |  |  | 16961.086 | 9787.98 | 209337956.25
Western Grid Total |  |  |  |  | 11731.125 | 6094.87 | 138063935.94
National Grid Total |  |  |  |  | 28692.211 | 15882.85 | 347401892.19
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-10-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10389.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4698.2 | MW
i) Dhaka area |  |  | 5595.03 |  | MW | i) Khulna area |  |  |  | 1769.5 | MW
ii) Chattogram area |  |  | 1455.5 |  | MW | ii) Barishal area |  |  |  | 458.4 | MW
iii) Cumilla area |  |  | 1472 |  | MW | iii) Rajshahi area |  |  |  | 1561.3 | MW
iv) Mymensingh area |  |  | 1269 |  | MW | iv) Rangpur area |  |  |  | 909 | MW
v) Sylhet area |  |  | 598 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15087.73 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 12:00 | 72 | Hatirjheel | 77 | 15:00 | 143 | PHP | 11 | 22:00
2 | AKSML | 164 | 14:00 | 73 | Ishurdi | 75 | 23:00 | 144 | Pabna | 109 | 18:30
3 | Aftabnagar | 46 | 13:00 | 74 | Jaldhaka | 69 | 21:00 | 145 | Palashbari | 120 | 03:00
4 | Agargaon | 130 | 13:00 | 75 | Jamalpur | 134 | 00:00 | 146 | Panchagarh | 70 | 18:30
5 | Agrabad | 72 | 16:00 | 76 | Jashore | 131 | 18:30 | 147 | Patiya | 29.6 | 00:00
6 | Amnura | 30 | 13:00 | 77 | Jhenaidah | 90 | 19:30 | 148 | Patnitala | 36 | 21:00
7 | Araihazar | 104 | 07:00 | 78 | Joydebpur | 163 | 16:00 | 149 | Patuakhali | 62.5 | 22:00
8 | Ashuganj | 0 | 00:00 | 79 | Joypurhat | 56 | 21:00 | 150 | Payra | 34 | 21:00
9 | Ashuganj-230 | 102 | 23:00 | 80 | Juldah | 17 | 14:00 | 151 | Postogola | 66 | 23:00
10 | BSRM | 200 | 11:00 | 81 | KSRM | 24 | 16:00 | 152 | Pubail | 51 | 09:00
11 | Bagerhat | 82 | 14:00 | 82 | Kabirpur | 258 | 17:00 | 153 | Purbachal | 31 | 13:00
12 | Bajitpur | 98 | 04:00 | 83 | Kachua | 92 | 19:30 | 154 | Purbasadipur | 124 | 19:00
13 | Bakerganj | 13.4 | 21:00 | 84 | Kaliganj | 39 | 01:00 | 155 | Rahanpur | 38 | 18:30
14 | Bakulia | 100 | 15:00 | 85 | Kallyanpur | 120 | 15:00 | 156 | Rahim | 33 | 22:00
15 | Banani | 58 | 13:00 | 86 | Kalurghat | 39 | 12:00 | 157 | Rajbari | 77 | 00:00
16 | Bangabhaban | 7 | 11:00 | 87 | Kamrangirchar | 83 | 13:00 | 158 | Rajendrapur | 132 | 16:00
17 | Barapukuria | 55 | 23:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 112 | 23:00
18 | Barguna | 22 | 21:00 | 89 | Kasba | 39 | 21:00 | 160 | Rajshahi-230 | 115 | 12:00
19 | Barishal | 95 | 22:00 | 90 | Kazla | 129 | 11:00 | 161 | Ramganj | 96 | 21:00
20 | Barishal-230 | 106 | 13:00 | 91 | Keranigonj | 88 | 17:00 | 162 | Rampur | 46 | 18:00
21 | Baroaulia | 43 | 12:00 | 92 | Khagrachori | 36 | 18:00 | 163 | Rangamati | 19 | 18:00
22 | Baroirhat | 56 | 16:00 | 93 | Khulna | 58 | 18:00 | 164 | Rangpur | 124 | 12:00
23 | Bashundhara | 208 | 13:00 | 94 | Khulshi | 184 | 21:00 | 165 | Ruppur | 3 | 10:00
24 | BashundharaCement | 7 | 22:00 | 95 | Kishoreganj | 134 | 21:00 | 166 | SSM | 11 | 01:00
25 | Beanibazar | 66 | 20:00 | 96 | Kodda | 313 | 19:30 | 167 | Saidpur | 100 | 18:30
26 | Benapole | 70 | 18:30 | 97 | Kulaura | 50 | 20:00 | 168 | Santhia | 34 | 13:00
27 | Bhaluka | 168 | 16:00 | 98 | Kurigram | 59 | 07:00 | 169 | Satkhira | 144 | 20:00
28 | Bhandaria | 52 | 22:00 | 99 | Kushtia | 134 | 07:00 | 170 | Satmasjid | 109 | 18:30
29 | Bhangura | 33 | 07:00 | 100 | Laksam | 36 | 01:00 | 171 | Savar | 218 | 16:00
30 | Bheramara(GK) | 60 | 22:00 | 101 | Lakshmipur | 56 | 18:30 | 172 | SevenRings | 17.62 | 09:00
31 | Bhulta | 198 | 08:00 | 102 | Lalbag | 82 | 13:00 | 173 | ShahCement | 18 | 00:00
32 | Bog-Sherpur | 70 | 21:00 | 103 | Lalmonirhat | 54 | 21:00 | 174 | Shahjadpur | 85 | 19:00
33 | Bogura | 219 | 23:00 | 104 | MI_Cement | 16.4 | 12:00 | 175 | Shahjibazar | 125 | 20:00
34 | Borhanuddin | 68 | 17:00 | 105 | Madanganj | 45 | 22:00 | 176 | Shahmirpur | 55 | 01:00
35 | Brahmanbaria | 134 | 23:00 | 106 | Madaripur | 92 | 20:00 | 177 | Shariatpur | 89 | 21:00
36 | Cantonment | 136 | 13:00 | 107 | Madartek | 92 | 23:00 | 178 | Sherpur | 158 | 20:00
37 | Chandina | 19 | 18:30 | 108 | Madunaghat | 69 | 22:00 | 179 | Shikalbaha | 19 | 18:00
38 | Chandpur | 80 | 20:00 | 109 | Magura | 63 | 21:00 | 180 | Shitalakhya | 83.7 | 16:00
39 | Chandraghona | 30 | 18:00 | 110 | Mahasthangarh | 75 | 23:00 | 181 | Sholosohor | 49 | 18:00
40 | Chapai | 78 | 23:00 | 111 | Maijdee | 38 | 14:00 | 182 | Shomvuganj | 52 | 22:00
41 | Charfasson | 30 | 18:00 | 112 | Manikganj | 124 | 05:00 | 183 | Shyampur | 152 | 11:00
42 | Charsaidpur | 30 | 00:00 | 113 | Maniknagar | 66 | 23:00 | 184 | Siddhirganj | 138 | 15:00
43 | Chauddagram | 67 | 00:00 | 114 | Matarbari | 64 | 18:00 | 185 | Sirajganj | 124 | 19:00
44 | Chhatak | 34 | 17:00 | 115 | Matuail | 78 | 12:00 | 186 | Sitakunda | 37 | 18:00
45 | Chowmuhani | 160 | 18:00 | 116 | Metrorail_Motijheel | 23 | 19:30 | 187 | Sonargaon | 117 | 17:00
46 | Chuadanga | 118 | 22:00 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreemongol | 70 | 17:00
47 | Coxsbazar | 136 | 16:00 | 118 | Millgate | 100 | 15:00 | 189 | Sreepur | 127 | 13:00
48 | Cumilla(N) | 157 | 18:00 | 119 | Mirpur | 164 | 18:00 | 190 | Srinagar | 45 | 02:00
49 | Cumilla(S) | 164 | 22:00 | 120 | Mirsorai | 49 | 08:00 | 191 | Sunamganj | 54 | 14:00
50 | Daganbhuiyan | 38 | 22:00 | 121 | Mirzapur | 49 | 13:00 | 192 | Sylhet | 131 | 14:00
51 | Daudkandi | 136 | 00:00 | 122 | Mithapukur | 74 | 19:30 | 193 | Sylhet_(South) | 57 | 18:00
52 | DhakaUniversity | 88 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 94 | 10:00 | 124 | Mogbazar | 70.9 | 23:00 | 195 | Tangail | 186 | 23:00
54 | Dhanmondi | 115 | 13:00 | 125 | Mongla | 40 | 18:30 | 196 | Taraganj | 30 | 12:00
55 | Dohazari | 104 | 19:00 | 126 | Monirampur | 25 | 01:00 | 197 | Tasnim | 45 | 17:00
56 | Faridpur | 189 | 21:00 | 127 | Motijheel | 52 | 13:00 | 198 | Thakurgaon | 108 | 18:30
57 | Fatullah | 129 | 15:00 | 128 | Muktagacha | 46 | 18:30 | 199 | Tongi | 186 | 17:00
58 | Fenchuganj | 43 | 21:00 | 129 | Munshiganj | 111 | 16:00 | 200 | Ullahpara | 39 | 21:00
59 | Feni | 110 | 22:00 | 130 | Muradnagar | 48 | 00:00 | 201 | Ullon | 48 | 00:00
60 | GPH | 15 | 01:00 | 131 | Mymensingh | 160 | 22:00 | 202 | Uttara | 102 | 18:30
61 | Ghatail | 103 | 00:00 | 132 | Nabinagar | 116 | 12:00 | 203 | UttaraNew | 59 | 23:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 113 | 22:00 | 204 | Zigatola | 94 | 13:00
63 | Ghorashal-230 | 92 | 22:00 | 134 | Narail | 60 | 19:30
64 | Goalpara | 42 | 22:00 | 135 | Narinda | 77 | 13:00
65 | Gollamari | 102 | 21:00 | 136 | Narshingdi | 178 | 20:00
66 | Gopalganj | 99 | 07:00 | 137 | Natore | 146 | 18:00
67 | Gulshan | 108 | 13:00 | 138 | Nawabganj | 46.5 | 04:00
68 | Halishahar | 103.5 | 14:00 | 139 | Netrakona | 136 | 17:00
69 | HaripurSBU | 121 | 04:00 | 140 | New | 66.4 | 18:00
70 | Hasnabad | 99 | 13:00 | 141 | Niamatpur | 66 | 19:00
71 | Hathazari | 82 | 19:00 | 142 | Noapara | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14643.68 | 1426 |  | 16133.85
1:00 | 13845.36 | 2136 |  | 16077.36
2:00 | 13619.07 | 2083 |  | 15796.07
3:00 | 13580.05 | 2017 |  | 15688.05
4:00 | 13529.91 | 1752 |  | 15360.91
5:00 | 13424.83 | 1411 |  | 14898.83
6:00 | 13253.93 | 785 |  | 14073.93
7:00 | 13472.03 | 361 |  | 13849.03
8:00 | 13477.33 | 347 |  | 13840.33
9:00 | 13504.66 | 255 |  | 13770.66
10:00 | 13443.46 | 150 |  | 13600.46
11:00 | 13804.94 | 0 |  | 13804.94
12:00 | 14495.33 | 21 |  | 14517.33
13:00 | 14915.3 | 23 |  | 14939.3
14:00 | 14964.64 | 194 |  | 15167.64
15:00 | 14723.02 | 1116 |  | 15889.02
16:00 | 14433.61 | 727 |  | 15193.61
17:00 | 14673.45 | 698 |  | 15402.86
18:00 | 14920.98 | 1634 |  | 16628.98
19:00 | 15215.96 | 2017 |  | 17323.96
19:30 | 15689.33 | 1876 |  | 17649.33
20:00 | 15615.68 | 1837 |  | 17535.68
21:00 | 15882.85 | 2247 |  | 18230.85
22:00 | 15772.73 | 1768 |  | 17620.73
23:00 | 15636.05 | 2037 |  | 17765.05
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8920.5 | 5723.18 | 14643.68 | DAILY GENERATION CURVE
00:30 | 8659.5 | 5585.02 | 14244.52
01:00 | 8398.5 | 5446.86 | 13845.36 | 03-10-2026
01:30 | 8259 | 5473.215 | 13732.215
02:00 | 8119.5 | 5499.57 | 13619.07
02:30 | 8099.65 | 5499.91 | 13599.56
03:00 | 8079.8 | 5500.25 | 13580.05
03:30 | 8086.8 | 5468.18 | 13554.98
04:00 | 8093.8 | 5436.11 | 13529.91
04:30 | 8011.3 | 5466.07 | 13477.37
05:00 | 7928.8 | 5496.03 | 13424.83
05:30 | 7938.375 | 5401.005 | 13339.38
06:00 | 7947.95 | 5305.98 | 13253.93
06:30 | 8000.4 | 5362.58 | 13362.98
07:00 | 8052.85 | 5419.18 | 13472.03
07:30 | 8014.07 | 5460.61 | 13474.68
08:00 | 7975.29 | 5502.04 | 13477.33
08:30 | 7968.295 | 5522.7 | 13490.995
09:00 | 7961.3 | 5543.36 | 13504.66
09:30 | 7897.315 | 5576.745 | 13474.06
10:00 | 7833.33 | 5610.13 | 13443.46
10:30 | 7950.89 | 5673.31 | 13624.2
11:00 | 8068.45 | 5736.49 | 13804.94
11:30 | 8278.195 | 5871.94 | 14150.135
12:00 | 8487.94 | 6007.39 | 14495.33
12:30 | 8642.28 | 6063.035 | 14705.315
13:00 | 8796.62 | 6118.68 | 14915.3
13:30 | 8847 | 6092.97 | 14939.97
14:00 | 8897.38 | 6067.26 | 14964.64
14:30 | 8841.13 | 6002.7 | 14843.83
15:00 | 8784.88 | 5938.14 | 14723.02
15:30 | 8677.165 | 5901.15 | 14578.315
16:00 | 8569.45 | 5864.16 | 14433.61
16:30 | 8735.79 | 5817.74 | 14553.53
17:00 | 8902.13 | 5771.32 | 14673.45
17:30 | 9065.025 | 5732.19 | 14797.215
18:00 | 9227.92 | 5693.06 | 14920.98
18:30 | 9353 | 5715.47 | 15068.47
19:00 | 9478.08 | 5737.88 | 15215.96
19:30 | 9924.08 | 5765.25 | 15689.33
20:00 | 9801.48 | 5814.2 | 15615.68
20:30 | 9794.73 | 5954.535 | 15749.265 |  | Executive Engineer
21:00 | 9787.98 | 6094.87 | 15882.85 |  | Network Operation Division
21:30 | 9740.95 | 6086.84 | 15827.79
22:00 | 9693.92 | 6078.81 | 15772.73
22:30 | 9673.42 | 6030.97 | 15704.39
23:00 | 9652.92 | 5983.13 | 15636.05

## En-Curve
QF-LDC-12
Date | 03-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3137 | 1794.5 | 809 | 0 | 66 | 593.98 | 220 | 5120 | 0 | 281 | 2622.2 | 0 | 0 | 0 | 1426 | DAILY ENERGY CURVE
00:30 | 3161 | 1768.5 | 809.5 | 0 | 65 | 555.82 | 220.5 | 5122 | 0 | 246 | 2296.2 | 0 | 0 | 0 | 1781 | 03-10-2026
01:00 | 3185 | 1742.5 | 810 | 0 | 64 | 517.66 | 221 | 5124 | 0 | 211 | 1970.2 | 0 | 0 | 0 | 2136
01:30 | 3154 | 1704 | 858 | 0 | 63 | 513.515 | 221 | 5120 | 0 | 206 | 1892.7 | 0 | 0 | 0 | 2109.5 | Energy Generated | 347.4019 |  | MKWHr
02:00 | 3123 | 1665.5 | 906 | 0 | 62 | 509.37 | 221 | 5116 | 0 | 201 | 1815.2 | 0 | 0 | 0 | 2083 | Energy not Served | 27.042 |  | MKWHr
02:30 | 3110 | 1652.65 | 906 | 0 | 61 | 508.71 | 221.5 | 5116.5 | 0 | 201 | 1822.2 | 0 | 0 | 0 | 2050 | Total Energy Requirement | 374.4439 |  | MKWHr
03:00 | 3097 | 1639.8 | 906 | 0 | 60 | 508.05 | 222 | 5117 | 0 | 201 | 1829.2 | 0 | 0 | 0 | 2017
03:30 | 3109 | 1659.3 | 902.5 | 0 | 60 | 510.48 | 222 | 5086 | 0 | 201 | 1804.7 | 0 | 0 | 0 | 1884.5
04:00 | 3121 | 1678.8 | 899 | 0 | 60 | 512.91 | 222 | 5055 | 0 | 201 | 1780.2 | 0 | 0 | 0 | 1752
04:30 | 3107.5 | 1661.8 | 899 | 0 | 60 | 513.37 | 221 | 5074.5 | 0 | 201 | 1739.2 | 0 | 0 | 0 | 1581.5
05:00 | 3094 | 1644.8 | 899 | 0 | 60 | 513.83 | 220 | 5094 | 0 | 201 | 1698.2 | 0 | 0 | 0 | 1411
05:30 | 3044 | 1634.8 | 899.5 | 0 | 59 | 514.06 | 219.5 | 5088 | 0.32 | 189 | 1691.2 | 0 | 0 | 0 | 1098
06:00 | 2994 | 1624.8 | 900 | 0 | 58 | 514.29 | 219 | 5082 | 0.64 | 177 | 1684.2 | 0 | 0 | 0 | 785
06:30 | 3064 | 1668.4 | 852.5 | 0 | 57 | 513.075 | 218.5 | 5101.5 | 46.305 | 166 | 1675.7 | 0 | 0 | 0 | 573
07:00 | 3134 | 1712 | 805 | 0 | 56 | 511.86 | 218 | 5121 | 91.97 | 155 | 1667.2 | 0 | 0 | 0 | 361
07:30 | 3128 | 1679 | 805 | 0 | 58 | 531.835 | 218 | 5126.5 | 180.245 | 154 | 1594.1 | 0 | 0 | 0 | 354
08:00 | 3122 | 1646 | 805 | 0 | 60 | 551.81 | 218 | 5132 | 268.52 | 153 | 1521 | 0 | 0 | 0 | 347
08:30 | 3176 | 1687.75 | 852.5 | 0 | 62 | 552.54 | 218.5 | 5120.5 | 362.705 | 127.5 | 1331 | 0 | 0 | 0 | 301
09:00 | 3230 | 1729.5 | 900 | 0 | 64 | 553.27 | 219 | 5109 | 456.89 | 102 | 1141 | 0 | 0 | 0 | 255
09:30 | 3278.5 | 1711 | 899.5 | 0 | 65 | 558.91 | 219.5 | 5062 | 529.65 | 140 | 1010 | 0 | 0 | 0 | 202.5
10:00 | 3327 | 1692.5 | 899 | 0 | 66 | 564.55 | 220 | 5015 | 602.41 | 178 | 879 | 0 | 0 | 0 | 150
10:30 | 3353 | 1750.5 | 899.5 | 0 | 68 | 569.065 | 220 | 5074.5 | 607.135 | 187 | 895.5 | 0 | 0 | 0 | 75
11:00 | 3379 | 1808.5 | 900 | 0 | 70 | 573.58 | 220 | 5134 | 611.86 | 196 | 912 | 0 | 0 | 0 | 0
11:30 | 3372 | 1784.5 | 901 | 0 | 74 | 576.04 | 220.5 | 5167.1 | 645.995 | 205 | 1203 | 0 | 0 | 1 | 10.5
12:00 | 3365 | 1760.5 | 902 | 0 | 78 | 578.5 | 221 | 5200.2 | 680.13 | 214 | 1494 | 0 | 0 | 2 | 21
12:30 | 3350 | 1702.5 | 901.5 | 0 | 77 | 572.48 | 221 | 5206.7 | 682.135 | 188.5 | 1799.5 | 0 | 0 | 4 | 22
13:00 | 3335 | 1644.5 | 901 | 0 | 76 | 566.46 | 221 | 5213.2 | 684.14 | 163 | 2105 | 0 | 0 | 6 | 23
13:30 | 3353.5 | 1639 | 901.5 | 0 | 77 | 572.165 | 221 | 5198.7 | 615.605 | 163 | 2193.5 | 0 | 0 | 5 | 108.5
14:00 | 3372 | 1633.5 | 902 | 0 | 78 | 577.87 | 221 | 5184.2 | 547.07 | 163 | 2282 | 0 | 0 | 4 | 194
14:30 | 3375 | 1595 | 901.5 | 0 | 78 | 572.93 | 170.5 | 5225.2 | 463.7 | 163 | 2296 | 0 | 0 | 3 | 655
15:00 | 3378 | 1556.5 | 901 | 0 | 78 | 567.99 | 120 | 5266.2 | 380.33 | 163 | 2310 | 0 | 0 | 2 | 1116
15:30 | 3359 | 1508 | 901 | 0 | 74 | 567.89 | 121 | 5274.7 | 293.725 | 163 | 2315 | 0 | 0 | 1 | 921.5
16:00 | 3340 | 1459.5 | 901 | 0 | 70 | 567.79 | 122 | 5283.2 | 207.12 | 163 | 2320 | 0 | 0 | 0 | 727
16:30 | 3334.5 | 1518.5 | 844 | 0 | 68 | 564.73 | 101 | 5282.7 | 130.89 | 214.71 | 2494.5 | 0 | 0 | 0 | 712.5
17:00 | 3329 | 1577.5 | 787 | 0 | 66 | 561.67 | 80 | 5282.2 | 54.66 | 266.42 | 2669 | 0 | 0 | 0 | 698
17:30 | 3343 | 1563 | 734.5 | 0 | 73 | 612.165 | 150 | 5299.2 | 27.33 | 357.42 | 2637.6 | 0 | 0 | 0 | 1166
18:00 | 3357 | 1548.5 | 682 | 0 | 80 | 662.66 | 220 | 5316.2 | 0 | 448.42 | 2606.2 | 0 | 0 | 0 | 1634
18:30 | 3346 | 1551.15 | 635 | 0 | 72 | 708.07 | 220 | 5349.2 | 0 | 479.92 | 2707.13 | 0 | 0 | 0 | 1825.5
19:00 | 3335 | 1553.8 | 588 | 0 | 64 | 753.48 | 220 | 5382.2 | 0 | 511.42 | 2808.06 | 0 | 0 | 0 | 2017
19:30 | 3434 | 1799.8 | 588 | 0 | 78 | 748.85 | 220 | 5378.2 | 0 | 526.42 | 2916.06 | 0 | 0 | 0 | 1876
20:00 | 3413 | 1690.2 | 588 | 0 | 78 | 737.8 | 220 | 5377.2 | 0 | 527.42 | 2984.06 | 0 | 0 | 0 | 1837
20:30 | 3403.5 | 1691.6 | 697 | 0 | 77 | 723.635 | 220.5 | 5375.7 | 0 | 528.42 | 3031.91 | 0 | 0 | 0 | 2042
21:00 | 3394 | 1693 | 806 | 0 | 76 | 709.47 | 221 | 5374.2 | 0 | 529.42 | 3079.76 | 0 | 0 | 0 | 2247
21:30 | 3412 | 1724.4 | 806 | 0 | 78 | 699.94 | 221.5 | 5374.7 | 0 | 461.92 | 3049.33 | 0 | 0 | 0 | 2007.5
22:00 | 3430 | 1755.8 | 806 | 0 | 80 | 690.41 | 222 | 5375.2 | 0 | 394.42 | 3018.9 | 0 | 0 | 0 | 1768
22:30 | 3413 | 1770.3 | 806.5 | 0 | 82 | 692.57 | 222 | 5325.2 | 0 | 394.42 | 2998.4 | 0 | 0 | 0 | 1902.5
23:00 | 3396 | 1784.8 | 807 | 0 | 84 | 694.73 | 222 | 5275.2 | 0 | 394.42 | 2977.9 | 0 | 0 | 0 | 2037
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 03-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 28 | 17 | 186 | 178 | 878 | 430 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 16 | 14 | 146 | 168 | 900 | 410
2:00 | 38 | 6 | 178 | 164 | 974 | 418 |  | Import | 0
3:00 | 37 | 6 | 180 | 158 | 978 | 404
4:00 | 39 | 6 | 198 | 168 | 942 | 418 | Ishurdi-Ghorashal Ckt-2 | Export | 1513818.18
5:00 | 40 | 9 | 204 | 170 | 968 | 424
6:00 | 49 | 13 | 116 | 128 | 996 | 436 |  | Import | 21745.45
7:00 | 28 | 20 | 92 | 138 | 938 | 438
8:00 | 56 | 27 | 148 | 148 | 1110 | 498 | Sirajganj-Sreepur Ckt-1 | Export | 1157000
9:00 | 111 | 40 | 226 | 140 | 1310 | 564
10:00 | 135 | 43 | 278 | 128 | 1350 | 364 |  | Import | 0
11:00 | 142 | 48 | 336 | 186 | 1482 | 652
12:00 | 138 | 52 | 342 | 224 | 1434 | 712 | Sirajganj-Sreepur Ckt-2 | Export | 1162000
13:00 | 117 | 44 | 302 | 206 | 1316 | 696
14:00 | 111 | 31 | 340 | 210 | 1400 | 664 |  | Import | 0
15:00 | 103 | 35 | 288 | 182 | 1340 | 638
16:00 | 119 | 51 | 310 | 202 | 1434 | 718 | Gopalganj-Aminbazar Ckt-1 | Export | 13770000
17:00 | 89 | 53 | 222 | 184 | 1350 | 640
18:00 | 68 | 34 | 290 | 172 | 1368 | 608 |  | Import | 0
18:30 | 9 | 25 | 136 | 146 | 1088 | 508
19:00 | 6 | 33 | 48 | 134 | 1020 | 508 | Gopalganj-Aminbazar Ckt-2 | Export | 13540000
19:30 | -15 | 22 | 22 | 152 | 884 | 466
20:00 | -19 | 19 | 26 | 160 | 890 | 452 |  | Import | 0
21:00 | 13 | -2 | 84 | 160 | 960 | 444
22:00 | 26 | 7 | 78 | 146 | 980 | 450 |  | Total Export | 31142818.18
23:00 | 41 | 17 | 120 | 164 | 1058 | 508 |  | Total Import | 21745.45
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 06:00 | 359 | 12:00 | Madunaghat | 399 | 00:00 | 393 | 11:00
Amtali | 412 | 04:00 | 407 | 22:00 | Meghnaghat | 388 | 06:00 | 370 | 13:00
Ashuganj | 395 | 6:00 | 371 | 13:00 | Mirsorai | 398 | 01:00 | 389 | 11:00
Bhulta | 387 | 02:00 | 363 | 12:00 | Payra | 415 | 05:00 | 409 | 12:00
Bibiana | 385 | 01:00 | 376 | 13:00 | Rahanpur | 410 | 18:00 | 393 | 19:30
BIPTC | 402 | 19:30 | 391 | 16:00 | Rampal | 396 | 05:00 | 385 | 13:00
Bogura | 405 | 18:00 | 377 | 21:00
Gopalganj | 392 | 06:00 | 381 | 12:00
Kaliakoir | 374 | 01:00 | 336 | 22:00
Korerhat | 397 | 01:00 | 387 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 04:00 | 215 | 13:00 | Hasnabad | 227 | 05:00 | 209 | 13:00
AKSML | 235 | 01:00 | 228 | 11:00 | Hathazari | 236 | 00:00 | 229 | 10:00
Aminbazar | 232 | 06:00 | 216 | 12:00 | Ishurdi | 234 | 17:00 | 219 | 21:00
Ashuganj | 225 | 05:00 | 215 | 12:00 | Jhenaidah | 225 | 06:00 | 208 | 21:00
Ashuganj-400 | 225 | 05:00 | 215 | 12:00 | Kachua | 227 | 07:00 | 219 | 13:00
Baghabari | 231 | 05:00 | 222 | 21:00 | Kaliakoir | 232 | 01:00 | 215 | 12:00
Barapukuria | 236 | 18:00 | 220 | 19:00 | Keranigonj | 228 | 06:00 | 212 | 12:00
Barapukuria-230 | 236 | 18:00 | 220 | 19:00 | Khulna(S) | 226 | 10:00 | 215 | 21:00
Barapukuria(N) | 235 | 18:00 | 220 | 19:30 | Korerhat | 226 | 01:00 | 219 | 13:00
Barishal | 226 | 01:00 | 222 | 11:00 | Madunaghat | 238 | 00:00 | 232 | 10:00
Bheramara | 233 | 18:00 | 217 | 21:00 | Madunaghat-400 | 240 | 00:00 | 234 | 11:00
Bhulta | 223 | 03:00 | 207 | 12:00 | Maniknagar | 221 | 02:00 | 205 | 12:00
Bibiana | 220 | 06:00 | 212 | 13:00 | Meghnaghat | 231 | 05:00 | 214 | 13:00
BIPTC | 234 | 08:00 | 218 | 21:00 | Meghnaghat-400 | 225 | 06:00 | 211 | 13:00
Birulia | 232 | 06:00 | 215 | 13:00 | Mirsorai | 231 | 01:00 | 225 | 11:00
Bogura | 244 | 18:00 | 227 | 19:30 | Naogaon | 225 | 17:00 | 199 | 18:00
Bogura-400 | 245 | 18:00 | 227 | 19:30 | Purbasadipur | 229 | 18:00 | 217 | 19:30
Borhanuddin | 228 | 02:00 | 226 | 04:00 | Rajshahi | 232 | 17:00 | 215 | 21:00
BSRM | 226 | 00:00 | 220 | 13:00 | Rampal | 225 | 06:00 | 215 | 21:00
Charfasson | 232 | 06:00 | 226 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 00:00 | 219 | 11:00 | Rampura | 222 | 03:00 | 204 | 13:00
Cumilla(N) | 220 | 02:00 | 211 | 12:00 | Shikalbaha | 239 | 18:30 | 231 | 10:00
Faridpur | 221 | 02:00 | 215 | 21:00 | Shyampur | 225 | 01:00 | 209 | 13:00
Fenchuganj | 220 | 06:00 | 213 | 13:00 | Siddhirganj | 224 | 03:00 | 208 | 12:00
Feni | 224 | 01:00 | 216 | 13:00 | Sirajgonj | 236 | 05:00 | 227 | 21:00
Ghorashal | 230 | 00:00 | 215 | 16:00 | Sreepur | 222 | 06:00 | 211 | 12:00
Ghorashal-230 | 223 | 01:00 | 202 | 12:00 | Tongi | 227 | 04:00 | 205 | 11:00
Gopalganj | 223 | 06:00 | 217 | 12:00
GPH | 234 | 01:00 | 227 | 11:00
Haripur | 223 | 06:00 | 207 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 124 | 13:00 | Madanganj | 134 | 05:00 | 125 | 12:00
Agargaon | 139 | 02:00 | 127 | 13:00 | Madaripur | 130 | 01:00 | 128 | 12:00
Agrabad | 138 | 00:00 | 131 | 10:00 | Madartek | 137 | 06:00 | 124 | 13:00
AKS | 135 | 00:00 | 130 | 10:00 | Madunaghat | 138 | 00:00 | 134 | 10:00
Aminbazar | 133 | 06:00 | 123 | 12:00 | Magura | 134 | 07:00 | 123 | 21:00
Amnura | 132 | 00:00 | 124 | 21:00 | Mahasthangarh | 137 | 18:30 | 127 | 19:30
Araihazar | 128 | 03:00 | 117 | 12:00 | Maijdee | 127 | 01:00 | 123 | 13:00
Ashuganj | 132 | 10:00 | 126 | 12:00 | Manikganj | 130 | 02:00 | 122 | 12:00
Ashuganj-230 | 135 | 00:00 | 130 | 12:00 | Maniknagar | 138 | 05:00 | 124 | 13:00
Bagerhat | 127 | 17:00 | 119 | 22:00 | Matarbari | 128 | 01:00 | 114 | 18:00
Bajitpur | 128 | 05:00 | 119 | 09:00 | Matuail | 134 | 05:00 | 124 | 12:00
Bakerganj | 133 | 00:00 | 130 | 11:00 | Metrorail_Motijheel | 138 | 05:00 | 124 | 13:00
Bakulia | 137 | 18:30 | 132 | 10:00 | Metrorail_Uttara | 135 | 01:00 | 119 | 12:00
Banani | 137 | 04:00 | 123 | 13:00 | Millgate | 137 | 03:00 | 120 | 12:00
Bangabhaban | 139 | 06:00 | 125 | 13:00 | Mirpur | 132 | 02:00 | 122 | 13:00
Barapukuria | 141 | 18:00 | 128 | 19:00 | Mirzapur | 131 | 01:00 | 122 | 12:00
Barguna | 132 | 03:00 | 129 | 11:00 | Mithapukur | 137 | 18:30 | 123 | 19:30
Barishal | 132 | 01:00 | 129 | 10:00 | MI_Cement | 133.6 | 03:00 | 119.4 | 13:00
Barishal-230 | 132 | 01:00 | 128 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 138 | 00:00 | 132 | 11:00 | Mogbazar | 138 | 05:00 | 123 | 12:00
Baroirhat | 131 | 01:00 | 127 | 12:00 | Mongla | 127 | 17:00 | 119 | 21:00
Bashundhara | 136 | 01:00 | 119 | 12:00 | Monirampur | 126 | 17:00 | 112 | 21:00
BashundharaCement | 134 | 05:00 | 125 | 11:00 | Motijheel | 139 | 06:00 | 125 | 13:00
Beanibazar | 123 | 06:00 | 117 | 14:00 | Muktagacha | 130 | 18:30 | 118 | 13:00
Benapole | 134 | 06:00 | 114 | 22:00 | Munshiganj | 134 | 04:00 | 123 | 12:00
Bhaluka | 133 | 06:00 | 120 | 12:00 | Muradnagar | 125 | 01:00 | 118 | 13:00
Bhandaria | 129 | 17:00 | 125 | 19:30 | Mymensingh | 130 | 18:30 | 106 | 09:00
Bhangura | 133 | 17:00 | 126 | 21:00 | Nabinagar | 135 | 03:00 | 118 | 12:00
Bheramara | 137 | 17:00 | 128 | 21:00 | Naogaon | 135 | 06:00 | 120 | 18:00
Bheramara(GK) | 137 | 17:00 | 127 | 21:00 | Narail | 133 | 04:00 | 121 | 21:00
Bhulta | 125 | 00:00 | 119 | 12:00 | Narinda |  | 05:00 | 124 | 13:00
Bhulta-400 | 128 | 00:00 | 119 | 12:00 | Narshingdi | 132 | 00:00 | 115 | 13:00
Birulia | 136 | 06:00 | 126 | 13:00 | Natore | 135 | 17:00 | 126 | 21:00
Bog-Sherpur | 136 | 17:00 | 120 | 18:30 | Nawabganj | 137 | 02:00 | 126 | 13:00
Bogura | 137 | 17:00 | 126 | 18:00 | Netrakona | 122 | 10:00 | 101 | 09:00
Bogura-230 | 144 | 18:00 | 130 | 19:30 | New | 136 | 02:00 | 122 | 12:00
Brahmanbaria | 129 | 04:00 | 124 | 12:00 | Niamatpur | 134 | 05:00 | 127 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 138 | 02:00 | 128 | 12:00 | Noapara | 128 | 06:00 | 120 | 21:00
Chandina | 129 | 06:00 | 122 | 13:00 | Pabna | 133 | 06:00 | 125 | 21:00
Chandpur | 131 | 18:30 | 127 | 10:00 | Palashbari | 136 | 18:30 | 122 | 19:30
Chandraghona | 138 | 04:00 | 134 | 11:00 | Panchagarh | 139 | 06:00 | 129 | 09:00
Chapai | 133 | 17:00 | 127 | 22:00 | Patiya | 137 | 00:00 | 129 | 11:00
Charsaidpur | 134 | 05:00 | 123 | 13:00 | Patnitala | 133 | 06:00 | 125 | 18:00
Chauddagram | 128 | 01:00 | 123 | 12:00 | Patuakhali | 132 | 01:00 | 129 | 11:00
Chhatak | 120 | 00:00 | 113 | 14:00 | Payra | 135 | 00:00 | 134 | 10:00
Chowmuhani | 127 | 00:00 | 124 | 16:00 | PHP | 131 | 01:00 | 127 | 12:00
Chuadanga | 133 | 17:00 | 120 | 21:00 | Postogola | 135 | 04:00 | 124 | 12:00
Coxsbazar | 124 | 06:00 | 120 | 19:00 | Pubail | 133 | 04:00 | 120 | 12:00
Cumilla(N) | 128 | 02:00 | 122 | 12:00 | Purbachal | 137 | 02:00 | 124 | 12:00
Cumilla(S) | 133 | 04:00 | 122 | 12:00 | Purbasadipur | 138 | 16:00 | 131 | 19:30
Daganbhuiyan | 129 | 01:00 | 125 | 12:00 | Rahanpur | 136 | 04:00 | 130 | 21:00
Daudkandi | 127 | 05:00 | 116 | 13:00 | Rahanpur-400 | 136 | 06:00 | 131 | 19:30
DhakaUniversity | 137 | 02:00 | 124 | 13:00 | Rahim | 134 | 04:00 | 123 | 13:00
Dhamrai | 135 | 05:00 | 120 | 12:00 | Rajbari | 126 | 04:00 | 122 | 12:00
Dhanmondi | 137 | 04:00 | 124 | 12:00 | Rajendrapur | 133 | 06:00 | 125 | 12:00
Dohazari | 133 | 00:00 | 125 | 11:00 | Rajshahi | 132 | 17:00 | 124 | 21:00
Faridpur | 127 | 02:00 | 125 | 12:00 | Rajshahi-230 | 133 | 08:00 | 123 | 22:00
Fatullah | 134 | 01:00 | 121 | 13:00 | Ramganj | 127 | 19:00 | 122 | 13:00
Fenchuganj | 129 | 01:00 | 126 | 13:00 | Rampur | 138 | 00:00 | 130 | 11:00
Feni | 130 | 00:00 | 124 | 12:00 | Rampura | 137 | 06:00 | 124 | 13:00
Feni-230 | 130 | 01:00 | 125 | 12:00 | Rangamati | 137 | 03:00 | 133 | 16:00
Ghatail | 128 | 18:30 | 116 | 12:00 | Rangpur | 142 | 18:00 | 123 | 19:00
Ghorashal | 134 | 01:00 | 123 | 13:00 | Ruppur | 136 | 03:00 | 127 | 21:00
Goalpara | 131 | 17:00 | 122 | 22:00 | Saidpur | 139 | 18:00 | 130 | 19:30
Gollamari | 130 | 06:00 | 123 | 21:00 | Santhia | 134 | 06:00 | 126 | 21:00
Gopalganj | 131 | 17:00 | 124 | 12:00 | Satkhira | 125 | 10:00 | 112 | 22:00
Gopalganj-400 | 131 | 01:00 | 127 | 12:00 | Satmasjid | 139 | 04:00 | 127 | 13:00
Gulshan | 136 | 02:00 | 123 | 13:00 | Savar | 132 | 00:00 | 123 | 12:00
Halishahar | 139 | 00:00 | 130 | 11:00 | SevenRings | 134 | 02:00 | 123 | 12:00
Haripur | 134 | 02:00 | 124 | 13:00 | ShahCement | 134 | 06:00 | 123 | 13:00
HaripurSBU | 134 | 02:00 | 125 | 14:00 | Shahjadpur | 129 | 04:00 | 125 | 22:00
Hasnabad | 134 | 00:00 | 124 | 12:00 | Shahjibazar | 129 | 10:00 | 124 | 13:00
Hathazari | 138 | 00:00 | 133 | 10:00 | Shahmirpur | 138 | 00:00 | 133 | 10:00
Hatirjheel | 137 | 03:00 | 124 | 13:00 | Shariatpur | 129 | 05:00 | 125 | 12:00
Ishurdi | 137 | 17:00 | 128 | 21:00 | Sherpur | 133 | 18:30 | 116 | 03:00
Jaldhaka | 136 | 18:00 | 126 | 19:30 | Shikalbaha | 128 | 05:00 | 121 | 11:00
Jamalpur | 135 | 18:30 | 119 | 02:00 | Shikalbaha-230 | 138 | 03:00 | 133 | 10:00
Jashore | 136 | 06:00 | 116 | 22:00 | Shitalakhya | 133.6 | 03:00 | 119.4 | 13:00
Jhenaidah | 137 | 05:00 | 125 | 22:00 | Sholosohor | 138 | 00:00 | 131 | 11:00
Jhenaidah-230 | 139 | 09:00 | 125 | 21:00 | Shomvuganj | 123 | 18:30 | 110 | 09:00
Joydebpur | 132 | 18:30 | 113 | 14:00 | Shyampur | 132 | 00:00 | 124 | 13:00
Joypurhat | 133 | 17:00 | 121 | 18:00 | Shyampur-230 | 135 | 01:00 | 124 | 15:00
Juldah | 138 | 00:00 | 132 | 11:00 | Siddhirganj | 134 | 02:00 | 124 | 12:00
Kabirpur | 134 | 01:00 | 116 | 12:00 | Sirajganj | 131 | 06:00 | 120 | 18:30
Kachua | 129 | 17:00 | 125 | 11:00 | Sitakunda | 137 | 00:00 | 132 | 11:00
Kaliakoir | 137 | 01:00 | 127 | 12:00 | Sonargaon | 133 | 04:00 | 120 | 13:00
Kaliganj | 137 | 04:00 | 125 | 21:00 | Sreemongol | 127 | 01:00 | 122 | 13:00
Kallyanpur | 132 | 05:00 | 121 | 13:00 | Sreepur | 136 | 06:00 | 126 | 12:00
Kalurghat | 138 | 00:00 | 134 | 10:00 | Srinagar | 137 | 03:00 | 126 | 13:00
Kamrangirchar | 138 | 03:00 | 120 | 12:00 | SSM | 140 | 00:00 | 138 | 14:00
Kaptai | 139 | 1:00 | 137 | 10:00 | Sunamganj | 119 | 04:00 | 111 | 14:00
Kasba | 126 | 06:00 | 118 | 13:00 | Sylhet | 123 | 02:00 | 119 | 12:00
Kazla | 138 | 06:00 | 125 | 13:00 | Sylhet_(South) | 124 | 03:00 | 120 | 13:00
Keranigonj | 139 | 06:00 | 127 | 13:00 | Tangail | 129 | 18:30 | 116 | 16:00
Khagrachori | 136 | 08:00 | 133 | 17:00 | Taraganj | 137 | 18:00 | 129 | 09:00
Khulna | 129 | 09:00 | 121 | 21:00 | Tasnim | 131 | 02:00 | 120 | 13:00
Khulna(S) | 130 | 06:00 | 123 | 21:00 | Thakurgaon | 141 | 06:00 | 130 | 09:00
Khulshi | 137 | 00:00 | 129 | 11:00 | TK | 138 | 00:00 | 134 | 10:00
Kishoreganj | 127 | 05:00 | 114 | 09:00 | Tongi | 138 | 04:00 | 124 | 11:00
Kodda | 135 | 18:30 | 120 | 12:00 | Ullahpara | 133 | 06:00 | 125 | 21:00
Korerhat | 134 | 06:00 | 129 | 12:00 | Ullon | 137 | 06:00 | 124 | 13:00
KSRM | 137 | 00:00 | 132 | 16:00 | Uttara | 136 | 03:00 | 121 | 12:00
Kulaura | 128 | 01:00 | 124 | 12:00 | UttaraNew | 135 | 01:00 | 119 | 12:00
Kurigram | 136 | 18:30 | 119 | 19:30 | Zigatola | 138 | 03:00 | 127 | 13:00
Kushtia | 135 | 06:00 | 125 | 21:00
Laksam | 129 | 19:00 | 125 | 12:00
Lakshmipur | 125 | 09:00 | 121 | 13:00
Lalbag | 138 | 02:00 | 127 | 12:00
Lalmonirhat | 135 | 18:30 | 119 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division