## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-10-2026 | during | 05-10-2026 | during | 05-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 412 | 412 | 412 | 372 | 372 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 322 | 335 | 335 | 305 | 305 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 143 | 149.36 | 149.36 | 15 | 15 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 11 | 11 | 24.75 | 24.75 | 13 | 13 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 50 | 52.19 | 52.19 | 24 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 278 | 278 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 107 | 138 | 149 | 149 | 97 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 480 | 584 | 584 | 526 | 526 | AGC+FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 360 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2329.42 | 2880.42 | 5576.91 | 5544.91 | 2493.12 | 2880.09
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 219 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 44 | 42 | 0 | 0 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 20 | 30 | 42 | 30 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 43 | 64 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.43 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 158 | 212 | 300 | 300 | 230 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 109 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 53 | 163 | 163 | 35 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1055 | 1055 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3312.43 | 3657.86 | 4080 | 4122.96 | 3467.04 | 3715.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 195 | 219 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 319 | 343 | 350.01 | 350.01 | 314.01 | 314.01 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 320 | 342.01 | 342.01 | 306.01 | 306.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 31 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 46 | 40 | 52.82 | 52.82 | 47 | 47 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 163 | 195 | 195 | 187 | 187 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 125 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 107 | 106 | 163 | 163 | 108 | 108 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 51 | 200 | 200 | 17 | 51 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 76 | 80 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 86 | 86 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 72 | 71 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 109 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1831 | 1859.2 | 2363.44 | 2287.44 | 1813.47 | 1908.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-10-2026 | during | 05-10-2026 | during | 05-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.8 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 164 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 87 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.96 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 255.76 | 275 | 663.6 | 591.5 | 268.1 | 294
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 113 | 113 | 113 | 113 | FGMO+ AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 139 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 0 | 0 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 241 | 240 | 341 | 341 | 260 | 260 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 276 | 281 | 280 | 280 | 280 | 280 | STG Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 400 | 400 | 383 | 383 | 383 | 383 | ps availability is less
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1342 | 1339 | 1548 | 1548 | 1483 | 1483
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 763 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 28 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75.38 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 180 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.1 | 1234.1 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2229.58 | 2289.2 | 3574.2 | 3479.2 | 3026.1 | 2931.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 965 | 1100 | 800 | 800 | 1000 | 1100 | AGC+FGMO
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 119 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 280 | 280 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2069.64 | 2271 | 2008 | 2007 | 2069 | 2168
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.18 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.7 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 664.44 | 701.97 | 550 | 650 | 500 | 600 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.58 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1439.1 | 1458.17 | 2220.11 | 2101.99 | 1363.11 | 1415.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 46 | 50 | 50 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 157 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 27 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 107 | 0 | 191.27 | 0 | 191.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 439.6 | 431 | 684.27 | 458 | 544.27 | 397
System Total |  |  |  |  | 28843.2 | 28692.211 | 15248.53 | 16460.85 | 22718.53 | 22141 | 16527.21 | 17193.51
Forecast Scenario (05-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15190 |  | 2180 |  | 17370
|  |  |  | 1:00 | 14440 |  | 2720 |  | 17160
|  |  |  | 2:00 | 14470 |  | 2630 |  | 17100
|  |  |  | 3:00 | 14330 |  | 2580 |  | 16910
|  |  |  | 4:00 | 14160 |  | 2460 |  | 16620
|  |  |  | 5:00 | 14080 |  | 2370 |  | 16450
|  |  |  | 6:00 | 14050 |  | 2150 |  | 16200
|  |  |  | 7:00 | 14160 |  | 2030 |  | 16190
|  |  |  | 8:00 | 14200 |  | 1620 |  | 15820
|  |  |  | 9:00 | 14480 |  | 0 |  | 14480
|  |  |  | 10:00 | 14920 |  | 0 |  | 14920
|  |  |  | 11:00 | 15180 |  | 582.55 |  | 15790
|  |  |  | 12:00 | 15250 |  | 1222.4 |  | 16530
|  |  |  | 13:00 | 15290 |  | 1155.55 |  | 16500
|  |  |  | 14:00 | 15180 |  | 1165.1 |  | 16400
|  |  |  | 15:00 | 15180 |  | 1824.05 |  | 17090
|  |  |  | 16:00 | 15060 |  | 1451.6 |  | 16580
|  |  |  | 17:00 | 15100 |  | 1212.85 |  | 16370
|  |  |  | 18:00 | 15970 |  | 582.55 |  | 16580
|  |  |  | 18:30 | 16110 |  | 1088.7 |  | 17250
|  |  |  | 19:00 | 16260 |  | 1585.3 |  | 17920
|  |  |  | 19:30 | 16450 |  | 1518.45 |  | 18040
|  |  |  | 20:00 | 16440 |  | 1317.9 |  | 17820
|  |  |  | 21:00 | 15880 |  | 2186.95 |  | 18170
|  |  |  | 22:00 | 15770 |  | 1938.65 |  | 17800
|  |  |  | 23:00 | 15640 |  | 2129.65 |  | 17870
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 16530.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2187
Probable Maximum Demand at Evening Peak: |  |  | 18170.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16450.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 360.68 MKWHr. |  | 256 | 178 | 412 | 296 | 146 | 273 | 136 | 345 | 145 | 2187
*** This report is generated digitally from Operation Information System (OIS) at 08:17 hrs on 05-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-10-2026 | [28 empty] | Date: | 04-10-2026 | [28 empty] | Date: | 04-10-2026 | [28 empty] | Date: | 04-10-2026 | [28 empty] | Date: | 04-10-2026 | [16 empty] | Date: | 04-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 112 | 15 | 278 | 55 | 55 | 162 | 0 | 0 | 350 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 340 | 109 | 212 | 45 | 0 | 0 | 51 | 28 | 36 | 24 | 12 | 0 | 220 | 92 | 35 | 1055 | 18 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 182 | 0 | 315 | 230 | 44 | 30 | 162 | 37 | 69 | 107 | 22 | 57 | 19 | 86 | 82 | 52.2 | 0 | 0 | 246 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 78 | 0 | 200 | 0 | 0 | 0 | 12 | 9232.42 | 806 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 690.14 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 91 | 5925.54 | 15157.96 | 106.59
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 35 | 35 | 130 | 15 | 278 | 55 | 35 | 72 | 0 | 0 | 440 | 0 | 35 | 266 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 350 | 107 | 68 | 45 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0 | 220 | 92 | 37 | 1055 | 16 | 0 | 46 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 290 | 47 | 44 | 39 | 211 | 37 | 69 | 107 | 16 | 24 | 19 | 86 | 82 | 52.2 | 0 | 0 | 244 | 400 | 246 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8665.42 | 807 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 653.96 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 15 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 156 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0.29 | 110 | 307 | 114 | 180 | 0 | 1000 | 300 | 54 | 5774.65 | 14440.07 | 106.59
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 35 | 133 | 15 | 225 | 55 | 35 | 72 | 0 | 0 | 585 | 0 | 35 | 282 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 360 | 109 | 68 | 46 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0 | 220 | 92 | 37 | 1055 | 18 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 307 | 47 | 44 | 46 | 201 | 36 | 69 | 107 | 16 | 0 | 19 | 86 | 80 | 52.2 | 0 | 0 | 260 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 30 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8781.42 | 806 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 549.57 | 0 | 0 | 0 | 95 | 50 | 0 | 0 | 15 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 180 | 0 | 1000 | 300 | 54 | 5684.97 | 14466.39 | 106.59
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 35 | 35 | 133 | 15 | 196 | 55 | 35 | 72 | 0 | 0 | 510 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 390 | 107 | 67 | 45 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0 | 220 | 92 | 37 | 1055 | 16 | 0 | 50 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 345 | 29 | 44 | 47 | 208 | 36 | 69 | 107 | 16 | 0 | 19 | 86 | 78 | 52.2 | 0 | 0 | 248 | 400 | 266 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8616.42 | 807 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 513.82 | 0 | 0 | 0 | 95 | 108 | 0 | 0 | 15 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5714.22 | 14330.64 | 106.59
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 35 | 133 | 15 | 196 | 55 | 35 | 72 | 0 | 0 | 455 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 350 | 107 | 68 | 45 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0 | 220 | 96 | 37 | 1055 | 18 | 0 | 50 | 0 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 325 | 40 | 44 | 47 | 196 | 33 | 69 | 107 | 16 | 0 | 19 | 86 | 76 | 52.2 | 0 | 0 | 244 | 400 | 266 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8533.42 | 806 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 512.01 | 0 | 0 | 0 | 55 | 110 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 152 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5625.41 | 14158.83 | 106.59
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 35 | 35 | 133 | 15 | 196 | 55 | 0 | 72 | 0 | 0 | 395 | 0 | 17 | 280 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 360 | 107 | 68 | 46 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0 | 219 | 101 | 0 | 1055 | 16 | 0 | 0 | 0 | 92 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 337 | 55 | 44 | 47 | 202 | 33 | 68 | 107 | 16 | 0 | 19 | 86 | 76 | 52.2 | 0 | 0 | 249 | 400 | 266 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8417.42 | 855 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 513.6 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5658 | 14075.42 | 106.59
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 35 | 35 | 133 | 15 | 196 | 55 | 0 | 72 | 0 | 0 | 390 | 0 | 17 | 277 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 335 | 107 | 68 | 46 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0.03 | 219 | 102 | 24 | 1055 | 18 | 0 | 0 | 0 | 85 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 185 | 0 | 320 | 95 | 44 | 47 | 194 | 33 | 64 | 107 | 16 | 0 | 19 | 86 | 74 | 52.2 | 0 | 0 | 248 | 400 | 276 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 0.08 | 67 | 0 | 0 | 0.05 | 12 | 8421.58 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 510.95 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.04 | 154 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5623.54 | 14045.12 | 106.59
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 35 | 133 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 410 | 0 | 17 | 285 | 0 | 0 | 4 | 143.42 | 10.8 | 22 | 0 | 400 | 107 | 68 | 45 | 0 | 0 | 51 | 28 | 0 | 24 | 12 | 0.38 | 217 | 103 | 22 | 1055 | 18 | 0 | 0 | 0 | 97 | 220 | 0 | 0 | 0 | 1224 | 4 | 150 | 187 | 0 | 334 | 136 | 35 | 47 | 205 | 33 | 51 | 107 | 16 | 0 | 19 | 86 | 70 | 52.2 | 2 | 0 | 248 | 400 | 276 | 40 | 40 | 0 | 1 | 0 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 3.02 | 67 | 0 | 0.3 | 7.4 | 8 | 8530.52 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1234.2 | 17 | 0 | 0 | 519.2 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 8.28 | 12 | 0 | 0 | 6.62 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.62 | 154 | 0 | 115 | 2 | 34 | 0 | 0 | 0 | 0.2 | 26 | 0.07 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5626.39 | 14156.91 | 106.59
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 35 | 133 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 385 | 0 | 17 | 265 | 0 | 0 | 12 | 143.42 | 12 | 22 | 0 | 320 | 109 | 68 | 46 | 0 | 0 | 51 | 27 | 0 | 24 | 12 | 0.9 | 217 | 106 | 3 | 1060 | 16 | 0 | 0 | 0 | 105 | 220 | 0 | 0 | 0 | 1224 | 9 | 150 | 187 | 0 | 300 | 145 | 35 | 47 | 183 | 32 | 51 | 107 | 16 | 3 | 19 | 86 | 76 | 52.2 | 9 | 0 | 241 | 400 | 276 | 40 | 40 | 0 | 2 | 8 | 0 | 80 | 0 | 139 | 0 | 100 | 0 | 59 | 7.55 | 67 | 0 | 0.8 | 18.87 | 12 | 8405.74 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1234.2 | 17 | 0 | 0 | 533.6 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 22.23 | 39 | 0 | 0 | 18.25 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.7 | 158 | 0 | 115 | 2 | 34 | 0 | 0 | 0 | 2.2 | 69 | 0.23 | 110 | 307 | 110 | 180 | 0 | 1000 | 300 | 54 | 5793.61 | 14199.35 | 106.59
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 20 | 122 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 345 | 0 | 17 | 285 | 0 | 0 | 20 | 143.42 | 11.5 | 22 | 0 | 345 | 107 | 152 | 46 | 0 | 0 | 0 | 27 | 30 | 24 | 12 | 1.32 | 217 | 104 | 5 | 1055 | 18 | 0 | 0 | 8 | 105 | 217 | 0 | 0 | 0 | 1224 | 14 | 150 | 187 | 0 | 335 | 185 | 35 | 47 | 200 | 29 | 51 | 107 | 16 | 57 | 19 | 86 | 64 | 8 | 32 | 0 | 240 | 400 | 276 | 40 | 40 | 0 | 7 | 16 | 0 | 80 | 0 | 140 | 0 | 100 | 0 | 59 | 8.36 | 70 | 0 | 1 | 29.68 | 12 | 8598.28 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.78 | 1234.2 | 17 | 0 | 0 | 568.24 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 36.25 | 65 | 0 | 0 | 34.49 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 3.19 | 158 | 0 | 115 | 8 | 34 | 0 | 0 | 0 | 4.1 | 70 | 0.4 | 110 | 307 | 115 | 220 | 0 | 1000 | 300 | 54 | 5879.85 | 14478.13 | 106.59
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 35 | 108 | 30 | 220 | 55 | 35 | 54 | 0 | 0 | 345 | 0 | 17 | 311 | 0 | 0 | 27 | 143.42 | 11.2 | 22 | 0 | 385 | 109 | 154 | 47 | 0 | 0 | 0 | 27 | 36 | 24 | 12 | 2.89 | 217 | 110 | 2 | 1055 | 16 | 0 | 0 | 8 | 105 | 216 | 0 | 0 | 0 | 1160 | 5 | 150 | 187 | 0 | 339 | 290 | 44 | 44 | 206 | 33 | 51 | 107 | 33 | 63 | 19 | 86 | 70 | 8 | 26 | 0 | 241 | 400 | 276 | 40 | 40 | 0 | 10 | 16 | 0 | 80 | 0 | 140 | 0 | 100 | 0 | 59 | 16.98 | 116 | 0 | 1.7 | 38.18 | 12 | 8951.37 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1230 | 17 | 0 | 0 | 570.39 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 48.28 | 86 | 0 | 0 | 45.43 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 3.99 | 156 | 0 | 115 | 15 | 34 | 0 | 0 | 0 | 3.9 | 110 | 0.29 | 110 | 307 | 114 | 220 | 0 | 990 | 300 | 54 | 5970.48 | 14921.85 | 106.59
11:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 35 | 108 | 30 | 278 | 55 | 35 | 54 | 0 | 0 | 355 | 0 | 17 | 319 | 0 | 0 | 29 | 143.42 | 11 | 21 | 0 | 415 | 107 | 157 | 43 | 0 | 1 | 0 | 28 | 36 | 12 | 12 | 2.27 | 218 | 107 | 0 | 1055 | 16 | 0 | 0 | 8 | 105 | 216 | 0 | 0 | 0 | 1170 | 15 | 150 | 187 | 0 | 343 | 300 | 44 | 46 | 211 | 27 | 55 | 107 | 52 | 73 | 19 | 86 | 74 | 8 | 65 | 0 | 240 | 396 | 276 | 40 | 40 | 0 | 7 | 16 | 0 | 80 | 0 | 140 | 0 | 100 | 0 | 59 | 18.14 | 116 | 0 | 1.9 | 46.43 | 5 | 9196.16 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 1212 | 17 | 0 | 0 | 618.99 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 54.68 | 20 | 0 | 0 | 48.8 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 4.87 | 158 | 0 | 115 | 27 | 34 | 0 | 0 | 0 | 5.8 | 106 | 0.61 | 110 | 307 | 114 | 220 | 0 | 969 | 300 | 54 | 5983.95 | 15180.11 | 106.58
12:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 107 | 45 | 278 | 50 | 35 | 54 | 0 | 0 | 350 | 0 | 17 | 300 | 0 | 0 | 31 | 143.42 | 11 | 0 | 0 | 320 | 109 | 158 | 43 | 0 | 3 | 0 | 44 | 36 | 12 | 12 | 1.43 | 219 | 93 | 4 | 1055 | 16 | 0 | 0 | 8 | 105 | 216 | 0 | 0 | 0 | 1160 | 18 | 150 | 187 | 0 | 319 | 320 | 44 | 46 | 195 | 29 | 53 | 107 | 51 | 72 | 19 | 86 | 76 | 8 | 69 | 0 | 241 | 400 | 276 | 40 | 40 | 0 | 9 | 16 | 0 | 80 | 0 | 140 | 0 | 100 | 0 | 59 | 20.8 | 115 | 0 | 2 | 46.96 | 12 | 9070.61 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.38 | 1234.2 | 17 | 0 | 0 | 664.44 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 55.18 | 88 | 0 | 0 | 55.58 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.7 | 157 | 0 | 115 | 30 | 27 | 0 | 0 | 0 | 3.6 | 107 | 0.64 | 110 | 307 | 113 | 220 | 0 | 965 | 300 | 54 | 6177.92 | 15248.53 | 106.58
13:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 35 | 107 | 45 | 278 | 45 | 35 | 54 | 0 | 0 | 350 | 0 | 17 | 310 | 0 | 0 | 28 | 143.42 | 11 | 0 | 0 | 415 | 107 | 158 | 50 | 0 | 5 | 0 | 38 | 36 | 12 | 12 | 2.38 | 219 | 94 | 9 | 1055 | 16 | 0 | 0 | 8 | 105 | 217 | 0 | 0 | 0 | 1192 | 18 | 150 | 187 | 0 | 338 | 340 | 44 | 45 | 207 | 30 | 53 | 81 | 51 | 74 | 19 | 86 | 78 | 8 | 35 | 0 | 243 | 398 | 276 | 40 | 40 | 0 | 10 | 16 | 0 | 79 | 0 | 138 | 0 | 100 | 0 | 58 | 18.22 | 115 | 0 | 1.9 | 2.5 | 12 | 9137.42 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 1234.2 | 17 | 0 | 0 | 664.88 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 53.33 | 89 | 0 | 0 | 53.56 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.37 | 156 | 0 | 115 | 29 | 34 | 0 | 0 | 0 | 5.3 | 109 | 0.53 | 110 | 307 | 113 | 220 | 0 | 961 | 300 | 54 | 6155.17 | 15292.59 | 106.58
14:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 107 | 45 | 278 | 55 | 35 | 54 | 0 | 0 | 365 | 0 | 35 | 307 | 0 | 0 | 24 | 143.42 | 11 | 14 | 0 | 335 | 109 | 158 | 51 | 0 | 6 | 0 | 38 | 36 | 12 | 12 | 0.54 | 220 | 82 | 5 | 1055 | 16 | 0 | 0 | 8 | 105 | 215 | 0 | 0 | 0 | 1192 | 16 | 147 | 187 | 0 | 336 | 320 | 44 | 45 | 197 | 29 | 53 | 81 | 51 | 71 | 19 | 86 | 82 | 8 | 51 | 0 | 243 | 394 | 276 | 40 | 38 | 0 | 7 | 16 | 0 | 79 | 0 | 140 | 0 | 100 | 0 | 58 | 15.2 | 115 | 0 | 1.5 | 39.16 | 12 | 9096.82 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.54 | 1228 | 17 | 0 | 0 | 670.9 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 34 | 45.03 | 78 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.03 | 154 | 0 | 115 | 24 | 34 | 0 | 0 | 0 | 4.9 | 127 | 0.33 | 110 | 307 | 113 | 220 | 0 | 992 | 300 | 54 | 6082.06 | 15178.88 | 106.58
15:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 35 | 97 | 69 | 278 | 55 | 35 | 54 | 0 | 0 | 400 | 0 | 35 | 310 | 0 | 0 | 18 | 143.42 | 11 | 14 | 0 | 400 | 107 | 158 | 45 | 0 | 2 | 0 | 39 | 36 | 12 | 12 | 0.79 | 222 | 88 | 3 | 1055 | 18 | 0 | 0 | 0 | 105 | 215 | 0 | 0 | 0 | 1192 | 11 | 145 | 167 | 0 | 334 | 305 | 44 | 46 | 191 | 29 | 51 | 80 | 51 | 71 | 19 | 86 | 78 | 25 | 35 | 0 | 240 | 391 | 276 | 40 | 38 | 0 | 5 | 13 | 0 | 79 | 0 | 140 | 0 | 100 | 0 | 58 | 9.84 | 114 | 0 | 1 | 25.8 | 12 | 9108.85 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.94 | 1229 | 17 | 0 | 0 | 673.38 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 42 | 41.46 | 56 | 0 | 0 | 33.54 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.61 | 150 | 0 | 115 | 18 | 34 | 0 | 0 | 0 | 3.8 | 101 | 0.29 | 110 | 307 | 112 | 220 | 0 | 976 | 300 | 72 | 6068.02 | 15176.87 | 106.58
16:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 35 | 89 | 125 | 278 | 55 | 35 | 144 | 0 | 0 | 385 | 0 | 35 | 307 | 0 | 0 | 9 | 143.42 | 11 | 22 | 0 | 370 | 107 | 175 | 49 | 0 | 1 | 0 | 39 | 36 | 12 | 12 | 0.85 | 222 | 92 | 3 | 1055 | 16 | 0 | 0 | 0 | 105 | 214 | 0 | 0 | 0 | 1196 | 6 | 143 | 140 | 0 | 325 | 300 | 44 | 45 | 188 | 29 | 51 | 80 | 51 | 71 | 19 | 86 | 80 | 52.2 | 18 | 0 | 242 | 393 | 276 | 40 | 38 | 0 | 3 | 16 | 0 | 79 | 0 | 139 | 0 | 100 | 0 | 58 | 1.87 | 114 | 0 | 1 | 13.37 | 12 | 9165.71 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.85 | 1227 | 17 | 0 | 0 | 670.38 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 15.45 | 27 | 0 | 0 | 17.21 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.58 | 154 | 0 | 115 | 3 | 29 | 0 | 0 | 0 | 2 | 51 | 0.18 | 110 | 307 | 113 | 220 | 0 | 966 | 300 | 54 | 5892.85 | 15058.56 | 106.58
17:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 35 | 35 | 89 | 141 | 278 | 55 | 55 | 162 | 0 | 0 | 380 | 0 | 35 | 290 | 0 | 0 | 2 | 143.42 | 11 | 22 | 0 | 325 | 109 | 208 | 55 | 0 | 0 | 0 | 39 | 36 | 12 | 12 | 0.25 | 222 | 92 | 5 | 1055 | 16 | 0 | 8 | 0 | 105 | 214 | 0 | 0 | 0 | 1165 | 1 | 140 | 128 | 0 | 310 | 285 | 44 | 46 | 193 | 29 | 52 | 107 | 51 | 71 | 19 | 86 | 72 | 52.2 | 5 | 0 | 243 | 395 | 276 | 39 | 38 | 0 | 1 | 16 | 0 | 80 | 0 | 139 | 0 | 100 | 0 | 58 | 2.14 | 124 | 0 | 0.1 | 3.02 | 12 | 9151.13 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 2.3 | 1230 | 17 | 0 | 0 | 664.44 | 0 | 0 | 0 | 113 | 69 | 0 | 0 | 0 | 43 | 3.77 | 8 | 0 | 0 | 4.44 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.35 | 152 | 0 | 115 | 1 | 38 | 0 | 0 | 0 | 0.6 | 14 | 0.04 | 110 | 307 | 114 | 220 | 0 | 965 | 300 | 72 | 5950.94 | 15102.07 | 106.58
18:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 35 | 90 | 141 | 278 | 55 | 55 | 162 | 0 | 0 | 350 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 425 | 107 | 209 | 59 | 0 | 0 | 35 | 43 | 36 | 24 | 24 | 0 | 222 | 92 | 16 | 1055 | 90 | 0 | 25 | 1 | 105 | 218 | 0 | 0 | 0 | 1190 | 0 | 140 | 133 | 0 | 354 | 330 | 44 | 47 | 211 | 26 | 80 | 107 | 52 | 70 | 19 | 86 | 88 | 52.2 | 0 | 0 | 246 | 395 | 276 | 40 | 38 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 0 | 129 | 0 | 0 | 0 | 8 | 9658.62 | 905 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 703.98 | 0 | 0 | 0 | 113 | 110 | 0 | 0 | 18 | 43 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 0 | 115 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 113 | 220 | 0 | 1100 | 300 | 137 | 6309.18 | 15967.8 | 106.58
19:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 35 | 130 | 141 | 278 | 55 | 55 | 162 | 0 | 0 | 380 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 400 | 107 | 212 | 64 | 0 | 0 | 51 | 43 | 54.36 | 24 | 24 | 0 | 221 | 106 | 6 | 1055 | 159 | 0 | 45 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 140 | 163 | 0 | 330 | 305 | 44 | 47 | 218 | 26 | 115 | 107 | 51 | 71 | 19 | 86 | 84 | 52.2 | 0 | 0 | 243 | 400 | 278 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 78 | 0 | 173 | 0 | 0 | 0 | 21 | 10011.48 | 763 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 700.05 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 38 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 137 | 6245.45 | 16256.93 | 106.58
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 35 | 133 | 144 | 278 | 55 | 55 | 162 | 0 | 0 | 355 | 0 | 55 | 316 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 440 | 108 | 212 | 64 | 0 | 0 | 51 | 42 | 54.36 | 24 | 24 | 0 | 221 | 110 | 9 | 1055 | 161 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 134 | 163 | 0 | 338 | 310 | 44 | 47 | 219 | 27 | 115 | 106 | 51 | 72 | 19 | 86 | 84 | 52.2 | 0 | 0 | 242 | 400 | 278 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 10054.48 | 763 | 0 | 28 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 697.93 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 38 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 5 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1100 | 300 | 137 | 6391.33 | 16445.81
20:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 35 | 133 | 132 | 278 | 55 | 55 | 162 | 0 | 0 | 355 | 0 | 55 | 322 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 440 | 108 | 212 | 64 | 0 | 0 | 51 | 42 | 54.36 | 24 | 24 | 0 | 220 | 110 | 12 | 1055 | 162 | 0 | 49 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 135 | 165 | 0 | 320 | 295 | 44 | 47 | 220 | 31 | 115 | 106 | 51 | 70 | 19 | 86 | 68 | 52.2 | 0 | 0 | 240 | 400 | 278 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 10006.48 | 763 | 0 | 28 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 696.85 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 38 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 137 | 6436.25 | 16442.73 | 106.57
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 138 | 143 | 278 | 55 | 55 | 162 | 0 | 0 | 360 | 0 | 55 | 322 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 480 | 107 | 212 | 64 | 0 | 0 | 51 | 42 | 54.36 | 24 | 24 | 0 | 219 | 110 | 20 | 1055 | 53 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 125 | 163 | 0 | 343 | 320 | 44 | 40 | 219 | 31 | 109 | 106 | 51 | 71 | 19 | 86 | 80 | 52.2 | 0 | 0 | 240 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 87 | 0 | 164 | 0 | 0 | 0 | 24 | 10011.48 | 763 | 0 | 28 | 0 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 701.97 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 119 | 6449.37 | 16460.85 | 106.57
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 145 | 128 | 278 | 55 | 55 | 162 | 0 | 0 | 370 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 10.5 | 22 | 0 | 470 | 109 | 212 | 58 | 0 | 0 | 51 | 42 | 54.36 | 24 | 24 | 0 | 218 | 110 | 23 | 1055 | 18 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 137 | 167 | 0 | 334 | 305 | 44 | 43 | 219 | 28 | 108 | 106 | 52 | 70 | 19 | 86 | 80 | 52.2 | 0 | 0 | 240 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 87 | 0 | 164 | 0 | 0 | 0 | 24 | 9910.98 | 763 | 0 | 28 | 0 | 0 | 0 | 0 | 237 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 699.27 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 119 | 6502.67 | 16413.65 | 106.57
23:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 54 | 35 | 145 | 129 | 196 | 55 | 55 | 162 | 0 | 0 | 325 | 0 | 55 | 295 | 0 | 0 | 0 | 143.42 | 10.5 | 22 | 0 | 390 | 107 | 212 | 42 | 0 | 0 | 51 | 44 | 36 | 24 | 24 | 0 | 218 | 110 | 25 | 1055 | 16 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 143 | 168 | 0 | 312 | 290 | 44 | 36 | 205 | 28 | 89 | 106 | 51 | 72 | 19 | 86 | 80 | 52.2 | 0 | 0 | 241 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 1 | 86 | 0 | 164 | 0 | 0 | 0 | 24 | 9583.62 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 239 | 0 | 67 | 0 | 1234.2 | 17 | 0 | 0 | 692.31 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 50 | 115 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 115 | 220 | 0 | 1000 | 300 | 100 | 6346.71 | 15930.33 | 106.57
Total KWH | 0 | 1623360 | 390240 | 0 | 0 | 0 | 0 | 0 | 9630000 | 0 | 0 | 781200 | 854280 | 2902464 | 1566720 | 5812309 | 1319583 | 799072 | 2344320 | 0 | 0 | 9445624 | 0 | 798071 | 7277621 | 0 | 0 | 204855 | 3493200 | 258000 | 464760 | 0 | 9284090.91 | 2583109 | 3424909 | 1181760 | 0 | 14880 | 748514 | 743043 | 660957 | 476160 | 362880 | 14762 | 5284015 | 2427964 | 383520 | 25381818.18 | 817964 | 0 | 564960 | 191325.6 | 2514109 | 5210491 | 0 | 0 | 0 | 28909088 | 122175 | 3521090 | 4198545 | 0 | 8347400 | 5476000 | 971848 | 1064640 | 4977000 | 743760 | 1674240 | 2435683 | 893280 | 1155000 | 454330 | 2066820 | 1856640 | 945058 | 365491 | 0 | 5839000 | 9530800 | 6663000 | 950000 | 925440 | 0 | 59617 | 419992 | 0 | 1958400 | 65184 | 3150000 | 0 | 2402690 | 57600 | 1542000 | 111502 | 2664000 | 0 | 12250 | 288750 | 349920 | 219405143.69 | 20480727 | 0 | 246240 | 0 | 0 | 0 | 0 | 1715466 | 0 | 464688 | 501840 | 29600000 | 415680 | 0 | 0 | 14789385 | 0 | 0 | 0 | 1707840 | 1894080 | 0 | 0 | 229009 | 1194720 | 390976 | 699430 | 240712 | 0 | 339744 | 0 | 0 | 0 | 0 | 0 | 0 | 9571345 | 0 | 27840 | 3853000 | 210763 | 2744378 | 158928 | 1363401 | 0 | 0 | 0 | 35754.72 | 934560 | 3720 | 2642784 | 7396000 | 2747000 | 5354050 | 0 | 24305454 | 7239272.73 | 1740000 | 145238787.45 | 364643931.14

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15248.53 | MW | 12:00 Hr. | Energy Generated |  |  | 364.6439 |  | MKWHr.
| Day Peak Demand |  |  | 16147.53 | MW | 12:00 Hr. | Energy Unserverd |  |  | 31.242 |  | MKWHr.
| Evening Peak Generation |  |  | 16460.85 | MW | 21:00 Hr. | Energy Demand |  |  | 395.8859 |  | MKWHr.
| Evening Peak Demand |  |  | 17797.85 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 14045.12 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 880.17 |  | MMCFD
| Maximum Generation of the Day |  |  | 16460.85 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 8.4701 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.3601 | 0 | 22.6848 | 0 | 0 | 0.20486 | 0 | 0 | 59.2498 | Gas | 120.2002 | Gas | 415548850.1247
| Chattogram Zone |  |  | 5.594 | 54.2909 | 16.6977 | 0 | 5.284 | 0.13694 | 0 | 0.01488 | 82.0184 | Coal | 126.8954 | Coal | 915289411.7335
| Cumilla Zone |  |  | 28.6692 | 0 | 10.2555 | 0 | 0 | 0.36549 | 1.8566 | 0 | 41.1468 | HFO | 69.135 | HFO | 1438067746.688
| Mymensingh Zone |  |  | 0 | 0 | 4.6135 | 0 | 0 | 0.4125 | 0 | 0 | 5.026 | HSD | 1.7155 | HSD | 34652413.2
| Sylhet Zone |  |  | 31.9045 | 0 | 0 | 0 | 0 | 0.059617 | 0 | 0 | 31.9641 | Hydro | 5.284 | Hydro | 528401.5
| Khulna Zone |  |  | 0 | 29.6 | 1.1266 | 1.7155 | 0 | 0.50184 | 20.4807 | 0 | 53.4246 | Solar | 4.2722 | Solar | 68183975.2304
| Barishal Zone |  |  | 8.1011 | 38.9407 | 4.3828 | 0 | 0 | 0.00372 | 0 | 0 | 51.4283 | Import | 37.1268 | Import | 216082765.62
| Rajshahi Zone |  |  | 9.5713 | 0 | 5.2664 | 0 | 0 | 1.458 | 14.7894 | 0 | 31.0851 | Wind | 0.01488 | Wind | 220819.2
| Rangpur Zone |  |  | 0 | 4.0638 | 4.1078 | 0 | 0 | 1.1292 | 0 | 0 | 9.3008
| Total |  |  | 120.2002 | 126.8954 | 69.135 | 1.7155 | 5.284 | 4.2722 | 37.1268 | 0.01488 | 364.6439
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 415548850.1247 |  | Hydro | 528401.5
|  |  |  | Coal | 915289411.7335 |  | Solar | 68183975.2304
|  |  |  | HFO | 1438067746.688 |  | Import | 216082765.62
|  |  |  | HSD | 34652413.2 |  | Wind | 220819.2
[5 empty] | Total: | 308,85,74,383 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4807 | Peak Hr Flow | 763.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 32228436.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.7894 | Peak Hr Flow | 701.97 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1247 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.8566 | Peak Hr Flow | 80.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1994 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.1268 | Peak Hr Flow | 1544.97 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 150 |  | 6239
|  |  |  | Chattogram |  | 104 |  | 1562
|  |  |  | Cumilla |  | 241 |  | 1717
|  |  |  | Mymensingh |  | 173 |  | 1420
|  |  |  | Sylhet |  | 85 |  | 731
|  |  |  | Khulna |  | 160 |  | 2042
|  |  |  | Barishal |  | 79 |  | 559
|  |  |  | Rajshahi |  | 202 |  | 1797
|  |  |  | Rangpur |  | 85 |  | 997
|  |  |  | Total |  | 1279 |  | 17064
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 247.5
|  |  |  | Total Unavailable Capacity |  |  |  | 547.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 10:38 | Pabna 132/33kV S/S T-2 LT Forced S/D Due to Kashinathpur 33 kv (PBS-2) Redhot
Maintenance work.
| 08:01 | 10:38 | Pabna 132/33kV S/S T-2 HT Forced S/D Due to Kashinathpur 33 kv (PBS-2) Redhot
Maintenance work.
| 09:18 | 16:29 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Annual maintenance
| 09:28 | 18:22 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Request by NLDC
|  | 09:50 | Chattak-Sunamganj 132 kV Ckt-2 is restored.
| 10:09 | 12:13 | Korerhat 400/230/132kV S/S 400kV BUS-1 Project Work S/D Due to DFDR Work
| 10:18 | 11:47 | Madunaghat 132/33kV S/S TR-2(517T) LT Scheduled S/D Due to Anonna 33kv feeder loop
maintenance work by BPDB.
| 10:29 | 11:14 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Tripped showing Distance Relay relays Due
to Distance Trip
| 11:00 | 17:59 | Nabinagar 132/33kV S/S Nabinagar-Dhamrai Ckt-2 Project Work S/D Due to Internal testing
of SAS
| 11:04 | 14:40 | Bogura 230/132kV S/S 132KV Main 2 Scheduled S/D Due to red hot maintenance
| 11:07 | 17:43 | Nabinagar 132/33kV S/S T-1 LT Project Work S/D Due to Internal testing of SAS | [7 empty] | 15.0MW load
interrup.
| 11:07 | 17:42 | Nabinagar 132/33kV S/S T-1 HT Project Work S/D Due to Internal testing of SAS
| 11:43 | 17:32 | Nabinagar 132/33kV S/S Main Bus-1 Project Work S/D Due to Internal testing of SAS
| 11:49 | 14:20 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to busbar protection
work by SPMD depratment,
| 11:58 |  | Kachua 230/132/33kV S/S ATR-1 LT Project Work S/D
| 12:00 |  | Kachua 230/132/33kV S/S ATR-1 HT Project Work S/D
| 12:23 | 17:55 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to Fire Fighter
| 12:24 | 17:53 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to Fire Fighter
| 13:26 | 15:05 | Bogura(New) South-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end
Due to red hot maintenance
|  | 14:04 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 14:04 | Khulna (C) S/S TR-1 425T LT is restored.
|  | 15:04 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT is restored.
|  | 15:06 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT is restored.
| 17:21 |  | Palashbari 132/33kV S/S TR2-404T LT Tripped showing O/C & E/F relays Due to 33Kv Feeder | [7 empty] | 75.0MW load
|  |  | Fault | [7 empty] | interrup.
| 17:21 |  | Palashbari 132/33kV S/S TR1-414T HT Tripped showing O/C & E/F relays Due to 33Kv Feeder | [7 empty] | 75.0MW load
|  |  | Fault | [7 empty] | interrup.
| 17:21 |  | Palashbari 132/33kV S/S TR1-414T LT Tripped showing O/C & E/F relays Due to 33 kv feeder | [7 empty] | 74.0MW load
|  |  | Fault | [7 empty] | interrup.
| 17:21 | 18:11 | Palashbari 132/33kV S/S TR2-404T HT Tripped showing O/C & E/F relays Due to 33 KV Feeder | [7 empty] | 75.0MW load
|  |  | fault | [7 empty] | interrup.
|  | 18:11 | Palashbari 132/33kV S/S TR2-404T HT is restored.
| 19:28 |  | Barapukuria TPP Unit-1 Synchronized
| 19:40 |  | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to 33kv Feeder Fault | [7 empty] | 25.0MW load
interrup.
| 19:40 |  | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to 33Kv Feeder Fautl | [7 empty] | 25.0MW load
interrup.
| 21:00 |  | Evening Peak Generation: 16461 MW.
| 22:21 |  | Full interruption is occurring under Hatirjheel grid s/s (DPDC) due to tripping of
Rampura-Hatirjheel ckt and Rampura-Ullon-Mogbazar ckt. Rampura grid s/s operators
reported there was a blast sound heard in switchyard at the time of tripping.
| 22:21 | 23:46 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing TEE Zone 1 Prot. | [7 empty] | 50.0MW load
|  |  | Trip (87TEE-1) TEE Zone 2 Prot. Trip (87TEE-2) Lockout Relay 1 & 2 612B Lockout | [7 empty] | interrup. Rampura
|  |  | Relay 1 & 2 615B Lockout Relay 1 & 2 618B relays Due to 132kV Ullon -02 Distance | [7 empty] | 230/132kV end
Protection 21/2 Z3 BCN Start (alarm) 132kV mog-2 Diff 87L trip
blue-phase distance trip 21.Z2 distance time trip 21.Z2
| 22:21 | 02:02 | Moghbazar-Rampura 132kV Ckt-2 Tripped from Rampura 230/132kV end showing TEE Zone 1
Prot. Trip (87TEE-1) TEE Zone 2 Prot. Trip (87TEE-2) Lockout Relay 1 & 2
612B Lockout Relay 1 & 2 615B Lockout Relay 1 & 2 618B relays Due to 132kV Ullon -02
Distance Protection 21/2 Z3 BCN Start (alarm) 132kV mog-2 Diff 87L trip
blue-phase distance trip 21.Z2 distance time trip 21.Z2
| 23:50 |  | Rampura-Ullon-Mogbazar ckt was switched ON.
| 02:15 |  | Rampura-Hatirjheel ckt was switched ON.
| 06:20 |  | Barapukuria TPP Unit-1 Tripped with remarks:- Monitor abnormal issues
| 06:20 |  | Barapukuria TPP Unit-1 Shutdown
| 06:39 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Redhot maintenance work at aminbazar end.
| 07:20 |  | Thakurgaon 132/33kV S/S 33kV Bus Scheduled S/D Due to গোয়ালপারা-২ ৩৩ কেভি ফিডারের সোর্স | [7 empty] | 45.0MW load
|  |  | সাইটের আইসোলেটরে সমস্যা হওয়ায় মেরামত কাজে ৩৩ কেভি বাস সাটডাউন নেয়া হয়। গোয়ালপারা-২, | [7 empty] | interrup.
বালিয়াডাঙ্গি, নেকমরদ, গোয়ালপারা-১, পীরগঞ্জ, আরইবি বীরগঞ্জ ও গোলাপগঞ্জ একই বাসে থাকার
কারণে উপরোক্ত ফিডারগুলো বন্ধ রয়েছে।
| 07:31 |  | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to Annual maintenance purpose.
| 07:32 |  | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to For annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9630000 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1319583 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7277621 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 781200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1566720 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 799072 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 798071 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 258000 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 464760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 390240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 5812309 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 138 | 2902464 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1623360 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2344320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204855 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 854280 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 9284090.91 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 360 | 9445624 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3493200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2880.42 | 59249769.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 191325.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122175 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 564960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5284015 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5210491 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2514109 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 743043 | plant availability zero
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 748514 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 476160 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 383520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 64 | 1181760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 212 | 3424909 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 660957 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2427964 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 362880 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2583109 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 53 | 817964 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28909088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 14880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1055 | 25381818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3657.86 | 82018403.78
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 219 | 4977000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 343 | 8347400 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 5476000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 31 | 743760 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 40 | 1064640 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 4198545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 971848 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 3521090 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 106 | 2435683 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 893280 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1856640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 945058 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 454330 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 2066820 | Machine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 71 | 1155000 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 109 | 1674240 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 365491 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1859.2 | 41146825
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 111502 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2664000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1542000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 349920 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 57600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 275 | 5026022
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 59617 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 950000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 925440 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3150000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 65184 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1958400 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2402690 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 419992 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 240 | 5839000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 281 | 6663000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9530800 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1339 | 31964123
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 763 | 20480727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 246240 | Fuel Shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | plant availability zero
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 415680 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 464688 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 501840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 180 | 1715466 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29600000 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2289.2 | 53424641
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24305454 | FGMO
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 2642784 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2747000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7239272.73 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5354050 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 119 | 1740000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7396000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3720 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2271 | 51428280.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 390976 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | plant availability zero
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 229009 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9571345 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 240712 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1194720 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1894080 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1707840 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 27840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 701.97 | 14789385 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 339744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 699430 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1458.17 | 31085081
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 210763 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3853000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1363401 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35754.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2744378 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158928 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 934560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 431 | 9300784.72
Eastern Grid Total |  |  |  |  | 16961.086 | 10011.48 | 219405143.69
Western Grid Total |  |  |  |  | 11731.125 | 6449.37 | 145238787.45
National Grid Total |  |  |  |  | 28692.211 | 16460.85 | 364643931.14
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-10-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10916.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4868.5 | MW
i) Dhaka area |  |  | 6088.83 |  | MW | i) Khulna area |  |  |  | 1881.5 | MW
ii) Chattogram area |  |  | 1458.2 |  | MW | ii) Barishal area |  |  |  | 479.6 | MW
iii) Cumilla area |  |  | 1476 |  | MW | iii) Rajshahi area |  |  |  | 1595.4 | MW
iv) Mymensingh area |  |  | 1247 |  | MW | iv) Rangpur area |  |  |  | 912 | MW
v) Sylhet area |  |  | 646 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15784.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 18:00 | 72 | Hatirjheel | 91 | 15:00 | 143 | PHP | 12 | 13:00
2 | AKSML | 156 | 14:00 | 73 | Ishurdi | 82 | 19:30 | 144 | Pabna | 103 | 22:00
3 | Aftabnagar | 50 | 13:00 | 74 | Jaldhaka | 66 | 20:00 | 145 | Palashbari | 116 | 03:00
4 | Agargaon | 144 | 14:00 | 75 | Jamalpur | 134 | 23:00 | 146 | Panchagarh | 70 | 18:30
5 | Agrabad | 74 | 11:00 | 76 | Jashore | 138 | 18:30 | 147 | Patiya | 27 | 23:00
6 | Amnura | 32 | 23:00 | 77 | Jhenaidah | 95 | 22:00 | 148 | Patnitala | 37 | 13:00
7 | Araihazar | 105 | 08:00 | 78 | Joydebpur | 181 | 19:00 | 149 | Patuakhali | 67.2 | 22:00
8 | Ashuganj | 0 | 00:00 | 79 | Joypurhat | 61 | 23:00 | 150 | Payra | 34 | 19:00
9 | Ashuganj-230 | 103 | 01:00 | 80 | Juldah | 18 | 00:00 | 151 | Postogola | 67 | 00:00
10 | BSRM | 201 | 18:30 | 81 | KSRM | 21 | 11:00 | 152 | Pubail | 52 | 19:00
11 | Bagerhat | 90 | 22:00 | 82 | Kabirpur | 276 | 19:00 | 153 | Purbachal | 32 | 00:00
12 | Bajitpur | 97 | 21:00 | 83 | Kachua | 96 | 22:00 | 154 | Purbasadipur | 126 | 19:30
13 | Bakerganj | 14.6 | 21:00 | 84 | Kaliganj | 40 | 18:00 | 155 | Rahanpur | 34 | 23:00
14 | Bakulia | 98 | 19:00 | 85 | Kallyanpur | 126 | 23:00 | 156 | Rahim | 42 | 23:00
15 | Banani | 74 | 13:00 | 86 | Kalurghat | 41 | 18:00 | 157 | Rajbari | 87 | 21:00
16 | Bangabhaban | 18 | 11:00 | 87 | Kamrangirchar | 86 | 13:00 | 158 | Rajendrapur | 124 | 12:00
17 | Barapukuria | 57 | 23:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 111 | 23:00
18 | Barguna | 22 | 18:00 | 89 | Kasba | 36 | 20:00 | 160 | Rajshahi-230 | 108 | 20:00
19 | Barishal | 107 | 20:00 | 90 | Kazla | 119 | 19:00 | 161 | Ramganj | 118 | 21:00
20 | Barishal-230 | 98 | 21:00 | 91 | Keranigonj | 99 | 18:00 | 162 | Rampur | 54 | 08:00
21 | Baroaulia | 38 | 08:00 | 92 | Khagrachori | 36 | 19:00 | 163 | Rangamati | 16 | 18:00
22 | Baroirhat | 60 | 21:00 | 93 | Khulna | 62 | 19:30 | 164 | Rangpur | 130 | 20:00
23 | Bashundhara | 210 | 13:00 | 94 | Khulshi | 180 | 18:00 | 165 | Ruppur | 5 | 11:00
24 | BashundharaCement | 7 | 00:00 | 95 | Kishoreganj | 133 | 00:00 | 166 | SSM | 13 | 05:00
25 | Beanibazar | 76 | 18:00 | 96 | Kodda | 323 | 21:00 | 167 | Saidpur | 104 | 09:00
26 | Benapole | 70 | 23:00 | 97 | Kulaura | 52 | 19:00 | 168 | Santhia | 34 | 22:00
27 | Bhaluka | 174 | 18:30 | 98 | Kurigram | 64 | 07:00 | 169 | Satkhira | 145 | 21:00
28 | Bhandaria | 54 | 22:00 | 99 | Kushtia | 156 | 13:00 | 170 | Satmasjid | 113 | 13:00
29 | Bhangura | 38 | 19:30 | 100 | Laksam | 36 | 18:00 | 171 | Savar | 224 | 12:00
30 | Bheramara(GK) | 73 | 21:00 | 101 | Lakshmipur | 50 | 18:00 | 172 | SevenRings | 22.33 | 16:00
31 | Bhulta | 210 | 21:00 | 102 | Lalbag | 83 | 13:00 | 173 | ShahCement | 18 | 01:00
32 | Bog-Sherpur | 68 | 19:30 | 103 | Lalmonirhat | 56 | 18:30 | 174 | Shahjadpur | 88 | 19:00
33 | Bogura | 215 | 23:00 | 104 | MI_Cement | 16.1 | 01:00 | 175 | Shahjibazar | 145 | 22:00
34 | Borhanuddin | 69 | 06:00 | 105 | Madanganj | 52 | 22:00 | 176 | Shahmirpur | 58 | 18:00
35 | Brahmanbaria | 141 | 21:00 | 106 | Madaripur | 111 | 22:00 | 177 | Shariatpur | 97 | 22:00
36 | Cantonment | 137 | 13:00 | 107 | Madartek | 96 | 23:00 | 178 | Sherpur | 162 | 00:00
37 | Chandina | 19 | 18:30 | 108 | Madunaghat | 52 | 15:00 | 179 | Shikalbaha | 32 | 18:30
38 | Chandpur | 92 | 20:00 | 109 | Magura | 67 | 22:00 | 180 | Shitalakhya | 85.1 | 12:00
39 | Chandraghona | 32 | 18:00 | 110 | Mahasthangarh | 75 | 18:00 | 181 | Sholosohor | 51 | 09:00
40 | Chapai | 79 | 21:00 | 111 | Maijdee | 34 | 13:00 | 182 | Shomvuganj | 50 | 00:00
41 | Charfasson | 31 | 20:00 | 112 | Manikganj | 154 | 19:30 | 183 | Shyampur | 146 | 16:00
42 | Charsaidpur | 26 | 23:00 | 113 | Maniknagar | 68 | 13:00 | 184 | Siddhirganj | 137 | 12:00
43 | Chauddagram | 71 | 18:00 | 114 | Matarbari | 53 | 19:30 | 185 | Sirajganj | 130 | 19:30
44 | Chhatak | 36 | 21:00 | 115 | Matuail | 78 | 23:00 | 186 | Sitakunda | 36 | 04:00
45 | Chowmuhani | 149 | 22:00 | 116 | Metrorail_Motijheel | 20 | 21:00 | 187 | Sonargaon | 117 | 10:00
46 | Chuadanga | 116 | 23:00 | 117 | Metrorail_Uttara | 0 | 00:00 | 188 | Sreemongol | 83 | 21:00
47 | Coxsbazar | 144 | 11:00 | 118 | Millgate | 106 | 15:00 | 189 | Sreepur | 142 | 12:00
48 | Cumilla(N) | 164 | 23:00 | 119 | Mirpur | 163 | 18:30 | 190 | Srinagar | 52.9 | 21:00
49 | Cumilla(S) | 168 | 18:00 | 120 | Mirsorai | 53 | 11:00 | 191 | Sunamganj | 58 | 13:00
50 | Daganbhuiyan | 40 | 22:00 | 121 | Mirzapur | 50 | 12:00 | 192 | Sylhet | 129 | 18:00
51 | Daudkandi | 129 | 21:00 | 122 | Mithapukur | 82 | 21:00 | 193 | Sylhet_(South) | 60 | 18:30
52 | DhakaUniversity | 110 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 108 | 18:00 | 124 | Mogbazar | 82.2 | 23:00 | 195 | Tangail | 188 | 20:00
54 | Dhanmondi | 135.5 | 13:00 | 125 | Mongla | 47 | 16:00 | 196 | Taraganj | 30 | 09:00
55 | Dohazari | 110 | 22:00 | 126 | Monirampur | 24 | 19:30 | 197 | Tasnim | 47 | 21:00
56 | Faridpur | 181 | 18:30 | 127 | Motijheel | 60 | 13:00 | 198 | Thakurgaon | 113 | 18:30
57 | Fatullah | 127 | 16:00 | 128 | Muktagacha | 41 | 00:00 | 199 | Tongi | 184 | 11:00
58 | Fenchuganj | 42 | 18:00 | 129 | Munshiganj | 124 | 21:00 | 200 | Ullahpara | 38 | 20:00
59 | Feni | 111 | 20:00 | 130 | Muradnagar | 48 | 18:00 | 201 | Ullon | 46 | 23:00
60 | GPH | 19 | 01:00 | 131 | Mymensingh | 162 | 18:30 | 202 | Uttara | 108 | 13:00
61 | Ghatail | 92 | 19:30 | 132 | Nabinagar | 110 | 10:00 | 203 | UttaraNew | 60 | 23:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 122 | 23:00 | 204 | Zigatola | 96 | 13:00
63 | Ghorashal-230 | 99 | 18:00 | 134 | Narail | 60 | 18:00
64 | Goalpara | 39 | 22:00 | 135 | Narinda | 82.5 | 13:00
65 | Gollamari | 110 | 19:30 | 136 | Narshingdi | 196 | 22:00
66 | Gopalganj | 105 | 19:00 | 137 | Natore | 144 | 19:30
67 | Gulshan | 132 | 12:00 | 138 | Nawabganj | 55.6 | 22:00
68 | Halishahar | 113 | 15:00 | 139 | Netrakona | 140 | 00:00
69 | HaripurSBU | 127 | 20:00 | 140 | New | 90 | 14:00
70 | Hasnabad | 111 | 21:00 | 141 | Niamatpur | 73 | 21:00
71 | Hathazari | 98 | 19:00 | 142 | Noapara | 45 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15157.96 | 2618 |  | 17893.77
1:00 | 14440.07 | 2607 |  | 17164.39
2:00 | 14466.39 | 2473 |  | 17050.39
3:00 | 14330.64 | 2359 |  | 16795.64
4:00 | 14158.83 | 2263 |  | 16523.83
5:00 | 14075.42 | 2146 |  | 16318.42
6:00 | 14045.12 | 733 |  | 14811.12
7:00 | 14156.91 | 808 |  | 15000.91
8:00 | 14199.35 | 699 |  | 14929.35
9:00 | 14478.13 | 392 |  | 14888.13
10:00 | 14921.85 | 37 |  | 14960.85
11:00 | 15180.11 | 30 |  | 15211.46
12:00 | 15248.53 | 860 |  | 16147.53
13:00 | 15292.59 | 892 |  | 16224.59
14:00 | 15178.88 | 1102 |  | 16330.88
15:00 | 15176.87 | 1501 |  | 16745.87
16:00 | 15058.56 | 1212 |  | 16325.56
17:00 | 15102.07 | 1037 |  | 16186.07
18:00 | 15967.8 | 1283 |  | 17308.8
19:00 | 16256.93 | 1431 |  | 17751.93
19:30 | 16445.81 | 1150 |  | 17647.81
20:00 | 16442.73 | 1135 |  | 17628.73
21:00 | 16460.85 | 1279 |  | 17797.85
22:00 | 16413.65 | 911 |  | 17365.65
23:00 | 15930.33 | 1434 |  | 17429.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9232.42 | 5925.54 | 15157.96 | DAILY GENERATION CURVE
00:30 | 8948.92 | 5850.095 | 14799.015
01:00 | 8665.42 | 5774.65 | 14440.07 | 04-10-2026
01:30 | 8723.42 | 5729.81 | 14453.23
02:00 | 8781.42 | 5684.97 | 14466.39
02:30 | 8698.92 | 5699.595 | 14398.515
03:00 | 8616.42 | 5714.22 | 14330.64
03:30 | 8574.92 | 5669.815 | 14244.735
04:00 | 8533.42 | 5625.41 | 14158.83
04:30 | 8475.42 | 5641.705 | 14117.125
05:00 | 8417.42 | 5658 | 14075.42
05:30 | 8419.5 | 5640.77 | 14060.27
06:00 | 8421.58 | 5623.54 | 14045.12
06:30 | 8476.05 | 5624.965 | 14101.015
07:00 | 8530.52 | 5626.39 | 14156.91
07:30 | 8468.13 | 5710 | 14178.13
08:00 | 8405.74 | 5793.61 | 14199.35
08:30 | 8502.01 | 5836.73 | 14338.74
09:00 | 8598.28 | 5879.85 | 14478.13
09:30 | 8774.825 | 5925.165 | 14699.99
10:00 | 8951.37 | 5970.48 | 14921.85
10:30 | 9073.765 | 5977.215 | 15050.98
11:00 | 9196.16 | 5983.95 | 15180.11
11:30 | 9133.385 | 6080.935 | 15214.32
12:00 | 9070.61 | 6177.92 | 15248.53
12:30 | 9104.015 | 6166.545 | 15270.56
13:00 | 9137.42 | 6155.17 | 15292.59
13:30 | 9117.12 | 6118.615 | 15235.735
14:00 | 9096.82 | 6082.06 | 15178.88
14:30 | 9102.835 | 6075.04 | 15177.875
15:00 | 9108.85 | 6068.02 | 15176.87
15:30 | 9137.28 | 5980.435 | 15117.715
16:00 | 9165.71 | 5892.85 | 15058.56
16:30 | 9158.42 | 5921.895 | 15080.315
17:00 | 9151.13 | 5950.94 | 15102.07
17:30 | 9404.875 | 6130.06 | 15534.935
18:00 | 9658.62 | 6309.18 | 15967.8
18:30 | 9835.05 | 6277.315 | 16112.365
19:00 | 10011.48 | 6245.45 | 16256.93
19:30 | 10054.48 | 6391.33 | 16445.81
20:00 | 10006.48 | 6436.25 | 16442.73
20:30 | 10008.98 | 6442.81 | 16451.79 |  | Executive Engineer
21:00 | 10011.48 | 6449.37 | 16460.85 |  | Network Operation Division
21:30 | 9961.23 | 6476.02 | 16437.25
22:00 | 9910.98 | 6502.67 | 16413.65
22:30 | 9747.3 | 6424.69 | 16171.99
23:00 | 9583.62 | 6346.71 | 15930.33

## En-Curve
QF-LDC-12
Date | 04-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3300 | 1597.8 | 806 | 0 | 82 | 690.14 | 220 | 5275.2 | 0 | 340.42 | 2846.4 | 0 | 0 | 0 | 2618 | DAILY ENERGY CURVE
00:30 | 3197.5 | 1633.8 | 806.5 | 0 | 82 | 672.05 | 220 | 5275.7 | 0.145 | 331.92 | 2579.4 | 0 | 0 | 0 | 2612.5 | 04-10-2026
01:00 | 3095 | 1669.8 | 807 | 0 | 82 | 653.96 | 220 | 5276.2 | 0.29 | 323.42 | 2312.4 | 0 | 0 | 0 | 2607
01:30 | 3106 | 1758.8 | 806.5 | 0 | 81 | 601.765 | 220 | 5275.7 | 0.145 | 323.42 | 2279.9 | 0 | 0 | 0 | 2540 | Energy Generated | 364.6439 |  | MKWHr
02:00 | 3117 | 1847.8 | 806 | 0 | 80 | 549.57 | 220 | 5275.2 | 0 | 323.42 | 2247.4 | 0 | 0 | 0 | 2473 | Energy not Served | 31.242 |  | MKWHr
02:30 | 3093.5 | 1839.8 | 806.5 | 0 | 79 | 531.695 | 220 | 5275.2 | 0 | 323.42 | 2229.4 | 0 | 0 | 0 | 2416 | Total Energy Requirement | 395.8859 |  | MKWHr
03:00 | 3070 | 1831.8 | 807 | 0 | 78 | 513.82 | 220 | 5275.2 | 0 | 323.42 | 2211.4 | 0 | 0 | 0 | 2359
03:30 | 3075.5 | 1782.3 | 806.5 | 0 | 77 | 512.915 | 220 | 5273.7 | 0 | 301.92 | 2194.9 | 0 | 0 | 0 | 2311
04:00 | 3081 | 1732.8 | 806 | 0 | 76 | 512.01 | 220 | 5272.2 | 0 | 280.42 | 2178.4 | 0 | 0 | 0 | 2263
04:30 | 3121 | 1691.8 | 830.5 | 0 | 76 | 512.805 | 219.5 | 5273.2 | 0 | 278.92 | 2113.4 | 0 | 0 | 0 | 2204.5
05:00 | 3161 | 1650.8 | 855 | 0 | 76 | 513.6 | 219 | 5274.2 | 0 | 277.42 | 2048.4 | 0 | 0 | 0 | 2146
05:30 | 3171.5 | 1647.3 | 878 | 0 | 75 | 512.275 | 219 | 5274.2 | 0.175 | 269.92 | 2012.9 | 0 | 0 | 0 | 1439.5
06:00 | 3182 | 1643.8 | 901 | 0 | 74 | 510.95 | 219 | 5274.2 | 0.35 | 262.42 | 1977.4 | 0 | 0 | 0 | 733
06:30 | 3219 | 1673.8 | 864 | 0 | 72 | 515.075 | 218 | 5274.2 | 45.62 | 262.42 | 1956.9 | 0 | 0 | 0 | 770.5
07:00 | 3256 | 1703.8 | 827 | 0 | 70 | 519.2 | 217 | 5274.2 | 90.89 | 262.42 | 1936.4 | 0 | 0 | 0 | 808
07:30 | 3219.5 | 1621.4 | 864.5 | 0 | 73 | 526.4 | 217 | 5278.7 | 169.31 | 261.92 | 1946.4 | 0 | 0 | 0 | 753.5
08:00 | 3183 | 1539 | 902 | 0 | 76 | 533.6 | 217 | 5283.2 | 247.73 | 261.42 | 1956.4 | 0 | 0 | 0 | 699
08:30 | 3197 | 1555.75 | 902.5 | 0 | 70 | 550.92 | 217 | 5280.7 | 319.15 | 235.92 | 2009.8 | 0 | 0 | 0 | 545.5
09:00 | 3211 | 1572.5 | 903 | 0 | 64 | 568.24 | 217 | 5278.2 | 390.57 | 210.42 | 2063.2 | 0 | 0 | 0 | 392
09:30 | 3281.5 | 1594.35 | 903 | 0 | 67 | 569.315 | 217 | 5238.1 | 450.605 | 243.92 | 2135.2 | 0 | 0 | 0 | 214.5
10:00 | 3352 | 1616.2 | 903 | 0 | 70 | 570.39 | 217 | 5198 | 510.64 | 277.42 | 2207.2 | 0 | 0 | 0 | 37
10:30 | 3382 | 1635.1 | 903 | 0 | 72 | 594.69 | 217.5 | 5184.5 | 517.07 | 304.42 | 2240.2 | 0 | 0 | 0.5 | 33.5
11:00 | 3412 | 1654 | 903 | 0 | 74 | 618.99 | 218 | 5171 | 523.5 | 331.42 | 2273.2 | 0 | 0 | 1 | 30
11:30 | 3413.5 | 1596 | 903 | 0 | 75 | 641.715 | 218.5 | 5174.6 | 570.885 | 346.92 | 2272.2 | 0 | 0 | 2 | 445
12:00 | 3415 | 1538 | 903 | 0 | 76 | 664.44 | 219 | 5178.2 | 618.27 | 362.42 | 2271.2 | 0 | 0 | 3 | 860
12:30 | 3432 | 1588 | 902.5 | 0 | 77 | 664.66 | 219 | 5191.7 | 569.68 | 350.92 | 2271.1 | 0 | 0 | 4 | 876
13:00 | 3449 | 1638 | 902 | 0 | 78 | 664.88 | 219 | 5205.2 | 521.09 | 339.42 | 2271 | 0 | 0 | 5 | 892
13:30 | 3395.5 | 1610.5 | 903 | 0 | 80 | 667.89 | 219.5 | 5216.6 | 524.825 | 339.42 | 2273 | 0 | 0 | 5.5 | 997
14:00 | 3342 | 1583 | 904 | 0 | 82 | 670.9 | 220 | 5228 | 528.56 | 339.42 | 2275 | 0 | 0 | 6 | 1102
14:30 | 3360.5 | 1619.5 | 904.5 | 0 | 80 | 672.14 | 221 | 5218.5 | 460.815 | 351.92 | 2285 | 0 | 0 | 4 | 1301.5
15:00 | 3379 | 1656 | 905 | 0 | 78 | 673.38 | 222 | 5209 | 393.07 | 364.42 | 2295 | 0 | 0 | 2 | 1501
15:30 | 3369 | 1626 | 905 | 0 | 79 | 671.88 | 222 | 5207 | 290.215 | 392.42 | 2353.7 | 0 | 0 | 1.5 | 1356.5
16:00 | 3359 | 1596 | 905 | 0 | 80 | 670.38 | 222 | 5205 | 187.36 | 420.42 | 2412.4 | 0 | 0 | 1 | 1212
16:30 | 3355.5 | 1567.5 | 905.5 | 0 | 76 | 667.41 | 222 | 5189.5 | 118.185 | 461.92 | 2516.3 | 0 | 0 | 0.5 | 1124.5
17:00 | 3352 | 1539 | 906 | 0 | 72 | 664.44 | 222 | 5174 | 49.01 | 503.42 | 2620.2 | 0 | 0 | 0 | 1037
17:30 | 3415 | 1585.5 | 905.5 | 0 | 80 | 684.21 | 222 | 5257.6 | 24.505 | 571.42 | 2789.2 | 0 | 0 | 0 | 1160
18:00 | 3478 | 1632 | 905 | 0 | 88 | 703.98 | 222 | 5341.2 | 0 | 639.42 | 2958.2 | 0 | 0 | 0 | 1283
18:30 | 3469 | 1643 | 834 | 0 | 86 | 702.015 | 221.5 | 5359.2 | 0 | 664.92 | 3132.73 | 0 | 0 | 0 | 1357
19:00 | 3460 | 1654 | 763 | 0 | 84 | 700.05 | 221 | 5377.2 | 0 | 690.42 | 3307.26 | 0 | 0 | 0 | 1431
19:30 | 3470 | 1671 | 763 | 0 | 84 | 697.93 | 221 | 5380.2 | 0 | 688.42 | 3320.26 | 150 | 0 | 0 | 1150
20:00 | 3450 | 1674 | 763 | 0 | 68 | 696.85 | 220 | 5425.2 | 0 | 676.42 | 3319.26 | 150 | 0 | 0 | 1135
20:30 | 3475 | 1696 | 763 | 0 | 74 | 699.41 | 219.5 | 5424.2 | 0 | 684.92 | 3250.76 | 165 | 0 | 0 | 1207
21:00 | 3500 | 1718 | 763 | 0 | 80 | 701.97 | 219 | 5423.2 | 0 | 693.42 | 3182.26 | 180 | 0 | 0 | 1279
21:30 | 3480.5 | 1722.75 | 763 | 0 | 80 | 700.62 | 218.5 | 5422.7 | 0 | 668.92 | 3171.76 | 208.5 | 0 | 0 | 1095
22:00 | 3461 | 1727.5 | 763 | 0 | 80 | 699.27 | 218 | 5422.2 | 0 | 644.42 | 3161.26 | 237 | 0 | 0 | 911
22:30 | 3430 | 1663.5 | 765.5 | 0 | 80 | 695.79 | 218 | 5373.7 | 0 | 641.92 | 3065.58 | 238 | 0 | 0 | 1172.5
23:00 | 3399 | 1599.5 | 768 | 0 | 80 | 692.31 | 218 | 5325.2 | 0 | 639.42 | 2969.9 | 239 | 0 | 0 | 1434
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 04-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 54 | 21 | 176 | 156 | 1110 | 472 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 52 | 24 | 146 | 134 | 1064 | 438
2:00 | 54 | 22 | 154 | 134 | 1068 | 440 |  | Import | 0
3:00 | 49 | 21 | 146 | 142 | 1032 | 446
4:00 | 36 | 14 | 120 | 120 | 996 | 396 | Ishurdi-Ghorashal Ckt-2 | Export | 1684436.36
5:00 | 46 | 12 | 130 | 126 | 1020 | 406
6:00 | 67 | 15 | 150 | 114 | 1102 | 448 |  | Import | 0
7:00 | 30 | 7 | 104 | 140 | 962 | 418
8:00 | 80 | 15 | 214 | 152 | 1188 | 458 | Sirajganj-Sreepur Ckt-1 | Export | 1109000
9:00 | 108 | 33 | 230 | 150 | 1334 | 588
10:00 | 108 | 30 | 210 | 152 | 1348 | 684 |  | Import | 0
11:00 | 87 | 25 | 254 | 180 | 1264 | 712
12:00 | 136 | 66 | 316 | 210 | 1542 | 844 | Sirajganj-Sreepur Ckt-2 | Export | 1115000
13:00 | 117 | 55 | 260 | 194 | 1426 | 824
14:00 | 103 | 43 | 240 | 188 | 1352 | 768 |  | Import | 0
15:00 | 103 | 42 | 262 | 188 | 1360 | 784
16:00 | 93 | 43 | 220 | 176 | 1312 | 734 | Gopalganj-Aminbazar Ckt-1 | Export | 14150000
17:00 | 91 | 44 | 230 | 190 | 1304 | 762
18:00 | 82 | 49 | 204 | 214 | 1202 | 752 |  | Import | 0
18:30 | 47 | 43 | 164 | 210 | 1042 | 646
19:00 | 46 | 52 | 134 | 190 | 1066 | 640 | Gopalganj-Aminbazar Ckt-2 | Export | 14170000
19:30 | 40 | 45 | 144 | 210 | 1102 | 652
20:00 | 43 | 44 | 130 | 184 | 1108 | 630 |  | Import | 0
21:00 | 39 | 39 | 140 | 200 | 1068 | 614
22:00 | 40 | 35 | 146 | 186 | 1088 | 570 |  | Total Export | 32228436.36
23:00 | 40 | 35 | 144 | 174 | 1126 | 584 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 16:00 | 354 | 12:00 | Madunaghat | 399 | 05:00 | 392 | 13:00
Amtali | 412 | 08:00 | 406 | 13:00 | Meghnaghat | 389 | 01:00 | 361 | 13:00
Ashuganj | 398 | 5:00 | 368 | 13:00 | Mirsorai | 397 | 00:00 | 385 | 13:00
Bhulta | 391 | 04:00 | 359 | 13:00 | Payra | 413 | 04:00 | 407 | 18:30
Bibiana | 385 | 01:00 | 374 | 13:00 | Rahanpur | 407 | 02:00 | 399 | 11:00
BIPTC | 399 | 03:00 | 392 | 14:00 | Rampal | 396 | 04:00 | 386 | 10:00
Bogura | 395 | 02:00 | 385 | 11:00
Gopalganj | 392 | 01:00 | 378 | 13:00
Kaliakoir | 376 | 04:00 | 351 | 12:00
Korerhat | 397 | 06:00 | 385 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 04:00 | 210 | 13:00 | Hasnabad | 225 | 01:00 | 204 | 12:00
AKSML | 236 | 08:00 | 229 | 13:00 | Hathazari | 235 | 07:00 | 230 | 13:00
Aminbazar | 231 | 06:00 | 212 | 12:00 | Ishurdi | 236 | 01:00 | 223 | 11:00
Ashuganj | 227 | 03:00 | 216 | 13:00 | Jhenaidah | 227 | 01:00 | 213 | 11:00
Ashuganj-400 | 227 | 03:00 | 216 | 13:00 | Kachua | 226 | 06:00 | 219 | 13:00
Baghabari | 232 | 01:00 | 225 | 10:00 | Kaliakoir | 232 | 01:00 | 214 | 12:00
Barapukuria | 227 | 00:00 | 224 | 07:00 | Keranigonj | 228 | 04:00 | 206 | 13:00
Barapukuria-230 | 227 | 00:00 | 224 | 07:00 | Khulna(S) | 226 | 01:00 | 218 | 11:00
Barapukuria(N) | 231 | 01:00 | 225 | 07:00 | Korerhat | 227 | 06:00 | 219 | 12:00
Barishal | 226 | 01:00 | 221 | 13:00 | Madunaghat | 239 | 00:00 | 234 | 12:00
Bheramara | 233 | 01:00 | 221 | 10:00 | Madunaghat-400 | 240 | 00:00 | 235 | 13:00
Bhulta | 224 | 04:00 | 203 | 12:00 | Maniknagar | 222 | 04:00 | 201 | 12:00
Bibiana | 219 | 01:00 | 211 | 12:00 | Meghnaghat | 230 | 04:00 | 210 | 13:00
BIPTC | 236 | 01:00 | 221 | 11:00 | Meghnaghat-400 | 226 | 04:00 | 206 | 13:00
Birulia | 232 | 04:00 | 211 | 13:00 | Mirsorai | 231 | 01:00 | 223 | 13:00
Bogura | 239 | 01:00 | 232 | 11:00 | Naogaon | 226 | 02:00 | 212 | 11:00
Bogura-400 | 239 | 02:00 | 232 | 11:00 | Purbasadipur | 227 | 01:00 | 220 | 07:00
Borhanuddin | 228 | 00:00 | 225 | 13:00 | Rajshahi | 227 | 01:00 | 219 | 11:00
BSRM | 227 | 04:00 | 219 | 13:00 | Rampal | 225 | 01:00 | 217 | 22:00
Charfasson | 230 | 16:00 | 225 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 01:00 | 218 | 13:00 | Rampura | 224 | 04:00 | 200 | 13:00
Cumilla(N) | 222 | 05:00 | 209 | 13:00 | Shikalbaha | 239 | 19:00 | 235 | 13:00
Faridpur | 221 | 01:00 | 214 | 13:00 | Shyampur | 225 | 04:00 | 205 | 13:00
Fenchuganj | 220 | 06:00 | 211 | 13:00 | Siddhirganj | 225 | 04:00 | 210 | 19:30
Feni | 224 | 00:00 | 215 | 13:00 | Sirajgonj | 236 | 01:00 | 230 | 11:00
Ghorashal | 230 | 01:00 | 215 | 11:00 | Sreepur | 224 | 02:00 | 214 | 11:00
Ghorashal-230 | 223 | 01:00 | 205 | 13:00 | Tongi | 223 | 04:00 | 206 | 11:00
Gopalganj | 222 | 01:00 | 216 | 11:00
GPH | 233 | 00:00 | 228 | 13:00
Haripur | 224 | 05:00 | 202 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 04:00 | 121 | 13:00 | Madanganj | 134 | 06:00 | 121 | 13:00
Agargaon | 139 | 04:00 | 124 | 13:00 | Madaripur | 130 | 00:00 | 126 | 11:00
Agrabad | 137 | 00:00 | 132 | 11:00 | Madartek | 138 | 04:00 | 121 | 13:00
AKS | 134 | 00:00 | 131 | 14:00 | Madunaghat | 138 | 00:00 | 134 | 14:00
Aminbazar | 132 | 04:00 | 120 | 12:00 | Magura | 133 | 12:00 | 126 | 11:00
Amnura | 134 | 01:00 | 127 | 11:00 | Mahasthangarh | 136 | 19:00 | 131 | 07:00
Araihazar | 128 | 01:00 | 115 | 12:00 | Maijdee | 127 | 00:00 | 123 | 11:00
Ashuganj | 133 | 01:00 | 125 | 13:00 | Manikganj | 131 | 18:30 | 122 | 13:00
Ashuganj-230 | 135 | 01:00 | 130 | 13:00 | Maniknagar | 138 | 04:00 | 121 | 13:00
Bagerhat | 125 | 12:00 | 119 | 21:00 | Matarbari | 120 | 00:00 | 116 | 11:00
Bajitpur | 128 | 06:00 | 121 | 18:00 | Matuail | 133 | 05:00 | 121 | 12:00
Bakerganj | 133 | 00:00 | 130 | 11:00 | Metrorail_Motijheel | 138 | 04:00 | 121 | 13:00
Bakulia | 137 | 00:00 | 133 | 13:00 | Metrorail_Uttara | 134 | 05:00 | 116 | 13:00
Banani | 139 | 05:00 | 121 | 13:00 | Millgate | 136 | 04:00 | 122 | 13:00
Bangabhaban | 137 | 05:00 | 121 | 13:00 | Mirpur | 132 | 04:00 | 115 | 13:00
Barapukuria | 138 | 00:00 | 132 | 07:00 | Mirzapur | 131 | 01:00 | 119 | 13:00
Barguna | 132 | 00:00 | 129 | 11:00 | Mithapukur | 135 | 19:00 | 128 | 07:00
Barishal | 131 | 00:00 | 129 | 11:00 | MI_Cement | 132.8 | 04:00 | 117 | 13:00
Barishal-230 | 132 | 01:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 136 | 18:30 | 133 | 11:00 | Mogbazar | 139 | 04:00 | 121 | 13:00
Baroirhat | 132 | 00:00 | 126 | 13:00 | Mongla | 125 | 01:00 | 119 | 21:00
Bashundhara | 139 | 04:00 | 121 | 13:00 | Monirampur | 123 | 01:00 | 114 | 21:00
BashundharaCement | 134 | 06:00 | 121 | 13:00 | Motijheel | 137 | 05:00 | 121 | 13:00
Beanibazar | 122 | 01:00 | 116 | 13:00 | Muktagacha | 126 | 09:00 | 115 | 13:00
Benapole | 135 | 01:00 | 116 | 21:00 | Munshiganj | 133 | 03:00 | 120 | 13:00
Bhaluka | 133 | 05:00 | 123 | 19:30 | Muradnagar | 127 | 05:00 | 116 | 12:00
Bhandaria | 128 | 00:00 | 124 | 22:00 | Mymensingh | 127 | 00:00 | 115 | 13:00
Bhangura | 133 | 01:00 | 129 | 07:00 | Nabinagar | 136 | 05:00 | 118 | 12:00
Bheramara | 138 | 01:00 | 130 | 11:00 | Naogaon | 136 | 01:00 | 127 | 11:00
Bheramara(GK) | 137 | 01:00 | 131 | 10:00 | Narail | 134 | 01:00 | 123 | 22:00
Bhulta | 126 | 00:00 | 115 | 11:00 | Narinda | 138 | 04:00 | 121 | 13:00
Bhulta-400 | 129 | 04:00 | 116 | 12:00 | Narshingdi | 131 | 03:00 | 113 | 13:00
Birulia | 136 | 04:00 | 123 | 13:00 | Natore | 134 | 01:00 | 129 | 11:00
Bog-Sherpur | 136 | 01:00 | 131 | 10:00 | Nawabganj | 138 | 05:00 | 123 | 13:00
Bogura | 138 | 18:00 | 134 | 07:00 | Netrakona | 123 | 06:00 | 111 | 00:00
Bogura-230 | 139 | 02:00 | 133 | 11:00 | New | 136 | 01:00 | 124 | 11:00
Brahmanbaria | 130 | 07:00 | 123 | 13:00 | Niamatpur | 133 | 03:00 | 129 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 138 | 03:00 | 124 | 13:00 | Noapara | 128 | 01:00 | 121 | 22:00
Chandina | 129 | 01:00 | 120 | 13:00 | Pabna | 134 | 01:00 | 127 | 11:00
Chandpur | 130 | 00:00 | 126 | 14:00 | Palashbari | 132 | 18:30 | 126 | 11:00
Chandraghona | 138 | 00:00 | 135 | 13:00 | Panchagarh | 139 | 06:00 | 134 | 19:30
Chapai | 133 | 01:00 | 129 | 10:00 | Patiya | 135 | 00:00 | 131 | 11:00
Charsaidpur | 134 | 03:00 | 121 | 13:00 | Patnitala | 133 | 04:00 | 128 | 00:00
Chauddagram | 128 | 00:00 | 122 | 13:00 | Patuakhali | 133 | 00:00 | 130 | 01:00
Chhatak | 124 | 04:00 | 112 | 21:00 | Payra | 135 | 00:00 | 133 | 11:00
Chowmuhani | 127 | 00:00 | 123 | 13:00 | PHP | 131 | 01:00 | 126 | 13:00
Chuadanga | 134 | 01:00 | 123 | 21:00 | Postogola | 133 | 01:00 | 121 | 12:00
Coxsbazar | 121 | 00:00 | 118 | 07:00 | Pubail | 130 | 01:00 | 123 | 08:00
Cumilla(N) | 130 | 05:00 | 120 | 12:00 | Purbachal | 140 | 04:00 | 121 | 13:00
Cumilla(S) | 133 | 05:00 | 121 | 13:00 | Purbasadipur | 138 | 01:00 | 133 | 07:00
Daganbhuiyan | 129 | 00:00 | 124 | 13:00 | Rahanpur | 136 | 01:00 | 132 | 11:00
Daudkandi | 126 | 05:00 | 115 | 12:00 | Rahanpur-400 | 136 | 01:00 | 133 | 07:00
DhakaUniversity | 139 | 03:00 | 122 | 13:00 | Rahim | 134 | 05:00 | 121 | 12:00
Dhamrai | 137 | 04:00 | 120 | 12:00 | Rajbari | 125 | 00:00 | 120 | 22:00
Dhanmondi | 139.5 | 05:00 | 121 | 13:00 | Rajendrapur | 134 | 02:00 | 128 | 11:00
Dohazari | 132 | 04:00 | 127 | 13:00 | Rajshahi | 133 | 01:00 | 126 | 11:00
Faridpur | 127 | 00:00 | 125 | 10:00 | Rajshahi-230 | 132 | 01:00 | 128 | 07:00
Fatullah | 134 | 04:00 | 119 | 12:00 | Ramganj | 126 | 00:00 | 122 | 13:00
Fenchuganj | 130 | 04:00 | 124 | 18:00 | Rampur | 137 | 06:00 | 132 | 10:00
Feni | 130 | 03:00 | 124 | 12:00 | Rampura | 139 | 04:00 | 122 | 13:00
Feni-230 | 130 | 00:00 | 125 | 13:00 | Rangamati | 137 | 03:00 | 130 | 19:30
Ghatail | 124 | 00:00 | 113 | 13:00 | Rangpur | 133 | 18:30 | 127 | 07:00
Ghorashal | 133 | 01:00 | 126 | 09:00 | Ruppur | 136 | 03:00 | 131 | 11:00
Goalpara | 130 | 17:00 | 125 | 07:00 | Saidpur | 136 | 01:00 | 131 | 07:00
Gollamari | 129 | 00:00 | 123 | 21:00 | Santhia | 134 | 03:00 | 128 | 11:00
Gopalganj | 128 | 00:00 | 123 | 11:00 | Satkhira | 129 | 11:00 | 114 | 21:00
Gopalganj-400 | 131 | 00:00 | 127 | 11:00 | Satmasjid | 139 | 05:00 | 122 | 13:00
Gulshan | 137 | 05:00 | 122 | 13:00 | Savar | 131 | 00:00 | 117 | 12:00
Halishahar | 137 | 01:00 | 132 | 13:00 | SevenRings | 133 | 01:00 | 124 | 13:00
Haripur | 134 | 04:00 | 121 | 13:00 | ShahCement | 134 | 03:00 | 121 | 13:00
HaripurSBU | 134 | 05:00 | 121 | 13:00 | Shahjadpur | 132 | 16:00 | 125 | 00:00
Hasnabad | 133 | 07:00 | 118 | 13:00 | Shahjibazar | 129 | 01:00 | 122 | 18:00
Hathazari | 138 | 02:00 | 133 | 12:00 | Shahmirpur | 137 | 00:00 | 133 | 13:00
Hatirjheel | 139 | 04:00 | 121 | 13:00 | Shariatpur | 128 | 00:00 | 123 | 22:00
Ishurdi | 138 | 01:00 | 131 | 11:00 | Sherpur | 125 | 09:00 | 114 | 01:00
Jaldhaka | 133 | 18:30 | 128 | 07:00 | Shikalbaha | 126 | 23:00 | 124 | 00:00
Jamalpur | 128 | 00:00 | 117 | 13:00 | Shikalbaha-230 | 138 | 01:00 | 135 | 11:00
Jashore | 137 | 01:00 | 117 | 22:00 | Shitalakhya | 132.8 | 04:00 | 117 | 13:00
Jhenaidah | 137 | 01:00 | 130 | 21:00 | Sholosohor | 137 | 00:00 | 133 | 11:00
Jhenaidah-230 | 138 | 01:00 | 129 | 21:00 | Shomvuganj | 121 | 04:00 | 113 | 00:00
Joydebpur | 127 | 00:00 | 120 | 09:00 | Shyampur | 132 | 03:00 | 122 | 12:00
Joypurhat | 132 | 06:00 | 128 | 00:00 | Shyampur-230 | 135 | 05:00 | 123 | 13:00
Juldah | 136 | 07:00 | 133 | 11:00 | Siddhirganj | 134 | 03:00 | 120 | 13:00
Kabirpur | 135 | 03:00 | 119 | 12:00 | Sirajganj | 132 | 02:00 | 125 | 11:00
Kachua | 130 | 00:00 | 125 | 12:00 | Sitakunda | 136 | 00:00 | 133 | 15:00
Kaliakoir | 137 | 01:00 | 127 | 12:00 | Sonargaon | 132 | 05:00 | 119 | 12:00
Kaliganj | 137 | 01:00 | 128 | 22:00 | Sreemongol | 128 | 01:00 | 121 | 13:00
Kallyanpur | 130 | 00:00 | 116 | 13:00 | Sreepur | 136 | 02:00 | 129 | 12:00
Kalurghat | 138 | 00:00 | 135 | 11:00 | Srinagar | 138 | 05:00 | 123 | 13:00
Kamrangirchar | 137 | 01:00 | 116 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | 139 | 1:00 | 137 | 16:00 | Sunamganj | 122 | 04:00 | 109 | 13:00
Kasba | 126 | 05:00 | 115 | 12:00 | Sylhet | 123 | 05:00 | 118 | 13:00
Kazla | 138 | 05:00 | 122 | 13:00 | Sylhet_(South) | 124 | 04:00 | 118 | 18:00
Keranigonj | 138 | 01:00 | 124 | 13:00 | Tangail | 127 | 08:00 | 115 | 13:00
Khagrachori | 136 | 08:00 | 133 | 13:00 | Taraganj | 135 | 18:30 | 130 | 11:00
Khulna | 128 | 00:00 | 122 | 21:00 | Tasnim | 131 | 04:00 | 118 | 13:00
Khulna(S) | 131 | 01:00 | 124 | 21:00 | Thakurgaon | 140 | 06:00 | 136 | 19:30
Khulshi | 135 | 00:00 | 131 | 11:00 | TK | 138 | 03:00 | 134 | 17:00
Kishoreganj | 126 | 04:00 | 118 | 13:00 | Tongi | 138 | 04:00 | 125 | 13:00
Kodda | 134 | 18:30 | 120 | 09:00 | Ullahpara | 134 | 02:00 | 128 | 11:00
Korerhat | 134 | 06:00 | 129 | 12:00 | Ullon | 138 | 02:00 | 122 | 13:00
KSRM | 137 | 00:00 | 133 | 11:00 | Uttara | 134 | 01:00 | 121 | 18:00
Kulaura | 128 | 04:00 | 123 | 14:00 | UttaraNew | 134 | 04:00 | 116 | 13:00
Kurigram | 130 | 19:00 | 124 | 07:00 | Zigatola | 138 | 04:00 | 124 | 13:00
Kushtia | 136 | 12:00 | 130 | 10:00
Laksam | 129 | 00:00 | 124 | 12:00
Lakshmipur | 126 | 00:00 | 122 | 12:00
Lalbag | 139 | 07:00 | 123 | 12:00
Lalmonirhat | 128 | 01:00 | 122 | 18:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division