## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15215.93 | 2520 |  | 17849.33
1:00 | 14218.77 | 2719 |  | 17059.77
2:00 | 14050.82 | 2622 |  | 16790.82
3:00 | 13951.82 | 2575 |  | 16642.82
4:00 | 13843.82 | 2460 |  | 16414.82
5:00 | 13764.82 | 2365 |  | 16235.82
6:00 | 13642.51 | 2144 |  | 15882.51
7:00 | 13513.33 | 2023 |  | 15627.33
8:00 | 13539.16 | 1611 |  | 15222.16
9:00 | 14440.88 | 203 |  | 14652.88
10:00 | 14957.98 | 180 |  | 15145.98
11:00 | 14980.76 | 507 |  | 15510.76
12:00 | 15066.41 | 1028 |  | 16140.41
13:00 | 14784.81 | 911 |  | 15736.81
14:00 | 14897.05 | 549 |  | 15471.05
15:00 | 14848.72 | 991 |  | 15884.72
16:00 | 14728.19 | 772 |  | 15535.19
17:00 | 14708.03 | 978 |  | 15730.03
18:00 | 15230.44 | 1554 |  | 16854.44
19:00 | 15580.64 | 1806 |  | 17467.64
19:30 | 15699.21 | 2106 |  | 17900.21
20:00 | 15693.37 | 1761 |  | 17533.37
21:00 | 15603.34 | 1660 |  | 17338.34
22:00 | 15562.15 | 1690 |  | 17328.15
23:00 | 15512.84 | 1659 |  | 17246.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 05-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3292 | 1562.8 | 769 | 0 | 80 | 693.21 | 218 | 5115.1 | 0 | 572.42 | 2675.4 | 238 | 0 | 0 | 2520 | DAILY ENERGY CURVE
00:30 | 3310.5 | 1608.3 | 768.5 | 0 | 80 | 694.08 | 219.5 | 4916.15 | 0 | 554.42 | 2358.9 | 207 | 0 | 0 | 2619.5 | 05-10-2026
01:00 | 3329 | 1653.8 | 768 | 0 | 80 | 694.95 | 221 | 4717.2 | 0 | 536.42 | 2042.4 | 176 | 0 | 0 | 2719
01:30 | 3347.5 | 1687.3 | 768 | 0 | 73 | 691.975 | 220.5 | 4608.7 | 0 | 527.92 | 2046.4 | 163.5 | 0 | 0 | 2670.5 | Energy Generated | 353.9345 |  | MKWHr
02:00 | 3366 | 1720.8 | 768 | 0 | 66 | 689 | 220 | 4500.2 | 0 | 519.42 | 2050.4 | 151 | 0 | 0 | 2622 | Energy not Served | 37.288 |  | MKWHr
02:30 | 3428 | 1774.3 | 768 | 0 | 66 | 640.5 | 220 | 4500.7 | 0 | 519.42 | 2008.9 | 75.5 | 0 | 0 | 2598.5 | Total Energy Requirement | 391.2225 |  | MKWHr
03:00 | 3490 | 1827.8 | 768 | 0 | 66 | 592 | 220 | 4501.2 | 0 | 519.42 | 1967.4 | 0 | 0 | 0 | 2575
03:30 | 3468.5 | 1815.3 | 767.5 | 0 | 66 | 586.5 | 220.5 | 4501.2 | 0 | 505.42 | 1966.9 | 0 | 0 | 0 | 2517.5
04:00 | 3447 | 1802.8 | 767 | 0 | 66 | 581 | 221 | 4501.2 | 0 | 491.42 | 1966.4 | 0 | 0 | 0 | 2460
04:30 | 3436 | 1799.8 | 767.5 | 0 | 66 | 583.5 | 221 | 4500.7 | 0 | 491.42 | 1938.4 | 0 | 0 | 0 | 2412.5
05:00 | 3425 | 1796.8 | 768 | 0 | 66 | 586 | 221 | 4500.2 | 0 | 491.42 | 1910.4 | 0 | 0 | 0 | 2365
05:30 | 3408 | 1790.4 | 768 | 0 | 64 | 579 | 221 | 4499.2 | 0.345 | 491.42 | 1882.3 | 0 | 0 | 0 | 2254.5
06:00 | 3391 | 1784 | 768 | 0 | 62 | 572 | 221 | 4498.2 | 0.69 | 491.42 | 1854.2 | 0 | 0 | 0 | 2144
06:30 | 3398.5 | 1759 | 768 | 0 | 60 | 573.075 | 221 | 4444.2 | 42.525 | 477.42 | 1834.2 | 0 | 0 | 0 | 2083.5
07:00 | 3406 | 1734 | 768 | 0 | 58 | 574.15 | 221 | 4390.2 | 84.36 | 463.42 | 1814.2 | 0 | 0 | 0 | 2023
07:30 | 3387 | 1674 | 768 | 0 | 59 | 570.955 | 220 | 4388.7 | 159.47 | 463.42 | 1835.7 | 0 | 0 | 0 | 1817
08:00 | 3368 | 1614 | 768 | 0 | 60 | 567.76 | 219 | 4387.2 | 234.58 | 463.42 | 1857.2 | 0 | 0 | 0 | 1611
08:30 | 3387 | 1626.9 | 838 | 0 | 59 | 573.07 | 219 | 4521.7 | 336.73 | 463.42 | 1965.2 | 0 | 0 | 0 | 907
09:00 | 3406 | 1639.8 | 908 | 0 | 58 | 578.38 | 219 | 4656.2 | 438.88 | 463.42 | 2073.2 | 0 | 0 | 0 | 203
09:30 | 3449.5 | 1696.3 | 908 | 0 | 57 | 583.49 | 218.5 | 4784.7 | 445.42 | 444.42 | 2112.1 | 0 | 0 | 0 | 191.5
10:00 | 3493 | 1752.8 | 908 | 0 | 56 | 588.6 | 218 | 4913.2 | 451.96 | 425.42 | 2151 | 0 | 0 | 0 | 180
10:30 | 3449.5 | 1715.65 | 907.5 | 0 | 63 | 578.29 | 218 | 4911.7 | 510.81 | 424.42 | 2190.5 | 0 | 0 | 0 | 343.5
11:00 | 3406 | 1678.5 | 907 | 0 | 70 | 567.98 | 218 | 4910.2 | 569.66 | 423.42 | 2230 | 0 | 0 | 0 | 507
11:30 | 3442.5 | 1688.15 | 907.5 | 0 | 70 | 571.05 | 218.5 | 4910.2 | 560.765 | 410.42 | 2244.5 | 0 | 0 | 0 | 767.5
12:00 | 3479 | 1697.8 | 908 | 0 | 70 | 574.12 | 219 | 4910.2 | 551.87 | 397.42 | 2259 | 0 | 0 | 0 | 1028
12:30 | 3437.5 | 1651.3 | 908 | 0 | 69 | 566.875 | 219.5 | 4911.7 | 539.315 | 369.42 | 2252.5 | 0 | 0 | 0.5 | 969.5
13:00 | 3396 | 1604.8 | 908 | 0 | 68 | 559.63 | 220 | 4913.2 | 526.76 | 341.42 | 2246 | 0 | 0 | 1 | 911
13:30 | 3372.5 | 1641.3 | 908 | 0 | 70 | 566.735 | 220 | 4912.2 | 538.775 | 337.92 | 2272 | 0 | 0 | 1.5 | 730
14:00 | 3349 | 1677.8 | 908 | 0 | 72 | 573.84 | 220 | 4911.2 | 550.79 | 334.42 | 2298 | 0 | 0 | 2 | 549
14:30 | 3387 | 1684.9 | 907.5 | 0 | 57 | 572.86 | 220 | 4921.2 | 472.505 | 334.42 | 2314 | 0 | 0 | 1.5 | 770
15:00 | 3425 | 1692 | 907 | 0 | 42 | 571.88 | 220 | 4931.2 | 394.22 | 334.42 | 2330 | 0 | 0 | 1 | 991
15:30 | 3412.5 | 1700.5 | 907.5 | 0 | 51 | 573.835 | 220.5 | 4934.2 | 276 | 334.42 | 2377.5 | 0 | 0 | 0.5 | 881.5
16:00 | 3400 | 1709 | 908 | 0 | 60 | 575.79 | 221 | 4937.2 | 157.78 | 334.42 | 2425 | 0 | 0 | 0 | 772
16:30 | 3393 | 1668 | 908 | 0 | 61 | 571.665 | 220.5 | 4932.7 | 101.325 | 350.42 | 2511.5 | 0 | 0 | 0 | 875
17:00 | 3386 | 1627 | 908 | 0 | 62 | 567.54 | 220 | 4928.2 | 44.87 | 366.42 | 2598 | 0 | 0 | 0 | 978
17:30 | 3376 | 1667.5 | 813.5 | 0 | 69 | 611.9 | 220 | 4941.7 | 22.435 | 481.42 | 2720.78 | 45 | 0 | 0 | 1266
18:00 | 3366 | 1708 | 719 | 0 | 76 | 656.26 | 220 | 4955.2 | 0 | 596.42 | 2843.56 | 90 | 0 | 0 | 1554
18:30 | 3346.5 | 1682.5 | 719 | 0 | 76 | 664.86 | 220.5 | 4952.7 | 0 | 622.42 | 2959.06 | 162 | 0 | 0 | 1680
19:00 | 3327 | 1657 | 719 | 0 | 76 | 673.46 | 221 | 4950.2 | 0 | 648.42 | 3074.56 | 234 | 0 | 0 | 1806
19:30 | 3346 | 1728 | 719 | 0 | 76 | 677.03 | 221 | 4953.2 | 0 | 661.42 | 3082.56 | 235 | 0 | 0 | 2106
20:00 | 3401 | 1684 | 719 | 0 | 72 | 673.19 | 221 | 4931.2 | 0 | 669.42 | 3086.56 | 236 | 0 | 0 | 1761
20:30 | 3382.5 | 1663.5 | 719 | 0 | 71 | 669.325 | 221 | 4915.7 | 0 | 673.42 | 3096.41 | 236.5 | 0 | 0 | 1710.5
21:00 | 3364 | 1643 | 719 | 0 | 70 | 665.46 | 221 | 4900.2 | 0 | 677.42 | 3106.26 | 237 | 0 | 0 | 1660
21:30 | 3378.5 | 1659.5 | 721.5 | 0 | 70 | 668.045 | 221 | 4918.2 | 0 | 638.92 | 3069.58 | 237.5 | 0 | 0 | 1675
22:00 | 3393 | 1676 | 724 | 0 | 70 | 670.63 | 221 | 4936.2 | 0 | 600.42 | 3032.9 | 238 | 0 | 0 | 1690
22:30 | 3380.5 | 1673 | 748.5 | 0 | 70 | 677.475 | 220 | 4948.7 | 0 | 583.92 | 2997.4 | 238 | 0 | 0 | 1674.5
23:00 | 3368 | 1670 | 773 | 0 | 70 | 684.32 | 219 | 4961.2 | 0 | 567.42 | 2961.9 | 238 | 0 | 0 | 1659
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 05-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 60 | 24 | 150 | 120 | 1060 | 528 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 65 | 13 | 150 | 122 | 1214 | 440
2:00 | 54 | 12 | 152 | 96 | 1164 | 442 |  | Import | 0
3:00 | 33 | 8 | 70 | 90 | 1004 | 406
4:00 | 30 | 9 | 68 | 88 | 948 | 400 | Ishurdi-Ghorashal Ckt-2 | Export | 1512145.45
5:00 | 27 | 5 | 58 | 78 | 964 | 390
6:00 | 40 | 10 | 90 | 84 | 1038 | 418 |  | Import | 0
7:00 | 24 | 9 | 52 | 94 | 924 | 394
8:00 | 66 | 21 | 154 | 102 | 1120 | 460 | Sirajganj-Sreepur Ckt-1 | Export | 889000
9:00 | 104 | 23 | 200 | 118 | 1218 | 584
10:00 | 106 | 29 | 222 | 130 | 1206 | 648 |  | Import | 0
11:00 | 98 | 21 | 242 | 136 | 1208 | 626
12:00 | 101 | 22 | 250 | 150 | 1270 | 664 | Sirajganj-Sreepur Ckt-2 | Export | 894000
13:00 | 93 | 13 | 200 | 108 | 1188 | 574
14:00 | 89 | 8 | 208 | 130 | 1174 | 568 |  | Import | 0
15:00 | 84 | 8 | 180 | 112 | 1096 | 550
16:00 | 80 | 13 | 180 | 120 | 1082 | 550 | Gopalganj-Aminbazar Ckt-1 | Export | 13010000
17:00 | 82 | 19 | 200 | 130 | 1102 | 566
18:00 | 60 | 31 | 220 | 166 | 994 | 522 |  | Import | 0
18:30 | 28 | 16 | 130 | 136 | 1018 | 504
19:00 | 47 | 26 | 130 | 140 | 1052 | 532 | Gopalganj-Aminbazar Ckt-2 | Export | 13060000
19:30 | 52 | 27 | 160 | 146 | 1024 | 540
20:00 | 46 | 23 | 130 | 136 | 998 | 506 |  | Import | 0
21:00 | 30 | 13 | 100 | 128 | 946 | 476
22:00 | 44 | 20 | 130 | 138 | 936 | 492 |  | Total Export | 29365145.45
23:00 | 58 | 20 | 100 | 126 | 936 | 492 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9368.42 | 5847.51 | 15215.93 | DAILY GENERATION CURVE
00:30 | 8958.92 | 5758.43 | 14717.35
01:00 | 8549.42 | 5669.35 | 14218.77 | 05-10-2026
01:30 | 8479.42 | 5655.375 | 14134.795
02:00 | 8409.42 | 5641.4 | 14050.82
02:30 | 8483.42 | 5517.9 | 14001.32
03:00 | 8557.42 | 5394.4 | 13951.82
03:30 | 8523.42 | 5374.4 | 13897.82
04:00 | 8489.42 | 5354.4 | 13843.82
04:30 | 8447.42 | 5356.9 | 13804.32
05:00 | 8405.42 | 5359.4 | 13764.82
05:30 | 8354.505 | 5349.16 | 13703.665
06:00 | 8303.59 | 5338.92 | 13642.51
06:30 | 8273.625 | 5304.295 | 13577.92
07:00 | 8243.66 | 5269.67 | 13513.33
07:30 | 8175.61 | 5350.635 | 13526.245
08:00 | 8107.56 | 5431.6 | 13539.16
08:30 | 8414.5 | 5575.52 | 13990.02
09:00 | 8721.44 | 5719.44 | 14440.88
09:30 | 8964.935 | 5734.495 | 14699.43
10:00 | 9208.43 | 5749.55 | 14957.98
10:30 | 9171.915 | 5797.455 | 14969.37
11:00 | 9135.4 | 5845.36 | 14980.76
11:30 | 9178.975 | 5844.61 | 15023.585
12:00 | 9222.55 | 5843.86 | 15066.41
12:30 | 9113.225 | 5812.385 | 14925.61
13:00 | 9003.9 | 5780.91 | 14784.81
13:30 | 9046.1 | 5794.83 | 14840.93
14:00 | 9088.3 | 5808.75 | 14897.05
14:30 | 9083.71 | 5789.175 | 14872.885
15:00 | 9079.12 | 5769.6 | 14848.72
15:30 | 9110.62 | 5677.835 | 14788.455
16:00 | 9142.12 | 5586.07 | 14728.19
16:30 | 9127.7 | 5590.41 | 14718.11
17:00 | 9113.28 | 5594.75 | 14708.03
17:30 | 9309.53 | 5659.705 | 14969.235
18:00 | 9505.78 | 5724.66 | 15230.44
18:30 | 9543.28 | 5862.26 | 15405.54
19:00 | 9580.78 | 5999.86 | 15580.64
19:30 | 9694.78 | 6004.43 | 15699.21
20:00 | 9646.78 | 6046.59 | 15693.37
20:30 | 9624.63 | 6023.725 | 15648.355 |  | Executive Engineer
21:00 | 9602.48 | 6000.86 | 15603.34 |  | Network Operation Division
21:30 | 9589.8 | 5992.945 | 15582.745
22:00 | 9577.12 | 5985.03 | 15562.15
22:30 | 9522.62 | 6014.875 | 15537.495
23:00 | 9468.12 | 6044.72 | 15512.84

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15066.41 | MW | 12:00 Hr. | Energy Generated |  |  | 353.9345 |  | MKWHr.
| Day Peak Demand |  |  | 16140.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 37.288 |  | MKWHr.
| Evening Peak Generation |  |  | 15699.21 | MW | 19:30 Hr. | Energy Demand |  |  | 391.2225 |  | MKWHr.
| Evening Peak Demand |  |  | 17900.21 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.8 |  | °C
| Minimum Generation of the Day |  |  | 13513.33 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 876.34 |  | MMCFD
| Maximum Generation of the Day |  |  | 15699.21 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 8.4785 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.4924 | 0 | 24.0913 | 0 | 0 | 0.13876 | 0 | 0 | 61.7224 | Gas | 123.2285 | Gas | 424939548.7397
| Chattogram Zone |  |  | 5.3762 | 47.6345 | 16.4538 | 0 | 5.278 | 0.13648 | 0 | 0.00528 | 74.8843 | Coal | 115.055 | Coal | 832237389.2523
| Cumilla Zone |  |  | 30.4164 | 0 | 10.1963 | 0 | 0 | 0.40564 | 1.5898 | 0 | 42.6081 | HFO | 68.6701 | HFO | 1432290210.374
| Mymensingh Zone |  |  | 0.09984 | 0 | 4.649 | 0 | 0 | 0.40331 | 0 | 0 | 5.1522 | HSD | 1.7501 | HSD | 35351836.382
| Sylhet Zone |  |  | 31.8921 | 0 | 0 | 0 | 0 | 0.050969 | 0 | 0 | 31.943 | Hydro | 5.278 | Hydro | 527802.9
| Khulna Zone |  |  | 0 | 29.7018 | 0.87854 | 1.7501 | 0 | 0.58032 | 19.6167 | 0 | 52.5275 | Solar | 4.2014 | Solar | 67069787.8216
| Barishal Zone |  |  | 8.121 | 33.7095 | 4.3726 | 0 | 0 | 0.004042 | 0 | 0 | 46.2072 | Import | 35.7461 | Import | 208332802.96
| Rajshahi Zone |  |  | 9.8306 | 0 | 4.1101 | 0 | 0 | 1.3382 | 14.5396 | 0 | 29.8185 | Wind | 0.00528 | Wind | 78355.2
| Rangpur Zone |  |  | 0 | 4.0091 | 3.9184 | 0 | 0 | 1.1437 | 0 | 0 | 9.0712
| Total |  |  | 123.2285 | 115.055 | 68.6701 | 1.7501 | 5.278 | 4.2014 | 35.7461 | 0.00528 | 353.9345
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 424939548.7397 |  | Hydro | 527802.9
|  |  |  | Coal | 832237389.2523 |  | Solar | 67069787.8216
|  |  |  | HFO | 1432290210.374 |  | Import | 208332802.96
|  |  |  | HSD | 35351836.382 |  | Wind | 78355.2
[5 empty] | Total: | 300,08,27,733 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6167 | Peak Hr Flow | 719.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29365145.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.5396 | Peak Hr Flow | 677.03 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1236 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5898 | Peak Hr Flow | 76.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1621 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 35.7461 | Peak Hr Flow | 1472.03 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 283 |  | 6211
|  |  |  | Chattogram |  | 195 |  | 1683
|  |  |  | Cumilla |  | 300 |  | 1684
|  |  |  | Mymensingh |  | 298 |  | 1438
|  |  |  | Sylhet |  | 146 |  | 749
|  |  |  | Khulna |  | 345 |  | 2098
|  |  |  | Barishal |  | 145 |  | 599
|  |  |  | Rajshahi |  | 231 |  | 1679
|  |  |  | Rangpur |  | 163 |  | 1051
|  |  |  | Total |  | 2106 |  | 17192
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116 | 2 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 700 |  |  |  | Total | 193.5
|  |  |  | Total Unavailable Capacity |  |  |  | 893.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Aminbazar-Keraniganj 230kV Ckt-2 is restored.
| 08:06 | 17:44 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Annual Maintenance.
| 08:07 | 17:43 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Annual Maintenance.
| 09:17 | 17:05 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to AM
| 09:18 |  | BIPTC S/S 20DF13 Scheduled S/D Due to For Corrective Maintenance
| 09:19 | 17:27 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph HT Project Work S/D Due to CAF work
| 09:19 | 17:29 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph LT Project Work S/D Due to CAF WORK
|  | 09:21 | Thakurgaon 132/33kV S/S 33kV Bus is restored.
| 09:47 | 13:26 | Pabna- Shahjadpur 132kV Ckt-1 Project Work S/D from Pabna 132/33kV end.
| 09:55 | 17:52 | Nabinagar 132/33kV S/S T-1 LT Project Work S/D Due to Internal testing of SAS by project. | [7 empty] | 20.0MW load
interrup.
| 09:56 | 17:50 | Nabinagar 132/33kV S/S T-1 HT Project Work S/D Due to Internal testing of SAS by project. | [7 empty] | 20.0MW load
interrup.
| 10:12 | 17:55 | Nabinagar 132/33kV S/S Main Bus-1 Project Work S/D Due to Internal testing of SAS by
project.
| 10:14 | 18:06 | Nabinagar 132/33kV S/S Nabinagar-Dhamrai Ckt-2 Project Work S/D Due to Internal testing
of SAS by project.
| 10:42 | 18:03 | Korerhat 400/230/132kV S/S Mirsharai-2 Project Work S/D Due to DFDR Work
|  | 10:48 | Chandpur 132/33kV S/S 412T (T-2) LT is restored.
| 10:48 |  | Chandpur 132/33kV S/S 402T (T-01) LT Scheduled S/D
| 13:33 |  | Bhola Notun Biddut P/S - Choafasson S/S Ckt-1 S/D From Bhola Notun Biddut P/S End.
|  | 15:25 | Khulna (C) S/S Tr-2 415 T HT is restored.
|  | 15:25 | Khulna (C) S/S Tr-2 415 T LT is restored.
| 15:56 |  | Jashore 132/33kV S/S Cap. Bank-2 Tripped showing SPAJ160C relays.
| 16:55 | 18:33 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Forced S/D Due to Oil leakage at T-4 LT
CT
| 16:56 | 18:31 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Forced S/D Due to Oil leakage at T-4 LT
CT
| 05:03 | 06:40 | Barapukuria P/S-Purbasadipur 230 kV Ckt-2 Tripped from Purbasadipur 230/132/33kV end | [7 empty] | 166.0MW load
|  |  | showing Siemens,siprotech relays. | [7 empty] | interrup.
Purbasadipur
230/132/33kV end
| 05:03 |  | Barapukuria(N)-Barapukuria P/S 230kV Ckt-2 Tripped from Barapukuria(N) 230kV end showing | [7 empty] | 131.0MW load
|  |  | 7SL87 (Distance Relay). relays Due to Distance trip. | [7 empty] | interrup.
Barapukuria(N)
230kV end
| 05:03 | 06:11 | Barapukuria(N)-Bogura(west) 230kV Ckt-2 Tripped from Bogura 400/230kV end showing Others
parameter: Lockout Relay KT86.1 Operated Lockout Relay KT86.2 Operated Trip Zone-2
Trip relays.
| 05:03 | 06:05 | Barapukuria P/S-Bogura West 230kV Ckt-1 Tripped from Bogura 400/230kV end showing Lockout | [7 empty] | 132.0MW load
|  |  | Relay KT86.1 Operated Lockout Relay KT86.2 Operated relays Due to Signals | [7 empty] | interrup. Bogura
|  |  | (Main-1) R-Phase Trip Y-Phase Trip B-Phase Trip Zone-2/3 Trip Signals | [7 empty] | 400/230kV end
(Main-2): Trip Zone-2 Trip Distance =M1 116.7 km Current = (R-Phase =982 A, Y-Phase
| 05:03 | 06:40 | Barapukuria P/S-Purbasadipur 230 kV Ckt-1 Tripped from Purbasadipur 230/132/33kV end | [7 empty] | 166.0MW load
|  |  | showing Siprotech siemens relays Due to None | [7 empty] | interrup.
Purbasadipur
230/132/33kV end
| 05:05 |  | Barapukuria 275 MW TPP Unit-3 Tripped
| 06:00 |  | Minimum Generation: 13053 MW.
| 06:20 | 06:33 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing Frequency Supervision relay | [7 empty] | 43.0MW load
|  |  | relays Due to ROCOF Trip | [7 empty] | interrup.
| 06:20 | 06:33 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing Frequency supervision relay | [7 empty] | 42.0MW load
|  |  | relays Due to ROCOF Trip | [7 empty] | interrup.
| 06:25 | 06:49 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing O/C & E/F realy | [7 empty] | 32.0MW load
|  |  | relays. | [7 empty] | interrup.
| 06:25 | 06:52 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing O/C & E/F relay | [7 empty] | 10.0MW load
|  |  | relays. | [7 empty] | interrup.
| 06:25 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Tripped showing O/C Relay &
Distance relay 3 phase relays.
| 07:39 |  | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to Annual maintenance
| 07:39 |  | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to Annual maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 367 | 9043200 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1288327 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 307 | 7431303 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 781200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 3149280 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 799373 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 694716 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 226200 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 518400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 423840 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 5786465 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 145 | 2814768 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1725600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2358720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 138760 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 775800 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 470 | 10935909.09 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 410 | 9337345 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3493200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2859.42 | 61722406.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 18 | 212077.8 | Machine Problem
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115965 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 1171680 | Machine Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5278029 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5060803 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2519127 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 1000295 | plant availability zero
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 706442 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 383040 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 3 | 315360 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 12 | 384000 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 230 | 3540327 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 663947 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2518289 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 324480 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2601927 | Machine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 18 | 428218 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 29241815 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 5280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 940 | 18392727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3416.36 | 74884349.07
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 209 | 4925000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 338 | 8486200 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 310 | 7706000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 705240 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 10 | 600480 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 168 | 4148364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1037468 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 3598036 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 52768 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 107 | 2466511 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 890880 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1589760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 612557 | Fuel Shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 341150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 2086200 | Fuel Shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1283520 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1672320 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 405636 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1795 | 42608090
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 107211 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 99840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 185 | 2755200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1472400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 284500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 363120 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 58320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 276 | 5152191
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 50969 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 954000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 917880 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 16 | 220671.82 | ST synch process going on
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3132000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1967040 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2408030 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 398136 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 242 | 5734000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 276 | 6648000 | STG Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 397 | 9512300 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1348 | 31943026.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 719 | 19616727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 317760 | Fuel Shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 284160 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 276624 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 580320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 235 | 1750090.91 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29701820 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2265.2 | 52527501.91
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 800 | 19410909 | Coal Shortage + Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 2656608 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2720000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7163636.36 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5401020 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1716000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7135000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4042 | -
Barishal Area Total |  |  |  |  | 3326.69 | 1989 | 46207215.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 381264 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | plant availability zero
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 211293 | Fuel Shortage
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 350 | 9830618 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 282732 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1148664 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1240800 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1226592 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 29880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 677.03 | 14539631 | Machine Problem
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 341904 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 585150 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1374.23 | 29818528
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 291055 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 148 | 3718000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1231872 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28571.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2686576 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 169001 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 946080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 376 | 9071155.88
Eastern Grid Total |  |  |  |  | 16961.086 | 9694.78 | 216310062.98
Western Grid Total |  |  |  |  | 11731.125 | 6004.43 | 137624401.15
National Grid Total |  |  |  |  | 28692.211 | 15699.21 | 353934464.13
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-10-2026 | during | 06-10-2026 | during | 06-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 367 | 412 | 412 | 393 | 393 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 314 | 307 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 127 | 141 | 149.36 | 149.36 | 45 | 143 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10.8 | 8 | 24.75 | 24.75 | 12 | 12 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 50 | 52.19 | 52.19 | 24 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 278 | 295 | 300 | 300 | 154 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 123 | 145 | 149 | 149 | 97 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 485 | 470 | 584 | 584 | 526 | 526 | AGC+FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 365 | 410 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2539.22 | 2859.42 | 5576.91 | 5544.91 | 2631.42 | 3154.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 18 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 46 | 42 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 3 | 30 | 42 | 30 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 17 | 12 | 95.1 | 95.1 | 31 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.26 | 0 | 1.43 | 0 | 1.43 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 158 | 230 | 300 | 300 | 212 | 212 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 18 | 163 | 163 | 35 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1195 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 940 | 940 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3249.26 | 3416.36 | 4100.39 | 4172.96 | 3475.43 | 3727.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 212 | 209 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 355 | 338 | 350.01 | 350.01 | 314.01 | 314.01 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 310 | 342.01 | 342.01 | 306.01 | 306.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 34 | 41.65 | 41.65 | 28 | 28 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 30 | 10 | 52.82 | 52.82 | 47 | 47 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 175 | 168 | 195 | 195 | 188 | 188 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 106 | 107 | 163 | 163 | 107 | 107 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 200 | 200 | 17 | 51 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 76 | 84 | 78 | 76 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 16 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 86 | 86 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 70 | 73 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1842 | 1795 | 2363.44 | 2287.44 | 1893.47 | 1901.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-10-2026 | during | 06-10-2026 | during | 06-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 19.35 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.6 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 185 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 67 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.12 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 22 | From 00:00-17:00 hrs 12MW&18:00-24:00 hrs 24MW dis
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 262.07 | 276 | 663.6 | 591.5 | 280.1 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 39 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 16 | 163 | 163 | 147 | 147 | FGMO+ AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 139 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 237 | 242 | 341 | 341 | 240 | 240 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 276 | 276 | 280 | 280 | 280 | 280 | STG Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 395 | 397 | 383 | 383 | 383 | 383 | ps availability is less
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1330 | 1348 | 1634 | 1634 | 1467 | 1467
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 719 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 28 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 235 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.1 | 1234.1 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2224.2 | 2265.2 | 3564.2 | 3484.2 | 2988.1 | 2908.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 800 | 800 | 800 | 800 | 800 | machine problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 112 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 280 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 137 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1883.66 | 1989 | 2008 | 2007 | 1896 | 1895
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 47.81 | 0 | 53.42 | 0 | 53.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 4 | 36 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.89 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 574.12 | 677.03 | 550 | 650 | 550 | 650 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.48 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1340.3 | 1374.23 | 2222.01 | 2101.99 | 1373.63 | 1374.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 154 | 148 | 160 | 160 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 29 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 59 | 0 | 171.96 | 0 | 171.96 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 395.7 | 376 | 614.96 | 408 | 364.96 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 15066.41 | 15699.21 | 22747.51 | 22232 | 16370.11 | 16969.43
Forecast Scenario (06-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15220 |  | 2292 |  | 17620
|  |  |  | 1:00 | 14220 |  | 2473.45 |  | 16810
|  |  |  | 2:00 | 14050 |  | 2339.75 |  | 16500
|  |  |  | 3:00 | 13950 |  | 2196.5 |  | 16250
|  |  |  | 4:00 | 13840 |  | 1995.95 |  | 15930
|  |  |  | 5:00 | 13760 |  | 1690.35 |  | 15530
|  |  |  | 6:00 | 13640 |  | 1289.25 |  | 14990
|  |  |  | 7:00 | 13510 |  | 1231.95 |  | 14800
|  |  |  | 8:00 | 13540 |  | 964.55 |  | 14550
|  |  |  | 9:00 | 14440 |  | 343.8 |  | 14800
|  |  |  | 10:00 | 14960 |  | 105.05 |  | 15070
|  |  |  | 11:00 | 14980 |  | 372.45 |  | 15370
|  |  |  | 12:00 | 15070 |  | 1021.85 |  | 16140
|  |  |  | 13:00 | 14780 |  | 1165.1 |  | 16000
|  |  |  | 14:00 | 14900 |  | 993.2 |  | 15940
|  |  |  | 15:00 | 14850 |  | 1528 |  | 16450
|  |  |  | 16:00 | 14730 |  | 1184.2 |  | 15970
|  |  |  | 17:00 | 14710 |  | 935.9 |  | 15690
|  |  |  | 18:00 | 15600 |  | 200.55 |  | 15810
|  |  |  | 18:30 | 16110 |  | 372.45 |  | 16500
|  |  |  | 19:00 | 16260 |  | 888.15 |  | 17190
|  |  |  | 19:30 | 16450 |  | 744.9 |  | 17230
|  |  |  | 20:00 | 16440 |  | 668.5 |  | 17140
|  |  |  | 21:00 | 16460 |  | 849.95 |  | 17350
|  |  |  | 22:00 | 16410 |  | 754.45 |  | 17200
|  |  |  | 23:00 | 15930 |  | 1088.7 |  | 17070
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 16140.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 849.95
Probable Maximum Demand at Evening Peak: |  |  | 17350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16460.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 356.25 MKWHr. |  | 150 | 60 | 120 | 150 | 40 | 150 | 40 | 80 | 60 | 850
*** This report is generated digitally from Operation Information System (OIS) at 10:49 hrs on 06-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-10-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10543.51 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4543.1 | MW
i) Dhaka area |  |  | 5927.56 |  | MW | i) Khulna area |  |  |  | 1753 | MW
ii) Chattogram area |  |  | 1488.5 |  | MW | ii) Barishal area |  |  |  | 454.5 | MW
iii) Cumilla area |  |  | 1384.45 |  | MW | iii) Rajshahi area |  |  |  | 1447.6 | MW
iv) Mymensingh area |  |  | 1140 |  | MW | iv) Rangpur area |  |  |  | 888 | MW
v) Sylhet area |  |  | 603 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15086.61 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 15:00 | 72 | Hatirjheel | 83 | 12:00 | 143 | PHP | 13 | 13:00
2 | AKSML | 133.3 | 13:00 | 73 | Ishurdi | 76 | 11:00 | 144 | Pabna | 110 | 18:30
3 | Aftabnagar | 46 | 00:00 | 74 | Jaldhaka | 76 | 19:30 | 145 | Palashbari | 94 | 19:30
4 | Agargaon | 142 | 12:00 | 75 | Jamalpur | 130 | 14:00 | 146 | Panchagarh | 56 | 18:30
5 | Agrabad | 76 | 11:00 | 76 | Jashore | 141 | 18:30 | 147 | Patiya | 31 | 18:00
6 | Amnura | 32 | 00:00 | 77 | Jhenaidah | 92 | 18:00 | 148 | Patnitala | 33 | 21:00
7 | Araihazar | 94 | 10:00 | 78 | Joydebpur | 174 | 09:00 | 149 | Patuakhali | 64 | 21:00
8 | Ashuganj | 0.54 | 23:00 | 79 | Joypurhat | 56 | 22:00 | 150 | Payra | 32 | 21:00
9 | Ashuganj-230 | 107 | 00:00 | 80 | Juldah | 17.5 | 00:00 | 151 | Postogola | 66 | 00:00
10 | BSRM | 203 | 18:00 | 81 | KSRM | 28 | 10:00 | 152 | Pubail | 44 | 11:00
11 | Bagerhat | 83 | 21:00 | 82 | Kabirpur | 285 | 17:00 | 153 | Purbachal | 32 | 00:00
12 | Bajitpur | 101 | 00:00 | 83 | Kachua | 84 | 21:00 | 154 | Purbasadipur | 120 | 18:30
13 | Bakerganj | 13.4 | 23:00 | 84 | Kaliganj | 40 | 18:00 | 155 | Rahanpur | 33 | 18:30
14 | Bakulia | 97 | 19:30 | 85 | Kallyanpur | 129 | 00:00 | 156 | Rahim | 45 | 05:00
15 | Banani | 70 | 10:00 | 86 | Kalurghat | 44 | 16:00 | 157 | Rajbari | 74 | 21:00
16 | Bangabhaban | 18 | 11:00 | 87 | Kamrangirchar | 86 | 13:00 | 158 | Rajendrapur | 126 | 17:00
17 | Barapukuria | 56 | 20:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 109 | 22:00
18 | Barguna | 20 | 19:30 | 89 | Kasba | 35 | 02:00 | 160 | Rajshahi-230 | 101 | 12:00
19 | Barishal | 98 | 11:00 | 90 | Kazla | 133 | 12:00 | 161 | Ramganj | 98 | 18:00
20 | Barishal-230 | 96 | 15:00 | 91 | Keranigonj | 89 | 15:00 | 162 | Rampur | 56 | 19:30
21 | Baroaulia | 42 | 10:00 | 92 | Khagrachori | 38 | 18:00 | 163 | Rangamati | 15 | 18:00
22 | Baroirhat | 63 | 18:30 | 93 | Khulna | 56 | 11:00 | 164 | Rangpur | 114 | 19:00
23 | Bashundhara | 220 | 12:00 | 94 | Khulshi | 182 | 17:00 | 165 | Ruppur | 4.8 | 16:00
24 | BashundharaCement | 7 | 09:00 | 95 | Kishoreganj | 136 | 15:00 | 166 | SSM | 11 | 00:00
25 | Beanibazar | 66 | 18:00 | 96 | Kodda | 315 | 19:30 | 167 | Saidpur | 99 | 09:00
26 | Benapole | 71 | 20:00 | 97 | Kulaura | 51 | 18:00 | 168 | Santhia | 36 | 18:00
27 | Bhaluka | 149 | 12:00 | 98 | Kurigram | 56 | 18:30 | 169 | Satkhira | 149 | 21:00
28 | Bhandaria | 55 | 20:00 | 99 | Kushtia | 172 | 21:00 | 170 | Satmasjid | 111 | 12:00
29 | Bhangura | 34 | 09:00 | 100 | Laksam | 36 | 03:00 | 171 | Savar | 225 | 17:00
30 | Bheramara(GK) | 62 | 18:00 | 101 | Lakshmipur | 46 | 19:00 | 172 | SevenRings | 17.68 | 00:00
31 | Bhulta | 193 | 09:00 | 102 | Lalbag | 82 | 13:00 | 173 | ShahCement | 17 | 08:00
32 | Bog-Sherpur | 74 | 09:00 | 103 | Lalmonirhat | 54 | 18:00 | 174 | Shahjadpur | 86 | 18:30
33 | Bogura | 223 | 00:00 | 104 | MI_Cement | 16.2 | 13:00 | 175 | Shahjibazar | 151 | 18:00
34 | Borhanuddin | 65 | 19:00 | 105 | Madanganj | 53 | 10:00 | 176 | Shahmirpur | 61 | 17:00
35 | Brahmanbaria | 134 | 18:00 | 106 | Madaripur | 95 | 19:30 | 177 | Shariatpur | 88 | 18:00
36 | Cantonment | 138 | 12:00 | 107 | Madartek | 94 | 00:00 | 178 | Sherpur | 150 | 23:00
37 | Chandina | 20 | 09:00 | 108 | Madunaghat | 55 | 18:30 | 179 | Shikalbaha | 27 | 11:00
38 | Chandpur | 76 | 21:00 | 109 | Magura | 63 | 22:00 | 180 | Shitalakhya | 86 | 12:00
39 | Chandraghona | 31 | 13:00 | 110 | Mahasthangarh | 73 | 04:00 | 181 | Sholosohor | 48 | 09:00
40 | Chapai | 72 | 22:00 | 111 | Maijdee | 31 | 22:00 | 182 | Shomvuganj | 45 | 08:00
41 | Charfasson | 30 | 23:00 | 112 | Manikganj | 150 | 20:00 | 183 | Shyampur | 140 | 02:00
42 | Charsaidpur | 27 | 12:00 | 113 | Maniknagar | 66 | 00:00 | 184 | Siddhirganj | 133 | 18:00
43 | Chauddagram | 65 | 22:00 | 114 | Matarbari | 49 | 23:00 | 185 | Sirajganj | 124 | 19:00
44 | Chhatak | 33 | 14:00 | 115 | Matuail | 80 | 00:00 | 186 | Sitakunda | 36 | 18:00
45 | Chowmuhani | 146 | 00:00 | 116 | Metrorail_Motijheel | 28 | 17:00 | 187 | Sonargaon | 117 | 16:00
46 | Chuadanga | 113 | 20:00 | 117 | Metrorail_Uttara | 10 | 12:00 | 188 | Sreemongol | 75 | 22:00
47 | Coxsbazar | 143 | 17:00 | 118 | Millgate | 103 | 12:00 | 189 | Sreepur | 136 | 16:00
48 | Cumilla(N) | 160 | 18:30 | 119 | Mirpur | 163 | 18:00 | 190 | Srinagar | 46.5 | 13:00
49 | Cumilla(S) | 159 | 01:00 | 120 | Mirsorai | 56 | 06:00 | 191 | Sunamganj | 52 | 13:00
50 | Daganbhuiyan | 35 | 22:00 | 121 | Mirzapur | 46 | 03:00 | 192 | Sylhet | 135 | 18:00
51 | Daudkandi | 141 | 09:00 | 122 | Mithapukur | 78 | 00:00 | 193 | Sylhet_(South) | 58 | 18:00
52 | DhakaUniversity | 108 | 12:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 112 | 18:00 | 124 | Mogbazar | 106.4 | 01:00 | 195 | Tangail | 172 | 22:00
54 | Dhanmondi | 131 | 12:00 | 125 | Mongla | 44 | 16:00 | 196 | Taraganj | 30 | 09:00
55 | Dohazari | 98 | 22:00 | 126 | Monirampur | 23 | 18:00 | 197 | Tasnim | 44 | 00:00
56 | Faridpur | 190 | 18:30 | 127 | Motijheel | 58 | 12:00 | 198 | Thakurgaon | 108 | 18:30
57 | Fatullah | 122 | 15:00 | 128 | Muktagacha | 40 | 09:00 | 199 | Tongi | 173 | 10:00
58 | Fenchuganj | 39 | 17:00 | 129 | Munshiganj | 116 | 21:00 | 200 | Ullahpara | 37 | 19:30
59 | Feni | 106 | 18:00 | 130 | Muradnagar | 48 | 09:00 | 201 | Ullon | 45 | 00:00
60 | GPH | 18 | 09:00 | 131 | Mymensingh | 169 | 18:30 | 202 | Uttara | 103 | 12:00
61 | Ghatail | 85 | 14:00 | 132 | Nabinagar | 110 | 09:00 | 203 | UttaraNew | 58 | 00:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 113 | 23:00 | 204 | Zigatola | 98 | 13:00
63 | Ghorashal-230 | 99 | 16:00 | 134 | Narail | 63 | 18:00
64 | Goalpara | 39 | 07:00 | 135 | Narinda | 79.5 | 12:00
65 | Gollamari | 112 | 14:00 | 136 | Narshingdi | 192 | 19:00
66 | Gopalganj | 100 | 18:00 | 137 | Natore | 140 | 20:00
67 | Gulshan | 132 | 12:00 | 138 | Nawabganj | 45.1 | 20:00
68 | Halishahar | 140.5 | 15:00 | 139 | Netrakona | 127 | 14:00
69 | HaripurSBU | 139 | 09:00 | 140 | New | 92 | 12:00
70 | Hasnabad | 108 | 00:00 | 141 | Niamatpur | 70 | 18:30
71 | Hathazari | 89 | 18:30 | 142 | Noapara | 40 | 09:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 04:00 | 367 | 10:00 | Madunaghat | 405 | 02:00 | 396 | 11:00
Amtali | 414 | 07:00 | 410 | 13:00 | Meghnaghat | 393 | 05:00 | 376 | 12:00
Ashuganj | 396 | 05:00 | 385 | 11:00 | Mirsorai | 405 | 05:00 | 390 | 12:00
Bhulta | 397 | 05:00 | 372 | 12:00 | Payra | 416 | 05:00 | 411 | 10:00
Bibiana | 388 | 05:00 | 379 | 12:00 | Rahanpur | 409 | 18:00 | 400 | 16:00
BIPTC | 401 | 05:00 | 390 | 17:00 | Rampal | 400 | 01:00 | 389 | 16:00
Bogura | 397 | 05:00 | 387 | 10:00
Gopalganj | 396 | 05:00 | 385 | 11:00
Kaliakoir | 380 | 04:00 | 361 | 10:00
Korerhat | 404 | 03:00 | 390 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 05:00 | 219 | 12:00 | Hasnabad | 229 | 05:00 | 210 | 14:00
AKSML | 241 | 01:00 | 230 | 12:00 | Hathazari | 238 | 05:00 | 232 | 12:00
Aminbazar | 259 | 22:00 | 221 | 10:00 | Ishurdi | 235 | 01:00 | 223 | 16:00
Ashuganj | 233 | 06:00 | 221 | 12:00 | Jhenaidah | 227 | 01:00 | 213 | 16:00
Ashuganj-400 | 233 | 06:00 | 221 | 12:00 | Kachua | 230 | 02:00 | 221 | 12:00
Baghabari | 232 | 04:00 | 225 | 09:00 | Kaliakoir | 236 | 05:00 | 222 | 10:00
Barapukuria | 230 | 08:00 | 224 | 10:00 | Keranigonj | 231 | 05:00 | 215 | 12:00
Barapukuria-230 | 230 | 08:00 | 224 | 10:00 | Khulna(S) | 228 | 01:00 | 219 | 15:00
Barapukuria(N) | 231 | 08:00 | 227 | 16:00 | Korerhat | 231 | 03:00 | 222 | 12:00
Barishal | 229 | 08:00 | 224 | 11:00 | Madunaghat | 240 | 04:00 | 235 | 15:00
Bheramara | 233 | 08:00 | 221 | 10:00 | Madunaghat-400 | 244 | 02:00 | 237 | 13:00
Bhulta | 227 | 04:00 | 211 | 12:00 | Maniknagar | 224 | 04:00 | 210 | 10:00
Bibiana | 223 | 07:00 | 215 | 11:00 | Meghnaghat | 232 | 05:00 | 219 | 12:00
BIPTC | 236 | 08:00 | 221 | 16:00 | Meghnaghat-400 | 228 | 03:00 | 214 | 12:00
Birulia | 234 | 04:00 | 220 | 10:00 | Mirsorai | 235 | 05:00 | 227 | 10:00
Bogura | 239 | 08:00 | 233 | 10:00 | Naogaon | 225 | 00:00 | 214 | 10:00
Bogura-400 | 239 | 08:00 | 233 | 10:00 | Purbasadipur | 227 | 08:00 | 219 | 00:00
Borhanuddin | 230 | 07:00 | 227 | 10:00 | Rajshahi | 231 | 02:00 | 220 | 16:00
BSRM | 231 | 01:00 | 223 | 10:00 | Rampal | 227 | 01:00 | 219 | 15:00
Charfasson | 231 | 08:00 | 228 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 00:00 | 223 | 12:00 | Rampura | 226 | 04:00 | 208 | 12:00
Cumilla(N) | 226 | 04:00 | 215 | 11:00 | Shikalbaha | 242 | 02:00 | 236 | 11:00
Faridpur | 224 | 01:00 | 218 | 11:00 | Shyampur | 228 | 04:00 | 214 | 12:00
Fenchuganj | 222 | 04:00 | 216 | 12:00 | Siddhirganj | 225 | 01:00 | 211 | 12:00
Feni | 228 | 01:00 | 220 | 10:00 | Sirajgonj | 237 | 05:00 | 231 | 10:00
Ghorashal | 230 | 01:00 | 215 | 08:00 | Sreepur | 227 | 05:00 | 218 | 12:00
Ghorashal-230 | 225 | 05:00 | 207 | 10:00 | Tongi | 226 | 04:00 | 210 | 10:00
Gopalganj | 225 | 01:00 | 219 | 11:00
GPH | 238 | 02:00 | 231 | 10:00
Haripur | 227 | 05:00 | 211 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 04:00 | 126 | 12:00 | Madanganj | 131 | 20:00 | 126 | 10:00
Agargaon | 141 | 05:00 | 130 | 12:00 | Madaripur | 132 | 01:00 | 129 | 15:00
Agrabad | 139 | 01:00 | 132 | 14:00 | Madartek | 138 | 04:00 | 125 | 12:00
AKS | 136 | 01:00 | 131 | 15:00 | Madunaghat | 139 | 04:00 | 135 | 15:00
Aminbazar | 134 | 04:00 | 125 | 10:00 | Magura | 135 | 08:00 | 125 | 16:00
Amnura | 133 | 01:00 | 127 | 12:00 | Mahasthangarh | 135 | 08:00 | 131 | 10:00
Araihazar | 130 | 04:00 | 121 | 10:00 | Maijdee | 129 | 01:00 | 125 | 10:00
Ashuganj | 136 | 02:00 | 130 | 12:00 | Manikganj | 133 | 18:00 | 126 | 00:00
Ashuganj-230 | 137 | 04:00 | 134 | 00:00 | Maniknagar | 140 | 04:00 | 128 | 12:00
Bagerhat | 127 | 08:00 | 122 | 11:00 | Matarbari | 124 | 01:00 | 114 | 17:00
Bajitpur | 129 | 05:00 | 125 | 08:00 | Matuail | 135 | 03:00 | 125 | 12:00
Bakerganj | 135 | 18:30 | 131 | 04:00 | Metrorail_Motijheel | 140 | 04:00 | 128 | 12:00
Bakulia | 139 | 19:00 | 134 | 12:00 | Metrorail_Uttara | 136 | 03:00 | 122 | 12:00
Banani | 139 | 03:00 | 126 | 10:00 | Millgate | 137 | 03:00 | 125 | 10:00
Bangabhaban | 140 | 05:00 | 127 | 12:00 | Mirpur | 133 | 02:00 | 124 | 10:00
Barapukuria | 140 | 08:00 | 132 | 10:00 | Mirzapur | 134 | 01:00 | 127 | 09:00
Barguna | 134 | 07:00 | 8 | 01:00 | Mithapukur | 133 | 01:00 | 129 | 10:00
Barishal | 133 | 01:00 | 130 | 12:00 | MI_Cement | 135 | 02:00 | 122 | 12:00
Barishal-230 | 134 | 08:00 | 130 | 10:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 138 | 07:00 | 132 | 22:00 | Mogbazar | 140 | 04:00 | 125 | 12:00
Baroirhat | 134 | 01:00 | 129 | 10:00 | Mongla | 126 | 01:00 | 121 | 16:00
Bashundhara | 140 | 05:00 | 125 | 10:00 | Monirampur | 126 | 01:00 | 117 | 21:00
BashundharaCement | 131 | 20:00 | 126 | 12:00 | Motijheel | 140 | 05:00 | 127 | 12:00
Beanibazar | 124 | 07:00 | 118 | 18:00 | Muktagacha | 133 | 00:00 | 123 | 06:00
Benapole | 135 | 08:00 | 118 | 13:00 | Munshiganj | 134 | 01:00 | 125 | 10:00
Bhaluka | 134 | 07:00 | 127 | 12:00 | Muradnagar | 129 | 01:00 | 121 | 10:00
Bhandaria | 130 | 07:00 | 126 | 10:00 | Mymensingh | 136 | 00:00 | 121 | 09:00
Bhangura | 134 | 06:00 | 128 | 11:00 | Nabinagar | 134 | 01:00 | 121 | 12:00
Bheramara | 138 | 08:00 | 130 | 10:00 | Naogaon | 138 | 18:00 | 129 | 18:30
Bheramara(GK) | 137 | 01:00 | 130 | 10:00 | Narail | 134 | 03:00 | 124 | 23:00
Bhulta | 129 | 07:00 | 120 | 12:00 | Narinda | 140 | 04:00 | 128 | 12:00
Bhulta-400 | 131 | 03:00 | 122 | 10:00 | Narshingdi | 134 | 01:00 | 120 | 12:00
Birulia | 137 | 03:00 | 129 | 10:00 | Natore | 135 | 01:00 | 129 | 10:00
Bog-Sherpur | 136 | 18:00 | 131 | 10:00 | Nawabganj | 139 | 05:00 | 130 | 10:00
Bogura | 139 | 17:00 | 133 | 10:00 | Netrakona | 124 | 05:00 | 115 | 09:00
Bogura-230 | 139 | 18:00 | 134 | 10:00 | New | 138 | 03:00 | 126 | 10:00
Brahmanbaria | 134 | 06:00 | 126 | 12:00 | Niamatpur | 134 | 18:00 | 130 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 140 | 03:00 | 129 | 12:00 | Noapara | 130 | 01:00 | 123 | 15:00
Chandina | 132 | 02:00 | 124 | 12:00 | Pabna | 135 | 18:00 | 128 | 10:00
Chandpur | 132 | 01:00 | 128 | 10:00 | Palashbari | 132 | 18:00 | 127 | 10:00
Chandraghona | 140 | 02:00 | 136 | 10:00 | Panchagarh | 140 | 04:00 | 132 | 18:30
Chapai | 133 | 01:00 | 128 | 10:00 | Patiya | 137 | 02:00 | 131 | 12:00
Charsaidpur | 136 | 04:00 | 126 | 10:00 | Patnitala | 133 | 18:00 | 129 | 09:00
Chauddagram | 131 | 02:00 | 125 | 12:00 | Patuakhali | 134 | 18:00 | 130 | 18:30
Chhatak | 121 | 01:00 | 115 | 14:00 | Payra | 136 | 01:00 | 134 | 11:00
Chowmuhani | 127 | 00:00 | 125 | 12:00 | PHP | 134 | 01:00 | 129 | 10:00
Chuadanga | 134 | 01:00 | 123 | 23:00 | Postogola | 136 | 04:00 | 125 | 12:00
Coxsbazar | 123 | 12:00 | 118 | 18:00 | Pubail | 135 | 04:00 | 123 | 10:00
Cumilla(N) | 130 | 01:00 | 124 | 12:00 | Purbachal | 139 | 03:00 | 125 | 12:00
Cumilla(S) | 132 | 03:00 | 124 | 12:00 | Purbasadipur | 138 | 08:00 | 133 | 18:30
Daganbhuiyan | 132 | 02:00 | 127 | 10:00 | Rahanpur | 136 | 18:00 | 133 | 10:00
Daudkandi | 129 | 01:00 | 118 | 10:00 | Rahanpur-400 | 137 | 18:00 | 133 | 12:00
DhakaUniversity | 139 | 05:00 | 126 | 12:00 | Rahim | 135 | 03:00 | 126 | 10:00
Dhamrai | 136 | 03:00 | 125 | 10:00 | Rajbari | 128 | 08:00 | 123 | 10:00
Dhanmondi | 139 | 06:00 | 127 | 12:00 | Rajendrapur | 137 | 07:00 | 130 | 10:00
Dohazari | 133 | 01:00 | 127 | 13:00 | Rajshahi | 133 | 18:00 | 126 | 15:00
Faridpur | 130 | 01:00 | 126 | 00:00 | Rajshahi-230 | 133 | 08:00 | 127 | 10:00
Fatullah | 136 | 05:00 | 122 | 10:00 | Ramganj | 129 | 01:00 | 124 | 10:00
Fenchuganj | 131 | 06:00 | 127 | 10:00 | Rampur | 139 | 01:00 | 133 | 10:00
Feni | 132 | 02:00 | 126 | 12:00 | Rampura | 139 | 01:00 | 126 | 12:00
Feni-230 | 133 | 01:00 | 128 | 10:00 | Rangamati | 139 | 01:00 | 135 | 10:00
Ghatail | 130 | 00:00 | 119 | 09:00 | Rangpur | 133 | 06:00 | 129 | 00:00
Ghorashal | 136 | 07:00 | 125 | 08:00 | Ruppur | 138 | 08:00 | 131 | 09:00
Goalpara | 132 | 01:00 | 125 | 16:00 | Saidpur | 137 | 08:00 | 132 | 01:00
Gollamari | 132 | 01:00 | 125 | 15:00 | Santhia | 134 | 00:00 | 129 | 09:00
Gopalganj | 130 | 01:00 | 125 | 11:00 | Satkhira | 126 | 08:00 | 117 | 21:00
Gopalganj-400 | 132 | 01:00 | 129 | 10:00 | Satmasjid | 140 | 04:00 | 128 | 01:00
Gulshan | 138 | 04:00 | 126 | 12:00 | Savar | 133 | 04:00 | 123 | 12:00
Halishahar | 139 | 01:00 | 133 | 12:00 | SevenRings | 136 | 05:00 | 126 | 10:00
Haripur | 136 | 04:00 | 126 | 10:00 | ShahCement | 136 | 04:00 | 126 | 10:00
HaripurSBU | 136 | 04:00 | 126 | 10:00 | Shahjadpur | 132 | 04:00 | 126 | 10:00
Hasnabad | 136 | 06:00 | 125 | 12:00 | Shahjibazar | 134 | 05:00 | 125 | 18:00
Hathazari | 139 | 01:00 | 135 | 14:00 | Shahmirpur | 138 | 02:00 | 134 | 10:00
Hatirjheel | 139 | 04:00 | 126 | 12:00 | Shariatpur | 130 | 01:00 | 126 | 09:00
Ishurdi | 138 | 08:00 | 131 | 16:00 | Sherpur | 136 | 00:00 | 117 | 02:00
Jaldhaka | 133 | 01:00 | 127 | 18:30 | Shikalbaha | 127 | 21:00 | 123 | 13:00
Jamalpur | 139 | 00:00 | 122 | 02:00 | Shikalbaha-230 | 140 | 02:00 | 135 | 10:00
Jashore | 137 | 08:00 | 120 | 13:00 | Shitalakhya | 135 | 05:00 | 122 | 12:00
Jhenaidah | 137 | 00:00 | 128 | 16:00 | Sholosohor | 139 | 01:00 | 135 | 10:00
Jhenaidah-230 | 138 | 02:00 | 128 | 16:00 | Shomvuganj | 126 | 06:00 | 107 | 16:00
Joydebpur | 132 | 03:00 | 122 | 11:00 | Shyampur | 135 | 05:00 | 128 | 00:00
Joypurhat | 134 | 18:00 | 128 | 10:00 | Shyampur-230 | 137 | 04:00 | 128 | 12:00
Juldah | 140 | 01:00 | 134 | 14:00 | Siddhirganj | 136 | 05:00 | 126 | 10:00
Kabirpur | 137 | 18:00 | 120 | 09:00 | Sirajganj | 132 | 18:00 | 126 | 10:00
Kachua | 131 | 02:00 | 126 | 12:00 | Sitakunda | 139 | 01:00 | 134 | 12:00
Kaliakoir | 139 | 01:00 | 132 | 09:00 | Sonargaon | 133 | 07:00 | 124 | 10:00
Kaliganj | 137 | 01:00 | 127 | 16:00 | Sreemongol | 130 | 01:00 | 124 | 18:00
Kallyanpur | 134 | 05:00 | 124 | 10:00 | Sreepur | 138 | 05:00 | 132 | 10:00
Kalurghat | 138 | 01:00 | 137 | 00:00 | Srinagar | 139 | 04:00 | 130 | 10:00
Kamrangirchar | 139 | 01:00 | 122 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 119 | 06:00 | 112 | 13:00
Kasba | 129 | 02:00 | 120 | 10:00 | Sylhet | 124 | 07:00 | 120 | 12:00
Kazla | 140 | 06:00 | 127 | 12:00 | Sylhet_(South) | 125 | 05:00 | 120 | 18:00
Keranigonj | 140 | 05:00 | 130 | 12:00 | Tangail | 130 | 00:00 | 122 | 09:00
Khagrachori | 138 | 01:00 | 134 | 10:00 | Taraganj | 135 | 05:00 | 131 | 10:00
Khulna | 130 | 07:00 | 124 | 14:00 | Tasnim | 133 | 04:00 | 18 | 20:00
Khulna(S) | 132 | 01:00 | 126 | 11:00 | Thakurgaon | 141 | 04:00 | 134 | 18:30
Khulshi | 137 | 07:00 | 132 | 12:00 | TK | 138 | 06:00 | 135 | 00:00
Kishoreganj | 129 | 06:00 | 123 | 12:00 | Tongi | 137 | 04:00 | 128 | 10:00
Kodda | 138 | 18:00 | 122 | 12:00 | Ullahpara | 133 | 06:00 | 128 | 09:00
Korerhat | 136 | 01:00 | 131 | 10:00 | Ullon | 139 | 01:00 | 126 | 12:00
KSRM | 138 | 18:30 | 134 | 10:00 | Uttara | 137 | 04:00 | 123 | 10:00
Kulaura | 130 | 06:00 | 125 | 12:00 | UttaraNew | 136 | 03:00 | 122 | 12:00
Kurigram | 130 | 06:00 | 126 | 00:00 | Zigatola | 140 | 04:00 | 129 | 13:00
Kushtia | 137 | 08:00 | 128 | 16:00
Laksam | 130 | 01:00 | 126 | 00:00
Lakshmipur | 129 | 02:00 | 124 | 10:00
Lalbag | 139 | 07:00 | 129 | 12:00
Lalmonirhat | 129 | 12:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-10-2026 | [28 empty] | Date: | 05-10-2026 | [28 empty] | Date: | 05-10-2026 | [28 empty] | Date: | 05-10-2026 | [28 empty] | Date: | 05-10-2026 | [16 empty] | Date: | 05-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 35 | 98 | 129 | 196 | 55 | 55 | 162 | 0 | 0 | 345 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 380 | 107 | 212 | 40 | 0 | 0 | 51 | 44 | 36 | 12 | 12 | 0 | 218 | 110 | 25 | 1055 | 18 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 299 | 275 | 44 | 30 | 190 | 28 | 66 | 106 | 35 | 65 | 19 | 86 | 80 | 52.2 | 0 | 0 | 240 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 86 | 0 | 164 | 0 | 0 | 0 | 24 | 9368.42 | 769 | 0 | 28 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 1229.1 | 17 | 0 | 0 | 693.21 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 153 | 47 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 180 | 0 | 800 | 300 | 54 | 5847.51 | 15215.93 | 106.57
01:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 35 | 92 | 129 | 196 | 40 | 35 | 72 | 0 | 0 | 395 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 378 | 109 | 68 | 23 | 0 | 0 | 51 | 44 | 0 | 12 | 12 | 0 | 221 | 110 | 30 | 650 | 18 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 315 | 290 | 44 | 30 | 188 | 28 | 69 | 106 | 34 | 60 | 19 | 86 | 80 | 52.2 | 0 | 0 | 238 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8549.42 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 694.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 47 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5669.35 | 14218.77 | 106.56
02:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 35 | 91 | 129 | 196 | 55 | 30 | 72 | 0 | 0 | 410 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 410 | 107 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0 | 220 | 110 | 34 | 430 | 16 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 187 | 0 | 325 | 300 | 44 | 31 | 198 | 28 | 68 | 106 | 34 | 72 | 19 | 86 | 66 | 52.2 | 0 | 0 | 234 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 8 | 8409.42 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 47 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5641.4 | 14050.82 | 106.56
03:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35 | 35 | 91 | 129 | 196 | 55 | 35 | 72 | 0 | 0 | 425 | 0 | 35 | 320 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 490 | 109 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0 | 220 | 110 | 33 | 430 | 18 | 0 | 50 | 0 | 105 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 187 | 0 | 360 | 335 | 44 | 43 | 217 | 27 | 69 | 106 | 34 | 0 | 19 | 86 | 66 | 52.2 | 0 | 0 | 235 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8557.42 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 49 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5394.4 | 13951.82 | 106.55
04:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 35 | 35 | 91 | 129 | 196 | 55 | 35 | 72 | 0 | 0 | 385 | 0 | 35 | 317 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 500 | 107 | 68 | 20 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0 | 221 | 110 | 37 | 430 | 18 | 0 | 50 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 187 | 0 | 344 | 320 | 44 | 44 | 196 | 27 | 69 | 106 | 34 | 0 | 19 | 86 | 66 | 52.2 | 0 | 0 | 235 | 400 | 281 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 10 | 0 | 0 | 12 | 8489.42 | 767 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 48 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5354.4 | 13843.82 | 106.55
05:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 35 | 91 | 129 | 196 | 55 | 0 | 72 | 0 | 0 | 385 | 0 | 17 | 320 | 0 | 0 | 0 | 143.42 | 10.8 | 22 | 0 | 490 | 107 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0 | 221 | 110 | 39 | 430 | 16 | 0 | 50 | 0 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 150 | 187 | 0 | 348 | 325 | 44 | 46 | 192 | 27 | 69 | 106 | 34 | 0 | 19 | 86 | 66 | 52.2 | 0 | 0 | 235 | 400 | 256 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 0 | 67 | 12 | 0 | 0 | 12 | 8405.42 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 48 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5359.4 | 13764.82 | 106.54
06:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35 | 35 | 91 | 129 | 196 | 55 | 0 | 72 | 0 | 0 | 385 | 0 | 17 | 320 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 475 | 109 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0.01 | 221 | 100 | 38 | 435 | 18 | 0 | 50 | 0 | 105 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 187 | 0 | 350 | 320 | 44 | 46 | 176 | 27 | 63 | 106 | 34 | 0 | 19 | 86 | 62 | 8 | 0 | 0 | 237 | 400 | 256 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 0.16 | 67 | 0 | 0 | 0 | 12 | 8303.59 | 768 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1234.2 | 17 | 0 | 0 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.02 | 156 | 42 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 54 | 5338.92 | 13642.51 | 106.54
07:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 35 | 91 | 129 | 196 | 55 | 0 | 54 | 0 | 0 | 380 | 0 | 17 | 311 | 0 | 0 | 3 | 143.42 | 12 | 22 | 0 | 470 | 107 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 0.59 | 221 | 110 | 33 | 435 | 18 | 0 | 50 | 0 | 105 | 221 | 0 | 0 | 0 | 1224 | 3 | 150 | 170 | 0 | 335 | 310 | 44 | 26 | 198 | 27 | 51 | 106 | 33 | 0 | 19 | 86 | 58 | 8 | 8 | 0 | 239 | 400 | 256 | 40 | 40 | 0 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 59 | 0 | 67 | 10 | 0.2 | 4.45 | 12 | 8243.66 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1234.2 | 17 | 0 | 0 | 574.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 9.05 | 11 | 0 | 0 | 6.72 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.66 | 157 | 0 | 115 | 3 | 34 | 0 | 0 | 0 | 0.6 | 23 | 0.09 | 110 | 240 | 115 | 220 | 0 | 800 | 300 | 54 | 5269.67 | 13513.33 | 106.53
08:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 35 | 91 | 129 | 196 | 55 | 0 | 54 | 0 | 0 | 365 | 0 | 17 | 300 | 0 | 0 | 9 | 143.42 | 12 | 22 | 0 | 405 | 107 | 68 | 19 | 0 | 0 | 34 | 44 | 0 | 12 | 12 | 1.17 | 219 | 110 | 15 | 435 | 18 | 0 | 50 | 0 | 105 | 221 | 0 | 0 | 0 | 1224 | 9 | 145 | 158 | 0 | 327 | 295 | 44 | 20 | 194 | 28 | 51 | 107 | 34 | 2 | 19 | 86 | 60 | 8 | 6 | 0 | 235 | 400 | 276 | 40 | 40 | 0 | 2 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 59 | 0 | 67 | 10 | 0.7 | 15.27 | 12 | 8107.56 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1234.2 | 17 | 0 | 0 | 567.76 | 0 | 0 | 0 | 35 | 10 | 0 | 0 | 0 | 52.2 | 33.47 | 33 | 0 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.56 | 158 | 0 | 115 | 7 | 34 | 0 | 0 | 0 | 0 | 65 | 0.23 | 110 | 236 | 115 | 220 | 0 | 800 | 300 | 54 | 5431.6 | 13539.16 | 106.53
09:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 35 | 91 | 129 | 196 | 55 | 0 | 54 | 0 | 0 | 360 | 0 | 17 | 320 | 0 | 0 | 15 | 143.42 | 10.8 | 22 | 0 | 470 | 109 | 154 | 19 | 0 | 0 | 34 | 44 | 36 | 12 | 12 | 2.32 | 219 | 110 | 0 | 730 | 18 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1162 | 14 | 145 | 158 | 0 | 354 | 320 | 44 | 20 | 211 | 25 | 51 | 107 | 32 | 58 | 0 | 86 | 58 | 8 | 46 | 0 | 236 | 400 | 276 | 40 | 40 | 0 | 7 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 59 | 12.41 | 72 | 12 | 1.2 | 28.29 | 12 | 8721.44 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1234.2 | 17 | 0 | 0 | 578.38 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 48.6 | 58 | 0 | 0 | 33.76 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 3.1 | 154 | 0 | 115 | 5 | 34 | 0 | 0 | 0 | 0.8 | 110 | 0.4 | 110 | 276 | 114 | 220 | 0 | 800 | 300 | 54 | 5719.44 | 14440.88 | 106.52
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17 | 35 | 95 | 129 | 196 | 55 | 35 | 54 | 0 | 0 | 410 | 0 | 17 | 318 | 0 | 0 | 23 | 143.42 | 10.8 | 22 | 0 | 500 | 107 | 155 | 20 | 0 | 0 | 34 | 42 | 36 | 12 | 12 | 2.9 | 218 | 110 | 0 | 940 | 16 | 0 | 50 | 8 | 105 | 216 | 0 | 0 | 0 | 1195 | 17 | 150 | 167 | 0 | 357 | 330 | 44 | 27 | 214 | 27 | 51 | 107 | 33 | 70 | 16 | 86 | 56 | 8 | 54 | 0 | 240 | 397 | 276 | 40 | 40 | 0 | 8 | 16 | 0 | 80 | 0 | 139 | 0 | 100 | 0 | 59 | 15.9 | 113 | 12 | 1.6 | 35.81 | 12 | 9208.43 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1234.2 | 17 | 0 | 0 | 588.6 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 34 | 40.23 | 76 | 0 | 0 | 44.24 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.14 | 157 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 3.6 | 55 | 0.54 | 110 | 307 | 113 | 220 | 0 | 800 | 280 | 54 | 5749.55 | 14957.98 | 106.52
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 35 | 35 | 118 | 127 | 235 | 55 | 35 | 54 | 0 | 0 | 375 | 0 | 17 | 304 | 0 | 0 | 17 | 143.42 | 10.5 | 22 | 0 | 465 | 109 | 156 | 19 | 0 | 0 | 34 | 42 | 36 | 12 | 12 | 3.08 | 218 | 110 | 0 | 940 | 16 | 0 | 50 | 8 | 105 | 216 | 0 | 0 | 0 | 1193 | 19 | 150 | 167 | 0 | 335 | 305 | 44 | 30 | 200 | 26 | 40 | 107 | 34 | 68 | 13 | 86 | 70 | 8 | 64 | 0 | 236 | 398 | 276 | 40 | 40 | 0 | 6 | 16 | 0 | 80 | 0 | 140 | 0 | 100 | 0 | 58 | 12.52 | 115 | 10 | 0.8 | 43.08 | 12 | 9135.4 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1234.2 | 0 | 0 | 0 | 567.98 | 0 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 34 | 30.28 | 59 | 0 | 0 | 55.52 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.83 | 156 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 4.2 | 168 | 0.35 | 110 | 307 | 113 | 220 | 0 | 800 | 280 | 54 | 5845.36 | 14980.76 | 106.51
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35 | 0 | 123 | 127 | 278 | 55 | 35 | 54 | 0 | 0 | 365 | 0 | 17 | 314 | 0 | 0 | 24 | 143.42 | 10.8 | 22 | 0 | 485 | 107 | 158 | 17 | 0 | 0 | 0 | 46 | 36 | 12 | 12 | 2.26 | 219 | 110 | 0 | 940 | 16 | 0 | 50 | 8 | 105 | 216 | 0 | 0 | 0 | 1195 | 0 | 150 | 175 | 0 | 355 | 345 | 44 | 30 | 212 | 30 | 51 | 106 | 34 | 70 | 11 | 86 | 70 | 8 | 65 | 0 | 237 | 395 | 276 | 40 | 40 | 0 | 4 | 15 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 19.35 | 115 | 10 | 1.6 | 46.12 | 12 | 9222.55 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1234.2 | 0 | 0 | 0 | 574.12 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 4 | 34 | 47.81 | 100 | 0 | 0 | 56.48 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.89 | 154 | 0 | 115 | 35 | 29 | 0 | 0 | 0 | 3.7 | 59 | 0.66 | 110 | 307 | 112 | 220 | 0 | 800 | 280 | 54 | 5843.86 | 15066.41 | 106.51
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 0 | 114 | 131 | 278 | 55 | 35 | 54 | 0 | 0 | 365 | 0 | 17 | 290 | 0 | 0 | 20 | 143.42 | 10.8 | 22 | 0 | 420 | 109 | 158 | 12 | 0 | 1 | 0 | 42 | 36 | 12 | 12 | 2.57 | 220 | 110 | 0 | 940 | 18 | 0 | 50 | 8 | 105 | 218 | 0 | 0 | 0 | 1195 | 17 | 150 | 186 | 0 | 316 | 345 | 44 | 30 | 192 | 27 | 51 | 108 | 34 | 72 | 11 | 86 | 68 | 8 | 60 | 0 | 238 | 396 | 276 | 40 | 40 | 0 | 8 | 15 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 57 | 15.52 | 115 | 10 | 1.7 | 34.89 | 12 | 9003.9 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1234.2 | 0 | 0 | 0 | 559.63 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 23.96 | 67 | 0 | 0 | 49.17 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.77 | 157 | 0 | 115 | 33 | 34 | 0 | 0 | 0 | 2.6 | 103 | 0.58 | 110 | 307 | 113 | 180 | 0 | 800 | 280 | 54 | 5780.91 | 14784.81 | 106.5
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 0 | 125 | 127 | 278 | 55 | 35 | 54 | 0 | 0 | 350 | 0 | 35 | 307 | 0 | 0 | 15 | 143.42 | 10.8 | 22 | 0 | 467 | 107 | 158 | 12 | 0 | 2 | 0 | 39 | 36 | 12 | 12 | 2.6 | 220 | 110 | 0 | 940 | 16 | 0 | 50 | 8 | 105 | 213 | 0 | 0 | 0 | 1224 | 15 | 150 | 186 | 0 | 342 | 345 | 44 | 30 | 203 | 27 | 51 | 107 | 34 | 72 | 11 | 86 | 72 | 8 | 50 | 0 | 238 | 389 | 271 | 40 | 40 | 0 | 4 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 15.03 | 115 | 8 | 1.4 | 37.05 | 12 | 9088.3 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1234.2 | 0 | 0 | 0 | 573.84 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 32.51 | 75 | 0 | 0 | 41.62 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 3.63 | 156 | 0 | 115 | 30 | 42 | 0 | 0 | 0 | 5.5 | 155 | 0.45 | 110 | 277 | 112 | 220 | 0 | 800 | 280 | 72 | 5808.75 | 14897.05 | 106.5
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 19 | 125 | 127 | 285 | 55 | 35 | 54 | 0 | 0 | 370 | 0 | 35 | 303 | 0 | 0 | 13 | 143.42 | 0 | 22 | 0 | 475 | 109 | 158 | 13 | 0 | 1 | 0 | 39 | 36 | 12 | 12 | 1.7 | 220 | 110 | 0 | 940 | 18 | 0 | 50 | 8 | 105 | 212 | 0 | 0 | 0 | 1224 | 10 | 150 | 186 | 0 | 335 | 345 | 44 | 30 | 196 | 27 | 54 | 107 | 34 | 70 | 0 | 86 | 42 | 8 | 38 | 0 | 237 | 394 | 276 | 40 | 38 | 9 | 3 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 10.52 | 115 | 8 | 1 | 26.48 | 12 | 9079.12 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1234.2 | 0 | 0 | 0 | 571.88 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 27.46 | 55 | 0 | 0 | 25.99 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.1 | 158 | 0 | 115 | 22 | 42 | 0 | 0 | 0 | 5.6 | 102 | 0.37 | 110 | 280 | 112 | 220 | 0 | 800 | 295 | 72 | 5769.6 | 14848.72 | 106.49
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17 | 35 | 123 | 127 | 295 | 55 | 35 | 162 | 0 | 0 | 370 | 0 | 35 | 313 | 0 | 0 | 4 | 143.42 | 8 | 16 | 0 | 475 | 107 | 158 | 12 | 0 | 0 | 0 | 39 | 36 | 12 | 12 | 0.78 | 221 | 92 | 0 | 940 | 18 | 0 | 45 | 8 | 105 | 213 | 0 | 0 | 0 | 1224 | 6 | 150 | 168 | 0 | 348 | 310 | 44 | 27 | 185 | 30 | 52 | 107 | 34 | 68 | 0 | 86 | 60 | 8 | 18 | 0 | 237 | 389 | 276 | 40 | 38 | 45 | 3 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 58 | 5.73 | 115 | 10 | 0.3 | 13.89 | 10 | 9142.12 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1234.2 | 0 | 0 | 0 | 575.79 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 43 | 10.91 | 16 | 0 | 0 | 9.95 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.92 | 158 | 0 | 115 | 12 | 37 | 0 | 0 | 0 | 2.1 | 25 | 0.2 | 110 | 281 | 107 | 220 | 0 | 800 | 300 | 72 | 5586.07 | 14728.19 | 106.49
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 35 | 35 | 122 | 127 | 295 | 55 | 55 | 162 | 0 | 0 | 365 | 0 | 35 | 302 | 0 | 0 | 2 | 143.42 | 8 | 15 | 0 | 460 | 109 | 210 | 11 | 0 | 0 | 0 | 39 | 38 | 12 | 12 | 0.17 | 220 | 92 | 0 | 940 | 16 | 0 | 44 | 8 | 105 | 214 | 0 | 0 | 0 | 1224 | 1 | 150 | 168 | 0 | 330 | 310 | 44 | 10 | 196 | 30 | 67 | 107 | 34 | 71 | 0 | 86 | 62 | 8 | 5 | 0 | 238 | 393 | 276 | 40 | 38 | 0 | 1 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 58 | 1.4 | 115 | 8 | 0.1 | 3.19 | 9 | 9113.28 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 1234.2 | 0 | 0 | 0 | 567.54 | 0 | 0 | 0 | 113 | 62 | 0 | 0 | 0 | 43 | 3.64 | 7 | 0 | 0 | 3.44 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.28 | 155 | 0 | 115 | 3 | 34 | 0 | 0 | 0 | 0.6 | 5 | 0.05 | 110 | 275 | 109 | 220 | 0 | 800 | 300 | 72 | 5594.75 | 14708.03 | 106.48
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 35 | 138 | 142 | 295 | 55 | 55 | 162 | 0 | 0 | 360 | 0 | 35 | 322 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 510 | 107 | 210 | 12 | 0 | 0 | 0 | 39 | 54.36 | 24 | 12 | 0 | 220 | 92 | 0 | 940 | 16 | 0 | 45 | 9 | 105 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 355 | 310 | 44 | 10 | 206 | 33 | 78 | 107 | 34 | 73 | 11 | 86 | 76 | 8 | 0 | 0 | 240 | 390 | 272 | 40 | 38 | 16 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 58 | 0 | 128 | 5 | 0 | 0 | 14 | 9505.78 | 719 | 0 | 25 | 0 | 0 | 0 | 0 | 90 | 0 | 32 | 0 | 1234.2 | 10 | 0 | 0 | 656.26 | 0 | 0 | 0 | 113 | 110 | 0 | 0 | 27 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 18 | 220 | 0 | 800 | 300 | 119 | 5724.66 | 15230.44 | 106.48
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 35 | 145 | 127 | 295 | 55 | 55 | 162 | 0 | 0 | 395 | 0 | 35 | 301 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 420 | 107 | 230 | 12 | 0 | 0 | 51 | 39 | 54.36 | 24 | 12 | 0 | 221 | 92 | 0 | 940 | 18 | 0 | 45 | 17 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 330 | 310 | 44 | 10 | 208 | 34 | 115 | 107 | 34 | 73 | 13 | 86 | 76 | 25 | 0 | 0 | 241 | 398 | 276 | 40 | 39 | 17 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 68 | 0 | 177 | 0 | 0 | 0 | 24 | 9580.78 | 719 | 0 | 32 | 0 | 0 | 0 | 0 | 234 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 673.46 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 145 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 800 | 300 | 137 | 5999.86 | 15580.64 | 106.47
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 35 | 145 | 141 | 295 | 55 | 55 | 162 | 0 | 0 | 410 | 0 | 35 | 307 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 470 | 107 | 230 | 12 | 0 | 0 | 51 | 42 | 54.36 | 24 | 12 | 0 | 221 | 92 | 3 | 940 | 18 | 0 | 45 | 18 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 338 | 310 | 44 | 10 | 209 | 34 | 115 | 107 | 34 | 73 | 16 | 86 | 76 | 25 | 0 | 0 | 242 | 397 | 276 | 40 | 39 | 16 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 67 | 0 | 185 | 0 | 0 | 0 | 24 | 9694.78 | 719 | 0 | 28 | 0 | 0 | 0 | 0 | 235 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 677.03 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 148 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 137 | 6004.43 | 15699.21
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 35 | 145 | 141 | 295 | 55 | 55 | 162 | 0 | 0 | 400 | 0 | 35 | 298 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 430 | 109 | 230 | 12 | 0 | 0 | 51 | 42 | 54.36 | 24 | 12 | 0 | 221 | 92 | 6 | 940 | 18 | 0 | 45 | 20 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 332 | 310 | 44 | 10 | 209 | 34 | 115 | 107 | 34 | 73 | 19 | 86 | 72 | 25 | 0 | 5 | 242 | 400 | 276 | 40 | 39 | 16 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 68 | 0 | 184 | 0 | 0 | 0 | 24 | 9646.78 | 719 | 0 | 28 | 0 | 0 | 0 | 0 | 236 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 673.19 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 39 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 126 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 137 | 6046.59 | 15693.37 | 106.47
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 35 | 145 | 141 | 295 | 55 | 55 | 162 | 0 | 0 | 395 | 0 | 35 | 293 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 400 | 107 | 230 | 12 | 0 | 0 | 51 | 42 | 54.36 | 24 | 12 | 0 | 221 | 92 | 2 | 940 | 18 | 0 | 45 | 25.5 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 320 | 310 | 44 | 10 | 214 | 34 | 109 | 84 | 34 | 73 | 19 | 86 | 70 | 52.2 | 0 | 16 | 240 | 400 | 276 | 40 | 39 | 16 | 0 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 0 | 68 | 0 | 184 | 0 | 0 | 0 | 24 | 9602.48 | 719 | 0 | 28 | 0 | 0 | 0 | 0 | 237 | 0 | 32 | 0 | 1234.2 | 17 | 0 | 0 | 665.46 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 110 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 137 | 6000.86 | 15603.34 | 106.46
22:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 35 | 35 | 149 | 143 | 295 | 49 | 55 | 162 | 0 | 0 | 400 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 445 | 107 | 230 | 12 | 0 | 0 | 51 | 42 | 35 | 24 | 18 | 0 | 221 | 92 | 3 | 940 | 16 | 0 | 45 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 334 | 310 | 44 | 10 | 218 | 34 | 108 | 84 | 41 | 72 | 19 | 86 | 70 | 52.2 | 0 | 16 | 241 | 400 | 276 | 40 | 40 | 17 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 78 | 0 | 194 | 0 | 0 | 0 | 24 | 9577.12 | 724 | 0 | 23 | 0 | 0 | 0 | 0 | 238 | 0 | 36 | 0 | 1234.2 | 17 | 0 | 0 | 670.63 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 131 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 800 | 300 | 90 | 5985.03 | 15562.15 | 106.46
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 35 | 149 | 146 | 262 | 40 | 55 | 162 | 0 | 0 | 395 | 0 | 35 | 307 | 0 | 0 | 0 | 143.42 | 8 | 22 | 0 | 440 | 109 | 230 | 12 | 0 | 0 | 51 | 44 | 35 | 24 | 24 | 0 | 219 | 92 | 10 | 940 | 17 | 0 | 45 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 334 | 310 | 44 | 10 | 201 | 33 | 87 | 77 | 65 | 73 | 19 | 86 | 70 | 52.2 | 0 | 16 | 240 | 398 | 276 | 40 | 40 | 15 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 1 | 78 | 0 | 194 | 0 | 0 | 0 | 24 | 9468.12 | 773 | 0 | 23 | 0 | 0 | 0 | 0 | 238 | 0 | 50 | 0 | 1234.2 | 19 | 0 | 0 | 684.32 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 52.2 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 108 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 800 | 300 | 54 | 6044.72 | 15512.84 | 106.45
Total KWH | 0 | 1725600 | 423840 | 0 | 0 | 0 | 0 | 0 | 9043200 | 0 | 0 | 781200 | 775800 | 2814768 | 3149280 | 5786465 | 1288327 | 799373 | 2358720 | 0 | 0 | 9337345 | 0 | 694716 | 7431303 | 0 | 0 | 138760 | 3493200 | 226200 | 518400 | 0 | 10935909.09 | 2601927 | 3540327 | 384000 | 0 | 5280 | 706442 | 1000295 | 663947 | 383040 | 324480 | 20520 | 5278029 | 2518289 | 315360 | 18392727.27 | 428218 | 0 | 1171680 | 212077.8 | 2519127 | 5060803 | 0 | 0 | 0 | 29241815 | 115965 | 3598036 | 4148364 | 0 | 8486200 | 7706000 | 1037468 | 600480 | 4925000 | 705240 | 1672320 | 2466511 | 890880 | 1283520 | 341150 | 2086200 | 1589760 | 612557 | 405636 | 52768 | 5734000 | 9512300 | 6648000 | 954000 | 917880 | 220671.82 | 50969 | 398136 | 0 | 1967040 | 0 | 3132000 | 0 | 2408030 | 58320 | 1472400 | 107211 | 2755200 | 99840 | 11600 | 284500 | 363120 | 216310062.98 | 19616727 | 0 | 317760 | 0 | 0 | 0 | 0 | 1750090.91 | 0 | 276624 | 580320 | 29701820 | 284160 | 0 | 0 | 14539631 | 0 | 0 | 0 | 1226592 | 1240800 | 0 | 0 | 211293 | 1148664 | 381264 | 585150 | 282732 | 0 | 341904 | 0 | 0 | 0 | 0 | 0 | 0 | 9830618 | 0 | 29880 | 3718000 | 291055 | 2686576 | 169001 | 1231872 | 0 | 0 | 0 | 28571.88 | 946080 | 4042 | 2656608 | 7135000 | 2720000 | 5401020 | 0 | 19410909 | 7163636.36 | 1716000 | 137624401.15 | 353934464.13