## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: August 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-08-01 |  | 2026-07-01 |  | 2025-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16973.07 | 2026-08-23 | 16716.67 | 2026-07-02 | 16076.4 | 2025-08-11 | 17200.79 | 2026-05-20
|  |  | 20:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 11539.62 | 2026-08-07 | 11329.86 | 2026-07-10 | 9865.74 | 2025-08-08 | 11665.13 | 2026-06-19
|  |  | 09:00 Hr. |  | 08:00 Hr. |  | 6:00 |  | 10:00 Hr.
3 | Maximum Evening Peak Generation (MW) | 16973.07 | 2026-08-23 | 16716.67 | 2026-07-02 | 16076.4 | 2025-08-11 | 17200.79 | 2026-05-20
|  |  | 20:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 15313.94 | 2026-08-25 | 15327.46 | 2026-07-02 | 14273.89 | 2025-08-12 | 15418.78 | 2026-05-20
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 19027.11 | 2026-08-27 | 17266.7 | 2026-07-26 | 16199.71 | 2025-08-11 | 19027.11 | 2026-08-27
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
6 | Average Generation (MW) at Evening Peak | 15826.7945 |  | 15613.7248 |  | 15029.8061 |  | 15826.7945 | 2026-08-01
7 | Average Generation (MW) at Day Peak | 14322.1223 |  | 14076.9597 |  | 13104.8316 |  | 14322.1223 | 2026-08-01
8 | Maximum Power Import from India, BIPTC (MW) | 952 | 2026-08-24 | 951 | 2026-07-09 | 973 | 2025-08-29 | 981 | 2025-06-20
|  |  | 1:00 |  | 11:30 |  | 7:30 |  | 02:00:00
9 | Maximum Power Import from Tripura, India (MW) | 198 | 2026-08-03 | 197 | 2026-07-04 | 62 | 2025-08-18 | 213 | 2026-04-22
|  |  | 15:00 |  | 16:00 |  | 13:00 |  | 16:00:00
10 | Maximum Load Shed (MW) at Evening Peak | 3007 | 2026-08-11 | 2335 | 2026-07-29 | 197 | 2025-08-18 | 4395 | 2022-10-04
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 20:00 |  | 21:00:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15833.37 | 2026-08-11 | 14798.75 | 2026-07-29 | 15945.99 | 2025-08-18 | 16531.26 | 2026-05-21
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 20:00 |  | 21:00 Hr.
12 | Minimum Load Shed (MW) at Evening Peak | 302 | 2026-08-17 | 30 | 2026-07-10 | 0 | 2025-08-01 | 302 | 2026-08-17
|  |  | 19:30 |  | 21:00 Hr. |  | 21:00 |  | 19:30
13 | Generation During Min. Load Shed (MW) at Evening Peak | 15891.47 | 2026-08-17 | 14358.07 | 2026-07-10 | 13620.22 | 2025-08-01 | 15891.47 | 2026-08-17
|  |  | 19:30 |  | 21:00 Hr. |  | 21:00 |  | 19:30
14 | Maximum Load Shed (MW) at Day Peak | 3590 | 2026-08-30 | 1949 | 2026-07-30 | 36 | 2025-08-28 | 3590 | 2026-08-30
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 13735.91 | 2026-08-30 | 13611.74 | 2026-07-30 | 13864.61 | 2025-08-28 | 14859 | 2025-07-23
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | 12:00:00
16 | Minimum Load Shed (MW) at Day Peak | 39 | 2026-08-07 | 15 | 2026-07-17 | 0 | 2025-08-01 | 90 | 2026-03-09
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | 12:00 Hr.
17 | Generation During Min. Load Shed (MW) at Day Peak | 12500.51 | 2026-08-07 | 12954.44 | 2026-07-17 | 11666.46 | 2025-08-01 | 13966.46 | 2026-06-10
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | 12:00 Hr.
18 | Nos. of Days Load Shed at Evening Peak | 30 |  | 31 |  | 13 |  | 31 | Aug-2022
19 | Nos. of Days Load Shed at Day Peak | 30 |  | 28 |  | 1 |  | 30 | Aug-2022
20 | Gross Generation of BPDB (MKWH) | 1378.7201 |  | 1143.3569 |  | 1209.5845 |  | 3805.7195 | Sep-2019
21 | Station Use of BPDB (MKWH) | 38.0229 |  | 26.7217 |  | 37.6999 |  | 206.7694 | Apr-2024
22 | Net Generation of BPDB (MKWH) | 1340.6972 |  | 1116.6352 |  | 1171.8847 |  | 3681.055 | Sep-2019
23 | Net Generation of IPP (MKWH) | 3096.1389 |  | 2754.1536 |  | 2717.094 |  | 6375.85 | Jul-2024
23b | Net Generation by Generation Companies | 4529.6978 |  | 4886.0001 |  | 4555.8076 |  | 4739.8645 | Jun-2026
24 | Net Generation of REB (MKWH) | 42.1957 |  | 48.4553 |  | 48.2344 |  | 171.4948 | Aug-2019
25 | Net Generation of Rental Power Plant (MKWH) | 102.2702 |  | 90.0345 |  | 132.6744 |  | 793.0297 | Jul-2018
26 | Total Net Generation (MKHWh) (Excluding Import) | 9110.9998 |  | 8895.2786 |  | 8625.6951 |  | 9110.9998 | 2026-08-01
27 | Energy Generation by Gas (MKWH) | 3461.0774 |  | 3659.1497 |  | 4290.1188 |  | 4815.0058 | Jul-2021
28 | Energy Generation by Diesel (MKWH) | 22.4356 |  | 9.5006 |  | 12.0531 |  | 736.5643 | Jul-2018
29 | Energy Generation by Furnace Oil (MKWH) | 1516.7899 |  | 1077.9349 |  | 935.2305 |  | 2402.1611 | Jul-2022
30 | Energy Generation by Hydro (MKWH) | 158.693 |  | 128.8827 |  | 162.1321 |  | 162.1321 | Aug-2025
31 | Energy Generation by Solar (MKWH) | 122.0357 |  | 105.8874 |  | 108.7313 |  | 149.0391 | Apr-2025
31b | Energy Generation by Wind (MKWH) | 13.7131 |  | 20.4389 |  | 10.2067 |  | 14.5906 | 2025-07-01
32 | Energy Generation by Coal (MKWH) | 3854.278 |  | 3920.2061 |  | 3144.9225 |  | 3854.278 | 2026-08-01
33 | Enegry Import from India (MKWH) | 1643.6807 |  | 1693.3611 |  | 1458.9205 |  | 1755.2156 | Jun-2026
34 | Monthly Load Factor (%) | 85.2212 |  | 85.3709 |  | 84.6288 |  | 92.6177 | Aug-2022

## QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: August 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16973.07 | 2026-08-23 | 20:00 Hr.
Generation Period
| Dhaka | MW | 6109.8
| Chattogram | MW | 1532.6
| Cumilla | MW | 1538
| Mymensingh | MW | 1221
| Sylhet | MW | 675
a) | Total supply in East zone | MW | 11076.4
| Khulna | MW | 1961
| Barisal | MW | 500.4
| Rajshahi | MW | 1703.8
| Rangpur | MW | 1150
b) | Total supply in West zone | MW | 5315.2
c) | Total supply in both zone ( a+b) | MW | 16391.6
Ref: | 27.21.0000.603.16.087.20.991 | Date: 17/09/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: August 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 782 | 2026-08-10 | 16:00
|  | MW | 301
| b) Ghorashal end | AMPS | 0
|  | MW | 0
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0
|  | MW | 0
| b) Ghorashal end | AMPS | 725 | 2026-08-10 | 16:00
|  | MW | 278
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 5337.67 | 2026-08-10 | N/A
| b) Ghorashal end | MWh | 0
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 4910.65 |  | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 104378.1835
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 101246.838
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1760 | 2026-08-06
|  | MW | 670
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Sirajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur end | AMPS |  |  | -
MW
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Sirajganj end | MWh | 6627 | 2026-08-06 | -
| b) Sreepur end | MWh |  | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh |  |  | -
28 | Total Energy Export through EWI/ NO-2
| a) Sirajganj end | MWh | 254708 | - | -
| b) Sreepur end | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 247209.2 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 2.94% | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3812 | 2026-08-03 | 10:00
|  | MW | 2238
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3802 | 2026-08-03 | 10:00
|  | MW | 2236
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 43610 | 2026-08-03 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 43469 0 | 2026-08-03
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1065560
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1061202
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.409
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | 03. Transformer-03 | 2026-08-04 01:52 | 2026-08-04 03:01 | 0.047917 | T | Earth fault | 17 | 19.55 | Power interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2026-08-06 07:33 | 2026-08-06 07:52 | 0.013194 | T | 33kV PBS feeder(No-14) fault . | 18 | 5.7 | Power interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2026-08-16 14:02 | 2026-08-16 14:14 | 0.0083333 | T | 33 kv Mpbs-02 feeder no-15( kathali) trip | 15 | 3 | Power interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-08-27 22:46 | 2026-08-27 23:08 | 0.015278 | T | Tripped | 60 | 22 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-08-27 22:46 | 2026-08-27 23:08 | 0.015278 | T | Tripped | 60 | 22 | Power interruption
Ghatail 132/33kV | T-1 | 2026-08-30 11:21 | 2026-08-30 14:35 | 0.13472 | T | The bus D/S insulator of a 33kV spare feeder of 33kV switching station has been broken due to heavy flashing. The reason of flashing discovered as a reason of bird landing. | 35 | 113.1667 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-08-04 09:44 | 2026-08-04 09:58 | 0.0097222 | T | 33kV Kabirpur feeder faulty (breaker & CT blast) | 70 | 16.3333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-08-04 09:44 | 2026-08-04 09:58 | 0.0097222 | T | 33kV Kabirpur feeder faulty ( breaker &CT) blast | 70 | 16.3333 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-08-13 10:05 | 2026-08-13 10:53 | 0.033333 | T | Wrong Feeder operation by PBS | 30 | 24 | Power interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-08-13 10:05 | 2026-08-13 10:53 | 0.033333 | T | Wrong Feeder operation by PBS | 50 | 40 | Power interruption
Kodda 132/33kV | Tr-3 (426T) | 2026-08-13 10:05 | 2026-08-13 11:41 | 0.066667 | T | Wrong Feeder operation by PBS | 50 | 80 | Power interruption
Kodda 132/33kV | Tr-4 (436T) | 2026-08-13 10:05 | 2026-08-13 10:54 | 0.034028 | T | Wrong Feeder operation by PBS | 30 | 24.5 | Power interruption
Kodda 132/33kV | Tr-5 (446T) | 2026-08-13 10:05 | 2026-08-13 10:55 | 0.034722 | T | Wrong Feeder operation by PBS | 50 | 41.6667 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2026-08-09 10:54 | 2026-08-09 14:14 | 0.13889 | T | OLTC oil Surge Trip | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2026-08-09 14:46 | 2026-08-10 11:14 | 0.85278 | T | Tripped | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-08-30 05:59 | 2026-08-30 06:08 | 0.00625 | T | Tripped | 60 | 9 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-08-30 05:59 | 2026-08-30 06:08 | 0.00625 | T | Tripped | 60 | 9 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2026-08-18 22:38 | 2026-08-18 23:46 | 0.047222 | E/O | PBS 33 kV Outgooing feeder Red hot restoration work. | 23 | 26.0667 | Power interruption
Pubail 132/33kV | TRX-2 | 2026-08-03 11:38 | 2026-08-03 13:01 | 0.057639 | E/O | Pbs work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2026-08-09 12:08 | 2026-08-09 12:34 | 0.018056 | E/O | Transformer oil sample collection. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-08-21 12:32 | 2026-08-21 13:39 | 0.046528 | E/O | Rajendrapur-02 Red-hot Maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-08-15 12:30 | 2026-08-15 13:22 | 0.036111 | E/O | 33 KV T-02 Bus DS maintenance. | 10 | 8.6667 | Power interruption
|  |  | Total : | 1899-12-31 15:59 |  | Unserved Energy: |  | 480.9833
Dhaka (South) Grid Circle :
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-08-09 06:15 | 2026-08-09 06:27 | 0.0083333 | T | Due to 33 kv Aganagar feeder CT explode. | 27 | 5.4 | Power interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-08-09 06:15 | 2026-08-09 06:27 | 0.0083333 | T | Due to 33KV Aganagar feeder CT explode | 27 | 5.4 | Power interruption
Mogbazar 132/33kV | GT-1 | 2026-08-18 07:22 | 2026-08-18 07:22 | 0 | T | Tripped | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2026-08-11 02:27 | 2026-08-11 16:29 | 0.58472 | T | 33 kV pbs bandhura feeder insulator burn. | 12 | 168.4 | Power interruption
Nawabganj 132/33kV | TR-1 | 2026-08-14 06:03 | 2026-08-14 06:10 | 0.0048611 | T | 33 kv pbs nawabganj &sholla feeder fault. | 27 | 3.15 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-08-25 00:17 | 2026-08-25 00:34 | 0.011806 | T | Due to pbs 33kv side langolbandh feeder CT brust | 55 | 15.5833 | Power interruption
Bashundhara 132/33kV | Tr-3 | 2026-08-10 05:42 | 2026-08-10 05:42 | 0 | E/O | Y phase HT bushing maintenance due to temperature show high | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-1 | 2026-08-31 09:18 | 2026-08-31 09:42 | 0.016667 | E/O | গেন্ট্রি স্ট্রাকচারের ইনসুলেটর ডিস্ক ও বাসের কন্ডাক্টর এর মধ্যকার স্থানে চিল/কাক কতৃক প্রায় ১১ ফিট লম্বা স্টিলের মেজারিং টেপ ফেলে, ফলে হেভি ফ্লাসিং হয়। | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-2 | 2026-08-31 09:19 | 2026-08-31 09:46 | 0.01875 | E/O | বাস-১ সাট ডাউন নেওয়ার পর ৮১৪ নং আইসোলেটরের রেট ফেজে হেভি ফ্লাসিং হয় । সুইচ ইয়ার্ডের ব্যাপক ক্ষয়ক্ষতি থেকে রক্ষা করতে তাৎক্ষণিকভাবে বাস-২ সাট ডাউন নেওয়া হয়। | 240 | 108 | Power interruption
Nawabganj 132/33kV | TR-1 | 2026-08-14 08:37 | 2026-08-14 10:27 | 0.076389 | E/O | Red hot maintenance of incomer -01 Bus DS ( B phase bus site). | 27 | 49.5 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-08-20 21:04 | 2026-08-20 22:36 | 0.063889 | E/O | Red hot maintenance.. | 27 | 41.4 | Power interruption
|  |  | Total : | 0.79375 |  | Unserved Energy: |  | 396.8333
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-1 | 2026-08-02 11:11 | 2026-08-02 11:20 | 0.00625 | T | A conductor on the Patiya 33kV feeder bus had snapped | 28 | 4.2 | Power interruption
Baroirhat 132/33kV | TR-1, 406T | 2026-08-13 08:33 | 2026-08-13 09:49 | 0.052778 | E/O | Red hot maintenance work at 33 Kv end by PBS | 22 | 27.8667 | Power interruption
Baroirhat 132/33kV | TR-1, 406T | 2026-08-27 07:26 | 2026-08-27 09:12 | 0.073611 | E/O |  | 22 | 38.8667 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2026-08-02 10:46 | 2026-08-02 17:15 | 0.27014 | E/O | due to oil leackage need emergency shutdown | 0 | 0 | No interruption
GPH 230/33kV | Transformer -2 (D07) | 2026-08-03 09:51 | 2026-08-03 12:40 | 0.11736 | E/O | need emergency maintenance in transformer-02 | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-08-15 10:32 | 2026-08-15 13:21 | 0.11736 | E/O | New Wasa Feeder Maintenance work by BPDB | 13 | 36.6167 | Power interruption
|  |  | Total : | 0.6375 |  | Unserved Energy: |  | 107.55
Cumilla Grid Circle :
Brahmanbaria 132/33kV | 403T | 2026-08-15 06:25 | 2026-08-15 06:48 | 0.015972 | T | Tripped | 65 | 24.9167 | Power interruption
Brahmanbaria 132/33kV | 403T | 2026-08-29 05:20 | 2026-08-29 06:27 | 0.046528 | T | Tripped | 60 | 67 | Power interruption
Chowmuhani 230/132/33kV | TR1 | 2026-08-01 18:25 | 2026-08-01 19:21 | 0.038889 | T | LBUS U/G cable fault. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2026-08-28 19:38 | 2026-08-28 19:54 | 0.011111 | T | 33 KV Laksam PDB feeder fault. | 30 | 8 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2026-08-20 11:22 | 2026-08-20 11:41 | 0.013194 | T | Winding temperature high (°C) HV-74 LV- 76 OIL- 73 Over temperature alarm didn't work. Tripped directly. | 35 | 11.0833 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-08-07 21:12 | 2026-08-07 21:35 | 0.015972 | T | Tripped | 54 | 20.7 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2026-08-13 19:49 | 2026-08-13 20:03 | 0.0097222 | T | Madhabpur-01 and Chunarughat Feeder U/F fault. | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2026-08-12 22:15 | 2026-08-12 22:31 | 0.011111 | T | During PDB Feeder fault our Transformer-1 trip | 28.5 | 7.6 | Power interruption
Sunamganj 132/33kV | Tr-2 | 2026-08-12 22:15 | 2026-08-12 22:35 | 0.013889 | T | During PDB Feeder trip our Tr-2 Trip | 30.5 | 10.1667 | Power interruption
Sylhet 132/33kV | T1 | 2026-08-02 00:59 | 2026-08-02 01:08 | 0.00625 | T | 33kv upashahar feeder trip O/C A phase & E/F. | 30 | 4.5 | Power interruption
Sylhet 132/33kV | T1 | 2026-08-02 01:35 | 2026-08-02 01:41 | 0.0041667 | T | 33kv MC college feeder trip A,B,C phase O/C & E/F | 22 | 2.2 | Power interruption
Sylhet 132/33kV | T2 | 2026-08-21 20:57 | 2026-08-21 21:08 | 0.0076389 | T | Ins O/C and E/F | 80 | 14.6667 | Power interruption
Ashuganj 132/33kV | OAT-12 | 2026-08-12 23:08 | 2026-08-13 03:19 | 0.17431 | E/O | Red hot maintenance | 150 | 627.5 | Power interruption
Brahmanbaria 132/33kV | 401T | 2026-08-29 06:08 | 2026-08-29 10:27 | 0.17986 | E/O | emergency maintanence | 30 | 129.5 | Power interruption
Brahmanbaria 132/33kV | 401T | 2026-08-31 08:48 | 2026-08-31 12:48 | 0.16667 | E/O | emergency maintanence | 35 | 140 | Power interruption
Chandina 132/33kV | TR-2 | 2026-08-14 20:54 | 2026-08-14 22:04 | 0.048611 | E/O | PDB feader red hot problem. | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-08-20 11:45 | 2026-08-20 23:07 | 0.47361 | E/O | For PDB feeder red hot problem. | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-08-20 23:45 | 2026-08-21 00:53 | 0.047222 | E/O | Pdb feeder ret hot problem. | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-08-22 00:34 | 2026-08-22 15:40 | 0.62917 | E/O | PDB feeder red hot problem. | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2026-08-22 00:10 | 2026-08-29 07:10 | 1900-01-06 07:00 | E/O | emergency maintanence | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2026-08-29 08:55 | 2026-08-29 08:55 | 0 | E/O | emergency maintanence | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-08-01 09:30 | 2026-08-01 10:23 | 0.036806 | E/O | emergency 33 kv bus maintanence | 20 | 17.6667 | Power interruption
Chowmuhani 230/132/33kV | TR3 | 2026-08-07 10:16 | 2026-08-07 12:24 | 0.088889 | E/O | 33kv Datterhat feeder R phase loop Red-hot. | 25 | 53.3333 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-08-20 13:24 | 2026-08-20 14:35 | 0.049306 | E/O | Tr-2 loop connection. | 35 | 41.4167 | Power interruption
Chowmuhani 230/132/33kV | TR2 | 2026-08-26 11:30 | 2026-08-26 12:42 | 0.05 | E/O | Redhot maintenance | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3 | 2026-08-26 12:45 | 2026-08-26 15:49 | 0.12778 | E/O | redhot maintenance | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-08-27 22:23 | 2026-08-28 00:41 | 0.095833 | E/O | 33kV BUS-3 Jumper Red Hot Maintenance. | 20 | 46 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-05 | 2026-08-06 21:07 | 2026-08-06 22:11 | 0.044444 | E/O | Red hot remove | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-05 | 2026-08-18 21:03 | 2026-08-18 23:13 | 0.090278 | E/O | Redhot Maintenance of 33 KV DS. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-08-20 21:31 | 2026-08-20 23:38 | 0.088194 | E/O | 33 KV BUS side red hot maintenance | 7 | 14.8167 | Power interruption
Kachua 230/132/33kV | TR-2 | 2026-08-20 09:12 | 2026-08-20 10:32 | 0.055556 | E/O | red hot maintenance | 35 | 46.6667 | Power interruption
Kachua 230/132/33kV | TR-1 | 2026-08-20 10:41 | 2026-08-20 11:38 | 0.039583 | E/O | Red hot maintenance. | 31 | 29.45 | Power interruption
Kachua 230/132/33kV | TR-2 | 2026-08-25 07:35 | 2026-08-25 09:01 | 0.059722 | E/O | red hot maintenance by PBS | 35 | 50.1667 | Power interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-08-16 11:43 | 2026-08-16 15:14 | 0.14653 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Sylhet_(South) 132/33kV | Trafo-1 | 2026-08-24 16:43 | 2026-08-24 17:52 | 0.047917 | E/O | 33kv redhot maintenance. | 0 | 0 | No interruption
Sylhet_(South) 132/33kV | Trafo-2 | 2026-08-24 16:54 | 2026-08-24 17:51 | 0.039583 | E/O | 33kv redhot maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 06:23 |  | Unserved Energy: |  | 1367.35
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) | 2026-08-06 11:36 | 2026-08-06 11:41 | 0.0034722 | T | 33kV WZPDCL Dopdapia 1 feeder fault | 50 | 4.1667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-08-19 18:47 | 2026-08-19 18:52 | 0.0034722 | T | 33kV PBS Charbaria feeder fault | 45 | 3.75 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-08-11 15:09 | 2026-08-11 15:18 | 0.00625 | T | 33 kv Benapole feeder trip | 22 | 3.3 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-08-31 05:51 | 2026-08-31 10:58 | 0.21319 | T | Unknown | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-08-31 11:17 | 2026-08-31 23:07 | 0.49306 | T | Unknown | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2026-08-03 19:19 | 2026-08-03 19:40 | 0.014583 | T | A short circuit occurred on the 33 kv rupsha oil feeder due to snake climbing onto the feeder. | 30 | 10.5 | Power interruption
Payra 400/132/33kV | 132/33 kV Transformer-03 | 2026-08-10 16:15 | 2026-08-12 12:07 | 1899-12-31 19:52 | T |  | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2026-08-14 06:43 | 2026-08-14 07:34 | 0.035417 | T | 33kV WZ Sajjankanda feeder. | 19 | 16.15 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-08-12 06:10 | 2026-08-12 09:18 | 0.13056 | E/O | TR-1 HT Bushing Red Hot Maintenance | 0 | 0 | No interruption
Charfasson 230/33kV | Power Transformer-2 | 2026-08-15 22:14 | 2026-08-15 23:43 | 0.061806 | E/O | 33 kv pbs red hot emergency maintenance work. | 30 | 44.5 | Power interruption
Gopalganj 132/33kV | T1 | 2026-08-19 09:07 | 2026-08-19 11:15 | 0.088889 | E/O | 33kv feeder loop change | 0 | 0 | No interruption
|  |  |  | 1900-01-01 21:05 |  | Unserved Energy: |  | 82.3667
HVDC Grid Circle :
BIPTC | 10CF26 | 2026-08-10 18:11 | 2026-08-10 19:51 | 0.069444 | T | Tripped by Capacitor Unbalance | 0 | 0 | No interruption
BIPTC | 20DF21 | 2026-08-16 18:35 | 2026-08-16 20:55 | 0.097222 | T | Tripped by Capacitor Unbalance 60/61 instant L1 Trip. | 0 | 0 | No interruption
BIPTC | 10CF25 | 2026-08-22 13:05 | 2026-08-22 14:41 | 0.066667 | T | Tripped by Capacitor bank 60C current Unbalance | 0 | 0 | No interruption
BIPTC | 10CF15 | 2026-08-27 12:48 | 2026-08-27 13:44 | 0.038889 | T | C1 unabalnce 60/61 instant L-1 trip | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-08-07 08:39 | 2026-08-07 10:06 | 0.060417 | T | oil temperature trip | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-08-08 08:26 | 2026-08-08 09:34 | 0.047222 | T | UNKNOWN | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-08-26 09:26 | 2026-08-26 14:48 | 0.22361 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-08-27 18:04 | 2026-08-27 20:25 | 0.097917 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2026-08-27 20:21 | 2026-08-27 22:30 | 0.089583 | T | Tripped | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-08-13 21:08 | 2026-08-13 22:21 | 0.050694 | E/O | Red Hot | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-08-09 14:52 | 2026-08-09 15:03 | 0.0076389 | E/O | to control the load | 27 | 4.95 | Power interruption
Jashore 132/33kV | T-1 | 2026-08-10 16:43 | 2026-08-10 18:16 | 0.064583 | E/O | 33kv T1A side out going-1, R-phase DS red hot maintenance(PBS) | 47 | 72.85 | Power interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-08-24 06:50 | 2026-08-25 11:03 | 1899-12-31 04:13 | E/O | Transformer T2 Shutdown for Red hot maintenance. | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2026-08-22 10:01 | 2026-08-22 11:33 | 0.063889 | E/O | T-3 Transformer এর ৩৩ কেভি সাইডে CT এর Y এবং R Phase এর রেডহট মেরামত কাজ। | 15 | 23 | Power interruption
|  |  | Total : | 1900-01-01 03:41 |  | Unserved Energy: |  | 100.8
Bogura Grid Circle:
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-08-06 14:58 | 2026-08-06 15:40 | 0.029167 | T | 33 kV PBS feeder fault | 30 | 21 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-08-06 14:58 | 2026-08-06 15:40 | 0.029167 | T | 33 kV PBS feeder fault | 30 | 21 | Power interruption
Bogura 230/132kV | T-01 | 2026-08-05 07:45 | 2026-08-05 08:24 | 0.027083 | T | Tripped | 0 | 0 | No interruption
Taraganj 132/33kV | TR-03 (404T) | 2026-08-23 10:27 | 2026-08-23 11:10 | 0.029861 | T | REF(Restricted earth fault) | 25 | 17.9167 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2026-08-29 00:05 | 2026-08-29 01:12 | 0.046528 | E/O | Red hot maintenance of 33kv Bus | 30 | 33.5 | Power interruption
Bogura 400/230kV | ATR-03 | 2026-08-20 12:07 | 2026-08-20 13:00 | 0.036806 | E/O | GAS Refilling of Com Sp-07(B Phase). | 0 | 0 | No interruption
Chapai 132/33kV | T-3 (425T) | 2026-08-12 10:48 | 2026-08-12 12:12 | 0.058333 | E/O | 132 kv ct oil leakage | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-08-20 12:29 | 2026-08-20 12:59 | 0.020833 | E/O | High temperature maintenance work at LT side bushing(R-phase). | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-08-29 11:11 | 2026-08-29 11:25 | 0.0097222 | E/O | 132 kv Y-phase CT high tempareture. | 5 | 1.1667 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-08-01 03:55 | 2026-08-01 09:24 | 0.22847 | E/O | 33 kV side Red Hot. | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-08-18 10:08 | 2026-08-18 11:58 | 0.076389 | E/O | Hot spot maintenance at T2 33kv DS | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | TR-4 | 2026-08-19 07:27 | 2026-08-19 09:10 | 0.071528 | E/O | Red hot maintenance at 33 kV Bus coupler DS between T-2& T-3 | 62 | 106.4333 | Power interruption
Rajshahi 230/132/33kV | 132/33 kV T-02 (416T) | 2026-08-08 06:17 | 2026-08-08 08:15 | 0.081944 | E/O | 33kv DS Hot spot maintenance. | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-2(412T) | 2026-08-19 07:18 | 2026-08-19 08:58 | 0.069444 | E/O | Due to red hot maintenance work at Goalpara feeder 33kV bus-2 DS. | 60 | 100 | Power interruption
|  |  | Total : | 0.81528 |  | Unserved Energy: |  | 301.0167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-18 05:03 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2026-08-21 15:52 | 2026-08-21 16:24 | 0.022222 | T | Trip | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-08-27 22:46 | 2026-08-29 01:58 | 1899-12-31 03:12 | T | Line disconnect | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2026-08-27 22:46 | 2026-08-28 01:07 | 0.097917 | T | Line Fault | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-08-12 02:08 | 2026-08-12 02:34 | 0.018056 | T | Tripped | 110 | 47.6667 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-08-27 22:46 | 2026-08-27 22:58 | 0.0083333 | T | Tripped | 125 | 25 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-08-27 22:46 | 2026-08-27 22:58 | 0.0083333 | T | Tripped | 125 | 25 | Power interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-08-12 02:10 | 2026-08-12 02:36 | 0.018056 | T | Extremely lightning. | 40 | 17.3333 | Power interruption
Kishoreganj 132/33kV | Bajitpur Ckt-2 | 2026-08-12 02:10 | 2026-08-12 02:40 | 0.020833 | T | Extreme lightning | 40 | 20 | Power interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-08-27 22:40 | 2026-08-29 01:57 | 1899-12-31 03:17 | T | Due to Bajitpur ckt-01 R phase conductor broken | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-2 | 2026-08-27 22:40 | 2026-08-28 01:04 | 0.1 | T | Due to thundering. | 104 | 249.6 | Power interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2026-08-12 02:10 | 2026-08-12 02:36 | 0.018056 | T | Bajitpur - Kishorganj both ckt tripped. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2026-08-12 22:43 | 2026-08-13 03:22 | 0.19375 | E/O | Emergency shutdown order by LDC | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2026-08-12 22:44 | 2026-08-13 03:23 | 0.19375 | E/O | Emergency shutdown order by NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 23:16 |  | Unserved Energy: |  | 384.6
Dhaka (South) Grid Circle :
Bhulta 400/230/132kV | 132kV Bhulta Old | 2026-08-09 16:07 | 2026-08-09 16:25 | 0.0125 | T | Tripped | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Bhulta Old | 2026-08-12 11:19 | 2026-08-12 11:38 | 0.013194 | T | Tripped | 160 | 50.6667 | Power interruption
Bhulta 400/230/132kV | 132kV Narsingdi | 2026-08-16 09:17 | 2026-08-16 10:59 | 0.070833 | T | Tripped | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-08-11 01:46 | 2026-08-11 12:56 | 0.46528 | T | Heavy rainfall with thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-08-27 11:18 | 2026-08-27 14:01 | 0.11319 | T | Zone- Trip(4.2 Km), B phase pick up | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-08-31 09:59 | 2026-08-31 12:13 | 0.093056 | T | Tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2026-08-09 11:27 | 2026-08-10 01:32 | 0.58681 | T | Tripped | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2026-08-22 03:06 | 2026-08-22 04:51 | 0.072917 | T | Fault at Narinda grid sub station | 19 | 33.25 | Power interruption
Maniknagar 132/33kV | Narinda Ckt-2 | 2026-08-22 03:06 | 2026-08-23 22:07 | 1899-12-31 19:01 | T | Fault at Narinda grid sub station | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-1 | 2026-08-24 07:47 | 2026-08-24 09:12 | 0.059028 | T | 400kV Reliance ckt-1 Tripped by Directional Earth Fault IDMT | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-2 | 2026-08-24 13:48 | 2026-08-25 17:36 | 1899-12-31 03:48 | T | Line Differential 87L | 0 | 0 | Power interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-08-16 08:14 | 2026-08-16 14:27 | 0.25903 | T | Line Fault. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2026-08-11 15:09 | 2026-08-11 19:22 | 0.17569 | E/O | Purpose of tree trimming | 0 | 0 | No interruption
Maniknagar 132/33kV | Matuail Single Ckt | 2026-08-23 23:39 | 2026-08-28 14:51 | 1900-01-03 15:12 | E/O | Emergency maint.work | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-08-19 11:22 | 2026-08-19 21:32 | 0.42361 | E/O | Maintenance work of EGCB. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-08-23 21:09 | 2026-08-23 23:33 | 0.1 | E/O | Corrective maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-1 | 2026-08-20 06:05 | 2026-08-20 09:37 | 0.14722 | E/O | According to the direction of NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 04:14 |  | Unserved Energy: |  | 83.9167
Chattogram Grid Circle :
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-08-22 12:00 | 2026-08-22 12:14 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-2 | 2026-08-02 15:41 | 2026-08-02 16:09 | 0.019444 | T | Tripped | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-2 | 2026-08-14 02:17 | 2026-08-14 20:43 | 0.76806 | T | Tripped | 0 | 0 | No interruption
Patiya 132/33kV | Patiya-Dohazari Ckt-01 | 2026-08-22 12:01 | 2026-08-22 12:14 | 0.0090278 | T | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-08-28 09:44 | 2026-08-28 21:21 | 0.48403 | E/O | Emergency maint.work | 0 | 0 | No interruption
Khulshi 132/33kV | Sholoshahar-Madunaghat CKT-1 | 2026-08-14 02:39 | 2026-08-14 20:41 | 0.75139 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 01:00 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 132/33kV | Bajitpur 132kV Circuit-1 | 2026-08-04 08:37 | 2026-08-04 08:57 | 0.013889 | T | Tripped | 80 | 26.6667 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-08-12 00:03 | 2026-08-12 02:52 | 0.11736 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2026-08-21 11:30 | 2026-08-21 16:36 | 0.2125 | T | Tripped | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-08-12 00:05 | 2026-08-12 02:54 | 0.11736 | T | Tripped | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-08-29 12:25 | 2026-08-29 12:38 | 0.0090278 | T | Fault Trip-Aided trip | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-08-17 14:57 | 2026-08-17 17:34 | 0.10903 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-08-17 14:57 | 2026-08-17 17:34 | 0.10903 | E/O | Emergency Maint.work | 0 | 0 | No interruption
|  |  | Total : | 0.68819 |  | Unserved Energy: |  | 26.6667
Khulna Grid Circle :
Amtali 400/132kV | Amtali - Gopalganj 400 kV Ckt - 1 | 2026-08-22 09:19 | 2026-08-22 10:44 | 0.059028 | T | Earth Fault transient, Couldn’t Operate Auto Reclose | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 132kV Gopalganj Ckt-1 | 2026-08-21 09:31 | 2026-08-21 11:23 | 0.077778 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-08-17 11:39 | 2026-08-17 14:06 | 0.10208 | E/O | Patuakhali line-1 230kV Bay T ponit top junction point redhot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0.23889 |  | Unserved Energy: |  | 0
HVDC Grid Circle :Nil
BIPTC | Baharampur-2 | 2026-08-27 11:05 | 2026-08-28 11:14 | 1899-12-31 00:09 | T | Tripped by 21.1 Main-1 | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 00:09 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-08-17 14:49 | 2026-08-17 21:06 | 0.26181 | T | Over Current | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-08-10 14:59 | 2026-08-10 15:24 | 0.017361 | T | Distance Trip | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-08-02 08:10 | 2026-08-02 08:48 | 0.026389 | T | General Trip, Earth Fault and Over Current , R & Y phase. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-08-03 06:17 | 2026-08-03 07:00 | 0.029861 | T | Heavy thurndaring . | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Joypurhat Ckt-1 | 2026-08-03 06:17 | 2026-08-03 07:02 | 0.03125 | T | Heavy Thurndaring | 48 | 36 | Power interruption
Palashbari 132/33kV | Mithapukur-01 | 2026-08-27 13:55 | 2026-08-27 14:09 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132 kV Amnura | 2026-08-03 04:38 | 2026-08-03 05:00 | 0.015278 | T | Thunder ring | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-08-03 12:13 | 2026-08-03 12:34 | 0.014583 | T | Unknown | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-08-10 14:59 | 2026-08-10 15:23 | 0.016667 | T | Phase to Phase Fault | 0 | 0 | No interruption
Amnura 132/33kV | CB-408B | 2026-08-10 12:12 | 2026-08-10 12:15 | 0.0020833 | E/O | For 31S 33kv bus section D/S open due to individual operation of T-01 and T-02. | 8 | 0.4 | Power interruption
Amnura 132/33kV | CB-418B | 2026-08-10 12:12 | 2026-08-10 12:15 | 0.0020833 | E/O | For 31S 33kv bus section D/S open due to individual operation of T-01 and T-02. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-16 20:16 | 2026-08-16 20:16 | 0 | E/O | Due to reduce overload at parbatipur Grid SS | 0 | 0 | No interruption
|  |  | Total : | 0.42708 |  | Unserved Energy: |  | 36.4
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-16 13:09 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2026-08-19 09:54 | 2026-08-19 18:01 | 8:07 | S/O | Ds Shaft connection | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2026-08-20 08:30 | 2026-08-20 18:59 | 10:29 | S/O | Bay-6 inter locking and CRM testing | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2026-08-10 16:56 | 2026-08-10 18:10 | 1:14 | S/O | Maint.work | 40 | 49.3333 | Power interruption
Bajitpur 132/33kV | 132 kV Bus-2 | 2026-08-11 09:25 | 2026-08-11 11:10 | 1:45 | S/O | High temperature maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2026-08-11 09:37 | 2026-08-11 11:21 | 1:44 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-08-22 08:21 | 2026-08-22 10:09 | 1:48 | S/O | Hot spot removing work. | 0 | 0 | No interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-08-13 06:29 | 2026-08-13 09:42 | 3:13 | S/O | High temp.minimize at 33kV bus by PBS. | 70 | 225.1667 | Power interruption
Birulia 230/132kV | ATR-2 | 2026-08-30 10:45 | 2026-08-30 10:45 | 0:00 | S/O | NLDC SCADA integration work | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-08-24 06:40 | 2026-08-24 10:11 | 3:31 | S/O | Work by pbs. | 50 | 175.8333 | Power interruption
Jamalpur 132/33kV | Bus-A | 2026-08-12 08:22 | 2026-08-13 16:48 | 32:26 | S/O | 132 KV CT replacement at 132 KV Bus Coupler Bay. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-1 | 2026-08-13 08:26 | 2026-08-13 11:21 | 2:55 | S/O | 33kv. Beltia feeder red hot problem | 5 | 14.5833 | Power interruption
Jamalpur 132/33kV | T-1 | 2026-08-14 07:13 | 2026-08-14 10:02 | 2:49 | S/O | T1&T2 33kv bus section Isulator maintenances work | 22.5 | 63.375 | Power interruption
Jamalpur 132/33kV | T-2 | 2026-08-14 07:13 | 2026-08-14 10:02 | 2:49 | S/O | T1&T2 33kv bus section Isulator maintenances work | 22.5 | 63.375 | Power interruption
Jamalpur 132/33kV | Bus-A | 2026-08-31 10:56 | 2026-08-31 15:14 | 4:18 | S/O | T-3 A-Bus DS Loop Connection work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bus-B | 2026-08-31 15:35 | 2026-08-31 19:20 | 3:45 | S/O | 132 kv T3 bus lop connection. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-I | 2026-08-07 16:01 | 2026-08-07 17:57 | 1:56 | S/O | 33kV Kobirpur Feeder CB Replacement work | 30 | 58 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2026-08-10 08:53 | 2026-08-10 21:11 | 12:18 | S/O | BBK Project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 230kV Bus 2 | 2026-08-11 11:02 | 2026-08-11 12:45 | 1:43 | S/O | Dismantle jumper between 230kV bus2 and DS. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2026-08-13 08:50 | 2026-08-13 21:16 | 12:26 | S/O | BBK project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-08-18 07:09 | 2026-08-18 09:47 | 2:38 | S/O | Jumper connection of 132kV bus-2 and 230/132kV ATr. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-08-29 08:40 | 2026-08-29 08:40 | 0:00 | S/O | SAS integration | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 230kV Bus 1 | 2026-08-29 09:32 | 2026-08-29 13:03 | 3:31 | S/O | measurement of tube bus | 0 | 0 | No interruption
Kodda 132/33kV | Tr-5 (446T) | 2026-08-13 15:01 | 2026-08-13 16:28 | 1:27 | S/O | 33 kV bus sec-3 maintenance by pbs | 140 | 203 | Power interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-08-22 06:25 | 2026-08-22 07:50 | 1:25 | S/O | Bus DS work | 50 | 70.8333 | Power interruption
Kodda 132/33kV | Tr-5 (446T) | 2026-08-29 08:30 | 2026-08-29 11:45 | 3:15 | S/O | Insulator change PBS side | 0 | 0 | No interruption
Kodda 132/33kV | 33kV BUS-1 of Section-3 | 2026-08-29 08:30 | 2026-08-29 11:38 | 3:08 | S/O | PBS WORK | 65 | 203.6667 | Power interruption
Kodda 132/33kV | 33kV BUS-2 of Section-3 | 2026-08-29 08:30 | 2026-08-29 11:38 | 3:08 | S/O | PBS WORK | 65 | 203.6667 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-08-31 15:55 | 2026-08-31 17:45 | 1:50 | S/O | PDB work | 55 | 100.8333 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-08-30 23:04 | 2026-08-31 00:19 | 1:15 | S/O | 33 kv bus section red hot maintenance by Dhaka PBS-1 | 75 | 93.75 | Power interruption
Pubail 132/33kV | TRX-2 | 2026-08-15 11:04 | 2026-08-15 14:50 | 3:46 | S/O | Low sf6 gas pressure in LCC | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-08-01 10:47 | 2026-08-10 18:33 | 223:46 | S/O | Project HV Test Purpose | 0 | 0 | No interruption
Rajendrapur 132/33kV | 132 kV BUS-1 | 2026-08-10 11:20 | 2026-08-19 13:54 | 218:34 | S/O | Sreepur Bay Extension Work | 0 | 0 | No interruption
Rajendrapur 132/33kV | 132 kV BUS-2 | 2026-08-19 17:28 | 2026-08-20 15:05 | 21:37 | S/O | Maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-08-20 11:33 | 2026-08-20 13:49 | 2:16 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2026-08-15 08:54 | 2026-08-15 12:30 | 3:36 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-08-15 08:56 | 2026-08-15 10:44 | 1:48 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2026-08-15 09:10 | 2026-08-15 12:26 | 3:16 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2026-08-15 10:45 | 2026-08-15 12:14 | 1:29 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2026-08-27 11:26 | 2026-08-27 15:11 | 3:45 | S/O | SCADA & RTU Integration work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2026-08-10 13:25 | 2026-08-10 13:52 | 0:27 | S/O | OLTC Oil Collection. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2026-08-15 09:30 | 2026-08-15 11:14 | 1:44 | S/O | Over temperature Removed. | 23 | 39.8667 | Power interruption
Shomvuganj 400/132kV | Transformer-3 ( TR-3) | 2026-08-25 12:20 | 2026-08-25 15:12 | 2:52 | S/O | Bus Stability test. | 50 | 143.3333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-08-26 08:54 | 2026-08-26 11:49 | 2:55 | S/O | PBS Work | 60 | 175 | Power interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-08-26 09:50 | 2026-08-26 11:26 | 1:36 | S/O | Rajen-2 DS repair work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-25 00:20 |  | Unserved Energy: |  | 1883.6167
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2026-08-12 06:04 | 2026-08-12 09:04 | 3:00 | S/O | For Redhot work in the section of GT-01 DS-114(R and B phase) and Bus DS-126( Y phase) | 60 | 180 | Power interruption
Bhulta 132/33kV | GT1 | 2026-08-22 07:00 | 2026-08-22 08:44 | 1:44 | S/O | GT-1 Trip, Signal- 1, genaral trip 2, Main PRD | 60 | 104 | Power interruption
Bhulta 132/33kV | GT1 | 2026-08-31 06:34 | 2026-08-31 09:36 | 3:02 | S/O | Red Hot Maintenance | 60 | 182 | Power interruption
Bhulta 400/230/132kV | 132kV Bus-2 | 2026-08-02 14:37 | 2026-08-02 18:44 | 4:07 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-1 | 2026-08-20 06:39 | 2026-08-20 09:28 | 2:49 | S/O | CB 911 B open for 132 KV Sonargao-1 Jack bus work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2026-08-25 09:35 | 2026-08-25 14:55 | 5:20 | S/O | Maintenance work of 33kV Nawabganj-1 & Zinzira-1 feeder. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2026-08-25 10:50 | 2026-08-25 14:54 | 4:04 | S/O | 33kV DS red hot maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-08-25 15:14 | 2026-08-25 17:34 | 2:20 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2026-08-25 15:29 | 2026-08-25 15:29 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-08-10 06:09 | 2026-08-10 08:00 | 1:51 | S/O | maintenance work due to over temperature | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-08-22 06:18 | 2026-08-22 17:52 | 11:34 | S/O | High Temperature | 0 | 0 | No interruption
Maniknagar 132/33kV | Main Bus | 2026-08-22 07:48 | 2026-08-22 07:48 | 0:00 | S/O | To do maintenance work at Narinda ckt-2 main bus isolator. | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR -03 | 2026-08-14 07:36 | 2026-08-14 11:50 | 4:14 | S/O | Fire fighting connection & testing purpose | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 02 | 2026-08-23 09:28 | 2026-08-23 14:21 | 4:53 | S/O | Requested by NLDC | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-08-06 09:47 | 2026-08-06 17:58 | 8:11 | S/O | 33KV XLPE Cable Termination | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-08-09 07:43 | 2026-08-09 20:08 | 12:25 | S/O | 33 KV XLPE cable termination | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-08-10 07:03 | 2026-08-10 18:24 | 11:21 | S/O | 33kv XLPE Cable termination work | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-08-12 11:38 | 2026-08-12 17:55 | 6:17 | S/O | XLPE cable termination and related Maintenance works | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2026-08-13 08:37 | 2026-08-13 13:05 | 4:28 | S/O | 33KV XLPE cable termination and related maintenance works | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2026-08-03 15:40 | 2026-08-03 16:30 | 0:50 | S/O | T-4 BUS DS-2 (T-CLAMP) Hotspot Maintenance work. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-08-17 06:26 | 2026-08-17 08:17 | 1:51 | S/O | Pbs Anandabazar feeder bypass blade change | 68 | 125.8 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-08-20 06:02 | 2026-08-20 08:41 | 2:39 | S/O | 33KV incoming breaker DS finger point red hot | 68 | 180.2 | Power interruption
|  |  | Total : | 1900-01-03 01:00 |  | Unserved Energy: |  | 772
Chattogram Grid Circle :
Baroirhat 132/33kV | TR-2, 416T | 2026-08-06 10:50 | 2026-08-06 12:20 | 1:30 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-08-01 16:48 | 2026-08-01 17:55 | 1:07 | S/O | Banshkhali 33 kv Feeder BUS DS Maintenance. | 20 | 22.3333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-08-02 13:29 | 2026-08-02 15:16 | 1:47 | S/O | Patiya 33 kv Feeder BUS DS Loop repair and Maintenance | 20 | 35.6667 | Power interruption
Hathazari 230/132/33kV | MT-03 | 2026-08-15 07:56 | 2026-08-21 14:58 | 151:02 | S/O | MT-03 Shutdown required for 132KV R-Ph & Y-Ph Bushing change. | 0 | 0 | No interruption
Khulshi 132/33kV | 415T (T2) | 2026-08-07 06:05 | 2026-08-07 10:12 | 4:07 | S/O | Emergency maintenance work at 33kV Bus section -02 carried out by BPDB. | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-08-02 09:27 | 2026-08-02 17:48 | 8:21 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-08-03 10:02 | 2026-08-03 18:24 | 8:22 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-08-04 10:27 | 2026-08-04 17:45 | 7:18 | S/O | DFDR work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-08-22 08:56 | 2026-08-22 17:50 | 8:54 | S/O | Due to project work ( CAF) | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-08-22 08:56 | 2026-08-22 17:48 | 8:52 | S/O | Due to project work ( CAF) | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-08-24 09:06 | 2026-08-24 17:23 | 8:17 | S/O | Project Work (CAF) | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-08-25 09:07 | 2026-08-25 17:09 | 8:02 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-08-26 09:01 | 2026-08-26 17:26 | 8:25 | S/O | For project work | 0 | 0 | No interruption
Mirsorai 400/230/33kV | ATR-1 | 2026-08-02 10:01 | 2026-08-04 18:32 | 56:31 | S/O | Project work DFDR Testing | 0 | 0 | No interruption
Mirsorai 400/230/33kV | ATR-2 | 2026-08-29 10:25 | 2026-08-29 10:25 | 0:00 | S/O | Project Work (CAF/DFDR) | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-01 | 2026-08-15 20:20 | 2026-08-15 21:30 | 1:10 | S/O | Corrective redhot maintenance | 12 | 14 | Power interruption
Patiya 132/33kV | TRAFO-02 | 2026-08-15 20:21 | 2026-08-15 20:21 | 0:00 | S/O | Corrective redhot maintenance | 12 | 0 | No interruption
Patiya 132/33kV | TRAFO-01 | 2026-08-22 22:01 | 2026-08-23 00:09 | 2:08 | S/O | Red hot corrective maintenance | 13 | 27.7333 | Power interruption
Patiya 132/33kV | TRAFO-01 | 2026-08-29 07:02 | 2026-08-29 10:02 | 3:00 | S/O | Corrective red hot maintenance | 16 | 48 | Power interruption
|  |  | Total : | 1900-01-11 00:53 |  |  |  | 147.7333
Cumilla Grid Circle :
Ashuganj 132/33kV | Bus-1A | 2026-08-13 14:38 | 2026-08-22 17:18 | 218:40 | S/O | Project work. | 0 | 0 | No interruption
Ashuganj 132/33kV | Bus-2A | 2026-08-13 14:38 | 2026-08-22 17:18 | 218:40 | S/O | Project work. | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2026-08-01 10:08 | 2026-08-01 11:40 | 1:32 | S/O | Pbs work | 30 | 46 | Power interruption
Chandpur 132/33kV | Bus A | 2026-08-13 10:10 | 2026-08-13 13:26 | 3:16 | S/O | Maintenance Work | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-08-15 07:00 | 2026-08-15 09:30 | 2:30 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2026-08-15 07:00 | 2026-08-15 12:33 | 5:33 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-2 section | 2026-08-15 07:00 | 2026-08-15 09:27 | 2:27 | S/O | Maintenance work | 13 | 31.85 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2026-08-21 23:15 | 2026-08-22 00:10 | 0:55 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2026-08-21 23:15 | 2026-08-22 00:10 | 0:55 | S/O | Maintenance work | 18 | 16.5 | Power interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2026-08-29 07:10 | 2026-08-29 08:55 | 1:45 | S/O | Maintenance Work for High Temperature | 17 | 29.75 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2026-08-29 07:10 | 2026-08-29 08:55 | 1:45 | S/O | Bus section-1 shutdown | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-08-19 16:54 | 2026-08-19 18:11 | 1:17 | S/O | Red hot maintenance on pbs side | 30 | 38.5 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-08-23 08:28 | 2026-08-23 10:04 | 1:36 | S/O | Redhot maintans. | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2026-08-24 07:30 | 2026-08-24 09:30 | 2:00 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-08-27 07:19 | 2026-08-27 08:32 | 1:13 | S/O | 33 kv chowmuhani- 3 bus DS after flashing maintenance. | 25 | 30.4167 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-08-03 23:45 | 2026-08-04 01:11 | 1:26 | S/O | Redhot rectify work on 33kv balutopa feeder by BPDB. | 30 | 43 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-08-24 08:46 | 2026-08-24 16:57 | 8:11 | S/O | Red Hot Maintenance at 33kv companygonj feeder | 12 | 98.2 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-08-21 16:22 | 2026-08-21 17:33 | 1:11 | S/O | Due to PBS Hotspot maintenance 33KV bus side. | 20 | 23.6667 | Power interruption
Fenchuganj 230/132/33kV | TR-02 | 2026-08-26 09:26 | 2026-08-26 12:39 | 3:13 | S/O | 33KV Bus Rad Hot maintenance at PBS side | 17 | 54.6833 | Power interruption
Fenchuganj 230/132/33kV | TR-02 | 2026-08-28 07:47 | 2026-08-28 10:22 | 2:35 | S/O | Changing Tr-2 incomer DS(33KV) phase-B loop. | 18 | 46.5 | Power interruption
Feni 132/33kV | T-2(415T) | 2026-08-17 10:07 | 2026-08-17 17:22 | 7:15 | S/O | For T-2 Breaker Commission | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2026-08-22 07:18 | 2026-08-22 08:54 | 1:36 | S/O | REB Maintenance Work | 30 | 48 | Power interruption
Feni 132/33kV | Bus-2 | 2026-08-22 07:18 | 2026-08-22 07:19 | 0:01 | S/O | For Pbs Maintenance | 54 | 0.9 | Power interruption
Feni 230/132kV | ATR-1 | 2026-08-21 08:48 | 2026-08-23 10:45 | 49:57 | S/O | Boring and Installation of a submersible Pump | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2026-08-03 23:38 | 2026-08-04 00:40 | 1:02 | S/O | shutdown taken by pbs for load side ds red hot maintenance | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2026-08-29 08:28 | 2026-08-29 16:12 | 7:44 | S/O | Replacement of poles for PBS 33kV double circuit line. | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2026-08-29 12:37 | 2026-08-29 16:12 | 3:35 | S/O | PBS work new line construction | 20 | 71.6667 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-08-06 14:22 | 2026-08-06 16:20 | 1:58 | S/O | PBS 33 kv Bus DS redhot maintenance | 32 | 62.9333 | Power interruption
Kulaura 132/33kV | TR-2 | 2026-08-13 11:04 | 2026-08-13 13:00 | 1:56 | S/O |  | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-08-09 11:41 | 2026-08-09 15:59 | 4:18 | S/O | SCADA Integration | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-08-10 11:19 | 2026-08-10 17:07 | 5:48 | S/O | SCADA Integration Work. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-08-21 08:05 | 2026-08-21 10:45 | 2:40 | S/O | Redhot Maintenance Work | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-08-16 17:24 | 2026-08-16 18:19 | 0:55 | S/O | BREB 33KV RED HOT MAINTENANCE | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2026-08-02 11:22 | 2026-08-02 12:22 | 1:00 | S/O | Changing the Energy Meter of Tr-06. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2026-08-11 07:00 | 2026-08-11 08:26 | 1:26 | S/O | Tr-06 33kv D/S Redhot Maintenance. | 40 | 57.3333 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-08-27 07:12 | 2026-08-27 09:33 | 2:21 | S/O | Redhot Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2026-08-30 13:20 | 2026-08-30 15:32 | 2:12 | S/O | 33 kv Feeder maintenance | 50 | 110 | Power interruption
Sylhet 132/33kV | T1 | 2026-08-03 06:22 | 2026-08-03 08:35 | 2:13 | S/O | 33 kv Upashahar Feeder DS loop Maintenance by PDB S&D-2. | 16 | 35.4667 | Power interruption
Sylhet 132/33kV | T1 | 2026-08-22 06:14 | 2026-08-22 07:57 | 1:43 | S/O | 33 KV uposohor feeder red hot maintenance for PDB. | 10 | 17.1667 | Power interruption
Sylhet_(South) 132/33kV | Trafo-1 | 2026-08-13 06:56 | 2026-08-13 08:26 | 1:30 | S/O | DUE TO DS MAINTANENCE | 0 | 0 | No interruption
|  |  | Total : | 1900-01-23 05:50 |  |  |  | 862.5333
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-2 (413 T) | 2026-08-03 10:24 | 2026-08-03 11:11 | 0:47 | S/O | Pbs emergency maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-08-04 06:07 | 2026-08-04 07:32 | 1:25 | S/O | For replacing the damaged fuse of the auxiliary transformer. | 25 | 35.4167 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-08-06 08:02 | 2026-08-06 09:25 | 1:23 | S/O | 33 kV WZPDCL Jhalokathi feeder post insulator at 33kV bus repair work | 25 | 34.5833 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-08-21 09:16 | 2026-08-21 10:39 | 1:23 | S/O | Red hot maintenance at 33kV Bus at Polashpur feeder (WZPDCL) | 25 | 34.5833 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-08-22 08:50 | 2026-08-22 10:15 | 1:25 | S/O | WZPDCL Work | 30 | 42.5 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-08-29 10:42 | 2026-08-29 11:56 | 1:14 | S/O | T2 33 kv cb SF6 Leak check. | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2026-08-08 07:18 | 2026-08-08 10:15 | 2:57 | S/O | Korapur 33kv feeder B phase finger work | 23 | 67.85 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-08-08 07:19 | 2026-08-08 09:00 | 1:41 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2026-08-08 09:57 | 2026-08-08 12:13 | 2:16 | S/O | Hot spot | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2026-08-11 07:15 | 2026-08-11 09:22 | 2:07 | S/O | 33 kv bus DS maintenance work | 39 | 82.55 | Power interruption
Goalpara 132/33kV | T-5 | 2026-08-21 09:30 | 2026-08-21 11:58 | 2:28 | S/O | maint.work | 8 | 19.7333 | Power interruption
Goalpara 132/33kV | T-6 | 2026-08-21 09:30 | 2026-08-21 11:58 | 2:28 | S/O | maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2026-08-21 09:30 | 2026-08-21 11:58 | 2:28 | S/O | maint.work | 0 | 0 | No interruption
Gopalganj 132/33kV | Transformer-03 | 2026-08-22 10:11 | 2026-08-22 12:39 | 2:28 | S/O | BPBS-02 Red hot maintenance | 15 | 37 | Power interruption
Khulna (C) | TR-1 425T | 2026-08-19 16:34 | 2026-08-19 17:59 | 1:25 | S/O | Red hot maintenance porpoise. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-08-21 07:15 | 2026-08-21 08:42 | 1:27 | S/O | Hot Spot Maintenance. | 6 | 8.7 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-08-27 08:09 | 2026-08-27 09:44 | 1:35 | S/O | Hot Spot Maintenance | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2026-08-29 07:30 | 2026-08-29 13:54 | 6:24 | S/O | 33 KV Bus-Bar Shutdown Due to Red Hot Mentanence by WZPDCL. | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2026-08-29 07:30 | 2026-08-29 13:55 | 6:25 | S/O | 33 KV Bus-Bar Shutdown Due to Red Hot Mentanence BY WZPDCL. | 0 | 0 | No interruption
Mongla 132/33kV | 33 KV Bus | 2026-08-29 07:30 | 2026-08-29 13:54 | 6:24 | S/O | 33 KV Bus-Bar Shutdown Due to Red Hot Mentanence by WZPDCL | 27 | 172.8 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2026-08-25 06:43 | 2026-08-25 07:46 | 1:03 | S/O | Due to Redhot maintenance of 33kV N4 Feeder of 33kVBus Section -1 Side. | 26 | 27.3 | Power interruption
Noapara 132/33kV | T-2 | 2026-08-28 09:14 | 2026-08-28 21:29 | 12:15 | S/O | Changing Conductor, Clump & Connector of (33kV REB-1 & T-3) Feeder. | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-2 | 2026-08-28 09:21 | 2026-08-28 21:34 | 12:13 | S/O | Changing Conductor, Clump & Connector of (33kV REB-1 & T-3) Feeder. | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2026-08-29 07:41 | 2026-08-29 09:15 | 1:34 | S/O | T-1 Transformer 33 kv side (Y-phase) high tem. point maintenance. | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2026-08-31 15:04 | 2026-08-31 16:29 | 1:25 | S/O | maint.work | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-2 | 2026-08-31 15:12 | 2026-08-31 16:30 | 1:18 | S/O | maint.work | 17 | 22.1 | Power interruption
Patuakhali 132/33kV | 405T (T-1) | 2026-08-19 10:34 | 2026-08-19 13:56 | 3:22 | S/O | Breaker gas pressure problem fixation | 0 | 0 | No interruption
Patuakhali 132/33kV | 405T (T-1) | 2026-08-26 10:10 | 2026-08-26 11:20 | 1:10 | S/O | Due to 33kv Betagi feeder redhot maintenance. | 5 | 5.8333 | Power interruption
|  |  | Total : | 1900-01-02 12:30 |  | Unserved Energy : |  | 590.95
HVDC Grid Circle
BIPTC | 20DF24 | 2026-08-16 20:24 | 2026-08-16 20:55 | 0:31 | S/O | For Corrective Mantenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-08-16 12:36 | 2026-08-16 12:36 | 0:00 | S/O | bay equipment upgradation work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 1 | 2026-08-22 10:01 | 2026-08-22 11:10 | 1:09 | S/O | G to G project work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-08-22 15:24 | 2026-08-22 16:26 | 1:02 | S/O | G to G bay upgradation work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-08-29 12:53 | 2026-08-29 18:14 | 5:21 | S/O | maintenance | 0 | 0 | No interruption
Jashore 132/33kV | T-3 | 2026-08-10 07:54 | 2026-08-10 08:37 | 0:43 | S/O | Overtemperature Maintenance WZPDCL | 3 | 2.15 | Power interruption
Jhenaidah 230/132kV | Transformer-3 | 2026-08-03 09:57 | 2026-08-03 18:17 | 8:20 | S/O | DFDR & NLDC intregation and testing works | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 | 2026-08-13 08:43 | 2026-08-13 15:36 | 6:53 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 0.99931 |  | Unserved Energy : |  | 2.15
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2026-08-29 10:13 | 2026-08-29 11:23 | 1:10 | S/O | Maintenance work | 0 | 0 | No interruption
Amnura 132/33kV | T-2 (416T) | 2026-08-29 11:35 | 2026-08-29 12:54 | 1:19 | S/O | Maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-08-08 08:20 | 2026-08-08 13:27 | 5:07 | S/O | 33 kV Bus Section-2 maintenance | 10 | 51.1667 | Power interruption
Bogura 132/33kV | Transformer-4 | 2026-08-14 07:20 | 2026-08-14 09:29 | 2:09 | S/O | T-4 Bay nut-bolt tightening and maintenance work. | 20 | 43 | Power interruption
Bogura 230/132kV | T-02 | 2026-08-11 10:22 | 2026-08-11 19:04 | 8:42 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2026-08-12 10:47 | 2026-08-14 20:51 | 58:04 | S/O | oil filling | 0 | 0 | No interruption
Bogura 230/132kV | T-04 | 2026-08-20 08:38 | 2026-08-20 17:05 | 8:27 | S/O | ss upgradation | 0 | 0 | No interruption
Bogura 230/132kV | T-04 | 2026-08-21 07:47 | 2026-08-21 17:07 | 9:20 | S/O | ss upgradation | 0 | 0 | No interruption
Bogura 230/132kV | T-04 | 2026-08-22 08:00 | 2026-08-23 17:01 | 33:01 | S/O | Maint.work | 0 | 0 | No interruption
Chapai 132/33kV | T-4 (435T) | 2026-08-27 08:58 | 2026-08-29 13:17 | 52:19 | S/O | Oil centrifuge. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-08-02 15:31 | 2026-08-02 18:50 | 3:19 | S/O | T-2 Earthig Maintenance. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-08-03 15:37 | 2026-08-03 17:41 | 2:04 | S/O | T-2 TR Ground Wire Maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV | T-4 | 2026-08-31 07:38 | 2026-08-31 09:17 | 1:39 | S/O | 33KV Aux. Tr. Bus Ds Maintenance. Shutdown taken by AE. Nazmul Haque, - NESCO Division-1. | 45 | 74.25 | Power interruption
Natore 132/33kV | TR-1 (405 T) | 2026-08-15 06:54 | 2026-08-15 08:58 | 2:04 | S/O | Maint.work | 21 | 43.4 | Power interruption
Natore 132/33kV | TR-2 (415 T) | 2026-08-15 06:54 | 2026-08-15 08:59 | 2:05 | S/O | Maint.work | 21 | 43.75 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-08-08 17:30 | 2026-08-08 18:52 | 1:22 | S/O | Red Hot Maintenance | 20 | 27.3333 | Power interruption
Patnitala 132/33kV | T2 | 2026-08-17 11:17 | 2026-08-17 12:34 | 1:17 | S/O | Transformer LT side clamp and conductor moving | 0 | 0 | No interruption
Patnitala 132/33kV | T3 | 2026-08-17 11:18 | 2026-08-17 12:35 | 1:17 | S/O | Transformer LT side clamp and conductor moving | 0 | 0 | No interruption
Rangpur 132/33kV | 33KV Bus | 2026-08-13 06:15 | 2026-08-13 08:37 | 2:22 | S/O | Redhot removed of 33kv burirhat nesco feeder isolator connected to 33kv bus 1 | 25 | 59.1667 | Power interruption
Saidpur 132/33kV | TR-01 | 2026-08-11 14:30 | 2026-08-11 15:40 | 1:10 | S/O | Power Plant internal work. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-2 (404T) | 2026-08-17 08:09 | 2026-08-17 09:30 | 1:21 | S/O | As the instructions of ALDC, Bogura | 0 | 0 | No interruption
Saidpur 132/33kV | TR-2 (404T) | 2026-08-21 08:50 | 2026-08-21 11:10 | 2:20 | S/O | Red hot Maintainance. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2026-08-21 08:52 | 2026-08-21 11:13 | 2:21 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV | BUS A | 2026-08-21 09:00 | 2026-08-21 11:02 | 2:02 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV | T2-(425) | 2026-08-22 10:20 | 2026-08-22 12:52 | 2:32 | S/O | 33kV Kazipur feeder wood pole Replacement work by Sirajganj PBS-2 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 16:53 |  | Unserved Energy : |  | 342.0667
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1909:25 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Meghnaghat-02 | 2026-08-27 06:14 | 2026-08-27 11:38 | 5:24 | S/O | Line DS female part change | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-01 | 2026-08-27 09:10 | 2026-08-27 18:29 | 9:19 | S/O | SPMD Work | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2026-08-22 10:47 | 2026-08-22 13:32 | 2:45 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-08-23 11:05 | 2026-08-29 01:58 | 134:53 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-08-13 08:44 | 2026-08-13 09:50 | 1:06 | S/O | High temperature minimize. | 40 | 44 | Power interruption
Birulia 230/132kV | Birulia-Kaliakoir 230KV Ckt-1 | 2026-08-24 12:05 | 2026-08-24 14:50 | 2:45 | S/O | SCADA Integration NLDC | 0 | 0 | No interruption
Birulia 230/132kV | Birulia-Aminbazar 230KV Ckt-1 | 2026-08-24 14:53 | 2026-08-24 16:05 | 1:12 | S/O | SCADA Integration NLDC | 0 | 0 | No interruption
Birulia 230/132kV | Birulia-Aminbazar 230KV Ckt-2 | 2026-08-25 10:32 | 2026-08-25 11:57 | 1:25 | S/O | SCADA Integration of NLDC | 0 | 0 | No interruption
Birulia 230/132kV | Birulia-Kaliakoir 230KV Ckt-2 | 2026-08-25 11:58 | 2026-08-25 12:50 | 0:52 | S/O | SCADA Integration of NLDC | 0 | 0 | No interruption
Birulia 230/132kV | Birulia-Aminbazar 230KV Ckt-1 | 2026-08-27 09:10 | 2026-08-27 18:29 | 9:19 | S/O | relay change at aminbazar grid | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-08-18 07:16 | 2026-08-18 10:13 | 2:57 | S/O | কালিয়াকৈর গ্রিড এ বাস শিফট জনিত কারনে সাটডাউন নেওয়া হয়। | 55 | 162.25 | Power interruption
Ghatail 132/33kV | Tangail-1 | 2026-08-21 05:39 | 2026-08-21 08:52 | 3:13 | S/O | Maint.work | 60 | 193 | Power interruption
Ghatail 132/33kV | Tangail -2 | 2026-08-21 05:39 | 2026-08-21 08:52 | 3:13 | S/O | Maint.work | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-2 | 2026-08-21 06:03 | 2026-08-21 08:59 | 2:56 | S/O | Maint.work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-08-31 15:30 | 2026-08-31 20:06 | 4:36 | S/O | 132 kv T3 bus lop connection. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-08-26 07:08 | 2026-08-26 10:57 | 3:49 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-08-26 11:14 | 2026-08-26 13:09 | 1:55 | S/O | Maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2026-08-10 16:21 | 2026-08-10 16:26 | 0:05 | S/O | 230/132kV ATR internal inspection & centrifuge. | 90 | 7.5 | Power interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-08-10 16:21 | 2026-08-10 16:25 | 0:04 | S/O | 230/132kV ATR internal inspection & oil centrifuge. | 90 | 6 | Power interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2026-08-12 05:52 | 2026-08-12 13:30 | 7:38 | S/O | NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2026-08-12 05:52 | 2026-08-12 16:13 | 10:21 | S/O | NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2026-08-18 07:17 | 2026-08-18 10:10 | 2:53 | S/O | Jumper connection of 132kV bus-2 and 230/132kV ATr. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-2 | 2026-08-22 09:44 | 2026-08-22 13:32 | 3:48 | S/O | For Insulator disc replacing | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-08-23 11:04 | 2026-08-23 13:58 | 2:54 | S/O | For insulator disc replace | 0 | 0 | No interruption
Muktagacha 132/33kV | Ghatail-2 | 2026-08-21 06:02 | 2026-08-21 09:00 | 2:58 | S/O | P/W | 0 | 0 | No interruption
Mymensingh 132/33kV | 50 MW Solar Plant | 2026-08-22 20:10 | 2026-08-22 22:40 | 2:30 | S/O | Maint.work | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-1 | 2026-08-16 12:16 | 2026-08-16 19:54 | 7:38 | S/O | Teleprotection work purpose. | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-2 | 2026-08-16 20:44 | 2026-08-16 22:08 | 1:24 | S/O | Teleprotection work purpose. | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-1 | 2026-08-20 09:08 | 2026-08-20 12:22 | 3:14 | S/O | A shutdown of the 132 kV Dhamrai-Nabinagar Circuit-1 was carried out under the directives of the NLDC to facilitate the construction of scaffolding for the re-conductoring project of the 230 kV Ghorashal-Ishwardi transmission line | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-2 | 2026-08-20 09:08 | 2026-08-20 12:22 | 3:14 | S/O | A shutdown of the 132 kV Dhamrai-Nabinagar Circuit-2 was carried out under the directives of the NLDC to facilitate the construction of scaffolding for the re-conductoring project of the 230 kV Ghorashal-Ishwardi transmission line | 110 | 355.6667 | Power interruption
Pubail 132/33kV | Joydebpur-1 | 2026-08-26 07:05 | 2026-08-26 11:08 | 4:03 | S/O | Scaffolding | 0 | 0 | No interruption
Pubail 132/33kV | Ghorasal-2 | 2026-08-26 07:07 | 2026-08-26 11:09 | 4:02 | S/O | Scaffolding | 0 | 0 | No interruption
Pubail 132/33kV | Joydebpur-2 | 2026-08-26 11:12 | 2026-08-26 13:10 | 1:58 | S/O | Scafolding | 0 | 0 | No interruption
Pubail 132/33kV | Ghorasal-1 | 2026-08-26 11:12 | 2026-08-26 13:11 | 1:59 | S/O | Scafolding | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-08-21 18:03 | 2026-08-22 10:28 | 16:25 | S/O | According to NLDC permission | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2026-08-22 10:39 | 2026-08-22 10:39 | 0:00 | S/O | Sreepur Line -1 Shifting Work. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2026-08-23 10:57 | 2026-08-23 10:57 | 0:00 | S/O | Loop connection at kodda 2 bay | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-08-09 09:03 | 2026-08-09 14:42 | 5:39 | S/O | work by mymensingh. | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-08-25 16:14 | 2026-08-25 17:06 | 0:52 | S/O | P/W | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Mymensingh Ckt-2 | 2026-08-25 17:09 | 2026-08-25 18:04 | 0:55 | S/O | P/W | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-08-07 07:18 | 2026-08-07 19:07 | 11:49 | S/O | PGNS work | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-08-07 07:18 | 2026-08-07 21:09 | 13:51 | S/O | PGNS work | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-08-08 06:28 | 2026-08-08 09:40 | 3:12 | S/O | Project work by PGNS (G2G) | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-08-08 06:29 | 2026-08-08 09:40 | 3:11 | S/O | Project work by PGNS (G2G) | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-08-13 08:45 | 2026-08-13 09:50 | 1:05 | S/O | Taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2026-08-20 21:54 | 2026-08-20 22:50 | 0:56 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2026-08-27 08:49 | 2026-08-27 17:04 | 8:15 | S/O | Line by pass by MRT Project. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 06:32 |  | Unserved Energy: |  | 768.4167
Dhaka (South) Grid Circle :
Bhulta 400/230/132kV | 132kV Haripur-01 | 2026-08-02 11:39 | 2026-08-02 18:48 | 7:09 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 230kV Ghorashal-01 | 2026-08-12 22:22 | 2026-08-13 12:40 | 14:18 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-01 | 2026-08-18 09:58 | 2026-08-18 17:20 | 7:22 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-02 | 2026-08-18 10:01 | 2026-08-18 17:22 | 7:21 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-01 | 2026-08-27 09:02 | 2026-08-27 21:09 | 12:07 | S/O | Line Parameter test | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-02 | 2026-08-27 09:03 | 2026-08-27 21:10 | 12:07 | S/O | Line.Parameter test | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-01 | 2026-08-29 10:34 | 2026-08-29 19:28 | 8:54 | S/O | Teleprotection Test | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-02 | 2026-08-29 10:36 | 2026-08-29 19:28 | 8:52 | S/O | Teleprotection Test | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-01 | 2026-08-30 11:11 | 2026-08-30 20:33 | 9:22 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-02 | 2026-08-30 11:13 | 2026-08-30 20:35 | 9:22 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-01 | 2026-08-31 07:07 | 2026-08-31 18:38 | 11:31 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Araihazar-02 | 2026-08-31 07:09 | 2026-08-31 07:09 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (3rd unit) - Ghorashal 230kv GIS switching Station. | 2026-08-06 15:57 | 2026-08-09 14:27 | 70:30 | S/O | For the Maintenance work of the 230kV Third Unit (D15) PT. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-08-09 06:59 | 2026-08-09 08:17 | 1:18 | S/O | Shutdown requisition from STGE Project | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2026-08-10 11:47 | 2026-08-10 12:42 | 0:55 | S/O | For Ghorashal End Ishwardi Bay VT conncetion rectification | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-08-13 10:40 | 2026-08-13 10:40 | 0:00 | S/O | Reconductoring work of iswardi ckt-1 by STGE project. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (3rd unit) - Ghorashal 230kv GIS switching Station. | 2026-08-31 10:41 | 2026-08-31 13:31 | 2:50 | S/O | CT&PT equipments reconnection and maintenance at Plant-03 side. | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-2 | 2026-08-17 07:06 | 2026-08-17 10:57 | 3:51 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-08-18 07:14 | 2026-08-18 11:49 | 4:35 | S/O | Taken from other end | 0 | 0 | No interruption
Haripur 230/132kV | Sonargaon 1 | 2026-08-20 06:06 | 2026-08-20 09:36 | 3:30 | S/O | High Temperature Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-08-28 08:56 | 2026-08-28 14:53 | 5:57 | S/O | From other end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2026-08-12 08:50 | 2026-08-12 11:37 | 2:47 | S/O | High temperature maintenance at CSE pot at Keaniganj end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-08-17 10:29 | 2026-08-17 11:35 | 1:06 | S/O | Maintenance work at Hasnabad ed. | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -1 | 2026-08-16 06:28 | 2026-08-16 12:19 | 5:51 | S/O | Maintenance Work (DPDC) | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -2 | 2026-08-16 12:30 | 2026-08-16 16:10 | 3:40 | S/O | Maintenance Work (DPDC) | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-2 | 2026-08-22 07:25 | 2026-08-23 22:07 | 38:42 | S/O | Maintenance Work in line isolator and main bus isolator due to temperature rise. | 0 | 0 | No interruption
Maniknagar 132/33kV | Haripur Ckt-2 | 2026-08-28 09:09 | 2026-08-28 09:09 | 0:00 | S/O | Requirement of DPDC for their project work at Green Model Town area, Only Earth switch operated ( close). CB and DS were open always from our end | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-08-02 09:15 | 2026-08-02 20:05 | 10:50 | S/O | Taken by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-08-03 09:41 | 2026-08-03 18:16 | 8:35 | S/O | taken by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-08-04 14:12 | 2026-08-04 17:46 | 3:34 | S/O | Taken by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-08-18 09:46 | 2026-08-18 18:25 | 8:39 | S/O | Requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-08-19 08:52 | 2026-08-19 18:03 | 9:11 | S/O | Requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-08-20 09:13 | 2026-08-20 21:17 | 12:04 | S/O | Taken by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-08-27 06:15 | 2026-08-27 11:42 | 5:27 | S/O | Requsted by NLDC | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 2 | 2026-08-17 07:06 | 2026-08-17 10:58 | 3:52 | S/O | Maintenance work | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 1 | 2026-08-18 07:14 | 2026-08-18 11:48 | 4:34 | S/O | Maintenance work | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-01 | 2026-08-12 08:49 | 2026-08-12 11:37 | 2:48 | S/O | Line maintenance by Keraniganj End. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 11:31 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2026-08-10 06:00 | 2026-08-10 06:00 | 0:00 | S/O | OPGW maintenance work at Bakalia Khulshi line(98-99 span) | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-08-10 06:29 | 2026-08-10 06:29 | 0:00 | S/O | OPGW maintenance work at Bakalia Khulshi line(98-99 span) | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2026-08-06 10:06 | 2026-08-06 13:43 | 3:37 | S/O | Korerhat grid work | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2026-08-18 15:14 | 2026-08-28 14:05 | 238:51 | S/O | New control and protection panel Commissioning | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-08-06 05:11 | 2026-08-06 20:00 | 14:49 | S/O | Due to OPGW conductor stringing and fiber splicing in four ckt tower near CEPZ. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-2 | 2026-08-06 05:25 | 2026-08-06 20:02 | 14:37 | S/O | Due to OPGW conductor stringing and fiber splicing in four ckt tower near CEPZ. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-08-06 05:33 | 2026-08-06 20:12 | 14:39 | S/O | Due to OPGW conductor stringing and fiber splicing in four ckt tower near CEPZ. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-08-07 05:00 | 2026-08-07 19:08 | 14:08 | S/O | Maint.work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-2 | 2026-08-07 05:05 | 2026-08-07 19:09 | 14:04 | S/O | Maint.work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-08-07 05:09 | 2026-08-07 19:19 | 14:10 | S/O | Maint.work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-08-08 07:19 | 2026-08-08 13:46 | 6:27 | S/O | OPGW Cable stringing and Fiber splicing | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-08-08 07:21 | 2026-08-08 14:07 | 6:46 | S/O | OPGW cable stringing and Fiber splicing | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-08-20 09:06 | 2026-08-20 12:39 | 3:33 | S/O | Hali -Khulshi ckt-03 Gis Bay selector switch maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-08-27 08:06 | 2026-08-27 14:05 | 5:59 | S/O | Maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2026-08-25 10:20 | 2026-08-25 20:00 | 9:40 | S/O | Maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-08-25 08:28 | 2026-08-25 18:08 | 9:40 | S/O | Maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-08-26 05:35 | 2026-08-26 17:55 | 12:20 | S/O | Earth wire and insulator disk changing work. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-08-27 05:52 | 2026-08-27 17:57 | 12:05 | S/O | Maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-08-31 09:01 | 2026-09-01 14:40 | 29:39 | S/O | Maint.work | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2026-08-06 05:32 | 2026-08-06 20:14 | 14:42 | S/O | Emergency maintenance work | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2026-08-07 05:10 | 2026-08-07 19:22 | 14:12 | S/O | OPGW work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-08-02 09:18 | 2026-08-02 21:05 | 11:47 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -1 | 2026-08-02 09:39 | 2026-08-02 17:35 | 7:56 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-08-03 10:00 | 2026-08-03 18:14 | 8:14 | S/O | For Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Chowmuhani-4 | 2026-08-03 10:12 | 2026-08-03 13:05 | 2:53 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Baraiyarhat-2 | 2026-08-06 10:36 | 2026-08-06 13:42 | 3:06 | S/O | Energy meter configuration | 0 | 0 | No interruption
Korerhat 400/230/132kV | Madunaghat-2 | 2026-08-11 09:46 | 2026-08-11 13:19 | 3:33 | S/O | DFDR WORK | 0 | 0 | No interruption
Korerhat 400/230/132kV | Madunaghat-1 | 2026-08-16 10:01 | 2026-08-16 17:25 | 7:24 | S/O | Project work. (DFDR) | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-08-18 09:48 | 2026-08-18 18:25 | 8:37 | S/O | Shunt Reactor work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-08-19 08:54 | 2026-08-19 17:58 | 9:04 | S/O | Shunt Redactor work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-08-20 09:42 | 2026-08-20 21:16 | 11:34 | S/O | Due to project work. | 0 | 0 | No interruption
Korerhat 400/230/132kV | Mirsharai-1 | 2026-08-02 10:06 | 2026-08-04 18:42 | 56:36 | S/O | For project work,Shutdown taken by Mirsharai end | 0 | 0 | No interruption
Korerhat 400/230/132kV | Mirsharai-2 | 2026-08-06 12:40 | 2026-08-09 18:16 | 77:36 | S/O | Shutdown taken by Mirsharai end | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-2 | 2026-08-11 06:27 | 2026-08-12 23:36 | 41:09 | S/O | loop maintenance work by khuslsi ss. | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-2 | 2026-08-11 09:41 | 2026-08-11 13:15 | 3:34 | S/O | Maint.work | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-1 | 2026-08-16 09:57 | 2026-08-16 17:26 | 7:29 | S/O | Maint.work | 0 | 0 | No interruption
Mirsorai 400/230/33kV | Korerhat-1 | 2026-08-02 10:10 | 2026-08-04 18:42 | 56:32 | S/O | Project work DFDR Testing | 0 | 0 | No interruption
|  |  | Total : | 1900-01-31 03:02 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 132/33kV | Shahjibazar 132 kV | 2026-08-13 14:37 | 2026-08-22 17:19 | 218:42 | S/O | Project work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-1 | 2026-08-18 05:43 | 2026-08-18 05:43 | 0:00 | S/O | Temperature issue at various clamp & conductor | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2026-08-19 05:20 | 2026-08-19 05:20 | 0:00 | S/O | For Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Cumilla(N) 230 kV Ckt-1 | 2026-08-25 09:09 | 2026-08-25 09:09 | 0:00 | S/O | For Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV | 230kv Busbar-2 | 2026-08-25 11:24 | 2026-08-25 11:24 | 0:00 | S/O | For Maintenance work. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-08-31 09:08 | 2026-08-31 11:12 | 2:04 | S/O | For Maintenance work. | 0 | 0 | No interruption
Chandina 132/33kV | Cumilla (N) Line-1 | 2026-08-02 12:47 | 2026-08-02 14:17 | 1:30 | S/O | For Voltage connection troubleshoot | 0 | 0 | No interruption
Chandina 132/33kV | Cumilla (N) Line-1 | 2026-08-31 11:52 | 2026-08-31 23:41 | 11:49 | S/O | Project Work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-08-10 07:40 | 2026-08-10 12:31 | 4:51 | S/O | Red hot maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2026-08-13 09:56 | 2026-08-13 13:10 | 3:14 | S/O | Maintenance Work | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-5 section | 2026-08-15 07:00 | 2026-08-15 09:27 | 2:27 | S/O | Maintenance work | 24 | 58.8 | Power interruption
Chauddagram 132/33kV | Feni-1 | 2026-08-02 09:22 | 2026-08-02 13:13 | 3:51 | S/O | Red Hot and Gas presser maintenance. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Lakshmipur-01 | 2026-08-20 13:01 | 2026-08-20 14:48 | 1:47 | S/O | S/D taken by Lakshmipur Grid | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-2 | 2026-08-21 08:43 | 2026-08-21 17:04 | 8:21 | S/O | Works for Tripura S/S | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2026-08-22 09:36 | 2026-08-22 09:36 | 0:00 | S/O | S/D Taken By SLDC,Tripura . | 0 | 0 | No interruption
Daudkandi 132/33kV | Titas 50 MW Power Plant Line | 2026-08-06 09:14 | 2026-08-06 13:21 | 4:07 | S/O | maintenance work at powerplant end. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-08-30 07:20 | 2026-08-30 17:12 | 9:52 | S/O | G to G Project Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2026-08-31 08:53 | 2026-08-31 17:36 | 8:43 | S/O | G to G project work | 0 | 0 | No interruption
Feni 230/132kV | Chauddagram-1 | 2026-08-02 09:16 | 2026-08-02 13:12 | 3:56 | S/O | chauddagram end CB gas pressure issue. | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-1 | 2026-08-02 09:34 | 2026-08-02 17:35 | 8:01 | S/O | korerhat end demand. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-08-10 07:21 | 2026-08-10 12:31 | 5:10 | S/O | Maintenance work for Chandpur end. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 1 | 2026-08-20 12:59 | 2026-08-20 14:50 | 1:51 | S/O | Energy Meter Replacement Work. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-08-13 14:33 | 2026-08-22 17:20 | 218:47 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-08-30 07:00 | 2026-08-30 17:13 | 10:13 | S/O | Power Grid Network Strengthening Project under PGCB | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-08-31 08:43 | 2026-08-31 17:40 | 8:57 | S/O | Project work for Moulvibazar Grid SS. | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-08-09 11:54 | 2026-08-09 16:37 | 4:43 | S/O | Circuit Breaker Pole Discrepency Maintenance Work | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet South Circuit 2 | 2026-08-16 13:26 | 2026-08-16 14:03 | 0:37 | S/O | Line Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-21 15:33 |  | Unserved Energy: |  | 58.8
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-08-11 12:56 | 2026-08-11 14:01 | 1:05 | S/O | 132 KVBagerhat Bhandaria Line tree trimming works. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-08-28 07:43 | 2026-08-28 15:00 | 7:17 | S/O | Project work on Tower No-69. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2026-08-29 07:45 | 2026-08-29 07:45 | 0:00 | S/O | Tower errection and stringing work on Tower No 69. | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-08-11 13:57 | 2026-08-11 14:02 | 0:05 | S/O | Shut down by ALDC | 0 | 0 | No interruption
Barishal 230/132kV | Barishal (N)-Patuakhali Ckt-01 | 2026-08-15 09:22 | 2026-08-15 12:36 | 3:14 | S/O | Red hot maintenance | 0 | 0 | No interruption
Barishal 230/132kV | Barishal (N)-Patuakhali Ckt-02 | 2026-08-15 12:55 | 2026-08-15 15:10 | 2:15 | S/O | Red hot maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-08-01 08:37 | 2026-08-01 17:28 | 8:51 | S/O | Project work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-08-01 08:39 | 2026-08-01 17:29 | 8:50 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-08-02 08:01 | 2026-08-02 17:01 | 9:00 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-08-02 08:02 | 2026-08-02 17:02 | 9:00 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-08-03 08:01 | 2026-08-03 17:13 | 9:12 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-08-03 08:01 | 2026-08-03 17:14 | 9:13 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-08-04 08:19 | 2026-08-04 18:18 | 9:59 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-08-04 08:20 | 2026-08-04 18:19 | 9:59 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-08-05 08:30 | 2026-08-05 17:06 | 8:36 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-08-05 08:32 | 2026-08-05 17:07 | 8:35 | S/O | Maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2026-08-29 10:13 | 2026-08-29 15:14 | 5:01 | S/O | KHULNA POWER STATION WOEKS. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-2 | 2026-08-29 10:13 | 2026-08-29 15:16 | 5:03 | S/O | KHULNA POWER STATION WORKS | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-08-21 09:30 | 2026-08-21 11:28 | 1:58 | S/O | R phase CT red hot maintenance. | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-01 | 2026-08-01 08:38 | 2026-08-01 17:26 | 8:48 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-02 | 2026-08-01 08:48 | 2026-08-01 17:27 | 8:39 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-01 | 2026-08-02 08:02 | 2026-08-02 16:59 | 8:57 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-02 | 2026-08-02 08:03 | 2026-08-02 17:00 | 8:57 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-01 | 2026-08-03 08:01 | 2026-08-03 17:13 | 9:12 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-02 | 2026-08-03 08:01 | 2026-08-03 17:14 | 9:13 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-01 | 2026-08-04 08:20 | 2026-08-04 18:18 | 9:58 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-02 | 2026-08-04 08:21 | 2026-08-04 18:19 | 9:58 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-01 | 2026-08-05 08:32 | 2026-08-05 17:05 | 8:33 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/230/132kV | 230kV Faridpur CKT-02 | 2026-08-05 08:33 | 2026-08-05 17:06 | 8:33 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-1 | 2026-08-04 13:11 | 2026-08-04 13:11 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-2 | 2026-08-17 10:55 | 2026-08-17 17:44 | 6:49 | S/O | Maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal(N)-Patuakhali 132kV Ckt-1 | 2026-08-17 11:35 | 2026-08-17 14:10 | 2:35 | S/O | Red hot | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal(N)-Patuakhali 132kV Ckt-2 | 2026-08-17 11:35 | 2026-08-17 14:11 | 2:36 | S/O | Red hot | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-08-17 11:36 | 2026-08-17 14:07 | 2:31 | S/O | Red hot | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 06:32 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-08-01 10:13 | 2026-08-01 16:53 | 6:40 | S/O | SCADA integration & Commissioning | 0 | 0 | No interruption
Bheramara 230/132kV | Kushtia 2 | 2026-08-14 17:39 | 2026-08-21 09:40 | 160:01 | S/O | Kushtia Grid Maitenance | 0 | 0 | No interruption
Bheramara 230/132kV | Kushtia 1 | 2026-08-21 07:04 | 2026-08-26 21:05 | 134:01 | S/O | End of kushtia Sub- Station project work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2026-08-21 07:49 | 2026-08-21 14:20 | 6:31 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2026-08-21 07:49 | 2026-08-21 14:22 | 6:33 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2026-08-24 10:30 | 2026-08-24 13:34 | 3:04 | S/O | scaffolding work by KEC project | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2026-08-25 09:36 | 2026-08-25 13:25 | 3:49 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-08-26 09:59 | 2026-08-26 18:21 | 8:22 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-08-09 06:43 | 2026-08-09 08:38 | 1:55 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-08-10 11:52 | 2026-08-10 12:41 | 0:49 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-08-13 10:50 | 2026-08-13 10:50 | 0:00 | S/O | reconductoring work under STGE project | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramara-1 | 2026-08-21 06:57 | 2026-08-26 21:06 | 134:09 | S/O | Erection & stringing work by DWZTGE project | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2026-08-26 09:58 | 2026-08-26 18:18 | 8:20 | S/O | Maint.work | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2026-08-24 10:23 | 2026-08-24 13:34 | 3:11 | S/O | S/D for Project Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-18 21:25 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-08-14 07:56 | 2026-08-14 18:50 | 10:54 | S/O | Project work GtoG | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-08-15 07:51 | 2026-08-15 20:28 | 12:37 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-08-04 09:53 | 2026-08-04 19:04 | 9:11 | S/O |  | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-08-31 12:25 | 2026-08-31 15:07 | 2:42 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Bogura 230/132kV | 230KV Main 1 | 2026-08-20 08:29 | 2026-08-20 16:52 | 8:23 | S/O | SS Upgradation | 0 | 0 | No interruption
Bogura 230/132kV | 230KV Main 2 | 2026-08-21 07:44 | 2026-08-21 17:15 | 9:31 | S/O | ss upgradation | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 2 | 2026-08-22 08:03 | 2026-08-23 11:11 | 27:08 | S/O |  | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 1 | 2026-08-23 11:37 | 2026-08-23 16:50 | 5:13 | S/O |  | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 2 | 2026-08-31 12:40 | 2026-08-31 14:44 | 2:04 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-01 09:30 | 2026-08-01 18:26 | 8:56 | S/O | Line parameter measurement and jumper connection. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-01 09:31 | 2026-08-01 18:27 | 8:56 | S/O | Line parameter measurement and jumper connection. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-02 08:00 | 2026-08-02 19:43 | 11:43 | S/O | Line parameters measure and jumper connection. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-02 08:00 | 2026-08-02 19:43 | 11:43 | S/O | Line parameters measure and jumper connection. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-11 10:07 | 2026-08-11 13:57 | 3:50 | S/O | SAS signal Interlock and operations Check at Barapukuria North SS | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-11 10:07 | 2026-08-11 14:01 | 3:54 | S/O | SAS signal Interlock and operations Check at Barapukuria North SS | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-12 09:59 | 2026-08-12 18:19 | 8:20 | S/O | Project work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur) 230kV Switching Substation | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-12 09:59 | 2026-08-12 18:19 | 8:20 | S/O | Project work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur) 230kV Switching Substation | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-13 09:26 | 2026-08-13 18:35 | 9:09 | S/O | Project work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur) 230kV Switching Substation | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-13 09:26 | 2026-08-13 18:35 | 9:09 | S/O | Project work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur) 230kV Switching Substation | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-01 | 2026-08-13 15:30 | 2026-08-13 16:41 | 1:11 | S/O | 400kV Rahanpur Line-01 Gas Refilling of 406 SP08 ES(R-Phase) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-08-14 07:55 | 2026-08-14 18:52 | 10:57 | S/O | project work. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-08-15 07:47 | 2026-08-15 18:43 | 10:56 | S/O | OPGW will be shifted from double circuit tower to LILO four circuit tower. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-08-15 12:58 | 2026-08-15 17:55 | 4:57 | S/O | SAS & interlock related works at Parbatipur SS. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-08-15 12:58 | 2026-08-15 17:55 | 4:57 | S/O | SAS & interlock related works at Parbatipur SS. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2026-08-23 13:13 | 2026-08-25 18:26 | 53:13 | S/O | Breaker stability test at Rooppur Power Station. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-08-28 07:13 | 2026-08-28 18:09 | 10:56 | S/O | Project Work S/D of barapukuria side. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-08-03 10:38 | 2026-08-03 17:07 | 6:29 | S/O | Old bay dismantle work | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-SPPP Ckt-1 | 2026-08-04 09:51 | 2026-08-04 19:02 | 9:11 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-2 | 2026-08-04 09:51 | 2026-08-04 19:02 | 9:11 | S/O | Project work | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2026-08-21 07:46 | 2026-08-21 14:20 | 6:34 | S/O |  | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2026-08-21 07:46 | 2026-08-21 14:22 | 6:36 | S/O |  | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Chowdala 132 KV Line Ckt-02 | 2026-08-06 10:12 | 2026-08-06 11:00 | 0:48 | S/O | PD Relay Replace | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2026-08-10 17:35 | 2026-08-10 19:13 | 1:38 | S/O | Transformer sedule checkup | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-1 | 2026-08-22 09:50 | 2026-08-22 22:27 | 12:37 | S/O | OPGW replacement at Sherpur SS End | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-2 | 2026-08-22 09:50 | 2026-08-22 22:27 | 12:37 | S/O | OPGW replacement at Sherpur SS End | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-01 | 2026-08-07 06:59 | 2026-08-08 09:41 | 26:42 | S/O | Sreepur end project work | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-02 | 2026-08-07 07:17 | 2026-08-08 08:42 | 25:25 | S/O | Sreepur end project work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 02:38 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-05-05 19:13 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2026
| Area | Previous Month (July' 2026) |  |  |  | Current Month (August'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 9 | 91 | 113 | 28 | 7 | 91 | 126
2 | Dhaka (South) Grid Circle. | 22 | 11 | 57 | 90 | 18 | 10 | 59 | 87
3 | Chattogram Grid Circle. | 16 | 15 | 64 | 95 | 5 | 7 | 56 | 68
4 | Cumilla Grid Circle. | 25 | 20 | 80 | 125 | 17 | 26 | 67 | 110
5 | Khulna Grid Circle. | 22 | 9 | 86 | 117 | 9 | 5 | 62 | 76
6 | HVDC Grid Circle | 26 | 16 | 29 | 71 | 11 | 5 | 22 | 38
7 | Bogura Grid Circle. | 21 | 30 | 48 | 99 | 13 | 13 | 62 | 88
8 | Others
9 | Total | 145 | 110 | 455 | 710 | 101 | 73 | 419 | 593
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: August 2026
| Area | Previous Month (July' 2026) |  |  |  | Current Month (August '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 1061.12 | 456.17 | 3581.01 | 5098.3 | 830.85 | 34.73 | 2652.04 | 3517.6167
2 | Dhaka (South) Grid Circle. | 453.38 | 81.67 | 2234.54 | 2769.59 | 281.85 | 198.9 | 772 | 1252.75
3 | Chattogram Grid Circle. | 119.17 | 38.67 | 649.62 | 807.46 | 4.2 | 103.35 | 147.73 | 255.2833
4 | Cumilla Grid Circle. | 218.04 | 388.47 | 435.23 | 1041.74 | 197.75 | 1196.52 | 921.33 | 2315.35
5 | Khulna Grid Circle. | 151.75 | 101.9 | 724.26 | 977.91 | 37.87 | 44.5 | 590.95 | 673.3167
6 | HVDC Grid Circle | 87.16 | 195.47 | 65.33 | 347.96 | - | 100.8 | 2.15 | 102.95
7 | Bogura Grid Circle. | 183.38 | 565.13 | 1378.69 | 2127.2 | 95.92 | 241.5 | 342.07 | 679.4833
8 | Others | bar: Energy unserved ( MWH ) due to Total
9 | Total | 2274 | 1827.48 | 9068.68 | 13170.16 | 1448.44 | 1920.3 | 5428.27 | 8796.75
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 17 | 16 | 33 | 8 | 5 | 20 | 2364.6
2 | Dhaka (South) | 5031.6 | 8 | 5 | 13 | 5 | 3 | 5 | 1168.83
3 | Chattogram | 2042 | 4 | 5 | 9 | 1 |  | 8 | 255.28
4 | Khulna | 2434 | 6 | 13 | 19 | 4 | 1 | 14 | 673.32
5 | HVDC | 5954.3 | 3 | 1 | 4 | 1 | 1 | 2 | 102.95
6 | Bogura | 3145.6 | 7 | 7 | 14 | 1 | 3 | 10 | 643.08
7 | Cumilla | 2981 | 21 | 19 | 40 | 10 | 3 | 27 | 2229.88
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 7437.94
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 98.98%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | HVDC | 99.99%
6 | Bogura | 99.95%
7 | Cumilla | 99.72% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 6 | 6 | 12 | 7 | - | 5 | 1153.02
2 | Dhaka (South) | 990.29 | - | 2 | - | 2 | 1 | - | 1 | 83.92
3 | Chattogram | 917 | - | - | - | - | - | - | - | 0
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | 0
5 | HVDC | 1325 | - | - | - | - | - | - | - | 0
6 | Bogura | 1803.3 |  | 2 | - | 2 | 1 | 1 |  | 36.4
7 | Cumilla | 1648.16 | - | 1 | 1 | 2 | 1 | - | 1 | 85.47
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1358.81
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-08-01 | 28 | - | 11 | 20 hr 12 min | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Amnura 132/33kV | 1 | 0.0020833 | 0.4
Ashuganj 132/33kV | 2 | 4:31 | 654.1667
Bagerhat 132/33kV | 1 | 1:25 | 35.4167
Bajitpur 132/33kV | 1 | 1:14 | 49.3333
Barapukuria 230/132/33kV | 1 | 1:07 | 33.5
Barishal 132/33kV | 5 | 4:21 | 119.5833
Barishal 230/132kV | 1 | 2:57 | 67.85
Baroirhat 132/33kV | 2 | 3:02 | 66.7333
Beanibazar 132/33kV | 1 | 1:32 | 46
Benapole 132/33kV | 1 | 0:09 | 3.3
Bhaluka 132/33kV | 10 | 7:33 | 439.0833
Bhulta 132/33kV | 3 | 7:46 | 466
Bhulta 400/230/132kV | 1 | 0:19 | 50.6667
Bog-Sherpur 132/33kV | 3 | 6:31 | 93.1667
Bogura 132/33kV | 1 | 2:09 | 43
Brahmanbaria 132/33kV | 4 | 0.40903 | 361.4167
Chandpur 132/33kV | 4 | 7:34 | 136.9
Charfasson 230/33kV | 1 | 1:29 | 44.5
Chauddagram 132/33kV | 1 | 1:17 | 38.5
Chowmuhani 230/132/33kV | 5 | 7:43 | 188.8333
Cumilla(S) 132/33kV | 2 | 1:42 | 51
Daganbhuiyan 132/33kV | 2 | 10:18 | 113.0167
Daudkandi 132/33kV | 1 | 0:19 | 11.0833
Dhamrai 132/33kV | 2 | 6:28 | 338.0833
Dohazari 132/33kV | 3 | 3:03 | 62.2
Faridpur 132/33kV | 1 | 2:07 | 82.55
Fenchuganj 230/132/33kV | 3 | 6:59 | 124.85
Feni 132/33kV | 3 | 2:00 | 69.6
Ghatail 132/33kV | 2 | 6:27 | 306.1667
Goalpara 132/33kV | 1 | 2:28 | 19.7333
Gopalganj 132/33kV | 1 | 2:28 | 37
Hasnabad 132/33kV | 2 | 0:24 | 10.8
Hasnabad 230/132kV | 1 | 0:27 | 108
Ishurdi 132/33kV | 1 | 0:11 | 4.95
Jamalpur 132/33kV | 3 | 8:33 | 141.3333
Jashore 132/33kV | 2 | 2:16 | 75
Kabirpur 132/33kV | 3 | 2:24 | 90.6667
Kachua 230/132/33kV | 3 | 3:43 | 126.2833
Kaliakoir 400/230/132kV | 2 | 0:09 | 13.5
Kasba 132/33kV | 1 | 3:35 | 71.6667
Khulna (C) | 1 | 1:27 | 8.7
Kishoreganj 132/33kV | 3 | 3:20 | 286.9333
Kodda 132/33kV | 9 | 13:59 | 891.3333
Kulaura 132/33kV | 1 | 1:58 | 62.9333
Kurigram 132/33kV | 1 | 0:14 | 1.1667
Madanganj 132/33kV | 0 | 0:00 | 0
Madunaghat 132/33kV | 1 | 2:49 | 36.6167
Maniknagar 132/33kV | 1 | 1:45 | 33.25
Meghnaghat 400/230kV | 0 | 0:00 | 0
Mirzapur 132/33kV | 1 | 1:08 | 26.0667
Mongla 132/33kV | 2 | 6:45 | 183.3
Mymensingh 132/33kV | 3 | 2:08 | 118.8333
Nabinagar 132/33kV | 2 | 4:29 | 449.4167
Naogaon 132/33kV | 2 | 2:24 | 110.25
Narail 132/33kV | 1 | 1:03 | 27.3
Natore 132/33kV | 2 | 4:09 | 87.15
Nawabganj 132/33kV | 4 | 17:31 | 262.45
Niamatpur 132/33kV | 1 | 1:22 | 27.3333
Noapara 132/33kV | 1 | 1:18 | 22.1
Pabna 132/33kV | 1 | 1:32 | 23
Patiya 132/33kV | 3 | 6:18 | 89.7333
Patuakhali 132/33kV | 1 | 1:10 | 5.8333
Purbasadipur 230/132/33kV | 1 | 1:43 | 106.4333
Rajbari 132/33kV | 1 | 0:51 | 16.15
Rajendrapur 132/33kV | 0 | 0:00 | 0
Rangpur 132/33kV | 1 | 2:22 | 59.1667
Shahjibazar 132/33kV | 2 | 3:38 | 167.3333
Sherpur 132/33kV | 1 | 1:44 | 39.8667
Shomvuganj 400/132kV | 1 | 2:52 | 143.3333
Sonargaon 132/33kV | 3 | 4:47 | 321.5833
Sreepur 230/132/33kV | 1 | 2:55 | 175
Sunamganj 132/33kV | 2 | 0:36 | 17.7667
Sylhet 132/33kV | 5 | 4:22 | 74
Tangail 132/33kV | 1 | 0:52 | 8.6667
Taraganj 132/33kV | 1 | 0:43 | 17.9167
Thakurgaon 132/33kV | 1 | 1:40 | 100
| 150 | 244:26 | 8796.75
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August 2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 24 | 2026-08-13 12:00
2 | AKSML | 183.2 | 2026-08-01 05:00
3 | Aftabnagar | 50 | 2026-08-28 00:00
4 | Agargaon | 135 | 2026-08-27 14:00
5 | Agrabad | 78 | 2026-08-25 18:30
6 | Amnura | 39 | 2026-08-02 12:00
7 | Araihazar | N/A | N/A
8 | Ashuganj | 109 | 2026-08-04 21:00
9 | BSRM | 207 | 2026-08-09 02:00
10 | Bagerhat | 98 | 2026-08-19 23:00
11 | Bajitpur | 108 | 2026-08-15 19:30
12 | Bakerganj | 16.2 | 2026-08-12 19:30
13 | Bakulia | 103 | 2026-08-08 20:00
14 | Banani | 80.8 | 2026-08-10 13:00
15 | Bangabhaban | 19 | 2026-08-02 10:00
16 | Barapukuria | 86 | 2026-08-12 22:00
17 | Barguna | 26 | 2026-08-26 02:00
18 | Barishal | 112 | 2026-08-03 12:00
19 | Barishal-230 | 122 | 2026-08-15 21:00
20 | Baroaulia | 73 | 2026-08-08 19:00
21 | Baroirhat | 70 | 2026-08-15 16:00
22 | Bashundhara | 256 | 2026-08-30 14:00
23 | BashundharaCement | 15 | 2026-08-10 19:00
24 | Beanibazar | 96 | 2026-08-31 22:00
25 | Benapole | 69 | 2026-08-13 07:00
26 | Bhaluka | 201 | 2026-08-19 17:00
27 | Bhandaria | 64 | 2026-08-21 22:00
28 | Bhangura | 44 | 2026-08-21 21:00
29 | Bheramara(GK) | 80 | 2026-08-23 19:30
30 | Bhulta | 239 | 2026-08-19 10:00
31 | Bog-Sherpur | 88 | 2026-08-12 22:00
32 | Bogura | 229 | 2026-08-22 23:00
33 | Borhanuddin | 84 | 2026-08-20 23:00
34 | Brahmanbaria | 142 | 2026-08-21 13:00
35 | Cantonment | 154 | 2026-08-30 13:00
36 | Chandina | 53 | 2026-08-20 14:00
37 | Chandpur | 96 | 2026-08-21 21:00
38 | Chandraghona | 41 | 2026-08-24 19:00
39 | Chapai | 86 | 2026-08-12 23:00
40 | Charfasson | 36 | 2026-08-22 23:00
41 | Charsaidpur | 48 | 2026-08-30 16:00
42 | Chauddagram | 87 | 2026-08-12 22:00
43 | Chhatak | 43 | 2026-08-13 21:00
44 | Chowmuhani | 172 | 2026-08-21 22:00
45 | Chuadanga | 132 | 2026-08-22 23:00
46 | Coxsbazar | 149 | 2026-08-07 21:00
47 | Cumilla(N) | 179 | 2026-08-26 20:00
48 | Cumilla(S) | 198 | 2026-08-03 15:00
49 | Daganbhuiyan | 48 | 2026-08-01 22:00
50 | Daudkandi | 171 | 2026-08-21 22:00
51 | DhakaUniversity | 108 | 2026-08-02 13:00
52 | Dhamrai | 112 | 2026-08-20 12:00
53 | Dhanmondi | 139.6 | 2026-08-30 13:00
54 | Dohazari | 127 | 2026-08-22 19:30
55 | Faridpur | 202 | 2026-08-22 22:00
56 | Fatullah | 121 | 2026-08-11 15:00
57 | Fenchuganj | 59 | 2026-08-12 22:00
58 | Feni | 124 | 2026-08-12 22:00
59 | GPH | 74 | 2026-08-09 05:00
60 | Ghatail | 107 | 2026-08-23 20:00
61 | Ghorashal | 0 | 2026-08-01 00:00
62 | Ghorashal-230 | 116 | 2026-08-17 09:00
63 | Goalpara | 45 | 2026-08-23 19:00
64 | Gollamari | 122 | 2026-08-12 12:00
65 | Gopalganj | 127 | 2026-08-28 20:00
66 | Gulshan | 138 | 2026-08-27 14:00
67 | Halishahar | 165 | 2026-08-22 11:00
68 | HaripurSBU | 151 | 2026-08-16 12:00
69 | Hasnabad | 118 | 2026-08-29 21:00
70 | Hathazari | 109 | 2026-08-28 01:00
71 | Hatirjheel | 99 | 2026-08-24 15:00
72 | Ishurdi | 91 | 2026-08-31 19:30
73 | Jaldhaka | 108 | 2026-08-16 23:00
74 | Jamalpur | 144 | 2026-08-14 19:30
75 | Jashore | 186 | 2026-08-29 19:00
76 | Jhenaidah | 110 | 2026-08-23 00:00
77 | Joydebpur | 192 | 2026-08-29 19:00
78 | Joypurhat | 76 | 2026-08-23 21:00
79 | Juldah | 23 | 2026-08-12 17:00
80 | KSRM | 48.5 | 2026-08-12 07:00
81 | Kabirpur | 294 | 2026-08-29 19:30
82 | Kachua | 114 | 2026-08-12 22:00
83 | Kaliganj | 45 | 2026-08-20 19:00
84 | Kallyanpur | 138 | 2026-08-22 18:30
85 | Kalurghat | 66 | 2026-08-31 00:00
86 | Kamrangirchar | 86 | 2026-08-04 12:00
87 | Kaptai | N/A | N/A
88 | Kasba | 52 | 2026-08-29 18:30
89 | Kazla | 133 | 2026-08-11 13:00
90 | Keranigonj | 108 | 2026-08-30 19:30
91 | Khagrachori | 42 | 2026-08-12 20:00
92 | Khulna | 85 | 2026-08-22 13:00
93 | Khulshi | 195 | 2026-08-22 12:00
94 | Kishoreganj | 150 | 2026-08-21 21:00
95 | Kodda | 334 | 2026-08-18 21:00
96 | Kulaura | 64 | 2026-08-31 22:00
97 | Kurigram | 86 | 2026-08-31 19:30
98 | Kushtia | 185 | 2026-08-31 19:30
99 | Laksam | 40 | 2026-08-25 13:00
100 | Lakshmipur | 56 | 2026-08-14 22:00
101 | Lalbag | 107 | 2026-08-23 17:00
102 | Lalmonirhat | 78 | 2026-08-16 20:00
103 | MI_Cement | 19.4 | 2026-08-11 15:00
104 | Madanganj | 56 | 2026-08-13 19:00
105 | Madaripur | 133 | 2026-08-15 23:00
106 | Madartek | 102 | 2026-08-30 00:00
107 | Madunaghat | 64 | 2026-08-22 18:00
108 | Magura | 79 | 2026-08-12 22:00
109 | Mahasthangarh | 89 | 2026-08-12 23:00
110 | Maijdee | 51 | 2026-08-20 23:00
111 | Manikganj | 162 | 2026-08-22 22:00
112 | Maniknagar | 90 | 2026-08-23 14:00
113 | Matarbari | 60 | 2026-08-08 19:30
114 | Matuail | 84 | 2026-08-04 00:00
115 | Metrorail_Motijheel | 55 | 2026-08-20 18:30
116 | Metrorail_Uttara | 0 | 2026-08-01 00:00
117 | Millgate | 118 | 2026-08-10 16:00
118 | Mirpur | 174 | 2026-08-22 19:00
119 | Mirsorai | 53 | 2026-08-08 14:00
120 | Mirzapur | 56 | 2026-08-18 21:00
121 | Mithapukur | 92 | 2026-08-01 21:00
122 | Modern | N/A | N/A
123 | Mogbazar | 69.7 | 2026-08-31 17:00
124 | Mongla | 53 | 2026-08-13 11:00
125 | Motijheel | 58 | 2026-08-23 13:00
126 | Muktagacha | 51 | 2026-08-29 11:00
127 | Munshiganj | 135 | 2026-08-27 20:00
128 | Muradnagar | 58 | 2026-08-12 22:00
129 | Mymensingh | 166 | 2026-08-31 20:00
130 | Nabinagar | 146 | 2026-08-13 16:00
131 | Naogaon | 152 | 2026-08-16 00:00
132 | Narail | 69 | 2026-08-21 21:00
133 | Narinda | 82 | 2026-08-03 13:00
134 | Narshingdi | 211 | 2026-08-27 20:00
135 | Natore | 181 | 2026-08-26 20:00
136 | Nawabganj | 72.8 | 2026-08-22 22:00
137 | Netrakona | 150 | 2026-08-14 18:30
138 | New | 102 | 2026-08-25 11:00
139 | Niamatpur | 95 | 2026-08-15 23:00
140 | Noapara | 53 | 2026-08-12 22:00
141 | PHP | 15 | 2026-08-27 19:00
142 | Pabna | 121 | 2026-08-22 19:00
143 | Palashbari | 156 | 2026-08-27 23:00
144 | Panchagarh | 81 | 2026-08-15 19:30
145 | Patiya | 23 | 2026-08-30 04:00
146 | Patnitala | 41 | 2026-08-23 22:00
147 | Patuakhali | 76.5 | 2026-08-21 22:00
148 | Payra | 40 | 2026-08-12 21:00
149 | Postogola | 68 | 2026-08-01 13:00
150 | Pubail | 52 | 2026-08-10 20:00
151 | Purbachal | 40 | 2026-08-10 01:00
152 | Purbasadipur | 158 | 2026-08-12 22:00
153 | Rahanpur | 51 | 2026-08-12 21:00
154 | Rahim | 57 | 2026-08-03 04:00
155 | Rajbari | 100 | 2026-08-22 20:00
156 | Rajendrapur | 134 | 2026-08-22 18:30
157 | Rajshahi | 127 | 2026-08-12 22:00
158 | Rajshahi-230 | 118 | 2026-08-22 21:00
159 | Ramganj | 122 | 2026-08-21 19:00
160 | Rampur | 52 | 2026-08-07 21:00
161 | Rangamati | 21 | 2026-08-28 13:00
162 | Rangpur | 168 | 2026-08-31 19:00
163 | Ruppur | 20.8 | 2026-08-13 18:00
164 | SSM | 8 | 2026-08-30 04:00
165 | Saidpur | 123 | 2026-08-02 10:00
166 | Santhia | 46 | 2026-08-23 21:00
167 | Satkhira | 150 | 2026-08-22 19:00
168 | Satmasjid | 120 | 2026-08-22 19:00
169 | Savar | 232 | 2026-08-11 17:00
170 | SevenRings | 24.18 | 2026-08-24 16:00
171 | ShahCement | 37 | 2026-08-02 09:00
172 | Shahjadpur | 91 | 2026-08-09 22:00
173 | Shahjibazar | 165 | 2026-08-14 19:00
174 | Shahmirpur | 64 | 2026-08-24 02:00
175 | Shariatpur | 119 | 2026-08-22 22:00
176 | Sherpur | 170 | 2026-08-28 21:00
177 | Shikalbaha | 42 | 2026-08-31 20:00
178 | Shitalakhya | 90.1 | 2026-08-12 13:00
179 | Sholosohor | 60 | 2026-08-10 20:00
180 | Shomvuganj | 62 | 2026-08-21 22:00
181 | Shyampur | 194 | 2026-08-23 11:00
182 | Siddhirganj | 150 | 2026-08-29 13:00
183 | Sirajganj | 138 | 2026-08-26 21:00
184 | Sitakunda | 37 | 2026-08-03 19:00
185 | Sonargaon | 165 | 2026-08-17 15:00
186 | Sreemongol | 98 | 2026-08-21 21:00
187 | Sreepur | 156 | 2026-08-19 12:00
188 | Srinagar | 58.33 | 2026-08-27 22:00
189 | Sunamganj | 66 | 2026-08-21 19:30
190 | Sylhet | 151 | 2026-08-15 20:00
191 | Sylhet_(South) | 88 | 2026-08-11 22:00
192 | TK | 25 | 2026-08-01 18:30
193 | Tangail | 198 | 2026-08-28 20:00
194 | Taraganj | 39 | 2026-08-12 18:30
195 | Tasnim | 48 | 2026-08-04 15:00
196 | Thakurgaon | 131 | 2026-08-12 23:00
197 | Tongi | 173 | 2026-08-20 10:00
198 | Ullahpara | 43 | 2026-08-21 19:30
199 | Ullon | 67 | 2026-08-28 00:00
200 | Uttara | 112 | 2026-08-23 17:00
201 | UttaraNew | 62 | 2026-08-12 00:00
202 | Zigatola | 118 | 2026-08-11 22:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: August 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 6205.46 | 2026-08-22 | 19:00
Chattogram | 1667 | 2026-08-09 | 20:00
Cumilla | 1688 | 2026-08-21 | 23:00
Mymensingh | 1262 | 2026-08-21 | 22:00
Sylhet | 739 | 2026-08-21 | 22:00
Khulna | 2027 | 2026-08-22 | 23:00
Barishal | 544.6 | 2026-08-12 | 21:00
Rajshahi | 1743.4 | 2026-08-12 | 23:00
Rangpur | 1221 | 2026-08-12 | 22:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August 2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 434 | 2026-08-02 10:00 | 336 | 2026-08-03 12:00
2 | Amtali | 400 | 415 | 2026-08-08 17:00 | 399 | 2026-08-02 14:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 399 | 2026-08-07 07:00 | 345 | 2026-08-03 12:00
5 | Bibiana | 400 | 383 | 2026-08-07 07:00 | 360 | 2026-08-03 12:00
6 | BIPTC | 400 | 406 | 2026-08-28 18:00 | 390 | 2026-08-22 15:00
7 | Bogura | 400 | 401 | 2026-08-08 09:00 | 341 | 2026-08-15 23:00
8 | Gopalganj | 400 | 397 | 2026-08-21 05:00 | 365 | 2026-08-02 12:00
9 | Kaliakoir | 400 | 377 | 2026-08-21 20:00 | 327 | 2026-08-03 12:00
10 | Korerhat | 400 | 403 | 2026-08-07 06:00 | 365 | 2026-08-04 03:00
11 | Madunaghat | 400 | 405 | 2026-08-07 06:00 | 380 | 2026-08-02 13:00
12 | Meghnaghat | 400 | 394 | 2026-08-29 06:00 | 339 | 2026-08-02 13:00
13 | Mirsorai | 400 | 406 | 2026-08-29 04:00 | 371 | 2026-08-04 15:00
14 | Payra | 400 | 418 | 2026-08-29 05:00 | 401 | 2026-08-02 11:00
15 | Rahanpur | 400 | 414 | 2026-08-08 00:00 | 384 | 2026-08-24 00:00
16 | Rampal | 400 | 401 | 2026-08-29 02:00 | 375 | 2026-08-02 11:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 235 | 2026-08-29 03:00 | 201 | 2026-08-03 12:00
2 | AKSML | 230 | 241 | 2026-08-19 18:00 | 221 | 2026-08-02 11:00
3 | Aminbazar | 230 | 235 | 2026-08-03 12:00 | 202 | 2026-08-03 12:00
4 | Ashuganj | 230 | 232 | 2026-08-15 00:00 | 204 | 2026-08-13 12:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 237 | 2026-08-07 18:00 | 215 | 2026-08-12 22:00
7 | Barapukuria | 230 | 228 | 2026-08-08 18:30 | 207 | 2026-08-15 23:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barapukuria(N) | 230 | 230 | 2026-08-30 09:00 | 225 | 2026-08-30 07:00
10 | Barishal | 230 | 229 | 2026-08-07 07:00 | 216 | 2026-08-02 11:00
11 | Bheramara | 230 | 236 | 2026-08-21 23:00 | 205 | 2026-08-13 21:00
12 | Bhulta | 230 | 230 | 2026-08-07 07:00 | 196 | 2026-08-03 12:00
13 | Bibiana | 230 | 223 | 2026-08-08 18:00 | 207 | 2026-08-03 14:00
14 | BIPTC | 230 | 238 | 2026-08-01 02:00 | 206 | 2026-08-13 21:00
15 | Birulia | 230 | 234 | 2026-08-21 06:00 | 206 | 2026-08-18 12:00
16 | Bogura | 230 | 247 | 2026-08-07 18:30 | 220 | 2026-08-23 23:00
17 | Bogura-400 | 230 | 247 | 2026-08-07 18:30 | 220 | 2026-08-23 23:00
18 | Borhanuddin | 230 | 233 | 2026-08-23 21:00 | 221 | 2026-08-23 23:00
19 | BSRM | 230 | 232 | 2026-08-29 04:00 | 211 | 2026-08-04 15:00
20 | Charfasson | 230 | 235 | 2026-08-29 09:00 | 222 | 2026-08-24
21 | Chowmuhani | 230 | 231 | 2026-08-07 07:00 | 212 | 2026-08-03 12:00
22 | Cumilla(N) | 230 | 234 | 2026-08-08 00:00 | 203 | 2026-08-02 11:00
23 | Faridpur | 230 | 225 | 2026-08-07 07:00 | 195 | 2026-08-02 11:00
24 | Fenchuganj | 230 | 224 | 2026-08-08 18:00 | 209 | 2026-08-13 20:00
25 | Feni | 230 | 230 | 2026-08-29 05:00 | 207 | 2026-08-02 13:00
26 | Ghorashal | 230 | 230 | 2026-08-01 01:00 | 200 | 2026-08-18 10:00
27 | Ghorashal-230 | 230 | 223 | 2026-08-29 04:00 | 189 | 2026-08-02 14:00
28 | Gopalganj | 230 | 225 | 2026-08-07 06:00 | 210 | 2026-08-02 11:00
29 | GPH | 230 | 239 | 2026-08-29 14:00 | 220 | 2026-08-04 15:00
30 | Haripur | 230 | 230 | 2026-08-29 04:00 | 197 | 2026-08-03 12:00
31 | Hasnabad | 230 | 233 | 2026-08-29 06:00 | 198 | 2026-08-03 12:00
32 | Hathazari | 230 | 238 | 2026-08-07 02:00 | 223 | 2026-08-04 15:00
33 | Ishurdi | 230 | 237 | 2026-08-01 01:00 | 208 | 2026-08-13 21:00
34 | Jhenaidah | 230 | 229 | 2026-08-02 01:00 | 195 | 2026-08-12 22:00
35 | Kachua | 230 | 233 | 2026-08-08 19:30 | 211 | 2026-08-04 15:00
36 | Kaliakoir | 230 | 233 | 2026-08-07 07:00 | 200 | 2026-08-03 12:00
37 | Keranigonj | 230 | 233 | 2026-08-29 04:00 | 199 | 2026-08-02 13:00
38 | Khulna(S) | 230 | 230 | 2026-08-29 02:00 | 207 | 2026-08-13 21:00
39 | Korerhat | 230 | 231 | 2026-08-07 07:00 | 211 | 2026-08-04 15:00
40 | Madunaghat | 230 | 241 | 2026-08-21 20:00 | 227 | 2026-08-02 12:00
41 | Madunaghat-400 | 230 | 243 | 2026-08-21 21:00 | 228 | 2026-08-02 13:00
42 | Maniknagar | 230 | 229 | 2026-08-29 05:00 | 194 | 2026-08-03 12:00
43 | Meghnaghat | 230 | 237 | 2026-08-29 04:00 | 205 | 2026-08-03 12:00
44 | Meghnaghat-400 | 230 | 233 | 2026-08-29 04:00 | 200 | 2026-08-02 11:00
45 | Mirsorai | 230 | 236 | 2026-08-08 19:00 | 216 | 2026-08-04 12:00
46 | Naogaon | 230 | 230 | 2026-08-07 18:30 | 195 | 2026-08-20 21:00
47 | Purbasadipur | 230 | 228 | 2026-08-31 01:00 | 202 | 2026-08-15 23:00
48 | Rajshahi | 230 | 248 | 2026-08-03 17:00 | 203 | 2026-08-13 21:00
49 | Rampal | 230 | 229 | 2026-08-29 02:00 | 210 | 2026-08-13 20:00
50 | Rampur | 230 | N/A | N/A | N/A | N/A
51 | Rampura | 230 | 230 | 2026-08-29 06:00 | 194 | 2026-08-02 13:00
52 | Shikalbaha | 230 | 241 | 2026-08-15 00:00 | 226 | 2026-08-18 10:00
53 | Shyampur | 230 | 232 | 2026-08-29 06:00 | 198 | 2026-08-03 12:00
54 | Siddhirganj | 230 | 231 | 2026-08-29 05:00 | 199 | 2026-08-02 12:00
55 | Sirajgonj | 230 | 239 | 2026-08-08 | 223 | 2026-08-23 23:00
56 | Sreepur | 230 | 230 | 2026-08-08 02:00 | 198 | 2026-08-07 11:00
57 | Tongi | 230 | 225 | 2026-08-07 04:00 | 192 | 2026-08-02 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 140 | 2026-08-02 04:00 | 117 | 2026-08-03 12:00
2 | Agargaon | 132 | 141 | 2026-08-07 06:00 | 116 | 2026-08-02 12:00
3 | Agrabad | 132 | 138 | 2026-08-01 00:00 | 127 | 2026-08-18 11:00
4 | AKS | 132 | 135 | 2026-08-01 00:00 | 126 | 2026-08-04 11:00
5 | Aminbazar | 132 | 136 | 2026-08-29 06:00 | 113 | 2026-08-03 12:00
6 | Amnura | 132 | 139 | 2026-08-09 00:00 | 118 | 2026-08-18 22:00
7 | Araihazar | 132 | N/A | N/A | N/A | N/A
8 | Ashuganj | 132 | 134 | 2026-08-15 00:00 | 117 | 2026-08-04 15:00
9 | Ashuganj-230 | 132 | 135 | 2026-08-15 00:00 | 123 | 2026-08-07 11:00
10 | Bagerhat | 132 | 132 | 2026-08-29 09:00 | 114 | 2026-08-12 23:00
11 | Bajitpur | 132 | 130 | 2026-08-12 23:00 | 114 | 2026-08-03 16:00
12 | Bakerganj | 132 | 135 | 2026-08-07 07:00 | 124 | 2026-08-12 22:00
13 | Bakulia | 132 | 140 | 2026-08-01 01:00 | 129 | 2026-08-03 15:00
14 | Banani | 132 | 140 | 2026-08-10 03:00 | 116 | 2026-08-03 12:00
15 | Bangabhaban | 132 | 142 | 2026-08-29 04:00 | 111 | 2026-08-02 13:00
16 | Barapukuria | 132 | 139 | 2026-08-08 18:30 | 121 | 2026-08-15 23:00
17 | Barguna | 132 | 134 | 2026-08-07 07:00 | 124 | 2026-08-02 11:00
18 | Barishal | 132 | 134 | 2026-08-07 18:00 | 123 | 2026-08-02 11:00
19 | Barishal-230 | 132 | 134 | 2026-08-02 03:00 | 123 | 2026-08-23 23:00
20 | Baroaulia | 132 | 139 | 2026-08-01 00:00 | 128 | 2026-08-13 16:00
21 | Baroirhat | 132 | 134 | 2026-08-29 07:00 | 122 | 2026-08-03 12:00
22 | Bashundhara | 132 | 141 | 2026-08-10 04:00 | 111 | 2026-08-02 12:00
23 | BashundharaCement | 132 | 136 | 2026-08-29 06:00 | 117 | 2026-08-03 12:00
24 | Beanibazar | 132 | 126 | 2026-08-11 | 112 | 2026-08-12 18:00
25 | Benapole | 132 | 138 | 2026-08-05 18:00 | 105 | 2026-08-12 22:00
26 | Bhaluka | 132 | 138 | 2026-08-27 23:00 | 113 | 2026-08-02 17:00
27 | Bhandaria | 132 | 132 | 2026-08-01 04:00 | 117 | 2026-08-12 22:00
28 | Bhangura | 132 | 137 | 2026-08-14 17:00 | 120 | 2026-08-18 22:00
29 | Bheramara | 132 | 139 | 2026-08-30 09:00 | 120 | 2026-08-12 22:00
30 | Bheramara(GK) | 132 | 138 | 2026-08-01 01:00 | 120 | 2026-08-12 22:00
31 | Bhulta | 132 | 131 | 2026-08-07 07:00 | 115 | 2026-08-02 12:00
32 | Bhulta-400 | 132 | 133 | 2026-08-07 07:00 | 113 | 2026-08-03 12:00
33 | Birulia | 132 | 137 | 2026-08-29 03:00 | 122 | 2026-08-18 12:00
34 | Bog-Sherpur | 132 | 139 | 2026-08-07 18:30 | 121 | 2026-08-12 22:00
35 | Bogura | 132 | 141 | 2026-08-07 18:30 | 125 | 2026-08-16 21:00
36 | Bogura-230 | 132 | 142 | 2026-08-07 18:30 | 126 | 2026-08-12 22:00
37 | Brahmanbaria | 132 | 130 | 2026-08-29 06:00 | 115 | 2026-08-07 11:00
39 | Cantonment | 132 | 141 | 2026-08-07 07:00 | 116 | 2026-08-02 12:00
40 | Chandina | 132 | 134 | 2026-08-29 06:00 | 118 | 2026-08-02 11:00
41 | Chandpur | 132 | 137 | 2026-08-08 18:30 | 120 | 2026-08-04 15:00
42 | Chandraghona | 132 | 139 | 2026-08-01 01:00 | 130 | 2026-08-08 19:00
43 | Chapai | 132 | 136 | 2026-08-08 18:30 | 120 | 2026-08-20 21:00
44 | Charsaidpur | 132 | 137 | 2026-08-07 07:00 | 117 | 2026-08-02 11:00
45 | Chauddagram | 132 | 133 | 2026-08-29 05:00 | 118 | 2026-08-02 13:00
46 | Chhatak | 132 | 125 | 2026-08-01 02:00 | 107 | 2026-08-12 18:30
47 | Chowmuhani | 132 | 130 | 2026-08-07 07:00 | 118 | 2026-08-04 15:00
48 | Chuadanga | 132 | 139 | 2026-08-26 18:30 | 111 | 2026-08-12 22:00
49 | Coxsbazar | 132 | 134 | 2026-08-21 18:30 | 110 | 2026-08-28 13:00
50 | Cumilla(N) | 132 | 133 | 2026-08-07 07:00 | 118 | 2026-08-02 13:00
51 | Cumilla(S) | 132 | 133 | 2026-08-07 07:00 | 116 | 2026-08-22 14:00
52 | Daganbhuiyan | 132 | 133 | 2026-08-07 07:00 | 120 | 2026-08-02 13:00
53 | Daudkandi | 132 | 131 | 2026-08-29 06:00 | 113 | 2026-08-02 11:00
54 | DhakaUniversity | 132 | 140 | 2026-08-02 03:00 | 117 | 2026-08-03 12:00
55 | Dhamrai | 132 | 137 | 2026-08-08 01:00 | 114 | 2026-08-18 11:00
56 | Dhanmondi | 132 | 140 | 2026-08-02 05:00 | 117 | 2026-08-03 12:00
57 | Dohazari | 132 | 137 | 2026-08-29 14:00 | 124 | 2026-08-02 12:00
58 | Faridpur | 132 | 130 | 2026-08-07 07:00 | 115 | 2026-08-02 11:00
59 | Fatullah | 132 | 139 | 2026-08-07 07:00 | 116 | 2026-08-03 12:00
60 | Fenchuganj | 132 | 132 | 2026-08-12 03:00 | 122 | 2026-08-13 20:00
61 | Feni | 132 | 134 | 2026-08-29 05:00 | 121 | 2026-08-04 16:00
62 | Feni-230 | 132 | 134 | 2026-08-07 07:00 | 120 | 2026-08-02 13:00
63 | Ghatail | 132 | 130 | 2026-08-08 15:00 | 112 | 2026-08-02 20:00
64 | Ghorashal | 132 | 133 | 2026-08-21 19:30 | 115 | 2026-08-01 15:00
65 | Goalpara | 132 | 138 | 2026-08-29 04:00 | 122 | 2026-08-12 22:00
66 | Gollamari | 132 | 137 | 2026-08-14 18:00 | 122 | 2026-08-18 20:00
67 | Gopalganj | 132 | 134 | 2026-08-15 09:00 | 120 | 2026-08-13 20:00
68 | Gopalganj-400 | 132 | 134 | 2026-08-29 03:00 | 121 | 2026-08-25 12:00
69 | Gulshan | 132 | 139 | 2026-08-01 04:00 | 119 | 2026-08-02 13:00
70 | Halishahar | 132 | 140 | 2026-08-07 06:00 | 127 | 2026-08-13 17:00
71 | Haripur | 132 | 138 | 2026-08-29 06:00 | 118 | 2026-08-03 12:00
72 | HaripurSBU | 132 | 139 | 2026-08-23 03:00 | 118 | 2026-08-03 12:00
73 | Hasnabad | 132 | 138 | 2026-08-30 08:00 | 116 | 2026-08-03 12:00
74 | Hathazari | 132 | 139 | 2026-08-07 02:00 | 126 | 2026-08-06 07:00
75 | Hatirjheel | 132 | 140 | 2026-08-02 04:00 | 118 | 2026-08-02 13:00
76 | Ishurdi | 132 | 140 | 2026-08-01 01:00 | 122 | 2026-08-13 21:00
77 | Jaldhaka | 132 | 135 | 2026-08-31 01:00 | 117 | 2026-08-15 23:00
78 | Jamalpur | 132 | 139 | 2026-08-11 05:00 | 112 | 2026-08-04 02:00
79 | Jashore | 132 | 140 | 2026-08-17 16:00 | 113 | 2026-08-10 19:00
80 | Jhenaidah | 132 | 140 | 2026-08-05 16:00 | 110 | 2026-08-23 20:00
81 | Jhenaidah-230 | 132 | 141 | 2026-08-02 01:00 | 115 | 2026-08-12 22:00
82 | Joydebpur | 132 | 135 | 2026-08-07 19:00 | 112 | 2026-08-01 11:00
83 | Joypurhat | 132 | 136 | 2026-08-07 18:30 | 116 | 2026-08-12 22:00
84 | Juldah | 132 | 139 | 2026-08-01 00:00 | 129 | 2026-08-13 16:00
85 | Kabirpur | 132 | 136 | 2026-08-07 07:00 | 108 | 2026-08-18 12:00
86 | Kachua | 132 | 133 | 2026-08-07 07:00 | 120 | 2026-08-04 15:00
87 | Kaliakoir | 132 | 139 | 2026-08-07 07:00 | 119 | 2026-08-02 12:00
88 | Kaliganj | 132 | 140 | 2026-08-05 16:00 | 113 | 2026-08-12 22:00
89 | Kallyanpur | 132 | 139 | 2026-08-08 18:00 | 113 | 2026-08-03 12:00
90 | Kalurghat | 132 | 140 | 2026-08-19 18:00 | 131 | 2026-08-02 11:00
91 | Kamrangirchar | 132 | 140 | 2026-08-08 01:00 | 130 | 2026-08-02 12:00
92 | Kaptai | 132 | N/A | N/A | N/A | N/A
93 | Kasba | 132 | 131 | 2026-08-29 04:00 | 114 | 2026-08-02 11:00
94 | Kazla | 132 | 142 | 2026-08-29 06:00 | 111 | 2026-08-02 13:00
95 | Keranigonj | 132 | 141 | 2026-08-07 07:00 | 119 | 2026-08-03 12:00
96 | Khagrachori | 132 | 137 | 2026-08-01 01:00 | 130 | 2026-08-02 12:00
97 | Khulna | 132 | 137 | 2026-08-01 12:00 | 120 | 2026-08-12 22:00
98 | Khulna(S) | 132 | 138 | 2026-08-29 03:00 | 123 | 2026-08-13 20:00
99 | Khulshi | 132 | 137 | 2026-08-15 00:00 | 127 | 2026-08-04 12:00
100 | Kishoreganj | 132 | 130 | 2026-08-12 23:00 | 111 | 2026-08-02 22:00
101 | Kodda | 132 | 138 | 2026-08-28 19:30 | 114 | 2026-08-01 15:00
102 | Korerhat | 132 | 136 | 2026-08-07 06:00 | 124 | 2026-08-02 10:00
103 | KSRM | 132 | 139 | 2026-08-30 07:00 | 128 | 2026-08-03 12:00
104 | Kulaura | 132 | 130 | 2026-08-01 01:00 | 120 | 2026-08-13 20:00
105 | Kurigram | 132 | 134 | 2026-08-05 09:00 | 110 | 2026-08-14 19:00
106 | Kushtia | 132 | 138 | 2026-08-31 00:00 | 109 | 2026-08-12 22:00
107 | Laksam | 132 | 133 | 2026-08-08 19:30 | 119 | 2026-08-04 15:00
108 | Lakshmipur | 132 | 130 | 2026-08-07 07:00 | 117 | 2026-08-04 15:00
109 | Lalbag | 132 | 141 | 2026-08-29 04:00 | 118 | 2026-08-03 12:00
110 | Lalmonirhat | 132 | 132 | 2026-08-05 07:00 | 112 | 2026-08-12 22:00
111 | Madanganj | 132 | 136 | 2026-08-29 06:00 | 117 | 2026-08-03 12:00
112 | Madaripur | 132 | 133 | 2026-08-07 07:00 | 123 | 2026-08-02 11:00
113 | Madartek | 132 | 140 | 2026-08-10 03:00 | 117 | 2026-08-03 12:00
114 | Madunaghat | 132 | 139 | 2026-08-01 01:00 | 131 | 2026-08-02 12:00
115 | Magura | 132 | 138 | 2026-08-02 01:00 | 110 | 2026-08-12 22:00
116 | Mahasthangarh | 132 | 138 | 2026-08-07 16:00 | 120 | 2026-08-12 22:00
117 | Maijdee | 132 | 130 | 2026-08-29 04:00 | 117 | 2026-08-04 15:00
118 | Manikganj | 132 | 131 | 2026-08-07 19:00 | 116 | 2026-08-02 18:00
119 | Maniknagar | 132 | 142 | 2026-08-07 07:00 | 111 | 2026-08-02 13:00
120 | Matarbari | 132 | 136 | 2026-08-24 15:00 | 110 | 2026-08-02 19:30
121 | Matuail | 132 | 137.5 | 2026-08-29 06:00 | 117 | 2026-08-03 12:00
122 | Metrorail_Motijheel | 132 | 142 | 2026-08-07 07:00 | 111 | 2026-08-02 13:00
123 | Metrorail_Uttara | 132 | 136 | 2026-08-07 18:00 | 111 | 2026-08-02 13:00
124 | Millgate | 132 | 138 | 2026-08-08 02:00 | 111 | 2026-08-03 12:00
125 | Mirpur | 132 | 134 | 2026-08-29 05:00 | 112 | 2026-08-03 12:00
126 | Mirzapur | 132 | 132 | 2026-08-07 09:00 | 117 | 2026-08-13 12:00
127 | Mithapukur | 132 | 136 | 2026-08-08 19:00 | 118 | 2026-08-12 22:00
128 | MI_Cement | 132 | 137.4 | 2026-08-07 07:00 | 114 | 2026-08-02 13:00
129 | Modern | 132 | N/A | N/A | N/A | N/A
130 | Mogbazar | 132 | 143 | 2026-08-10 03:00 | 119 | 2026-08-03 12:00
131 | Mongla | 132 | 131 | 2026-08-29 10:00 | 113 | 2026-08-12 22:00
132 | Motijheel | 132 | 142 | 2026-08-29 04:00 | 111 | 2026-08-02 13:00
133 | Muktagacha | 132 | 133 | 2026-08-11 05:00 | 112 | 2026-08-12
134 | Munshiganj | 132 | 136 | 2026-08-29 03:00 | 116 | 2026-08-03 12:00
135 | Muradnagar | 132 | 132 | 2026-08-29 05:00 | 114 | 2026-08-03 13:00
136 | Mymensingh | 132 | 133 | 2026-08-08 15:00 | 110 | 2026-08-24 01:00
137 | Nabinagar | 132 | 136 | 2026-08-08 01:00 | 112 | 2026-08-18 11:00
139 | Naogaon | 132 | 138 | 2026-08-07 16:00 | 118 | 2026-08-20 21:00
140 | Narail | 132 | 139 | 2026-08-05 16:00 | 111 | 2026-08-12 22:00
141 | Narinda | 132 | 0 | 2026-08-01 00:00 | N/A | N/A
142 | Narshingdi | 132 | 132 | 2026-08-28 19:00 | 111 | 2026-08-02 10:00
143 | Natore | 132 | 137 | 2026-08-11 00:00 | 117 | 2026-08-12 22:00
144 | Nawabganj | 132 | 140 | 2026-08-07 07:00 | 119 | 2026-08-02 13:00
145 | Netrakona | 132 | 127 | 2026-08-11 04:00 | 103 | 2026-08-01 18:30
146 | New | 132 | 139 | 2026-08-07 07:00 | 114 | 2026-08-02 12:00
147 | Niamatpur | 132 | 138 | 2026-08-12 11:00 | 120 | 2026-08-20 21:00
148 | Noapara | 132 | 135 | 2026-08-02 03:00 | 118 | 2026-08-24 00:00
149 | Pabna | 132 | 137 | 2026-08-09 00:00 | 118 | 2026-08-26 12:00
150 | Palashbari | 132 | 134 | 2026-08-09 00:00 | 114 | 2026-08-12 22:00
151 | Panchagarh | 132 | 141 | 2026-08-19 12:00 | 121 | 2026-08-14 19:30
152 | Patiya | 132 | 139 | 2026-08-01 01:00 | 117 | 2026-08-23 07:00
153 | Patnitala | 132 | 134 | 2026-08-02 08:00 | 115 | 2026-08-12 23:00
154 | Patuakhali | 132 | 135 | 2026-08-07 06:00 | 124 | 2026-08-12 23:00
155 | Payra | 132 | 136 | 2026-08-07 08:00 | 130 | 2026-08-02 11:00
156 | PHP | 132 | 134 | 2026-08-29 02:00 | 121 | 2026-08-02 13:00
157 | Postogola | 132 | 139 | 2026-08-29 06:00 | 116 | 2026-08-02 13:00
158 | Pubail | 132 | 133 | 2026-08-07 10:00 | 110 | 2026-08-01 15:00
159 | Purbachal | 132 | 140 | 2026-08-02 03:00 | 116 | 2026-08-03 12:00
160 | Purbasadipur | 132 | 138 | 2026-08-08 07:00 | 122 | 2026-08-14 19:30
161 | Rahanpur | 132 | 139 | 2026-08-08 08:00 | 125 | 2026-08-20 21:00
162 | Rahanpur-400 | 132 | 139 | 2026-08-08 00:00 | 125 | 2026-08-20 21:00
163 | Rahim | 132 | 138 | 2026-08-29 06:00 | 118 | 2026-08-02 13:00
164 | Rajbari | 132 | 129 | 2026-08-04 07:00 | 111 | 2026-08-02 11:00
165 | Rajendrapur | 132 | 136 | 2026-08-21 17:00 | 113 | 2026-08-03 12:00
166 | Rajshahi | 132 | 134 | 2026-08-01 01:00 | 113 | 2026-08-12 22:00
167 | Rajshahi-230 | 132 | 135 | 2026-08-01 01:00 | 116 | 2026-08-12 22:00
168 | Ramganj | 132 | 132 | 2026-08-08 18:30 | 118 | 2026-08-04 14:00
169 | Rampur | 132 | 138 | 2026-08-01 00:00 | 128 | 2026-08-02 12:00
170 | Rampura | 132 | 140 | 2026-08-02 04:00 | 117 | 2026-08-03 12:00
171 | Rangamati | 132 | 139 | 2026-08-30 07:00 | 130 | 2026-08-04 15:00
172 | Rangpur | 132 | 134 | 2026-08-01 01:00 | 117 | 2026-08-12 23:00
173 | Ruppur | 132 | 139 | 2026-08-07 20:00 | 119 | 2026-08-12 22:00
174 | Saidpur | 132 | 137 | 2026-08-31 01:00 | 121 | 2026-08-15 23:00
175 | Santhia | 132 | 137 | 2026-08-07 07:00 | 121 | 2026-08-23 20:00
176 | Satkhira | 132 | 134 | 2026-08-17 15:00 | 114 | 2026-08-23 22:00
177 | Satmasjid | 132 | 141 | 2026-08-07 07:00 | 114 | 2026-08-02 13:00
178 | Savar | 132 | 134 | 2026-08-07 19:30 | 113 | 2026-08-03 10:00
179 | SevenRings | 132 | 138 | 2026-08-28 16:00 | 115 | 2026-08-01 15:00
180 | ShahCement | 132 | 137 | 2026-08-07 07:00 | 117 | 2026-08-02 11:00
181 | Shahjadpur | 132 | 139 | 2026-08-09 02:00 | 126 | 2026-08-12 22:00
182 | Shahjibazar | 132 | 132 | 2026-08-30 15:00 | 115 | 2026-08-04 15:00
183 | Shahmirpur | 132 | 140 | 2026-08-28 18:30 | 125 | 2026-08-05 23:00
184 | Shariatpur | 132 | 132 | 2026-08-07 07:00 | 120 | 2026-08-18 22:00
185 | Sherpur | 132 | 134 | 2026-08-11 23:00 | 108 | 2026-08-04 02:00
186 | Shikalbaha | 132 | 129 | 2026-08-01 00:00 | 120 | 2026-08-02 12:00
187 | Shikalbaha-230 | 132 | 140 | 2026-08-01 00:00 | 130 | 2026-08-02 12:00
188 | Shitalakhya | 132 | 137.3 | 2026-08-07 07:00 | 114 | 2026-08-02 13:00
189 | Sholosohor | 132 | 139 | 2026-08-15 | 128 | 2026-08-04 15:00
190 | Shomvuganj | 132 | 126 | 2026-08-15 00:00 | 108 | 2026-08-03 22:00
191 | Shyampur | 132 | 138 | 2026-08-07 07:00 | 119 | 2026-08-02 11:00
192 | Shyampur-230 | 132 | 139 | 2026-08-29 06:00 | 117 | 2026-08-03 12:00
193 | Siddhirganj | 132 | 138 | 2026-08-29 04:00 | 118 | 2026-08-03 12:00
194 | Sirajganj | 132 | 136 | 2026-08-07 09:00 | 118 | 2026-08-12 22:00
195 | Sitakunda | 132 | 138 | 2026-08-01 01:00 | 129 | 2026-08-04 12:00
196 | Sonargaon | 132 | 135 | 2026-08-29 04:00 | 110 | 2026-08-11 16:00
197 | Sreemongol | 132 | 129 | 2026-08-08 17:00 | 117 | 2026-08-02 19:00
198 | Sreepur | 132 | 138 | 2026-08-27 23:00 | 116 | 2026-08-03 12:00
199 | Srinagar | 132 | 141 | 2026-08-29 06:00 | 119 | 2026-08-02 13:00
200 | SSM | 132 | 142 | 2026-08-22 01:00 | 132 | 2026-08-02 12:00
201 | Sunamganj | 132 | 124 | 2026-08-11 02:00 | 103 | 2026-08-12 18:00
202 | Sylhet | 132 | 126 | 2026-08-12 03:00 | 110 | 2026-08-12 18:00
203 | Sylhet_(South) | 132 | 128 | 2026-08-12 03:00 | 111 | 2026-08-12 18:00
204 | Tangail | 132 | 130 | 2026-08-30 00:00 | 113 | 2026-08-02 20:00
205 | Taraganj | 132 | 135 | 2026-08-04 19:30 | 119 | 2026-08-12 23:00
206 | Tasnim | 132 | 139 | 2026-08-15 05:00 | 116 | 2026-08-03 11:00
207 | Thakurgaon | 132 | 141 | 2026-08-19 12:00 | 122 | 2026-08-14 19:30
208 | TK | 132 | 140 | 2026-08-19 18:00 | 130 | 2026-08-01
209 | Tongi | 132 | 139 | 2026-08-05 18:00 | 117 | 2026-08-10 11:00
210 | Ullahpara | 132 | 136 | 2026-08-07 09:00 | 120 | 2026-08-23 20:00
211 | Ullon | 132 | 140 | 2026-08-07 07:00 | 117 | 2026-08-03 12:00
212 | Uttara | 132 | 138 | 2026-08-08 02:00 | 110 | 2026-08-03 12:00
212 | UttaraNew | 132 | 137 | 2026-08-07 07:00 | 111 | 2026-08-02 13:00
212 | Zigatola | 132 | 142 | 2026-08-07 07:00 | 119 | 2026-08-02 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: August 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 31-08-2026 | 13:00 | 420 | 250 | 93.995
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 31-08-2026 | 13:00 | 420 | 250 | 93.995
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 31-08-2026 | 13:00 | 420 | 250 | 93.995
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-08-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 14-08-2026 | 22:00 | 293 | 146 | 62.954
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 14-08-2026 | 22:00 | 293 | 146 | 62.954
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 01-08-2026 | 00:00 | 0 | 0 | 0
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 31-08-2026 | 22:00 | 325 | 74 | 64.0996
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 03-08-2026 | 05:00 | 375 | 137 | 53.2322
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 03-08-2026 | 05:00 | 375 | 137 | 53.2322
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 03-08-2026 | 05:00 | 375 | 137 | 53.2322
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 20-08-2026 | 19:00 | 147 | 63 | 49.2096
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 20-08-2026 | 19:00 | 147 | 63 | 49.2096
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 20-08-2026 | 19:00 | 147 | 63 | 49.2096
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 25-08-2026 | 22:00 | 150 | 37 | 20.5995
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 29-08-2026 | 08:00 | 397 | 157 | 82.0994
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 29-08-2026 | 08:00 | 397 | 157 | 82.0994
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 29-08-2026 | 11:00 | 284 | 80 | 90.7854
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 29-08-2026 | 11:00 | 284 | 80 | 90.7854
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 16-08-2026 | 13:00 | 335 | 127 | 47.7687
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 16-08-2026 | 13:00 | 335 | 127 | 47.7687
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 16-08-2026 | 13:00 | 335 | 127 | 47.7687
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 23-08-2026 | 11:00 | 488 | 178 | 69.26
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 23-08-2026 | 11:00 | 490 | 177 | 69.4651
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 23-08-2026 | 11:00 | 502 | 176 | 70.9278
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 22-08-2026 | 20:00 | 396 | 75 | 77.5076
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 22-08-2026 | 20:00 | 391 | 75 | 76.5631
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 12-08-2026 | 22:00 | 179 | 61 | 58.1872
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 12-08-2026 | 22:00 | 179 | 61 | 58.1872
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 20-08-2026 | 21:00 | 242 | 33 | 46.9692
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 20-08-2026 | 21:00 | 242 | 33 | 46.9692
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 02-08-2026 | 13:00 | 488 | 104 | 49.8959
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 04-08-2026 | 15:00 | 547 | 22 | 54.7442
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 | 07-08-2026 | 02:00 | 261 | 2 | 80.3101
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 02-08-2026 | 15:00 | 115 | 9 | 35.4928
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 | 07-08-2026 | 22:00 | 153 | 91 | 17.8017
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | 02-08-2026 | 22:00 | 152 | 91 | 17.7158
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 |  |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 |  |  |  |  | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 12-08-2026 | 13:00 | 197 | 82 | 71.1282
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 12-08-2026 | 13:00 | 197 | 82 | 71.1282
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 29-08-2026 | 08:00 | 176 | 46 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 29-08-2026 | 08:00 | 176 | 46 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 29-08-2026 | 08:00 | 176 | 46 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 01-08-2026 | 00:00 | 0 | 0 | 0
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 07-08-2026 | 05:00 | 240 | 80 | 84.3274
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 22-08-2026 | 20:00 | 191 | 66 | 67.3606
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 22-08-2026 | 19:30 | 146 | 47 | 68.1683
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 16-08-2026 | 20:00 | 161 | 68 | 77.6761
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 13-08-2026 | 00:00 | 135 | 85 | 70.9025
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 16-08-2026 | 20:00 | 148 | 46 | 51.6613
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 17-08-2026 | 13:00 | 107 | 7 | 35.7429
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 17-08-2026 | 13:00 | 107 | 7 | 35.7429
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 27-08-2026 | 21:00 | 142 | 43 | 65.9412
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 27-08-2026 | 21:00 | 142 | 43 | 65.9412
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 13-08-2026 | 01:00 | 198 | 72 | 93.6376
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 13-08-2026 | 01:00 | 198 | 72 | 93.6376
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 23-08-2026 | 01:00 | 248 | 88 | 87.7167
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 13-08-2026 | 01:00 | 266 | 100 | 94.7253
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | - | - | - | - | -
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | - | - | - | - | -
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | - | - | - | - | -
Purbasadipur 230/132kV Grid Sub-Station | ATR-01 | 230/132 | 300 | 16-08-2026 | 20:00 | 127 | 19 | 42.8045
Purbasadipur 230/132kV Grid Sub-Station | ATR-02 | 230/132 | 300 | 16-08-2026 | 20:00 | 128 | 19 | 43.1342
Purbasadipur 230/132kV Grid Sub-Station | ATR-03 | 230/132 | 300 | 16-08-2026 | 20:00 | 127 | 19 | 42.8045
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 14-08-2026 | 10:00 | 79 | 47 | 40.8551
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 14-08-2026 | 10:00 | 78 | 47 | 40.4737
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 14-08-2026 | 10:00 | 86 | 49 | 43.991
Chowmohani 230/132 kV Grid Sub-Station | ATR-01 | 230/132 | 350 | 05-08-2026 | 07:00 | 85 | 18 | 24.8243
Chowmohani 230/132 kV Grid Sub-Station | ATR-02 | 230/132 | 350 | 05-08-2026 | 07:00 | 85 | 18 | 24.8243
Chowmohani 230/132 kV Grid Sub-Station | ATR-03 | 230/132 | 350 | 05-08-2026 | 07:00 | 85 | 18 | 24.8243
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 15-08-2026 | 18:30 | 202 | 76 | 71.9413
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 15-08-2026 | 18:30 | 253 | 97 | 90.3192
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 13-08-2026 | 18:00 | 40 | 23 | 15.3804
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 21-08-2026 | 14:00 | 54 | 31 | 20.7552
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 21-08-2026 | 14:00 | 54 | 31 | 20.7552
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 02-08-2026 | 03:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 01-08-2026 | 00:00 | 0 | 0 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 15-08-2026 | 02:00 | 159 | 95 | 82.3195
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 15-08-2026 | 02:00 | 170 | 95 | 86.5526
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 15-08-2026 | 02:00 | 163 | 99 | 84.7596
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 22-08-2026 | 15:00 | 141 | 46 | 65.9173
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 22-08-2026 | 15:00 | 141 | 46 | 65.9173
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 10-08-2026 | 07:00 | 123 | 48 | 58.6818
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 20-08-2026 | 18:30 | 108 | 53 | 80.2025
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-08-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 13-08-2026 | 16:00 | 86 | 43 | 64.1006
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 20-08-2026 | 18:30 | 108 | 53 | 80.2025
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 16-08-2026 | 04:00 | 105 | 43 | 50.4283
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 27-08-2026 | 21:00 | 149 | 66 | 72.4281
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 27-08-2026 | 20:00 | 149 | 64 | 72.0727
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 21-08-2026 | 08:00 | 237 | 67 | 82.0961
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 21-08-2026 | 08:00 | 237 | 67 | 82.0961
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 29-08-2026 | 00:00 | 254 | 56 | 86.7
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 27-08-2026 | 20:00 | 136 | 48 | 48.074
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 27-08-2026 | 20:00 | 136 | 48 | 48.074
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 27-08-2026 | 20:00 | 136 | 48 | 48.074
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 19-08-2026 | 23:00 | 137 | 58 | 66.1207
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 19-08-2026 | 23:00 | 137 | 58 | 66.1207
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 19-08-2026 | 23:00 | 178 | 67 | 63.3973
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 20-08-2026 | 18:30 | 112 | 19 | 37.8667
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 20-08-2026 | 18:30 | 112 | 19 | 37.8667
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 20-08-2026 | 18:30 | 112 | 19 | 37.8667
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 12-08-2026 | 12:00 | 187 | 81 | 67.9297
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 21-08-2026 | 17:00 | 199 | 45 | 68.0082
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 24-08-2026 | 05:00 | 112 | 2 | 37.3393
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 24-08-2026 | 05:00 | 112 | 2 | 37.3393
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-08-2026 | 00:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-08-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 30-08-2026 | 14:00 | 286 | 76 | 65.7613
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 30-08-2026 | 14:00 | 286 | 76 | 65.7613
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 30-08-2026 | 14:00 | 286 | 76 | 65.7613
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 20-08-2026 | 18:30 | 221 | 122 | 84.146
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 20-08-2026 | 18:30 | 221 | 122 | 84.146
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 26-08-2026 | 09:00 | 110 | 37 | 38.6853
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 23-08-2026 | 11:00 | 144 | 65 | 52.6635
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 01-08-2026 | 00:00 | 0 | 0 | 0
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 15-08-2026 | 01:00 | 192 | 113 | 74.2615
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 21-08-2026 | 20:00 | 260 | 127 | 96.4532
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 21-08-2026 | 20:00 | 260 | 127 | 96.4532
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 22-08-2026 | 18:30 | 160 | 65 | 76.7552
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 22-08-2026 | 18:30 | 155 | 60 | 73.8701
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 13-08-2026 | 19:00 | 165 | 60 | 78.0313
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 | 12-08-2026 | 11:00 | 300 | 140 | 73.5686
Bhulta 230/132kV Grid Sub-Station | ATR1 | 230/132 | 300 | 15-08-2026 | 02:00 | 168 | 0 | 56
Bhulta 230/132kV Grid Sub-Station | ATR2 | 230/132 | 300 | 15-08-2026 | 02:00 | 168 | 0 | 56
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: August 2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: August 2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-08-01 | 15355.19 | 17520.19 | 2072 | 21:00 Hr. | 394 | 167 | 291 | 284 | 168 | 252 | 87 | 204 | 225 | - | 2026-08-01 | 13618.42 | 16388.42 | 2651 | 12:00 Hr. | 733 | 127 | 285 | 390 | 102 | 353 | 87 | 369 | 205 | -
2026-08-02 | 15562.5 | 17878.22 | 2216 | 21:00 Hr. | 508 | 150 | 294 | 234 | 171 | 302 | 91 | 268 | 198 | - | 2026-08-02 | 14425.58 | 16688.01 | 2165 | 12:00 Hr. | 871 | 61 | 251 | 362 | 162 | 281 | 79 | 57 | 41 | -
2026-08-03 | 15373.78 | 17811.78 | 2333 | 21:00 Hr. | 491 | 164 | 297 | 340 | 171 | 317 | 125 | 283 | 145 | - | 2026-08-03 | 13663.58 | 16501.58 | 2716 | 12:00 Hr. | 922 | 191 | 199 | 339 | 209 | 439 | 20 | 257 | 140 | -
2026-08-04 | 15195.18 | 17478.18 | 2185 | 21:00 Hr. | 381 | 189 | 301 | 239 | 132 | 352 | 108 | 272 | 211 | - | 2026-08-04 | 14070.23 | 16182.23 | 2021 | 12:00 Hr. | 925 | 184 | 254 | 82 | 132 | 98 | 4 | 209 | 133 | -
2026-08-05 | 14553.75 | 14553.75 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-08-05 | 12931.85 | 13030.85 | 95 | 12:00 Hr. | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | -
2026-08-06 | 14894.74 | 16362.74 | 1405 | 21:00 Hr. | 201 | 116 | 115 | 169 | 13 | 288 | 10 | 310 | 183 | - | 2026-08-06 | 14159.71 | 14369.71 | 201 | 12:00 Hr. | 161 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | -
2026-08-07 | 14534.38 | 15623.38 | 1042 | 21:00 Hr. | 70 | 0 | 159 | 194 | 88 | 146 | 44 | 220 | 121 | - | 2026-08-07 | 12500.51 | 12541.27 | 39 | 12:00 Hr. | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | -
2026-08-08 | 15076.62 | 17850.62 | 2655 | 21:00 Hr. | 537 | 31 | 286 | 486 | 195 | 366 | 132 | 334 | 288 | - | 2026-08-08 | 13435.88 | 15326.88 | 1810 | 12:00 Hr. | 603 | 114 | 142 | 273 | 103 | 154 | 107 | 198 | 116 | -
2026-08-09 | 15312.82 | 18156.82 | 2722 | 20:00 Hr. | 547 | 0 | 300 | 416 | 222 | 523 | 87 | 339 | 288 | - | 2026-08-09 | 13335.69 | 16796.69 | 3312 | 12:00 Hr. | 841 | 83 | 374 | 516 | 144 | 460 | 176 | 419 | 299 | -
2026-08-10 | 15706.04 | 18519.18 | 2692 | 21:00 Hr. | 364 | 74 | 385 | 527 | 218 | 420 | 146 | 294 | 264 | - | 2026-08-10 | 14075.95 | 17139.95 | 2932 | 12:00 Hr. | 847 | 182 | 318 | 394 | 140 | 351 | 128 | 323 | 249 | - | 0
2026-08-11 | 15833.37 | 18975.37 | 3007 | 21:00 Hr. | 585 | 208 | 368 | 490 | 191 | 356 | 152 | 361 | 296 | - | 2026-08-11 | 14114.98 | 17308.98 | 3056 | 12:00 Hr. | 848 | 194 | 293 | 307 | 180 | 481 | 168 | 296 | 289 | -
2026-08-12 | 16092.99 | 18744.99 | 2538 | 21:00 Hr. | 445 | 5 | 324 | 575 | 256 | 303 | 0 | 337 | 293 | - | 2026-08-12 | 14635.83 | 17444.83 | 2688 | 12:00 Hr. | 1002 | 176 | 309 | 411 | 188 | 173 | 76 | 233 | 120 | -
2026-08-13 | 16280.28 | 17257.28 | 935 | 19:30 Hr. | 285 | 0 | 94 | 522 | 0 | 0 | 0 | 0 | 34 | - | 2026-08-13 | 15053 | 15481 | 410 | 12:00 Hr. | 231 | 0 | 27 | 152 | 0 | 0 | 0 | 0 | 0 | -
2026-08-14 | 16293.03 | 16707.03 | 396 | 21:00 Hr. | 69 | 0 | 0 | 255 | 50 | 0 | 0 | 0 | 22 | - | 2026-08-14 | 14174.33 | 14174.33 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-08-15 | 16190.24 | 17813.24 | 1553 | 21:00 Hr. | 164 | 7 | 60 | 462 | 159 | 292 | 5 | 166 | 238 | - | 2026-08-15 | 15091.25 | 15725.25 | 607 | 12:00 Hr. | 91 | 0 | 0 | 223 | 0 | 63 | 2 | 91 | 137 | -
2026-08-16 | 16120.55 | 16854.83 | 629 | 21:00 Hr. | 114 | 0 | 16 | 289 | 77 | 133 | 0 | 0 | 0 | - | 2026-08-16 | 14951.75 | 15701.75 | 718 | 12:00 Hr. | 239 | 0 | 94 | 167 | 0 | 124 | 2 | 30 | 62 | -
2026-08-17 | 15891.47 | 16207.47 | 302 | 19:30 Hr. | 93 | 0 | 0 | 207 | 0 | 0 | 0 | 2 | 0 | - | 2026-08-17 | 14356.77 | 15289.77 | 893 | 12:00 Hr. | 352 | 87 | 0 | 93 | 53 | 44 | 0 | 143 | 121 | -
2026-08-18 | 16208.16 | 16761.16 | 529 | 19:30 Hr. | 154 | 0 | 50 | 256 | 0 | 49 | 0 | 20 | 0 | - | 2026-08-18 | 14871.51 | 15049.51 | 170 | 12:00 Hr. | 97 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | -
2026-08-19 | 15680.74 | 18070.79 | 2266 | 21:00 Hr. | 643 | 154 | 244 | 354 | 134 | 274 | 104 | 159 | 200 | - | 2026-08-19 | 14366.74 | 14910.35 | 117 | 10:00 Hr. | 75 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | -
2026-08-20 | 16174.37 | 17893.27 | 1589 | 21:00 Hr. | 558 | 0 | 198 | 314 | 163 | 167 | 2 | 108 | 79 | - | 2026-08-20 | 15306.19 | 15987.19 | 652 | 12:00 Hr. | 524 | 0 | 20 | 93 | 9 | 0 | 0 | 0 | 6 | -
2026-08-21 | 16376.3 | 16940.3 | 540 | 21:00 Hr. | 214 | 0 | 33 | 282 | 11 | 0 | 0 | 0 | 0 | - | 2026-08-21 | 14726.98 | 14966.98 | 230 | 12:00 Hr. | 56 | 0 | 5 | 169 | 0 | 0 | 0 | 0 | 0 | -
2026-08-22 | 16523.02 | 18733.02 | 2115 | 20:00 Hr. | 599 | 111 | 215 | 377 | 135 | 223 | 92 | 184 | 179 | - | 2026-08-22 | 15250.85 | 15641.85 | 374 | 12:00 Hr. | 265 | 0 | 0 | 79 | 11 | 0 | 0 | 19 | 0 | -
2026-08-23 | 16973.07 | 18166.41 | 913 | 20:00 Hr. | 195 | 35 | 54 | 383 | 70 | 29 | 8 | 73 | 66 | - | 2026-08-23 | 15310.44 | 16115.44 | 770 | 12:00 Hr. | 510 | 0 | 24 | 214 | 20 | 0 | 0 | 2 | 0 | -
2026-08-24 | 16613.99 | 17566.99 | 912 | 19:30 Hr. | 174 | 32 | 35 | 374 | 81 | 210 | 0 | 6 | 0 | - | 2026-08-24 | 14999.35 | 15803.35 | 769 | 12:00 Hr. | 692 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | -
2026-08-25 | 16361 | 18250.36 | 1808 | 21:00 Hr. | 418 | 0 | 187 | 298 | 177 | 217 | 84 | 241 | 186 | - | 2026-08-25 | 15313.94 | 16384.94 | 1025 | 12:00 Hr. | 760 | 0 | 24 | 220 | 21 | 0 | 0 | 0 | 0 | -
2026-08-26 | 16187.07 | 17727.07 | 1474 | 20:00 Hr. | 166 | 108 | 157 | 456 | 160 | 184 | 10 | 147 | 86 | - | 2026-08-26 | 14558.57 | 15258.57 | 670 | 12:00 Hr. | 83 | 0 | 48 | 6 | 0 | 204 | 71 | 144 | 114 | -
2026-08-27 | 16062.11 | 19027.11 | 2933 | 21:00 Hr. | 736 | 126 | 378 | 406 | 187 | 374 | 115 | 351 | 260 | - | 2026-08-27 | 14631.56 | 17271.56 | 2526 | 12:00 Hr. | 888 | 105 | 227 | 340 | 118 | 296 | 136 | 236 | 180 | -
2026-08-28 | 15893.95 | 17378.95 | 1421 | 21:00 Hr. | 335 | 29 | 266 | 326 | 49 | 70 | 0 | 195 | 151 | - | 2026-08-28 | 14383.74 | 15888.74 | 1440 | 12:00 Hr. | 192 | 88 | 164 | 342 | 93 | 131 | 51 | 213 | 166 | -
2026-08-29 | 15756.06 | 18830.06 | 2942 | 20:00 Hr. | 697 | 196 | 261 | 463 | 220 | 427 | 86 | 333 | 259 | - | 2026-08-29 | 13979.45 | 16562.04 | 1378 | 10:00 Hr. | 318 | 141 | 82 | 180 | 94 | 196 | 63 | 168 | 136 | -
2026-08-30 | 15828.82 | 18329.82 | 2393 | 21:00 Hr. | 573 | 13 | 282 | 530 | 172 | 311 | 12 | 262 | 238 | - | 2026-08-30 | 13735.91 | 17487.91 | 3590 | 12:00 Hr. | 1121 | 198 | 323 | 515 | 178 | 428 | 138 | 378 | 311 | -
2026-08-31 | 15725.04 | 18266.82 | 2397 | 21:00 Hr. | 743 | 134 | 181 | 571 | 174 | 173 | 84 | 152 | 185 | - | 2026-08-31 | 13955.25 | 17170.97 | 2465 | 11:00 Hr. | 964 | 139 | 211 | 346 | 143 | 279 | 26 | 202 | 155 | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: August 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16973.07 | 2026-08-23 | 20:00 Hr.
2 | Maximum Day Peak Genaration | MW | 15313.94 | 2026-08-25 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 19027.11 | 2026-08-27 | 21:00 Hr.
4 | Minimum Generation | MW | 11539.62 | 2026-08-07 | 09:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 15826.7945 | - | -
6 | Average of the daily day peak Genaration | MW | 14322.1223 | - | -
7 | Maximum load shed (Evening Peak) | MW | 3007 | 2026-08-11 | 21:00 Hr.
8 | Minimum load shed | MW | 302 | 2026-08-17 | 19:30:00 Hr
9 | Total nos. of load shed days | Day | 30 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 1683.9 | - | -
11 | Total Generation | MkWh | 10792.7035 | - | -
12 | Total Generation by BPDB | MkWh | 1378.7201 | % of total Gen. | 12.77%
13 | Total Generation by IPP | MkWh | 3096.1389 | '' | 28.69%
14 | A) Total Generation by Generation Companies | MkWh | 4529.6978 | '' | 41.97%
| B) Total Generation by REB | MkWh | 42.1957 | " | 0.391%
| C) Total Generation by RENTAL | MkWh | 102.2702 | " | 0.9476%
| D) Total Imported from India (BIPTC) | MkWh | 667.3799 | " | 6.184%
| E) Total Imported from Tripura, India (A.C) | MkWh | 137.8787 | " | 1.278%
| F) Total Imported from Nepal | MkWh | 24.472 | " | 0.2267%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 813.9501 | " | 7.542%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3461.0774 | % of total Gen. | 32.07%
| B) Oil | MkWh | 1539.2255 | '' | 14.26%
| C) Hydro | MkWh | 158.693 | '' | 1.47%
| D) Solar | MkWh | 122.0357 | '' | 1.131%
| E) Coal | MkWh | 3854.278 | '' | 35.71%
| F) BIPTC (Import from India) | MkWh | 667.3799 | '' | 6.184%
| G) A.C (Import from Tripura, India) | MkWh | 137.8787 | '' | 1.278%
| H) Total Imported from Nepal | MkWh | 24.472 | '' | 0.2267%
| I) Adani (Import from India) | MkWh | 813.9501 | '' | 7.542%
| J) Wind | MkWh | 13.7131 | '' | 0.1271%
16 | Maximun of the daily total Generation . | MkWh | 375.476 | 2026-08-23
17 | Monthly Load factor | % | 85.2212 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 81140.6474 | - | -
| A) Gas | M.Taka | 12091.9702 | - | -
| B) Coal | M.Taka | 26656.1174 | - | -
| C) HFO | M.Taka | 29605.3109 | - | -
| D) HSD | M.Taka | 582.1046 | - | -
| E) Hydro | M.Taka | 15.8693 | - | -
| F) Solar | M.Taka | 1971.4813 | - | -
| G) Total Import | M.Taka | 10016.0738 | - | -
| H) Wind | M.Taka | 201.72 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2997.0686 | 2026-08-23
| A) Gas | M.Taka | 450.7319 | 2026-08-18
| B) Coal | M.Taka | 925.5496 | 2026-08-24
| C) HFO | M.Taka | 1243.188 | 2026-08-23
| D) HSD | M.Taka | 76.0389 | 2026-08-31 | -
| E) Hydro | M.Taka | 0.54104 | 2026-08-06 | -
| F) Solar | M.Taka | 84.5274 | 2026-08-27 | -
| G) Total Import | M.Taka | 391.1688 | 2026-08-04
| H) Wind | M.Taka | 16.4375 | 2026-08-12
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 7.5398
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 7.7519
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/8/2026 | 06:00
b) | Actual | FT (MSL) | 106.23 | 31/8/2026 | 06:00
22 | Peak Genaration of August 2025 | MW | 16076.4 | 2025-08-11 | 19:30 Hr.
23 | Peak Demand of August 2025 | MW | 16199.71 | 2025-08-11 | 19:30 Hr.
24 | Maximum peak Generation recorded upto 31/08/2026 | MW | 17200.79 | 2026-05-20 | 21:00 Hr.
25 | Maximum peak Demand recorded upto 31/08/2026 | MW | 17610.79 | 2026-05-20 | 21:00 Hr.
26 | Maximum load shed recorded upto 31/08/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [79 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 27.08.2026 | 20.08.2026 | 13.08.2026 | 06.08.2026 | 30.07.2026 | 23.07.2026 | 16.07.2026 | 09.07.2026 | 02.07.2026 | 25.06.2026 | 18.06.2026 | 11.06.2026 | 04.06.2026 | 28.05.2026 | 21.05.2026 | 14.05.2026 | 07.05.2026 | 30.04.2026 | 23.04.2026 | 16.04.2026 | 09.04.2026 | 02.04.2026 | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | [12 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [54 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [35 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable |  |  | 17 | 17 | 17 | 17 | 35 | 35 | [37 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [25 empty] | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | [12 empty] | 20 | 20 | 20 | 20 | [5 empty] | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [55 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | 30 | [17 empty] | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [79 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [21 empty] | 20 | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | 2 | 2 | 2 | [15 empty] | 2 | 2 | 2 | [32 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [58 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [27 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | [47 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | [19 empty] | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [84 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable |  |  | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | [5 empty] | 20 | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [53 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable |  | 33 | 33 | [7 empty] | 33 | 33 | 33 | 16.5 | 33 | 33 | 33 | 33 | 33 |  | 40 | 20 | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable | 40 | 40 | [6 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable |  |  |  | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | [10 empty] | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable | 20 | 40 | 20 |  |  | 10 | 40 | [5 empty] | 20 | 20 | 20 | 20 | 20 | [11 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [68 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 3041 | 4891 | 4051 | 5430 | 5430 | 5680 | 6495 | 5475 | 6060 | 6093 | 7377 | 6744 | 6794 | 4864 | 6567 | 6861 | 6051 | 4051 | 4051 | 4246 | 4752 | 5680 | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 160 | 218 | 160 | 170 | 170 | 205 | 268 | 213 | 223 | 263 | 296 | 264 | 274 | 232.5 | 291 | 286 | 236 | 186 | 186 | 198 | 238 | 304 | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 8 | 10 | 10 | 10 | 10 | 11 | 11 | 9 | 10 | 10 | 11 | 10 | 11 | 11 | 13 | 12 | 10 | 8 | 8 | 9 | 10 | 14 | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: August 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 |  |  |  | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | [9 empty] | √ | √ | √ | √ | √ | [10 empty] | √ |  | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 |  |  | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | [18 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | [20 empty] | √ | √ | √ |  |  | √ | √ |  |  |  | √
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | √ | [17 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 |  |  |  | √ | √ | √ |  |  |  | √ | √ | √ |  | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | [9 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | [12 empty] | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ |  |  | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | √ | √ |  |  | √ | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | [9 empty] | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | [19 empty] | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 |  |  |  | √ | √ | √ |  | √ | √ | √ | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718 | [25 empty] | √ | √ |  |  |  | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622
Patuakhali 1320 MW (RNPL)