## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-10-2026 | during | 08-10-2026 | during | 08-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 379 | 412 | 412 | 412 | 393 | 393 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 315 | 335 | 335 | 316 | 316 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 17 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 62 | 143 | 149.36 | 149.36 | 127 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 10 | 24.75 | 24.75 | 10 | 10 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 24 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 210 | 295 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 149 | 149 | 149 | 97 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 500 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 390 | 405 | 583 | 583 | 415 | 415 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2504.42 | 2930.42 | 5574.91 | 5544.91 | 2620.42 | 2919.39
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 219 | 219 | 219 | 219 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 94 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 54 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 51 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 100 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 8 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 39 | 52 | 95.1 | 95.1 | 12 | 48 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.68 | 0 | 4.23 | 0 | 4.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 160 | 212 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 100 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 16 | 163 | 163 | 18 | 18 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1060 | 1060 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3478.68 | 3750.86 | 4101.19 | 4157.96 | 3399.23 | 3599.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 205 | 209 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 334 | 355 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 330 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 33 | 41.65 | 41.65 | 33 | 33 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 30 | 52.82 | 52.82 | 20 | 20 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 128 | 165 | 195 | 195 | 160 | 160 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 147 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 21 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 72 | 77 | 163 | 163 | 84 | 84 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 24 | 139 | 200 | 200 | 34 | 34 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 72 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 0 | 0 | 8 | 25 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 12 | 24.5 | 24.5 | 10 | 10 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 86 | 99 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 71 | 73 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 110 | 115 | 115 | 70 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 46 | 0 | 67 | 0 | 67 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1689 | 1968.2 | 2308.24 | 2239.24 | 1789 | 1782
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-10-2026 | during | 08-10-2026 | during | 08-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 9.2 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.6 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 164 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 88 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 34.44 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 0 | 0 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 232.24 | 264 | 634.6 | 569.5 | 256.1 | 277
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 39 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 39 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 155 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 139 | 138 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 53 | 83 | 83 | 83 | 53 | 53 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 277 | 341 | 341 | 275 | 275 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 150 | 101 | 0 | 0 | 150 | 150 | STG Under Shutdown & Gas Shortage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 391 | 400 | 0 | 0 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1360 | 1340 | 921 | 921 | 1358 | 1358
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 921 | 779 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 32 | 32 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1230 | 1234.2 | 1234.2 | 1234.2 | 1234.1 | 1234.1 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2257 | 2169.2 | 3578.2 | 3486.2 | 2935.1 | 2875.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 1100 | 1100 | 1100 | 800 | 800 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 114 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 0 | 0 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 137 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 294 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1891.58 | 2288 | 2008 | 2007 | 1896 | 1895
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 43.15 | 0 | 53.42 | 0 | 53.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 17 | 25 | 25 | 25 | 25 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 337 | 300 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 26 | 26 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 100 | 100 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 40 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.58 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 607.37 | 717.41 | 600 | 700 | 550 | 650 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.78 | 0 | 64 | 0 | 64 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1229.88 | 1413.41 | 2392.11 | 2268.99 | 1443.11 | 1440.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 187 | 0 | 178.63 | 0 | 178.63 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 338.6 | 393 | 441.63 | 228 | 351.63 | 217
System Total |  |  |  |  | 28843.2 | 28692.211 | 14981.4 | 16517.09 | 21959.88 | 21422.8 | 16048.59 | 16364.34
Forecast Scenario (08-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15336 |  | 1048.8 |  | 16440
|  |  |  | 1:00 | 14243 |  | 1682.45 |  | 16014
|  |  |  | 2:00 | 14176 |  | 1548.5 |  | 15806
|  |  |  | 3:00 | 14003 |  | 979.45 |  | 15034
|  |  |  | 4:00 | 13909 |  | 272.65 |  | 14196
|  |  |  | 5:00 | 13568 |  | 44.65 |  | 13615
|  |  |  | 6:00 | 13464 |  | 32.3 |  | 13498
|  |  |  | 7:00 | 13698 |  | 187.15 |  | 13895
|  |  |  | 8:00 | 13749 |  | 123.5 |  | 13879
|  |  |  | 9:00 | 14000 |  | 285 |  | 14300
|  |  |  | 10:00 | 14200 |  | 304 |  | 14520
|  |  |  | 11:00 | 14350 |  | 418 |  | 14790
|  |  |  | 12:00 | 14500 |  | 665 |  | 15200
|  |  |  | 13:00 | 14650 |  | 855 |  | 15550
|  |  |  | 14:00 | 14700 |  | 684 |  | 15420
|  |  |  | 15:00 | 14850 |  | 712.5 |  | 15600
|  |  |  | 16:00 | 14800 |  | 570 |  | 15400
|  |  |  | 17:00 | 14700 |  | 332.5 |  | 15050
|  |  |  | 18:00 | 14600 |  | 532 |  | 15160
|  |  |  | 18:30 | 15000 |  | 869.25 |  | 15915
|  |  |  | 19:00 | 15800 |  | 826.5 |  | 16670
|  |  |  | 19:30 | 15850 |  | 712.5 |  | 16600
|  |  |  | 20:00 | 15900 |  | 608 |  | 16540
|  |  |  | 21:00 | 15980 |  | 484.5 |  | 16490
|  |  |  | 22:00 | 15600 |  | 798 |  | 16440
|  |  |  | 23:00 | 15200 |  | 1168.5 |  | 16430
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14511.78 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.19972 MKWHr. |  | 100 | 0 | 90 | 140 | 0 | 0 | 0 | 90 | 65 | 485
*** This report is generated digitally from Operation Information System (OIS) at 08:58 hrs on 08-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-10-2026 | [28 empty] | Date: | 07-10-2026 | [28 empty] | Date: | 07-10-2026 | [28 empty] | Date: | 07-10-2026 | [28 empty] | Date: | 07-10-2026 | [16 empty] | Date: | 07-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 34 | 100 | 30 | 278 | 55 | 55 | 162 | 0 | 0 | 380 | 0 | 55 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 385 | 109 | 212 | 52 | 0 | 0 | 51 | 56 | 35 | 24 | 25 | 0 | 220 | 110 | 15 | 1055 | 16 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 127 | 0 | 321 | 285 | 44 | 20 | 196 | 37 | 69 | 65 | 125 | 59 | 15 | 86 | 74 | 43 | 0 | 22 | 263 | 400 | 150 | 40 | 40 | 155 | 0 | 16 | 0 | 52 | 0 | 138 | 0 | 100 | 1 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9402.92 | 778 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 708 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 36 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 800 | 300 | 54 | 5538.2 | 14941.12 | 106.28
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 35 | 99 | 30 | 198 | 55 | 35 | 72 | 0 | 0 | 415 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 385 | 107 | 68 | 48 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0 | 219 | 109 | 21 | 1055 | 18 | 0 | 50 | 25.5 | 105 | 220 | 0 | 0 | 0 | 1160 | 0 | 150 | 147 | 0 | 325 | 300 | 44 | 20 | 199 | 36 | 69 | 65 | 48 | 67 | 15 | 86 | 66 | 43 | 0 | 23 | 267 | 400 | 150 | 40 | 40 | 154 | 0 | 16 | 0 | 52 | 0 | 138 | 0 | 100 | 17 | 58 | 0 | 68 | 0 | 0 | 0 | 12 | 8805.92 | 921 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 615.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 800 | 300 | 54 | 5277.21 | 14083.13 | 106.27
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 35 | 99 | 30 | 196 | 55 | 35 | 72 | 0 | 0 | 415 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 390 | 87 | 68 | 45 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0 | 219 | 97 | 27 | 1055 | 18 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 145 | 165 | 0 | 330 | 305 | 44 | 24 | 200 | 36 | 69 | 65 | 17 | 73 | 15 | 86 | 68 | 43 | 0 | 23 | 268 | 400 | 150 | 40 | 40 | 152 | 0 | 16 | 0 | 53 | 0 | 140 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8769.92 | 826 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 626.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 272 | 116 | 220 | 0 | 800 | 300 | 54 | 5145.79 | 13915.71 | 106.27
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 35 | 99 | 30 | 196 | 55 | 35 | 72 | 0 | 0 | 420 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 395 | 90 | 68 | 45 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0 | 219 | 95 | 30 | 1055 | 18 | 0 | 50 | 8 | 105 | 221 | 0 | 0 | 0 | 1160 | 0 | 143 | 185 | 0 | 328 | 305 | 44 | 35 | 200 | 36 | 69 | 110 | 17 | 0 | 15 | 86 | 68 | 43 | 0 | 23 | 264 | 400 | 150 | 40 | 40 | 155 | 0 | 16 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8758.42 | 826 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 617.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 277 | 116 | 220 | 0 | 800 | 300 | 54 | 5155.46 | 13913.88 | 106.26
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 35 | 97 | 30 | 196 | 55 | 35 | 72 | 0 | 0 | 420 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 430 | 91 | 68 | 45 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0 | 219 | 94 | 30 | 1055 | 17 | 0 | 50 | 8 | 105 | 220 | 0 | 0 | 0 | 1160 | 0 | 140 | 185 | 0 | 336 | 310 | 44 | 42 | 203 | 36 | 69 | 111 | 17 | 0 | 15 | 86 | 66 | 43 | 0 | 23 | 258 | 400 | 150 | 40 | 40 | 155 | 0 | 16 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8802.42 | 826 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 614.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 282 | 116 | 220 | 0 | 800 | 300 | 54 | 5105.86 | 13908.28 | 106.26
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 35 | 97 | 30 | 196 | 55 | 0 | 72 | 0 | 0 | 425 | 0 | 17 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 430 | 94 | 68 | 45 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0 | 219 | 93 | 14 | 1055 | 16 | 0 | 50 | 8 | 105 | 220 | 0 | 0 | 0 | 1166 | 0 | 137 | 187 | 0 | 333 | 305 | 44 | 42 | 203 | 36 | 69 | 111 | 17 | 0 | 10 | 86 | 64 | 34 | 0 | 23 | 263 | 400 | 150 | 40 | 40 | 158 | 0 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8732.42 | 778 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 569.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 280 | 116 | 220 | 0 | 800 | 300 | 54 | 5012.97 | 13745.39 | 106.25
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 35 | 97 | 30 | 196 | 50 | 0 | 72 | 0 | 0 | 420 | 0 | 17 | 292 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 395 | 92 | 68 | 47 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0.02 | 219 | 92 | 14 | 1055 | 17 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 147 | 148 | 0 | 327 | 305 | 44 | 43 | 195 | 36 | 66 | 110 | 17 | 0 | 10 | 86 | 62 | 43 | 0 | 23 | 266 | 400 | 150 | 40 | 40 | 159 | 0 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 58 | 0.24 | 67 | 0 | 0 | 0.22 | 12 | 8633.9 | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 1234.2 | 0 | 0 | 0 | 570.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0.02 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 276 | 116 | 220 | 0 | 800 | 300 | 54 | 4986.32 | 13620.22 | 106.25
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 17 | 35 | 97 | 30 | 196 | 53 | 0 | 54 | 0 | 0 | 430 | 0 | 17 | 310 | 0 | 0 | 4 | 143.42 | 11 | 7 | 0 | 455 | 97 | 68 | 47 | 0 | 0 | 51 | 36 | 0 | 24 | 25 | 0.41 | 219 | 92 | 13 | 1055 | 16 | 0 | 47 | 8 | 105 | 220 | 0 | 0 | 0 | 1170 | 4 | 150 | 148 | 0 | 347 | 320 | 44 | 44 | 170 | 36 | 51 | 83 | 17 | 0 | 10 | 86 | 60 | 43 | 9 | 23 | 265 | 400 | 150 | 40 | 40 | 160 | 2 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 58 | 2.3 | 67 | 0 | 0.3 | 7.61 | 7 | 8709.04 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1234.2 | 0 | 0 | 0 | 579.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 12 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0.58 | 0 | 0 | 115 | 4 | 34 | 0 | 0 | 0 | 0.7 | 23 | 0.09 | 106 | 295 | 115 | 220 | 0 | 800 | 300 | 54 | 5074.37 | 13783.41 | 106.24
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 35 | 104 | 30 | 196 | 53 | 0 | 54 | 0 | 0 | 405 | 0 | 17 | 303 | 0 | 0 | 11 | 143.42 | 10 | 18 | 0 | 410 | 101 | 68 | 45 | 0 | 0 | 36 | 36 | 0 | 24 | 25 | 1.42 | 219 | 92 | 9 | 1055 | 16 | 0 | 47 | 8 | 105 | 219 | 0 | 0 | 0 | 1195 | 10 | 150 | 128 | 0 | 334 | 310 | 44 | 31 | 200 | 37 | 51 | 85 | 17 | 3 | 10 | 86 | 66 | 43 | 7 | 23 | 266 | 400 | 150 | 40 | 40 | 158 | 5 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 58 | 6.8 | 67 | 0 | 0.7 | 17.36 | 12 | 8669.7 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 1234.2 | 0 | 0 | 0 | 570.15 | 0 | 0 | 0 | 35 | 1 | 0 | 0 | 0 | 0 | 18.6 | 28 | 0 | 0 | 19.42 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 1.82 | 0 | 0 | 115 | 12 | 0 | 0 | 0 | 0 | 2.8 | 46 | 0.24 | 109 | 280 | 115 | 220 | 0 | 800 | 300 | 54 | 5130.23 | 13799.93 | 106.24
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 35 | 115 | 62 | 196 | 55 | 0 | 54 | 0 | 0 | 370 | 0 | 17 | 288 | 0 | 0 | 19 | 143.42 | 10 | 22 | 0 | 370 | 109 | 152 | 46 | 0 | 0 | 51 | 36 | 17 | 24 | 25 | 2.41 | 219 | 92 | 2 | 1060 | 18 | 0 | 45 | 8 | 105 | 220 | 0 | 0 | 0 | 1190 | 15 | 150 | 128 | 0 | 310 | 285 | 44 | 10 | 191 | 36 | 51 | 85 | 17 | 34 | 10 | 86 | 68 | 34 | 52 | 23 | 265 | 399 | 146 | 40 | 39 | 157 | 8 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 59 | 14 | 104 | 0 | 0.9 | 28.5 | 12 | 8780.23 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 1233 | 0 | 0 | 0 | 593.5 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 32.59 | 59 | 0 | 0 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 3.07 | 0 | 0 | 115 | 22 | 0 | 0 | 0 | 0 | 4.6 | 111 | 0.4 | 110 | 270 | 115 | 220 | 0 | 800 | 300 | 54 | 5458.46 | 14238.69 | 106.23
10:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 35 | 115 | 62 | 196 | 55 | 35 | 54 | 0 | 0 | 365 | 0 | 17 | 303 | 0 | 0 | 26 | 143.42 | 10 | 22 | 0 | 395 | 107 | 154 | 45 | 0 | 0 | 51 | 36 | 36 | 24 | 25 | 3.5 | 219 | 92 | 2 | 1060 | 18 | 0 | 47 | 8 | 105 | 217 | 0 | 0 | 0 | 1160 | 18 | 140 | 128 | 0 | 334 | 310 | 44 | 12 | 203 | 32 | 51 | 78 | 17 | 69 | 10 | 86 | 70 | 16 | 56 | 23 | 267 | 393 | 146 | 40 | 38 | 157 | 10 | 0 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 13.16 | 116 | 0 | 0 | 40.4 | 12 | 9047.48 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 69.29 | 1234.2 | 0 | 0 | 0 | 615.32 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 39.93 | 79 | 0 | 0 | 44.86 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 4.01 | 0 | 0 | 115 | 27 | 0 | 0 | 0 | 0 | 6 | 38 | 0.54 | 110 | 211 | 114 | 220 | 0 | 800 | 300 | 54 | 5422.15 | 14469.63 | 106.22
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 35 | 115 | 62 | 210 | 55 | 35 | 54 | 0 | 0 | 390 | 0 | 17 | 305 | 0 | 0 | 30 | 143.42 | 10 | 22 | 0 | 470 | 107 | 160 | 39 | 0 | 0 | 51 | 36 | 36 | 24 | 25 | 3.68 | 219 | 92 | 0 | 1060 | 16 | 0 | 50 | 8 | 94 | 216 | 0 | 0 | 0 | 1224 | 18 | 150 | 128 | 0 | 334 | 310 | 44 | 20 | 205 | 33 | 51 | 72 | 24 | 71 | 10 | 86 | 74 | 8 | 46 | 23 | 275 | 391 | 150 | 40 | 38 | 156 | 10 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 59 | 9.2 | 116 | 0 | 1.6 | 34.44 | 12 | 9264.34 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 91 | 1230 | 0 | 0 | 0 | 607.37 | 0 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 0 | 43.15 | 91 | 0 | 0 | 51.78 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 4.58 | 0 | 0 | 115 | 30 | 0 | 0 | 0 | 0 | 6.6 | 187 | 0.58 | 110 | 294 | 113 | 220 | 0 | 800 | 300 | 54 | 5717.06 | 14981.4 | 106.21
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 0 | 115 | 30 | 246 | 55 | 35 | 54 | 0 | 0 | 390 | 0 | 17 | 297 | 0 | 0 | 31 | 143.42 | 10 | 22 | 0 | 425 | 107 | 160 | 34 | 0 | 0 | 51 | 22 | 36 | 24 | 25 | 3.84 | 219 | 92 | 0 | 1060 | 18 | 0 | 50 | 0 | 105 | 215 | 0 | 0 | 0 | 1224 | 18 | 150 | 135 | 0 | 320 | 295 | 44 | 20 | 202 | 33 | 51 | 71 | 49 | 71 | 10 | 86 | 78 | 8 | 45 | 22 | 277 | 393 | 150 | 39 | 36 | 155 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 10.01 | 116 | 0 | 0.8 | 20.71 | 12 | 9157.78 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 89 | 1230 | 0 | 0 | 0 | 609.54 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 56.27 | 99 | 0 | 0 | 39.66 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 4.95 | 0 | 0 | 115 | 26 | 0 | 0 | 0 | 0 | 6.8 | 132 | 0.67 | 110 | 307 | 113 | 220 | 0 | 800 | 300 | 54 | 5663.89 | 14821.67 | 106.2
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 0.72 | 115 | 30 | 260 | 55 | 35 | 54 | 0 | 0 | 375 | 0 | 17 | 290 | 0 | 0 | 30 | 143.42 | 10 | 22 | 0 | 385 | 107 | 160 | 42 | 0 | 0 | 49 | 25 | 36 | 24 | 25 | 3.3 | 219 | 92 | 0 | 1060 | 16 | 0 | 50 | 0 | 105 | 215 | 0 | 0 | 0 | 1170 | 18 | 138 | 168 | 0 | 315 | 290 | 44 | 20 | 196 | 36 | 51 | 66 | 51 | 68 | 10 | 86 | 74 | 8 | 66 | 22 | 271 | 393 | 150 | 39 | 37 | 155 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 58 | 1.3 | 116 | 0 | 0.8 | 36.1 | 4 | 8961.64 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 84.54 | 1230 | 0 | 0 | 0 | 615.26 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 51.11 | 94 | 0 | 0 | 42.33 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 2.46 | 0 | 0 | 115 | 16 | 0 | 0 | 0 | 0 | 6.4 | 110 | 0.58 | 110 | 307 | 108 | 220 | 0 | 800 | 300 | 54 | 5601.68 | 14563.32 | 106.19
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 32 | 115 | 30 | 278 | 55 | 35 | 54 | 0 | 0 | 375 | 0 | 35 | 292 | 0 | 0 | 25 | 0 | 10 | 22 | 0 | 370 | 107 | 159 | 38 | 0 | 0 | 50 | 27 | 36 | 24 | 25 | 2.75 | 219 | 93 | 0 | 1060 | 18 | 0 | 50 | 2 | 105 | 213 | 0 | 0 | 0 | 1160 | 16 | 142 | 170 | 0 | 320 | 295 | 44 | 22 | 195 | 36 | 54 | 65 | 59 | 70 | 10 | 86 | 80 | 8 | 54 | 21 | 277 | 393 | 100 | 39 | 39 | 154 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 16.67 | 116 | 0 | 0.5 | 1.14 | 0 | 8821.06 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70.2 | 1230 | 0 | 0 | 0 | 612.45 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 43 | 80 | 0 | 0 | 29.58 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 1.85 | 0 | 0 | 115 | 23 | 0 | 0 | 0 | 0 | 5.4 | 126 | 0.5 | 100 | 307 | 107 | 220 | 0 | 800 | 300 | 54 | 5555.98 | 14377.04 | 106.18
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 17 | 43 | 128 | 30 | 278 | 55 | 35 | 54 | 0 | 0 | 380 | 0 | 35 | 300 | 0 | 0 | 17 | 10 | 10 | 21 | 0 | 400 | 107 | 159 | 38 | 0 | 1 | 48 | 27 | 36 | 24 | 25 | 1.98 | 220 | 92 | 0 | 1060 | 18 | 0 | 50 | 8 | 105 | 213 | 0 | 0 | 0 | 1224 | 12 | 145 | 167 | 0 | 325 | 305 | 44 | 30 | 199 | 36 | 51 | 68 | 65 | 71 | 10 | 95 | 82 | 8 | 38 | 21 | 293 | 390 | 102 | 39 | 36 | 154 | 5 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 9.45 | 116 | 0 | 0.2 | 30 | 6 | 9012.63 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 49.24 | 1231 | 0 | 0 | 0 | 526.33 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 0 | 31.46 | 60 | 0 | 0 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 2.66 | 0 | 0 | 115 | 18 | 0 | 0 | 0 | 0 | 4 | 98 | 0.35 | 110 | 307 | 107 | 220 | 0 | 800 | 300 | 54 | 5347.84 | 14360.47 | 106.18
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 17 | 54 | 149 | 46 | 294 | 55 | 35 | 162 | 0 | 0 | 375 | 0 | 35 | 290 | 0 | 0 | 11 | 105 | 10 | 22 | 0 | 405 | 95 | 159 | 38 | 0 | 2 | 48 | 42 | 36 | 24 | 25 | 1.01 | 221 | 92 | 0 | 1060 | 16 | 0 | 50 | 14 | 105 | 213 | 0 | 0 | 0 | 1224 | 6 | 138 | 170 | 0 | 295 | 275 | 44 | 30 | 185 | 36 | 51 | 67 | 67 | 70 | 5 | 98 | 80 | 8 | 16 | 21 | 297 | 392 | 101 | 39 | 36 | 153 | 1 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 5.66 | 116 | 0 | 0.7 | 11.22 | 12 | 9147.59 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 26.93 | 1228 | 0 | 0 | 0 | 510.82 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 0 | 9.88 | 32 | 0 | 0 | 14.13 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 1.24 | 0 | 0 | 115 | 7 | 27 | 0 | 0 | 0 | 2.8 | 52 | 0.19 | 110 | 307 | 95 | 220 | 0 | 800 | 300 | 54 | 5194.99 | 14342.58 | 106.17
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 54 | 149 | 46 | 295 | 55 | 55 | 162 | 0 | 0 | 370 | 0 | 55 | 290 | 0 | 0 | 2 | 105 | 10 | 22 | 0 | 380 | 107 | 210 | 38 | 0 | 1 | 51 | 49 | 36 | 24 | 25 | 0.16 | 221 | 92 | 0 | 1060 | 18 | 0 | 50 | 10 | 105 | 213 | 0 | 0 | 0 | 1110 | 1 | 143 | 168 | 0 | 315 | 290 | 44 | 30 | 191 | 36 | 51 | 71 | 69 | 69 | 12 | 98 | 62 | 8 | 3 | 21 | 291 | 392 | 101 | 39 | 36 | 152 | 1 | 8 | 0 | 52 | 0 | 137 | 0 | 100 | 0 | 59 | 1.93 | 116 | 0 | 0.1 | 3.09 | 12 | 9088.28 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 6.47 | 1230 | 0 | 0 | 0 | 512.66 | 0 | 0 | 0 | 70 | 50 | 0 | 8 | 0 | 0 | 3.6 | 8 | 0 | 0 | 3.11 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0.26 | 0 | 0 | 115 | 2 | 80 | 0 | 0 | 0 | 0.9 | 13 | 0.04 | 110 | 291 | 108 | 180 | 0 | 800 | 300 | 100 | 5284.04 | 14372.32 | 106.16
18:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 96 | 295 | 55 | 55 | 162 | 0 | 0 | 350 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 490 | 107 | 210 | 40 | 0 | 0 | 51 | 54 | 54.36 | 60 | 36 | 0 | 221 | 92 | 0 | 1060 | 16 | 0 | 50 | 16 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 177 | 0 | 345 | 320 | 44 | 30 | 210 | 34 | 73 | 71 | 90 | 73 | 10 | 98 | 80 | 16 | 0 | 21 | 285 | 392 | 101 | 39 | 39 | 152 | 0 | 8 | 0 | 52 | 0 | 137 | 0 | 100 | 0 | 59 | 0 | 124 | 0 | 0 | 0 | 12 | 9696.78 | 778 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1188 | 0 | 0 | 0 | 616.61 | 0 | 0 | 0 | 110 | 102 | 0 | 60 | 30 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 80 | 0 | 0 | 0 | 0 | 110 | 307 | 108 | 220 | 0 | 800 | 300 | 137 | 5589.61 | 15286.39 | 106.15
19:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 143 | 295 | 55 | 55 | 162 | 0 | 0 | 375 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 385 | 107 | 211 | 57 | 0 | 0 | 51 | 54 | 54.36 | 89 | 100 | 0 | 222 | 92 | 0 | 1060 | 18 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 177 | 0 | 318 | 290 | 44 | 30 | 195 | 34 | 115 | 75 | 122 | 74 | 12 | 98 | 78 | 16 | 0 | 21 | 280 | 400 | 101 | 39 | 39 | 153 | 0 | 8 | 0 | 52 | 0 | 139 | 0 | 100 | 0 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9867.28 | 778 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 10 | 0 | 0 | 609.25 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 38 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 276 | 110 | 220 | 0 | 830 | 300 | 137 | 5750.45 | 15617.73 | 106.15
19:30 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 54 | 149 | 143 | 295 | 55 | 55 | 162 | 0 | 0 | 384 | 0 | 55 | 305 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 415 | 107 | 212 | 57 | 0 | 0 | 51 | 54 | 54.36 | 89 | 100 | 0 | 222 | 92 | 0 | 1060 | 18 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 168 | 0 | 335 | 310 | 44 | 30 | 202 | 33 | 115 | 73 | 136 | 74 | 12 | 99 | 80 | 16 | 0 | 21 | 282 | 400 | 101 | 39 | 39 | 152 | 0 | 8 | 0 | 74 | 0 | 137 | 0 | 100 | 0 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 10046.28 | 778 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 17 | 0 | 0 | 700.8 | 0 | 0 | 0 | 113 | 113 | 0 | 100 | 38 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 277 | 110 | 220 | 0 | 1000 | 300 | 137 | 6023 | 16069.28
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 50 | 149 | 143 | 295 | 55 | 55 | 162 | 0 | 0 | 375 | 0 | 55 | 295 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 395 | 107 | 212 | 55 | 0 | 0 | 51 | 54 | 54.36 | 100 | 100 | 0 | 222 | 92 | 2 | 1060 | 18 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 177 | 0 | 320 | 295 | 44 | 30 | 195 | 33 | 115 | 75 | 138 | 73 | 12 | 99 | 78 | 16 | 0 | 21 | 280 | 400 | 101 | 39 | 39 | 153 | 0 | 8 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 88 | 0 | 163 | 0 | 0 | 0 | 12 | 9996.28 | 778 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 17 | 0 | 0 | 710.14 | 0 | 17 | 0 | 113 | 113 | 0 | 93 | 38 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 298 | 115 | 220 | 0 | 1100 | 300 | 137 | 6175.34 | 16171.62 | 106.15
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 54 | 149 | 143 | 295 | 55 | 55 | 162 | 0 | 0 | 405 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 500 | 107 | 212 | 52 | 0 | 0 | 51 | 54 | 54.36 | 100 | 100 | 0 | 222 | 92 | 8 | 1060 | 16 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 147 | 165 | 0 | 355 | 330 | 44 | 30 | 209 | 33 | 110 | 77 | 139 | 73 | 12 | 99 | 72 | 52.2 | 0 | 21 | 277 | 400 | 101 | 39 | 39 | 155 | 0 | 8 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 88 | 0 | 164 | 0 | 0 | 0 | 12 | 10253.48 | 779 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 17 | 0 | 0 | 717.41 | 0 | 17 | 0 | 113 | 113 | 0 | 96 | 36 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1100 | 300 | 137 | 6263.61 | 16517.09 | 106.14
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 54 | 149 | 145 | 295 | 49 | 55 | 162 | 0 | 0 | 405 | 0 | 55 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 410 | 107 | 212 | 52 | 0 | 0 | 51 | 54 | 54.36 | 100 | 100 | 0 | 222 | 92 | 4 | 1060 | 18 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 157 | 0 | 330 | 305 | 44 | 20 | 220 | 33 | 107 | 77 | 147 | 73 | 12 | 99 | 70 | 52.2 | 0 | 21 | 275 | 400 | 101 | 40 | 39 | 156 | 0 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 88 | 0 | 165 | 0 | 0 | 0 | 12 | 10024.48 | 778 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 17 | 0 | 0 | 701 | 0 | 32 | 0 | 113 | 113 | 0 | 96 | 35 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 115 | 0 | 111 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 137 | 6192.2 | 16216.68 | 106.14
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 54 | 120 | 45 | 295 | 49 | 55 | 162 | 0 | 0 | 400 | 0 | 55 | 314 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 495 | 107 | 212 | 52 | 0 | 0 | 51 | 56 | 36 | 100 | 100 | 0 | 222 | 91 | 4 | 1060 | 17 | 0 | 50 | 25.5 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 344 | 325 | 44 | 20 | 221 | 31 | 96 | 77 | 154 | 73 | 12 | 99 | 72 | 52.2 | 0 | 15 | 275 | 400 | 101 | 40 | 40 | 153 | 0 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 1 | 88 | 0 | 165 | 0 | 0 | 0 | 12 | 9993.12 | 778 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 17 | 0 | 0 | 689.52 | 0 | 32 | 0 | 113 | 113 | 0 | 96 | 35 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 72 | 6077.72 | 16070.84 | 106.13
Total KWH | 0 | 1148160 | 493920 | 0 | 0 | 0 | 0 | 0 | 9547200 | 0 | 0 | 310680 | 892440 | 2911536 | 1401600 | 5782702 | 1312951 | 796851 | 2358720 | 0 | 0 | 9549600 | 0 | 825258 | 7256712 | 0 | 0 | 201861 | 3176400 | 261600 | 506880 | 0 | 10228636.36 | 2481491 | 3460036 | 1086720 | 0 | 2880 | 1198979 | 953010 | 661568 | 955200 | 980160 | 21601 | 5297605 | 2300000 | 206400 | 25490909.09 | 428218 | 0 | 1201920 | 331417.8 | 2541709 | 5135866 | 0 | 0 | 0 | 28587270 | 127305 | 3507709 | 3830545 | 0 | 8364700 | 7516000 | 963392 | 665760 | 4931000 | 830952 | 1676160 | 1882238 | 1539360 | 1265040 | 239690 | 2178540 | 1734720 | 668342 | 382427 | 518368 | 6582000 | 9493400 | 3185000 | 938000 | 911880 | 3731645.46 | 71810 | 175920 | 0 | 1327680 | 0 | 3120000 | 0 | 2414400 | 57240 | 1576800 | 88866 | 2640000 | 0 | 6950 | 238690 | 271440 | 221940636.71 | 20493091 | 0 | 331200 | 0 | 0 | 0 | 0 | 0 | 0 | 872352 | 596880 | 29512730 | 72960 | 0 | 0 | 14732000 | 0 | 115480 | 0 | 1150272 | 1229376 | 0 | 625184 | 209650 | 0 | 339896 | 664290 | 177684 | 0 | 297776 | 0 | 0 | 0 | 0 | 0 | 0 | 7870181 | 0 | 28680 | 0 | 0 | 2743051 | 184080 | 1233552 | 0 | 718515 | 0 | 45522.96 | 883440 | 4080 | 2591904 | 6960000 | 2715000 | 5447460 | 0 | 20770909 | 7298909.09 | 1729200 | 132645305.05 | 354585941.76

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14981.4 | MW | 11:00 Hr. | Energy Generated |  |  | 354.5859 |  | MKWHr.
| Day Peak Demand |  |  | 16220.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 25.855 |  | MKWHr.
| Evening Peak Generation |  |  | 16517.09 | MW | 21:00 Hr. | Energy Demand |  |  | 380.4409 |  | MKWHr.
| Evening Peak Demand |  |  | 17030.73 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 13620.22 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 851.58 |  | MMCFD
| Maximum Generation of the Day |  |  | 16517.09 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 8.4825 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.3506 | 0 | 21.4112 | 0 | 0 | 0.20186 | 0 | 0 | 58.9637 | Gas | 119.8297 | Gas | 414677253.1944
| Chattogram Zone |  |  | 5.3423 | 54.0782 | 18.5804 | 0 | 5.2976 | 0.14891 | 0 | 0.00288 | 83.4503 | Coal | 118.6207 | Coal | 852662434.465
| Cumilla Zone |  |  | 29.2243 | 0 | 11.3535 | 0 | 0 | 0.38243 | 1.7347 | 0 | 42.6949 | HFO | 68.9725 | HFO | 1436243318.644
| Mymensingh Zone |  |  | 0 | 0 | 4.5455 | 0 | 0 | 0.33451 | 0 | 0 | 4.88 | HSD | 0.71852 | HSD | 22187743.2
| Sylhet Zone |  |  | 31.8799 | 0 | 0 | 0 | 0 | 0.07181 | 0 | 0 | 31.9517 | Hydro | 5.2976 | Hydro | 529760.5
| Khulna Zone |  |  | 0 | 29.5127 | 1.2765 | 0 | 0 | 0.59688 | 20.4931 | 0 | 51.8792 | Solar | 4.1842 | Solar | 66848464.5372
| Barishal Zone |  |  | 8.1625 | 35.0298 | 4.3211 | 0 | 0 | 0.00408 | 0 | 0 | 47.5175 | Import | 36.9598 | Import | 214592749.01
| Rajshahi Zone |  |  | 7.8702 | 0 | 3.5076 | 0 | 0 | 1.3306 | 14.732 | 0 | 27.4405 | Wind | 0.00288 | Wind | 42739.2
| Rangpur Zone |  |  | 0 | 0 | 3.9766 | 0.71852 | 0 | 1.113 | 0 | 0 | 5.8082
| Total |  |  | 119.8297 | 118.6207 | 68.9725 | 0.71852 | 5.2976 | 4.1842 | 36.9598 | 0.00288 | 354.5859
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 414677253.1944 |  | Hydro | 529760.5
|  |  |  | Coal | 852662434.465 |  | Solar | 66848464.5372
|  |  |  | HFO | 1436243318.644 |  | Import | 214592749.01
|  |  |  | HSD | 22187743.2 |  | Wind | 42739.2
[5 empty] | Total: | 300,77,84,462 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4931 | Peak Hr Flow | 779.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 28145836.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.732 | Peak Hr Flow | 717.41 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1015 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7347 | Peak Hr Flow | 72.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1670 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.9598 | Peak Hr Flow | 1568.41 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 38 |  | 5857
|  |  |  | Chattogram |  | 53 |  | 1683
|  |  |  | Cumilla |  | 42 |  | 1617
|  |  |  | Mymensingh |  | 0 |  | 1230
|  |  |  | Sylhet |  | 32 |  | 731
|  |  |  | Khulna |  | 14 |  | 2000
|  |  |  | Barishal |  | 4 |  | 537
|  |  |  | Rajshahi |  | 12 |  | 1511
|  |  |  | Rangpur |  | 10 |  | 980
|  |  |  | Total |  | 205 |  | 16146
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 193.5
|  |  |  | Total Unavailable Capacity |  |  |  | 513.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 17:08 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Annual Maintenance work
| 08:03 | 17:07 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Annual Maintenance work
| 08:21 | 14:40 | Rajbari 132/33kV S/S 132 kV Bus-I Scheduled S/D Due to For Annual Maintenance work.
| 08:31 | 16:29 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Annual maintenance
| 08:31 | 16:27 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Annual maintenance
| 08:47 | 12:18 | Bogura 230/132kV S/S 230KV Main 2 Scheduled S/D Due to Annual Maintenance work.
| 09:09 | 17:25 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph LT Project Work S/D Due to Project work
(CAF)
| 09:09 | 17:24 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph HT Project Work S/D Due to Project work
(CAF)
| 09:12 | 17:52 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to SAS & DFDR WORK
| 09:12 | 17:52 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to SAS & DFDR WORK
| 09:30 |  | BIPTC S/S 20DF24 Scheduled S/D Due to 230 kV Shunt Reactor of Block-01 (20DF24) was taken
shutdown at 09:30 on 07-10-2026 for oil centrifuging.
| 09:34 | 14:01 | Korerhat 400/230/132kV S/S Madunaghat-1 Project Work S/D Due to Project work (DFDR)
| 09:35 | 17:27 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to A/M
| 09:35 | 10:31 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance
relay R Y B ph trip Z2 . D- 22 km relays Due to Fault near at kabirpur grid
| 09:36 | 14:02 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 Project Work S/D
| 10:16 | 11:33 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Barishal 132/33kV end Due to Bagerhat
grid work.
| 10:16 | 11:34 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Tree
trimming Between tower no 67 & 68
| 10:33 | 13:30 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D
| 11:58 | 13:06 | Madunaghat 132/33kV S/S TR-1(507T) LT Forced S/D Due to Station Supply Bus loop
connection.
| 12:00 |  | Day peak generation is 14822 MW.
| 12:48 | 16:49 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing distance 21 zone1
relays Due to distance trip AN zone1
| 13:23 | 14:03 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Incharge
took the shutdown for tree trimming Between towe 61 & 62
| 13:24 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to
Instruction by ALDC
| 13:51 | 14:05 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing P-141 relays
Due to 67/67N
| 14:34 | 15:57 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Shutdown for BPDB's Red Hot maintenance | [7 empty] | 12.0MW load
|  |  | work. | [7 empty] | interrup.
| 14:34 | 15:57 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Shutdown for BPDB's Red Hot maintenance | [7 empty] | 12.0MW load
|  |  | work. | [7 empty] | interrup.
| 14:52 | 15:58 | Bogura South-Confidence 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing GENERAL
TRIP, Z1,R-ph trip. KF861 Lockout relay. Fault location: 87.36m Fault Current:
15.92kA relays Due to due to bad weather with strong thunderstorm
| 14:53 | 22:48 | Bogura-Natore 132 kV Ckt-1 Tripped from Bogura 132/33kV end showing Phase A Trip, Phase
B Trip Phase C Trip Zone -1 Trip SOTF Trip relays.
| 16:18 | 16:45 | Chowmuhani 230/132/33kV S/S TR2 Forced S/D Due to emergency load shift | [7 empty] | 40.0MW load
interrup.
| 16:18 | 16:46 | Chowmuhani 230/132/33kV S/S TR3 Forced S/D Due to emergency load shift | [7 empty] | 40.0MW load
interrup.
|  | 16:30 | Khulna (C) S/S Tr-3 405T HT is restored.
|  | 16:31 | Khulna (C) S/S Tr-3 405T LT is restored.
| 16:45 | 17:15 | Sreepur 230/132/33kV S/S 132/33 kV T-3 LT Tripped showing FBCPU relays Due to OC | [7 empty] | 3.0MW load
interrup.
|  | 16:55 | Charfasson 230/33kV S/S Main Bus-1 is restored.
| 17:02 | 22:48 | Bogura-Natore 132 kV Ckt-1 Project Work S/D from Bogura 132/33kV end Due to Trip with
Distance Relay Zone-1
| 19:10 | 20:35 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to taken by BPDB Mohoa
| 21:00 |  | Evening Peak Generation: 16517 MW.
| 06:04 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end Due to
LILO work 400kv line and from Kishoreganj 132/33kV end Due to Mymensingh Control Room has
completed the shutdown process for work under the Power Grid Network Strengthening
Project.
| 07:28 |  | Rajbari 132/33kV S/S 132 kV Bus-II Scheduled S/D Due to Annual maintenance work 2026.
| 07:38 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to For annual maintenance
| 07:38 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to For annual maintenance
| 07:38 |  | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Taken by NLDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9547200 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1312951 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7256712 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 310680 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1401600 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 796851 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 825258 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 261600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 506880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 493920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 5782702 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2911536 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1148160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2358720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 201861 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 892440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10228636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 405 | 9549600 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3176400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2930.42 | 58963707.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 331417.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127305 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1201920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5297605 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5135866 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2541709 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 953010 | ps availability is less
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1198979 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 955200 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 206400 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 52 | 1086720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21601 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 212 | 3460036 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 661568 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2300000 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 980160 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2481491 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 428218 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28587270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 2880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1060 | 25490909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3750.86 | 83450264.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 209 | 4931000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8364700 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 330 | 7516000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 830952 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 30 | 665760 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 3830545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 963392 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 147 | 3507709 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 518368 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 77 | 1882238 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 139 | 1539360 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1734720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 668342 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 12 | 239690 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 2178540 | Machine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1265040 | plant availability zero
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 110 | 1676160 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 382427 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1968.2 | 42694943
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 88866 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2640000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1576800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 238690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 271440 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 57240 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 264 | 4879986
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 71810 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 938000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 911880 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3731645.46 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 138 | 3120000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1327680 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2414400 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 175920 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 277 | 6582000 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 101 | 3185000 | STG Under Shutdown & Gas Shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9493400 | -
Sylhet Area Total |  |  |  |  | 2325 | 1340 | 31951735.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 779 | 20493091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 331200 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 72960 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 872352 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 596880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29512730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2169.2 | 51879213
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 20770909 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 2591904 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 114 | 2715000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7298909.09 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5447460 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1729200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6960000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4080 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2288 | 47517462.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 339896 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 17 | 115480 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 209650 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 300 | 7870181 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 177684 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 625184 | ps availability is less
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1229376 | High Voltage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1150272 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 28680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 717.41 | 14732000 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 297776 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 664290 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1413.41 | 27440469
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 718515 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1233552 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45522.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2743051 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 184080 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 883440 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 393 | 5808160.96
Eastern Grid Total |  |  |  |  | 16961.086 | 10253.48 | 221940636.71
Western Grid Total |  |  |  |  | 11731.125 | 6263.61 | 132645305.05
National Grid Total |  |  |  |  | 28692.211 | 16517.09 | 354585941.76
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-10-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10953.08 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4989.1 | MW
i) Dhaka area |  |  | 5819.07 |  | MW | i) Khulna area |  |  |  | 1986.5 | MW
ii) Chattogram area |  |  | 1629.6 |  | MW | ii) Barishal area |  |  |  | 533.2 | MW
iii) Cumilla area |  |  | 1575.41 |  | MW | iii) Rajshahi area |  |  |  | 1499.4 | MW
iv) Mymensingh area |  |  | 1230 |  | MW | iv) Rangpur area |  |  |  | 970 | MW
v) Sylhet area |  |  | 699 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15942.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 21:00 | 72 | Hatirjheel | 81 | 12:00 | 143 | PHP | 13 | 11:00
2 | AKSML | 142.2 | 11:00 | 73 | Ishurdi | 79 | 21:00 | 144 | Pabna | 102 | 21:00
3 | Aftabnagar | 44 | 11:00 | 74 | Jaldhaka | 77 | 21:00 | 145 | Palashbari | 129 | 19:00
4 | Agargaon | 136 | 13:00 | 75 | Jamalpur | 133 | 19:00 | 146 | Panchagarh | 68 | 18:30
5 | Agrabad | 84 | 15:00 | 76 | Jashore | 136 | 18:30 | 147 | Patiya | 31 | 22:00
6 | Amnura | 30 | 00:00 | 77 | Jhenaidah | 96 | 21:00 | 148 | Patnitala | 32 | 20:00
7 | Araihazar | 108 | 23:00 | 78 | Joydebpur | 175 | 19:30 | 149 | Patuakhali | 78 | 22:00
8 | Ashuganj | 0.55 | 00:00 | 79 | Joypurhat | 56 | 21:00 | 150 | Payra | 36 | 22:00
9 | Ashuganj-230 | 106 | 02:00 | 80 | Juldah | 17 | 00:00 | 151 | Postogola | 64 | 13:00
10 | BSRM | 193 | 10:00 | 81 | KSRM | 21 | 15:00 | 152 | Pubail | 46 | 19:30
11 | Bagerhat | 91 | 21:00 | 82 | Kabirpur | 276 | 19:30 | 153 | Purbachal | 29 | 00:00
12 | Bajitpur | 90 | 08:00 | 83 | Kachua | 104 | 21:00 | 154 | Purbasadipur | 124 | 21:00
13 | Bakerganj | 15.4 | 22:00 | 84 | Kaliganj | 40 | 21:00 | 155 | Rahanpur | 40 | 20:00
14 | Bakulia | 105 | 21:00 | 85 | Kallyanpur | 117 | 16:00 | 156 | Rahim | 55 | 12:00
15 | Banani | 69.4 | 12:00 | 86 | Kalurghat | 47 | 02:00 | 157 | Rajbari | 89 | 22:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 87 | 13:00 | 158 | Rajendrapur | 133 | 10:00
17 | Barapukuria | 58 | 20:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 119 | 12:00
18 | Barguna | 24 | 20:00 | 89 | Kasba | 37 | 04:00 | 160 | Rajshahi-230 | 88 | 23:00
19 | Barishal | 107 | 22:00 | 90 | Kazla | 124 | 19:30 | 161 | Ramganj | 114 | 21:00
20 | Barishal-230 | 108 | 20:00 | 91 | Keranigonj | 96 | 19:30 | 162 | Rampur | 48 | 21:00
21 | Baroaulia | 44 | 15:00 | 92 | Khagrachori | 34 | 18:00 | 163 | Rangamati | 16 | 18:00
22 | Baroirhat | 64 | 21:00 | 93 | Khulna | 69 | 21:00 | 164 | Rangpur | 126 | 20:00
23 | Bashundhara | 196 | 14:00 | 94 | Khulshi | 186 | 12:00 | 165 | Ruppur | 4.6 | 16:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 129 | 20:00 | 166 | SSM | 10 | 04:00
25 | Beanibazar | 74 | 23:00 | 96 | Kodda | 314 | 22:00 | 167 | Saidpur | 99 | 18:30
26 | Benapole | 68 | 18:30 | 97 | Kulaura | 60 | 21:00 | 168 | Santhia | 36 | 18:00
27 | Bhaluka | 159 | 09:00 | 98 | Kurigram | 62 | 21:00 | 169 | Satkhira | 137 | 21:00
28 | Bhandaria | 61 | 21:00 | 99 | Kushtia | 166 | 20:00 | 170 | Satmasjid | 109 | 18:30
29 | Bhangura | 38 | 21:00 | 100 | Laksam | 39 | 22:00 | 171 | Savar | 222 | 10:00
30 | Bheramara(GK) | 70 | 22:00 | 101 | Lakshmipur | 54 | 18:00 | 172 | SevenRings | 7.57 | 14:00
31 | Bhulta | 198 | 22:00 | 102 | Lalbag | 97 | 13:00 | 173 | ShahCement | 17 | 09:00
32 | Bog-Sherpur | 66 | 07:00 | 103 | Lalmonirhat | 58 | 20:00 | 174 | Shahjadpur | 86 | 20:00
33 | Bogura | 193 | 00:00 | 104 | MI_Cement | 18.5 | 03:00 | 175 | Shahjibazar | 138 | 19:30
34 | Borhanuddin | 82 | 22:00 | 105 | Madanganj | 55 | 19:30 | 176 | Shahmirpur | 61 | 23:00
35 | Brahmanbaria | 127 | 06:00 | 106 | Madaripur | 121 | 21:00 | 177 | Shariatpur | 113 | 21:00
36 | Cantonment | 142 | 12:00 | 107 | Madartek | 86 | 00:00 | 178 | Sherpur | 150 | 19:00
37 | Chandina | 23 | 00:00 | 108 | Madunaghat | 58 | 22:00 | 179 | Shikalbaha | 29 | 23:00
38 | Chandpur | 94 | 21:00 | 109 | Magura | 72 | 22:00 | 180 | Shitalakhya | 84.4 | 16:00
39 | Chandraghona | 38 | 13:00 | 110 | Mahasthangarh | 77 | 00:00 | 181 | Sholosohor | 51 | 09:00
40 | Chapai | 76 | 21:00 | 111 | Maijdee | 43 | 21:00 | 182 | Shomvuganj | 52 | 18:00
41 | Charfasson | 34 | 21:00 | 112 | Manikganj | 147 | 21:00 | 183 | Shyampur | 160 | 12:00
42 | Charsaidpur | 42 | 15:00 | 113 | Maniknagar | 72 | 23:00 | 184 | Siddhirganj | 140 | 12:00
43 | Chauddagram | 81 | 21:00 | 114 | Matarbari | 61 | 18:30 | 185 | Sirajganj | 118 | 21:00
44 | Chhatak | 34 | 21:00 | 115 | Matuail | 78 | 15:00 | 186 | Sitakunda | 35 | 18:00
45 | Chowmuhani | 169 | 21:00 | 116 | Metrorail_Motijheel | 18 | 19:30 | 187 | Sonargaon | 114 | 04:00
46 | Chuadanga | 123 | 21:00 | 117 | Metrorail_Uttara | 7 | 13:00 | 188 | Sreemongol | 91 | 21:00
47 | Coxsbazar | 153 | 21:00 | 118 | Millgate | 103 | 12:00 | 189 | Sreepur | 150 | 11:00
48 | Cumilla(N) | 153 | 21:00 | 119 | Mirpur | 162 | 14:00 | 190 | Srinagar | 52.8 | 19:30
49 | Cumilla(S) | 165 | 15:00 | 120 | Mirsorai | 50 | 11:00 | 191 | Sunamganj | 58 | 11:00
50 | Daganbhuiyan | 38 | 20:00 | 121 | Mirzapur | 54 | 19:00 | 192 | Sylhet | 147 | 21:00
51 | Daudkandi | 134 | 19:00 | 122 | Mithapukur | 68 | 21:00 | 193 | Sylhet_(South) | 61 | 18:30
52 | DhakaUniversity | 102 | 12:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 96 | 21:00 | 124 | Mogbazar | 71.8 | 18:00 | 195 | Tangail | 178 | 19:00
54 | Dhanmondi | 123 | 12:00 | 125 | Mongla | 37 | 12:00 | 196 | Taraganj | 35 | 20:00
55 | Dohazari | 105 | 06:00 | 126 | Monirampur | 27 | 22:00 | 197 | Tasnim | 43 | 16:00
56 | Faridpur | 191 | 21:00 | 127 | Motijheel | 55 | 13:00 | 198 | Thakurgaon | 111 | 18:30
57 | Fatullah | 109 | 23:00 | 128 | Muktagacha | 39 | 15:00 | 199 | Tongi | 166 | 10:00
58 | Fenchuganj | 46 | 23:00 | 129 | Munshiganj | 116 | 20:00 | 200 | Ullahpara | 39 | 20:00
59 | Feni | 112 | 21:00 | 130 | Muradnagar | 57 | 04:00 | 201 | Ullon | 40 | 00:00
60 | GPH | 25 | 23:00 | 131 | Mymensingh | 160 | 22:00 | 202 | Uttara | 99 | 15:00
61 | Ghatail | 86 | 19:00 | 132 | Nabinagar | 112 | 15:00 | 203 | UttaraNew | 59 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 113 | 00:00 | 204 | Zigatola | 92 | 13:00
63 | Ghorashal-230 | 94 | 12:00 | 134 | Narail | 63 | 22:00
64 | Goalpara | 42 | 22:00 | 135 | Narinda | 79 | 13:00
65 | Gollamari | 110 | 23:00 | 136 | Narshingdi | 188 | 20:00
66 | Gopalganj | 124 | 21:00 | 137 | Natore | 145 | 20:00
67 | Gulshan | 122 | 11:00 | 138 | Nawabganj | 54.1 | 22:00
68 | Halishahar | 142 | 16:00 | 139 | Netrakona | 154 | 19:00
69 | HaripurSBU | 130 | 11:00 | 140 | New | 89.8 | 12:00
70 | Hasnabad | 111 | 21:00 | 141 | Niamatpur | 64 | 22:00
71 | Hathazari | 98 | 21:00 | 142 | Noapara | 48 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14941.12 | 2126 |  | 17163.12
1:00 | 14083.13 | 2449 |  | 16642.13
2:00 | 13915.71 | 2355 |  | 16376.71
3:00 | 13913.88 | 2126 |  | 16135.88
4:00 | 13908.28 | 1381 |  | 15351.28
5:00 | 13745.39 | 1160 |  | 14957.39
6:00 | 13620.22 | 703 |  | 14355.22
7:00 | 13783.41 | 711 |  | 14526.41
8:00 | 13799.93 | 859 |  | 14697.93
9:00 | 14238.69 | 203 |  | 14450.69
10:00 | 14469.63 | 55 |  | 14527.11
11:00 | 14981.4 | 101 |  | 15087.4
12:00 | 14821.67 | 1339 |  | 16220.67
13:00 | 14563.32 | 1245 |  | 15864.32
14:00 | 14377.04 | 1345 |  | 15783.04
15:00 | 14360.47 | 1641 |  | 16075.47
16:00 | 14342.58 | 1161 |  | 15555.58
17:00 | 14372.32 | 793 |  | 15201.32
18:00 | 15286.39 | 1276 |  | 16619.39
19:00 | 15617.73 | 1352 |  | 17030.73
19:30 | 16069.28 | 844 |  | 16951.28
20:00 | 16171.62 | 679 |  | 16881.62
21:00 | 16517.09 | 205 |  | 16731.09
22:00 | 16216.68 | 198 |  | 16423.68
23:00 | 16070.84 | 392 |  | 16480.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9402.92 | 5538.2 | 14941.12 | DAILY GENERATION CURVE
00:30 | 9104.42 | 5407.705 | 14512.125
01:00 | 8805.92 | 5277.21 | 14083.13 | 07-10-2026
01:30 | 8787.92 | 5211.5 | 13999.42
02:00 | 8769.92 | 5145.79 | 13915.71
02:30 | 8764.17 | 5150.625 | 13914.795
03:00 | 8758.42 | 5155.46 | 13913.88
03:30 | 8780.42 | 5130.66 | 13911.08
04:00 | 8802.42 | 5105.86 | 13908.28
04:30 | 8767.42 | 5059.415 | 13826.835
05:00 | 8732.42 | 5012.97 | 13745.39
05:30 | 8683.16 | 4999.645 | 13682.805
06:00 | 8633.9 | 4986.32 | 13620.22
06:30 | 8671.47 | 5030.345 | 13701.815
07:00 | 8709.04 | 5074.37 | 13783.41
07:30 | 8689.37 | 5102.3 | 13791.67
08:00 | 8669.7 | 5130.23 | 13799.93
08:30 | 8724.965 | 5294.345 | 14019.31
09:00 | 8780.23 | 5458.46 | 14238.69
09:30 | 8913.855 | 5440.305 | 14354.16
10:00 | 9047.48 | 5422.15 | 14469.63
10:30 | 9155.91 | 5569.605 | 14725.515
11:00 | 9264.34 | 5717.06 | 14981.4
11:30 | 9211.06 | 5690.475 | 14901.535
12:00 | 9157.78 | 5663.89 | 14821.67
12:30 | 9059.71 | 5632.785 | 14692.495
13:00 | 8961.64 | 5601.68 | 14563.32
13:30 | 8891.35 | 5578.83 | 14470.18
14:00 | 8821.06 | 5555.98 | 14377.04
14:30 | 8916.845 | 5451.91 | 14368.755
15:00 | 9012.63 | 5347.84 | 14360.47
15:30 | 9080.11 | 5271.415 | 14351.525
16:00 | 9147.59 | 5194.99 | 14342.58
16:30 | 9117.935 | 5239.515 | 14357.45
17:00 | 9088.28 | 5284.04 | 14372.32
17:30 | 9392.53 | 5436.825 | 14829.355
18:00 | 9696.78 | 5589.61 | 15286.39
18:30 | 9782.03 | 5670.03 | 15452.06
19:00 | 9867.28 | 5750.45 | 15617.73
19:30 | 10046.28 | 6023 | 16069.28
20:00 | 9996.28 | 6175.34 | 16171.62
20:30 | 10124.88 | 6219.475 | 16344.355 |  | Executive Engineer
21:00 | 10253.48 | 6263.61 | 16517.09 |  | Network Operation Division
21:30 | 10138.98 | 6227.905 | 16366.885
22:00 | 10024.48 | 6192.2 | 16216.68
22:30 | 10008.8 | 6134.96 | 16143.76
23:00 | 9993.12 | 6077.72 | 16070.84

## En-Curve
QF-LDC-12
Date | 07-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3138 | 1725 | 778 | 0 | 74 | 708 | 220 | 4920.2 | 0 | 427.42 | 2950.5 | 0 | 0 | 0 | 2126 | DAILY ENERGY CURVE
00:30 | 3154.5 | 1757 | 849.5 | 0 | 70 | 661.605 | 219.5 | 4886.1 | 0 | 392.42 | 2521.5 | 0 | 0 | 0 | 2287.5 | 07-10-2026
01:00 | 3171 | 1789 | 921 | 0 | 66 | 615.21 | 219 | 4852 | 0 | 357.42 | 2092.5 | 0 | 0 | 0 | 2449
01:30 | 3169.5 | 1805.5 | 873.5 | 0 | 67 | 621 | 219 | 4835 | 0 | 357.42 | 2051.5 | 0 | 0 | 0 | 2402 | Energy Generated | 354.5859 |  | MKWHr
02:00 | 3168 | 1822 | 826 | 0 | 68 | 626.79 | 219 | 4818 | 0 | 357.42 | 2010.5 | 0 | 0 | 0 | 2355 | Energy not Served | 25.855 |  | MKWHr
02:30 | 3198.5 | 1843.5 | 826 | 0 | 68 | 622.025 | 219 | 4822.1 | 0 | 357.42 | 1958.25 | 0 | 0 | 0 | 2240.5 | Total Energy Requirement | 380.4409 |  | MKWHr
03:00 | 3229 | 1865 | 826 | 0 | 68 | 617.26 | 219 | 4826.2 | 0 | 357.42 | 1906 | 0 | 0 | 0 | 2126
03:30 | 3239.5 | 1883 | 826 | 0 | 67 | 615.96 | 219 | 4828.7 | 0 | 347.42 | 1884.5 | 0 | 0 | 0 | 1753.5
04:00 | 3250 | 1901 | 826 | 0 | 66 | 614.66 | 219 | 4831.2 | 0 | 337.42 | 1863 | 0 | 0 | 0 | 1381
04:30 | 3252 | 1894 | 802 | 0 | 65 | 592.215 | 219 | 4833.2 | 0 | 337.42 | 1832 | 0 | 0 | 0 | 1270.5
05:00 | 3254 | 1887 | 778 | 0 | 64 | 569.77 | 219 | 4835.2 | 0 | 337.42 | 1801 | 0 | 0 | 0 | 1160
05:30 | 3243 | 1850 | 778 | 0 | 63 | 570.12 | 219 | 4830.2 | 0.565 | 322.92 | 1806 | 0 | 0 | 0 | 931.5
06:00 | 3232 | 1813 | 778 | 0 | 62 | 570.47 | 219 | 4825.2 | 1.13 | 308.42 | 1811 | 0 | 0 | 0 | 703
06:30 | 3233 | 1840.5 | 778.5 | 0 | 61 | 574.98 | 219 | 4839.7 | 48.215 | 308.42 | 1798.5 | 0 | 0 | 0 | 707
07:00 | 3234 | 1868 | 779 | 0 | 60 | 579.49 | 219 | 4854.2 | 95.3 | 308.42 | 1786 | 0 | 0 | 0 | 711
07:30 | 3219 | 1819 | 779 | 0 | 63 | 574.82 | 219 | 4859.2 | 160.73 | 300.92 | 1797 | 0 | 0 | 0 | 785
08:00 | 3204 | 1770 | 779 | 0 | 66 | 570.15 | 219 | 4864.2 | 226.16 | 293.42 | 1808 | 0 | 0 | 0 | 859
08:30 | 3145 | 1719.5 | 850 | 0 | 67 | 581.825 | 219 | 4858.6 | 337.465 | 323.92 | 1917 | 0 | 0 | 0 | 531
09:00 | 3086 | 1669 | 921 | 0 | 68 | 593.5 | 219 | 4853 | 448.77 | 354.42 | 2026 | 0 | 0 | 0 | 203
09:30 | 3110.5 | 1677 | 920.5 | 0 | 69 | 604.41 | 219 | 4809.1 | 462.23 | 419.92 | 2062.5 | 0 | 0 | 0 | 129
10:00 | 3135 | 1685 | 920 | 0 | 70 | 615.32 | 219 | 4765.2 | 475.69 | 485.42 | 2099 | 0 | 0 | 0 | 55
10:30 | 3148.5 | 1745.5 | 920.5 | 0 | 72 | 611.345 | 219 | 4836.6 | 567.15 | 485.42 | 2119.5 | 0 | 0 | 0 | 78
11:00 | 3162 | 1806 | 921 | 0 | 74 | 607.37 | 219 | 4908 | 658.61 | 485.42 | 2140 | 0 | 0 | 0 | 101
11:30 | 3129.5 | 1787 | 921 | 0 | 76 | 608.455 | 219 | 4914.5 | 626.16 | 461.92 | 2158 | 0 | 0 | 0 | 720
12:00 | 3097 | 1768 | 921 | 0 | 78 | 609.54 | 219 | 4921 | 593.71 | 438.42 | 2176 | 0 | 0 | 0 | 1339
12:30 | 3083.5 | 1754 | 921 | 0 | 76 | 612.4 | 219 | 4894 | 583.315 | 373.92 | 2175.36 | 0 | 0 | 0 | 1292
13:00 | 3070 | 1740 | 921 | 0 | 74 | 615.26 | 219 | 4867 | 572.92 | 309.42 | 2174.72 | 0 | 0 | 0 | 1245
13:30 | 3052 | 1737 | 921 | 0 | 77 | 613.855 | 219 | 4862 | 539.255 | 238.71 | 2210.36 | 0 | 0 | 0 | 1295
14:00 | 3034 | 1734 | 921 | 0 | 80 | 612.45 | 219 | 4857 | 505.59 | 168 | 2246 | 0 | 0 | 0 | 1345
14:30 | 3045 | 1761.5 | 921 | 0 | 81 | 569.39 | 219.5 | 4889.5 | 456.365 | 176 | 2249 | 0 | 0 | 0.5 | 1493
15:00 | 3056 | 1789 | 921 | 0 | 82 | 526.33 | 220 | 4922 | 407.14 | 184 | 2252 | 0 | 0 | 1 | 1641
15:30 | 3007.5 | 1790 | 921 | 0 | 81 | 518.575 | 220.5 | 4920.5 | 302.95 | 247 | 2341 | 0 | 0 | 1.5 | 1401
16:00 | 2959 | 1791 | 921 | 0 | 80 | 510.82 | 221 | 4919 | 198.76 | 310 | 2430 | 0 | 0 | 2 | 1161
16:30 | 2987.5 | 1755 | 920.5 | 0 | 71 | 511.74 | 221 | 4855 | 124.21 | 350 | 2560 | 0 | 0 | 1.5 | 977
17:00 | 3016 | 1719 | 920 | 0 | 62 | 512.66 | 221 | 4791 | 49.66 | 390 | 2690 | 0 | 0 | 1 | 793
17:30 | 3069 | 1784.5 | 849 | 0 | 71 | 564.635 | 221 | 4835 | 24.83 | 555.21 | 2814.68 | 40 | 0 | 0.5 | 1034.5
18:00 | 3122 | 1850 | 778 | 0 | 80 | 616.61 | 221 | 4879 | 0 | 720.42 | 2939.36 | 80 | 0 | 0 | 1276
18:30 | 3082 | 1809 | 778 | 0 | 79 | 612.93 | 221.5 | 4901.6 | 0 | 794.42 | 3083.61 | 90 | 0 | 0 | 1314
19:00 | 3042 | 1768 | 778 | 0 | 78 | 609.25 | 222 | 4924.2 | 0 | 868.42 | 3227.86 | 100 | 0 | 0 | 1352
19:30 | 3102 | 1821 | 778 | 0 | 80 | 700.8 | 222 | 5095.2 | 0 | 865.42 | 3304.86 | 100 | 0 | 0 | 844
20:00 | 3070 | 1811 | 778 | 0 | 78 | 710.14 | 222 | 5216.2 | 0 | 874.42 | 3311.86 | 100 | 0 | 0 | 679
20:30 | 3125 | 1875 | 778.5 | 0 | 75 | 713.775 | 222 | 5220.7 | 0 | 875.42 | 3326.46 | 132.5 | 0 | 0 | 442
21:00 | 3180 | 1939 | 779 | 0 | 72 | 717.41 | 222 | 5225.2 | 0 | 876.42 | 3341.06 | 165 | 0 | 0 | 205
21:30 | 3151 | 1868 | 778.5 | 0 | 71 | 709.205 | 222 | 5225.2 | 0 | 866.92 | 3342.56 | 132.5 | 0 | 0 | 201.5
22:00 | 3122 | 1797 | 778 | 0 | 70 | 701 | 222 | 5225.2 | 0 | 857.42 | 3344.06 | 100 | 0 | 0 | 198
22:30 | 3150.5 | 1831 | 778 | 0 | 71 | 695.26 | 222 | 5225.2 | 0 | 805.92 | 3264.88 | 100 | 0 | 0 | 295
23:00 | 3179 | 1865 | 778 | 0 | 72 | 689.52 | 222 | 5225.2 | 0 | 754.42 | 3185.7 | 100 | 0 | 0 | 392
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 07-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 29 | 24 | 40 | 122 | 854 | 508 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 53 | 14 | 80 | 120 | 982 | 474
2:00 | 36 | 20 | 40 | 112 | 902 | 466 |  | Import | 0
3:00 | 46 | 25 | 40 | 112 | 922 | 472
4:00 | 46 | 25 | 70 | 130 | 920 | 474 | Ishurdi-Ghorashal Ckt-2 | Export | 1518836.36
5:00 | 44 | 16 | 70 | 132 | 926 | 476
6:00 | 54 | 22 | 110 | 142 | 980 | 512 |  | Import | 0
7:00 | 38 | 14 | 70 | 144 | 876 | 478
8:00 | 63 | 24 | 130 | 156 | 1104 | 536 | Sirajganj-Sreepur Ckt-1 | Export | 702000
9:00 | 119 | 32 | 250 | 150 | 1232 | 608
10:00 | 98 | 15 | 240 | 154 | 1146 | 610 |  | Import | 0
11:00 | 118 | 29 | 280 | 172 | 1272 | 686
12:00 | 117 | 50 | 230 | 160 | 1304 | 700 | Sirajganj-Sreepur Ckt-2 | Export | 705000
13:00 | 110 | 48 | 216 | 170 | 1230 | 662
14:00 | 113 | 46 | 160 | 154 | 1238 | 632 |  | Import | 0
15:00 | 100 | 40 | 154 | 160 | 1214 | 616
16:00 | 86 | 36 | 112 | 144 | 1068 | 576 | Gopalganj-Aminbazar Ckt-1 | Export | 12600000
17:00 | 77 | 30 | 80 | 146 | 1128 | 580
18:00 | 40 | 18 | 32 | 140 | 850 | 480 |  | Import | 0
18:30 | 34 | 10 | 70 | 142 | 878 | 492
19:00 | 32 | 9 | 72 | 146 | 906 | 498 | Gopalganj-Aminbazar Ckt-2 | Export | 12620000
19:30 | 35 | 5 | 80 | 148 | 1002 | 512
20:00 | 28 | 4 | 70 | 136 | 1020 | 446 |  | Import | 0
21:00 | 19 | 11 | 80 | 166 | 916 | 408
22:00 | 18 | 14 | 84 | 168 | 916 | 406 |  | Total Export | 28145836.36
23:00 | 19 | 19 | 74 | 162 | 946 | 440 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 02:00 | 369 | 11:00 | Madunaghat | 401 | 18:00 | 393 | 12:00
Amtali | 413 | 05:00 | 408 | 11:00 | Meghnaghat | 389 | 02:00 | 373 | 11:00
Ashuganj | 399 | 3:00 | 380 | 11:00 | Mirsorai | 399 | 02:00 | 386 | 11:00
Bhulta | 391 | 04:00 | 371 | 11:00 | Payra | 414 | 00:00 | 409 | 21:00
Bibiana | 388 | 04:00 | 379 | 11:00 | Rahanpur | 409 | 16:00 | 400 | 07:00
BIPTC | 402 | 05:00 | 390 | 17:00 | Rampal | 398 | 02:00 | 388 | 11:00
Bogura | 397 | 18:00 | 386 | 07:00
Gopalganj | 393 | 02:00 | 384 | 11:00
Kaliakoir | 374 | 01:00 | 357 | 11:00
Korerhat | 399 | 02:00 | 386 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 06:00 | 218 | 11:00 | Hasnabad | 225 | 03:00 | 213 | 11:00
AKSML | 238 | 00:00 | 229 | 11:00 | Hathazari | 237 | 19:00 | 230 | 11:00
Aminbazar | 231 | 02:00 | 220 | 12:00 | Ishurdi | 236 | 03:00 | 223 | 19:30
Ashuganj | 229 | 05:00 | 219 | 11:00 | Jhenaidah | 226 | 03:00 | 211 | 20:00
Ashuganj-400 | 229 | 5:00 | 219 | 11:00 | Kachua | 229 | 19:00 | 219 | 11:00
Baghabari | 231 | 00:00 | 224 | 19:30 | Kaliakoir | 232 | 02:00 | 219 | 11:00
Barapukuria | 232 | 16:00 | 221 | 07:00 | Keranigonj | 227 | 02:00 | 215 | 11:00
Barapukuria-230 | 232 | 16:00 | 220 | 9:00 | Khulna(S) | 227 | 06:00 | 216 | 21:00
Barapukuria(N) | 235 | 16:00 | 226 | 07:00 | Korerhat | 228 | 02:00 | 219 | 11:00
Barishal | 228 | 13:00 | 222 | 21:00 | Madunaghat | 240 | 19:00 | 234 | 11:00
Bheramara | 233 | 02:00 | 221 | 11:00 | Madunaghat-400 | 241 | 18:00 | 236 | 10:00
Bhulta | 223 | 02:00 | 210 | 11:00 | Maniknagar | 221 | 02:00 | 209 | 11:00
Bibiana | 223 | 04:00 | 216 | 11:00 | Meghnaghat | 230 | 06:00 | 219 | 13:00
BIPTC | 236 | 02:00 | 222 | 19:30 | Meghnaghat-400 | 225 | 02:00 | 214 | 11:00
Birulia | 231 | 02:00 | 218 | 11:00 | Mirsorai | 231 | 01:00 | 224 | 11:00
Bogura | 242 | 16:00 | 232 | 07:00 | Naogaon | 227 | 16:00 | 214 | 19:30
Bogura-400 | 241 | 18:00 | 232 | 07:00 | Purbasadipur | 230 | 16:00 | 218 | 03:00
Borhanuddin | 237 | 11:00 | 226 | 21:00 | Rajshahi | 231 | 05:00 | 220 | 11:00
BSRM | 228 | 19:00 | 220 | 11:00 | Rampal | 226 | 02:00 | 216 | 21:00
Charfasson | 230 | 03:00 | 226 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 01:00 | 224 | 10:00 | Rampura | 222 | 03:00 | 209 | 11:00
Cumilla(N) | 223 | 03:00 | 214 | 11:00 | Shikalbaha | 241 | 18:00 | 235 | 12:00
Faridpur | 223 | 17:00 | 216 | 21:00 | Shyampur | 225 | 02:00 | 213 | 11:00
Fenchuganj | 226 | 07:00 | 219 | 11:00 | Siddhirganj | 222 | 05:00 | 212 | 12:00
Feni | 226 | 02:00 | 218 | 11:00 | Sirajgonj | 237 | 03:00 | 230 | 07:00
Ghorashal | 230 | 01:00 | 220 | 08:00 | Sreepur | 225 | 03:00 | 216 | 11:00
Ghorashal-230 | 222 | 01:00 | 206 | 11:00 | Tongi | 224 | 00:00 | 210 | 09:00
Gopalganj | 224 | 02:00 | 218 | 11:00
GPH | 235 | 19:00 | 228 | 11:00
Haripur | 223 | 03:00 | 210 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 128 | 11:00 | Madanganj | 133 | 01:00 | 126 | 11:00
Agargaon | 139 | 03:00 | 130 | 11:00 | Madaripur | 131 | 17:00 | 126 | 21:00
Agrabad | 137 | 00:00 | 131 | 12:00 | Madartek | 137 | 05:00 | 127 | 11:00
AKS | 135 | 00:00 | 130 | 11:00 | Madunaghat | 139 | 00:00 | 135 | 11:00
Aminbazar | 132 | 02:00 | 125 | 11:00 | Magura | 132 | 03:00 | 122 | 20:00
Amnura | 134 | 18:00 | 129 | 11:00 | Mahasthangarh | 136 | 17:00 | 129 | 07:00
Araihazar | 128 | 03:00 | 119 | 11:00 | Maijdee | 128 | 18:00 | 123 | 11:00
Ashuganj | 136 | 17:00 | 129 | 11:00 | Manikganj | 134 | 18:30 | 125 | 11:00
Ashuganj-230 | 136 | 02:00 | 133 | 11:00 | Maniknagar | 138 | 05:00 | 128 | 12:00
Bagerhat | 128 | 04:00 | 118 | 21:00 | Matarbari | 130 | 07:00 | 114 | 21:00
Bajitpur | 129 | 16:00 | 123 | 19:30 | Matuail | 132.5 | 04:00 | 125 | 12:00
Bakerganj | 135 | 17:00 | 129 | 23:00 | Metrorail_Motijheel | 138 | 05:00 | 128 | 12:00
Bakulia | 137 | 01:00 | 133 | 11:00 | Metrorail_Uttara | 143 | 06:00 | 122 | 11:00
Banani | 137 | 04:00 | 127 | 11:00 | Millgate | 137 | 01:00 | 123 | 11:00
Bangabhaban | 138 | 03:00 | 127 | 12:00 | Mirpur | 131 | 02:00 | 122 | 11:00
Barapukuria | 137 | 16:00 | 127 | 07:00 | Mirzapur | 132 | 16:00 | 125 | 11:00
Barguna | 134 | 17:00 | 130 | 21:00 | Mithapukur | 134 | 16:00 | 127 | 07:00
Barishal | 133 | 17:00 | 128 | 21:00 | MI_Cement | 133 | 03:00 | 122 | 11:00
Barishal-230 | 132 | 01:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 00:00 | 133 | 12:00 | Mogbazar | 138 | 03:00 | 127 | 12:00
Baroirhat | 132 | 01:00 | 127 | 11:00 | Mongla | 125 | 04:00 | 119 | 11:00
Bashundhara | 138 | 05:00 | 122 | 11:00 | Monirampur | 125 | 01:00 | 112 | 21:00
BashundharaCement | 133 | 01:00 | 126 | 11:00 | Motijheel | 138 | 03:00 | 127 | 12:00
Beanibazar | 124 | 03:00 | 118 | 23:00 | Muktagacha | 130 | 16:00 | 121 | 03:00
Benapole | 130 | 06:00 | 114 | 21:00 | Munshiganj | 132 | 02:00 | 125 | 11:00
Bhaluka | 135 | 14:00 | 126 | 07:00 | Muradnagar | 127 | 01:00 | 120 | 11:00
Bhandaria | 130 | 06:00 | 123 | 21:00 | Mymensingh | 131 | 12:00 | 119 | 08:00
Bhangura | 133 | 12:00 | 128 | 00:00 | Nabinagar | 131 | 01:00 | 121 | 11:00
Bheramara | 137 | 03:00 | 129 | 19:30 | Naogaon | 137 | 18:00 | 129 | 19:30
Bheramara(GK) | 137 | 04:00 | 129 | 19:30 | Narail | 131 | 04:00 | 121 | 20:00
Bhulta | 126 | 07:00 | 120 | 11:00 | Narinda | 138 | 5:00 | 128 | 12:00
Bhulta-400 | 128 | 02:00 | 121 | 11:00 | Narshingdi | 132 | 18:00 | 117 | 12:00
Birulia | 136 | 02:00 | 127 | 11:00 | Natore | 134 | 14:00 | 127 | 19:30
Bog-Sherpur | 137 | 16:00 | 131 | 07:00 | Nawabganj | 137 | 02:00 | 129 | 11:00
Bogura | 139 | 17:00 | 133 | 07:00 | Netrakona | 122 | 00:00 | 109 | 14:00
Bogura-230 | 140 | 16:00 | 133 | 07:00 | New | 137 | 00:00 | 124 | 11:00
Brahmanbaria | 134 | 17:00 | 126 | 11:00 | Niamatpur | 135 | 17:00 | 131 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 139 | 03:00 | 129 | 11:00 | Noapara | 129 | 06:00 | 120 | 21:00
Chandina | 129 | 01:00 | 123 | 11:00 | Pabna | 135 | 16:00 | 127 | 19:30
Chandpur | 135 | 19:00 | 128 | 10:00 | Palashbari | 132 | 15:00 | 126 | 07:00
Chandraghona | 139 | 18:30 | 135 | 11:00 | Panchagarh | 140 | 03:00 | 133 | 07:00
Chapai | 132 | 18:30 | 131 | 00:00 | Patiya | 137 | 18:00 | 132 | 11:00
Charsaidpur | 132 | 01:00 | 125 | 11:00 | Patnitala | 134 | 17:00 | 126 | 22:00
Chauddagram | 129 | 01:00 | 124 | 11:00 | Patuakhali | 136 | 19:00 | 130 | 23:00
Chhatak | 122 | 01:00 | 113 | 21:00 | Payra | 136 | 01:00 | 134 | 22:00
Chowmuhani | 128 | 01:00 | 126 | 04:00 | PHP | 132 | 01:00 | 126 | 11:00
Chuadanga | 133 | 04:00 | 119 | 21:00 | Postogola | 133 | 00:00 | 124 | 11:00
Coxsbazar | 124 | 01:00 | 116 | 05:00 | Pubail | 133 | 18:00 | 122 | 09:00
Cumilla(N) | 129 | 03:00 | 122 | 11:00 | Purbachal | 137 | 04:00 | 127 | 11:00
Cumilla(S) | 133 | 05:00 | 124 | 11:00 | Purbasadipur | 138 | 03:00 | 131 | 07:00
Daganbhuiyan | 130 | 01:00 | 125 | 11:00 | Rahanpur | 138 | 16:00 | 134 | 01:00
Daudkandi | 126 | 03:00 | 118 | 11:00 | Rahanpur-400 | 137 | 16:00 | 134 | 07:00
DhakaUniversity | 137 | 02:00 | 128 | 11:00 | Rahim | 133 | 06:00 | 126 | 12:00
Dhamrai | 132 | 00:00 | 124 | 11:00 | Rajbari | 126 | 01:00 | 121 | 21:00
Dhanmondi | 138 | 05:00 | 128 | 11:00 | Rajendrapur | 139 | 02:00 | 128 | 11:00
Dohazari | 132 | 00:00 | 128 | 12:00 | Rajshahi | 132 | 06:00 | 126 | 11:00
Faridpur | 129 | 04:00 | 125 | 11:00 | Rajshahi-230 | 134 | 16:00 | 127 | 19:30
Fatullah | 133 | 02:00 | 124 | 11:00 | Ramganj | 130 | 19:00 | 124 | 09:00
Fenchuganj | 131 | 01:00 | 127 | 21:00 | Rampur | 137 | 00:00 | 132 | 11:00
Feni | 130 | 01:00 | 128 | 11:00 | Rampura | 137 | 03:00 | 128 | 11:00
Feni-230 | 131 | 01:00 | 126 | 11:00 | Rangamati | 137 | 00:00 | 134 | 11:00
Ghatail | 129 | 13:00 | 121 | 06:00 | Rangpur | 133 | 18:00 | 126 | 08:00
Ghorashal | 133 | 00:00 | 125 | 09:00 | Ruppur | 137 | 14:00 | 131 | 19:30
Goalpara | 131 | 02:00 | 122 | 21:00 | Saidpur | 136 | 06:00 | 130 | 07:00
Gollamari | 130 | 02:00 | 123 | 21:00 | Santhia | 135 | 04:00 | 129 | 11:00
Gopalganj | 131 | 17:00 | 124 | 11:00 | Satkhira | 126 | 15:00 | 113 | 21:00
Gopalganj-400 | 132 | 01:00 | 128 | 11:00 | Satmasjid | 138 | 01:00 | 129 | 12:00
Gulshan | 136 | 05:00 | 128 | 11:00 | Savar | 132 | 18:00 | 123 | 11:00
Halishahar | 138 | 00:00 | 133 | 11:00 | SevenRings | 134 | 18:00 | 125 | 13:00
Haripur | 133 | 02:00 | 126 | 11:00 | ShahCement | 132 | 01:00 | 125 | 11:00
HaripurSBU | 133 | 02:00 | 126 | 11:00 | Shahjadpur | 134 | 04:00 | 129 | 23:00
Hasnabad | 137 | 05:00 | 125 | 13:00 | Shahjibazar | 131 | 17:00 | 125 | 11:00
Hathazari | 138 | 19:00 | 135 | 11:00 | Shahmirpur | 139 | 18:00 | 134 | 11:00
Hatirjheel | 137 | 02:00 | 128 | 11:00 | Shariatpur | 129 | 01:00 | 123 | 21:00
Ishurdi | 137 | 00:00 | 130 | 19:30 | Sherpur | 133 | 12:00 | 117 | 01:00
Jaldhaka | 139 | 19:00 | 127 | 21:00 | Shikalbaha | 128 | 00:00 | 123 | 11:00
Jamalpur | 132 | 12:00 | 121 | 02:00 | Shikalbaha-230 | 140 | 18:00 | 135 | 12:00
Jashore | 132 | 02:00 | 116 | 21:00 | Shitalakhya | 133 | 03:00 | 122 | 11:00
Jhenaidah | 135 | 04:00 | 126 | 19:30 | Sholosohor | 138 | 00:00 | 133 | 11:00
Jhenaidah-230 | 137 | 02:00 | 125 | 21:00 | Shomvuganj | 124 | 16:00 | 118 | 08:00
Joydebpur | 131 | 18:00 | 120 | 09:00 | Shyampur | 133 | 02:00 | 126 | 12:00
Joypurhat | 134 | 17:00 | 129 | 07:00 | Shyampur-230 | 135 | 02:00 | 127 | 12:00
Juldah | 138 | 00:00 | 133 | 12:00 | Siddhirganj | 133 | 01:00 | 126 | 11:00
Kabirpur | 138 | 18:30 | 118 | 11:00 | Sirajganj | 133 | 14:00 | 126 | 19:30
Kachua | 131 | 18:00 | 125 | 10:00 | Sitakunda | 137 | 00:00 | 133 | 11:00
Kaliakoir | 138 | 18:00 | 130 | 11:00 | Sonargaon | 129 | 02:00 | 123 | 11:00
Kaliganj | 135 | 04:00 | 125 | 19:30 | Sreemongol | 129 | 03:00 | 124 | 11:00
Kallyanpur | 131 | 01:00 | 124 | 13:00 | Sreepur | 137 | 03:00 | 130 | 10:00
Kalurghat | 139 | 00:00 | 135 | 11:00 | Srinagar | 137 | 01:00 | 129 | 11:00
Kamrangirchar | 138 | 02:00 | 120 | 11:00 | SSM | 142 | 00:00 | 138 | 11:00
Kaptai | 140 | 1:00 | 138 | 10:00 | Sunamganj | 118 | 01:00 | 111 | 11:00
Kasba | 127 | 02:00 | 119 | 11:00 | Sylhet | 125 | 04:00 | 119 | 21:00
Kazla | 138 | 05:00 | 128 | 11:00 | Sylhet_(South) | 126 | 05:00 | 119 | 21:00
Keranigonj | 138 | 02:00 | 129 | 11:00 | Tangail | 129 | 16:00 | 122 | 11:00
Khagrachori | 137 | 19:00 | 132 | 19:30 | Taraganj | 134 | 17:00 | 128 | 07:00
Khulna | 128 | 04:00 | 121 | 21:00 | Tasnim | 131 | 02:00 | 123 | 11:00
Khulna(S) | 130 | 01:00 | 123 | 21:00 | Thakurgaon | 141 | 03:00 | 134 | 07:00
Khulshi | 136 | 00:00 | 131 | 12:00 | TK | 136 | 01:00 | 135 | 00:00
Kishoreganj | 128 | 16:00 | 122 | 08:00 | Tongi | 138 | 00:00 | 128 | 11:00
Kodda | 137 | 18:30 | 122 | 16:00 | Ullahpara | 134 | 14:00 | 128 | 11:00
Korerhat | 135 | 02:00 | 129 | 11:00 | Ullon | 138 | 03:00 | 128 | 11:00
KSRM | 139 | 00:00 | 133 | 11:00 | Uttara | 135 | 02:00 | 121 | 11:00
Kulaura | 130 | 01:00 | 126 | 11:00 | UttaraNew | 135 | 02:00 | 122 | 11:00
Kurigram | 129 | 18:00 | 120 | 07:00 | Zigatola | 138 | 04:00 | 129 | 11:00
Kushtia | 135 | 00:00 | 127 | 11:00
Laksam | 130 | 19:00 | 125 | 11:00
Lakshmipur | 127 | 01:00 | 122 | 11:00
Lalbag | 136 | 01:00 | 128 | 11:00
Lalmonirhat | 129 | 08:00 | 125 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division