## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-10-2026 | during | 09-10-2026 | during | 09-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 349 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 319 | 293 | 335 | 335 | 319 | 319 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 0 | 0 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 0 | 149.36 | 149.36 | 30 | 143
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 11 | 10.5 | 24.75 | 24.75 | 11 | 11 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 24 | 52.19 | 52.19 | 50 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 229 | 60 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 88 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 34 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 126 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 45 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 460 | 420 | 584 | 584 | 526 | 526 | AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 300 | 540 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2360.42 | 2279.92 | 5574.91 | 5544.91 | 2762.12 | 3042.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 89 | 49 | 105 | 105 | 95 | 95
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 28 | 34 | 24 | 54 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 12 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 37 | 49 | 95.1 | 95.1 | 34 | 52 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.73 | 0 | 4.23 | 0 | 4.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 158 | 100 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 98 | 29 | 110 | 110 | 99 | 99
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 95 | 0 | 116 | 116 | 92 | 92
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 16 | 163 | 163 | 18 | 18 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1204 | 1204
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 2 | 1 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1000 | 1060 | 1150 | 1150 | 1130 | 1130 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3349.73 | 3211.36 | 4119.19 | 4178.96 | 3499.23 | 3831.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 197 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 347 | 315 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 290 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 27 | 33 | 41.65 | 41.65 | 33 | 33
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 45 | 47 | 52.82 | 52.82 | 52.82 | 52.82 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 170 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 127 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 23 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 65 | 71 | 163 | 163 | 84 | 84 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 101 | 34 | 200 | 200 | 80 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 62 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 16 | 52.2 | 52.2 | 8 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 5 | 24.5 | 24.5 | 8 | 8 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 72 | 0 | 114 | 114 | 103 | 103
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 70 | 70 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 101 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 67 | 0 | 67 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1704 | 1605 | 2360.44 | 2287.44 | 1881.82 | 1912.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-10-2026 | during | 09-10-2026 | during | 09-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 19.46 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.9 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 110 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 65 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.5 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 244.86 | 187 | 663.6 | 591.5 | 263.1 | 277
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 138 | 138 | 140 | 140 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 83 | 83 | 53 | 53 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 0 | 16 | 16 | 8 | 8
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 267 | 341 | 341 | 290 | 290 | machine problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 150 | 150 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 397 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1367 | 1370 | 1326 | 1326 | 1199 | 1199
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 730 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 32 | 32 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 2 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1230 | 1212 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2223 | 1982 | 3564.2 | 3486.2 | 2921.2 | 2875.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 103 | 16 | 110 | 110 | 99 | 99
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 112 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 54 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2196.59 | 2112 | 2308 | 2307 | 2176 | 2175
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.1 | 0 | 53.42 | 0 | 53.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 42 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 334 | 278 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 26 | 26 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 42 | 35 | 113 | 113 | 50 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 35 | 113 | 113 | 55 | 113
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.99 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 664.88 | 601.75 | 550 | 650 | 550 | 650 | Unit-1 under maint
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.9 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 41 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1265.87 | 1145.75 | 2350.11 | 2225.99 | 1398.91 | 1495.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.7 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 80 | 35 | 115 | 115 | 104 | 104
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 58 | 0 | 177.63 | 0 | 177.63 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 145.7 | 105 | 460.63 | 248 | 370.63 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 14857.17 | 13998.03 | 22727.08 | 22196 | 16472.01 | 17044.99
Forecast Scenario (09-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14817.25 |  | 50 |  | 14867.25
|  |  |  | 1:00 | 13939.75 |  | 30 |  | 13969.75
|  |  |  | 2:00 | 13864.75 |  | 30 |  | 13894.75
|  |  |  | 3:00 | 13845.75 |  | 30 |  | 13875.75
|  |  |  | 4:00 | 13835.75 |  | 0 |  | 13835.75
|  |  |  | 5:00 | 13570 |  | 0 |  | 13570
|  |  |  | 6:00 | 13330 |  | 0 |  | 13330
|  |  |  | 7:00 | 13160 |  | 0 |  | 13160
|  |  |  | 8:00 | 13300 |  | 0 |  | 13300
|  |  |  | 9:00 | 12830 |  | 0 |  | 12830
|  |  |  | 10:00 | 12860 |  | 0 |  | 12860
|  |  |  | 11:00 | 13150 |  | 0 |  | 13150
|  |  |  | 12:00 | 13800 |  | 0 |  | 13800
|  |  |  | 13:00 | 14440 |  | 0 |  | 14440
|  |  |  | 14:00 | 13620 |  | 0 |  | 13620
|  |  |  | 15:00 | 13170 |  | 0 |  | 13170
|  |  |  | 16:00 | 13070 |  | 0 |  | 13070
|  |  |  | 17:00 | 13010 |  | 0 |  | 13010
|  |  |  | 18:00 | 13900 |  | 0 |  | 13900
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15071.59 |  | 0 |  | 15071.59
|  |  |  | 19:30 | 15237.01 |  | 0 |  | 15237.01
|  |  |  | 20:00 | 15397.01 |  | 0 |  | 15397.01
|  |  |  | 21:00 | 15554.61 |  | 0 |  | 15554.61
|  |  |  | 22:00 | 15574.61 |  | 0 |  | 15574.61
|  |  |  | 23:00 | 15373.25 |  | 0 |  | 15373.25
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15555.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15555.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 334.48432 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:54 hrs on 09-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-10-2026 | [28 empty] | Date: | 08-10-2026 | [28 empty] | Date: | 08-10-2026 | [28 empty] | Date: | 08-10-2026 | [28 empty] | Date: | 08-10-2026 | [16 empty] | Date: | 08-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 54 | 118 | 30 | 230 | 55 | 55 | 162 | 0 | 0 | 395 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 11.5 | 22 | 0 | 405 | 109 | 212 | 46 | 0 | 0 | 51 | 56 | 36 | 24 | 25 | 0 | 220 | 92 | 8 | 1060 | 16 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 305 | 285 | 44 | 20 | 202 | 32 | 72 | 71 | 154 | 68 | 12 | 99 | 72 | 43 | 0 | 15 | 275 | 400 | 101 | 40 | 40 | 153 | 0 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 17 | 88 | 0 | 165 | 0 | 0 | 0 | 12 | 9427.42 | 849 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 0 | 0 | 0 | 692.87 | 0 | 32 | 0 | 113 | 35 | 0 | 96 | 35 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1100 | 300 | 54 | 5918.07 | 15345.49 | 106.13
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 54 | 98 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 350 | 0 | 35 | 288 | 0 | 0 | 0 | 143.42 | 11.5 | 22 | 0 | 385 | 107 | 68 | 46 | 0 | 0 | 51 | 30 | 0 | 24 | 25 | 0 | 215 | 96 | 15 | 1060 | 17 | 0 | 47 | 8 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 283 | 240 | 44 | 20 | 190 | 32 | 71 | 71 | 108 | 66 | 12 | 96 | 70 | 43 | 0 | 15 | 270 | 400 | 101 | 40 | 40 | 155 | 0 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8609.92 | 919 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 629.32 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 115 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 117 | 220 | 0 | 1100 | 300 | 54 | 5634.52 | 14244.44 | 106.12
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 54 | 98 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 335 | 0 | 35 | 293 | 0 | 0 | 0 | 143.42 | 11.5 | 22 | 0 | 385 | 107 | 68 | 46 | 0 | 0 | 51 | 30 | 0 | 24 | 25 | 0 | 215 | 109 | 23 | 1060 | 16 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 148 | 0 | 280 | 240 | 44 | 20 | 190 | 32 | 72 | 85 | 102 | 70 | 12 | 90 | 66 | 43 | 0 | 15 | 272 | 400 | 101 | 40 | 40 | 151 | 0 | 8 | 0 | 53 | 0 | 138 | 0 | 100 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8598.92 | 857 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 667.82 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 117 | 220 | 0 | 1100 | 300 | 54 | 5577.02 | 14175.94 | 106.11
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 97 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 340 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 370 | 109 | 68 | 46 | 0 | 0 | 51 | 30 | 0 | 24 | 25 | 0 | 216 | 110 | 28 | 1060 | 17 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 150 | 148 | 0 | 291 | 255 | 44 | 20 | 194 | 32 | 69 | 85 | 103 | 0 | 8 | 99 | 66 | 43 | 0 | 15 | 268 | 400 | 101 | 40 | 40 | 150 | 0 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8477.42 | 777 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 664.59 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1100 | 300 | 72 | 5525.79 | 14003.21 | 106.1
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 54 | 97 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 335 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 375 | 109 | 68 | 46 | 0 | 0 | 51 | 29 | 0 | 24 | 25 | 0 | 216 | 110 | 29 | 1060 | 17 | 0 | 50 | 8 | 105 | 220 | 0 | 0 | 0 | 1145 | 0 | 150 | 147 | 0 | 287 | 245 | 44 | 20 | 194 | 30 | 69 | 85 | 102 | 0 | 8 | 99 | 64 | 43 | 0 | 10 | 270 | 400 | 101 | 40 | 40 | 151 | 0 | 0 | 0 | 53 | 0 | 138 | 0 | 100 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8441.42 | 777 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 669.01 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1100 | 300 | 54 | 5468.21 | 13909.63 | 106.09
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 54 | 97 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 335 | 0 | 35 | 293 | 0 | 0 | 0 | 68 | 12 | 22 | 0 | 375 | 107 | 68 | 46 | 0 | 0 | 51 | 29 | 0 | 24 | 25 | 0 | 217 | 110 | 29 | 1060 | 16 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1160 | 0 | 150 | 71 | 0 | 290 | 250 | 44 | 20 | 194 | 29 | 69 | 85 | 101 | 0 | 8 | 34 | 62 | 43 | 0 | 15 | 278 | 400 | 101 | 40 | 40 | 136 | 0 | 0 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8175 | 777 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 668.19 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1100 | 300 | 54 | 5393.39 | 13568.39 | 106.07
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 54 | 97 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 350 | 0 | 35 | 311 | 0 | 0 | 0 | 68 | 12 | 22 | 0 | 480 | 35 | 68 | 46 | 0 | 0 | 4 | 29 | 0 | 24 | 25 | 0.03 | 218 | 110 | 29 | 930 | 17 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1173 | 0 | 150 | 26 | 0 | 341 | 295 | 44 | 32 | 210 | 29 | 66 | 85 | 102 | 0 | 8 | 34 | 60 | 16 | 1 | 15 | 275 | 400 | 101 | 40 | 40 | 141 | 0 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 0.15 | 67 | 0 | 0 | 0.16 | 12 | 8154.34 | 777 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 580.16 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0.01 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 116 | 220 | 0 | 1100 | 300 | 54 | 5310.51 | 13464.85 | 106.05
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 54 | 97 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 350 | 0 | 17 | 297 | 0 | 0 | 5 | 68 | 12 | 22 | 0 | 420 | 84 | 68 | 46 | 0 | 0 | 0 | 29 | 0 | 24 | 25 | 0.61 | 222 | 102 | 25 | 930 | 17 | 0 | 50 | 8 | 105 | 222 | 0 | 0 | 0 | 1166 | 4 | 150 | 0 | 0 | 334 | 305 | 44 | 44 | 201 | 29 | 51 | 84 | 102 | 0 | 8 | 99 | 58 | 36 | 12 | 15 | 276 | 400 | 101 | 39 | 40 | 142 | 1 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 58 | 2.42 | 67 | 0 | 0.3 | 5.95 | 8 | 8170.28 | 777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 1234.2 | 0 | 0 | 0 | 673.7 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 14 | 0 | 0 | 6.35 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0.55 | 0 | 0 | 115 | 3 | 34 | 0 | 0 | 0 | 0 | 28 | 0.09 | 110 | 307 | 116 | 220 | 0 | 1100 | 300 | 54 | 5527.49 | 13697.77 | 106.03
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 54 | 102 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 345 | 0 | 17 | 298 | 0 | 0 | 7 | 68 | 12 | 22 | 0 | 395 | 107 | 68 | 47 | 0 | 0 | 0 | 29 | 0 | 24 | 25 | 1.49 | 222 | 100 | 18 | 930 | 16 | 0 | 50 | 8 | 105 | 221 | 0 | 0 | 0 | 1164 | 10 | 150 | 0 | 0 | 300 | 255 | 44 | 47 | 200 | 32 | 51 | 84 | 101 | 5 | 8 | 99 | 60 | 43 | 32 | 15 | 279 | 400 | 101 | 39 | 40 | 137 | 5 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 59 | 7.3 | 67 | 0 | 0.7 | 13.11 | 12 | 8130.6 | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 1220 | 0 | 0 | 0 | 667.83 | 0 | 32 | 0 | 35 | 5 | 0 | 0 | 0 | 0 | 19.98 | 35 | 0 | 0 | 18.69 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 1.77 | 0 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 0 | 52 | 0.24 | 110 | 307 | 115 | 220 | 0 | 1100 | 300 | 54 | 5618.51 | 13749.11 | 106.01
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 54 | 115 | 15 | 196 | 55 | 0 | 54 | 0 | 0 | 345 | 0 | 17 | 295 | 0 | 0 | 20 | 105 | 11 | 22 | 0 | 405 | 97 | 152 | 46 | 0 | 0 | 0 | 29 | 36 | 0 | 25 | 2.45 | 222 | 108 | 0 | 930 | 17 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1160 | 15 | 150 | 0 | 0 | 315 | 290 | 44 | 47 | 197 | 32 | 51 | 85 | 101 | 45 | 8 | 17 | 60 | 16 | 51 | 15 | 278 | 400 | 101 | 40 | 40 | 138 | 8 | 8 | 0 | 53 | 0 | 139 | 0 | 100 | 0 | 59 | 10.15 | 98 | 0 | 1.3 | 30.02 | 12 | 8351.92 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 54 | 1110 | 0 | 0 | 0 | 672.68 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 35.19 | 60 | 0 | 0 | 25.01 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 2.86 | 0 | 0 | 70 | 9 | 0 | 0 | 0 | 0 | 0 | 88 | 0.27 | 104 | 307 | 114 | 220 | 0 | 1100 | 300 | 54 | 5710.01 | 14061.93 | 106
10:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 54 | 115 | 15 | 196 | 55 | 35 | 54 | 0 | 0 | 325 | 0 | 17 | 303 | 0 | 0 | 26 | 105 | 11 | 22 | 0 | 430 | 85 | 152 | 45 | 0 | 0 | 0 | 29 | 36 | 0 | 25 | 2.83 | 222 | 101 | 2 | 930 | 16 | 0 | 50 | 8 | 91 | 219 | 0 | 0 | 0 | 1160 | 18 | 150 | 0 | 0 | 330 | 310 | 44 | 46 | 204 | 31 | 51 | 76 | 102 | 74 | 8 | 17 | 60 | 16 | 64 | 15 | 286 | 400 | 101 | 40 | 39 | 137 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 14.73 | 116 | 0 | 1.6 | 39.32 | 12 | 8537.48 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1195 | 0 | 0 | 0 | 669.9 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 44.41 | 55 | 0 | 0 | 43.24 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 4.11 | 0 | 0 | 34 | 28 | 0 | 0 | 0 | 0 | 0 | 28 | 0.54 | 100 | 307 | 111 | 220 | 0 | 1100 | 300 | 54 | 5732.2 | 14269.68 | 105.99
11:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 115 | 30 | 229 | 55 | 35 | 54 | 0 | 0 | 300 | 0 | 17 | 319 | 0 | 0 | 25 | 143.42 | 11 | 22 | 0 | 460 | 95 | 158 | 37 | 0 | 0 | 0 | 28 | 36 | 24 | 25 | 3.73 | 222 | 98 | 0 | 1000 | 17 | 0 | 50 | 8 | 89 | 216 | 0 | 0 | 0 | 1224 | 19 | 150 | 0 | 0 | 347 | 320 | 44 | 45 | 210 | 27 | 51 | 65 | 101 | 70 | 8 | 72 | 66 | 43 | 70 | 15 | 290 | 397 | 150 | 40 | 39 | 143 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 19.46 | 116 | 0 | 0.9 | 37.5 | 12 | 9026.01 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1230 | 5 | 0 | 0 | 664.88 | 0 | 32 | 0 | 55 | 42 | 0 | 0 | 0 | 0 | 48.1 | 41 | 0 | 0 | 43.9 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 4.99 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0.7 | 58 | 0.59 | 103 | 307 | 112 | 220 | 0 | 1100 | 300 | 54 | 5831.16 | 14857.17 | 105.98
12:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 115 | 47 | 246 | 55 | 35 | 72 | 0 | 0 | 295 | 0 | 17 | 320 | 0 | 0 | 28 | 143.42 | 11 | 0 | 0 | 475 | 89 | 158 | 43 | 0 | 0 | 0 | 22 | 36 | 24 | 25 | 2.87 | 220 | 94 | 0 | 1060 | 17 | 0 | 50 | 8 | 91 | 215 | 0 | 0 | 0 | 1161 | 7 | 150 | 0 | 0 | 340 | 315 | 44 | 47 | 209 | 31 | 51 | 65 | 101 | 70 | 8 | 88 | 70 | 34 | 70 | 14 | 280 | 392 | 150 | 40 | 38 | 139 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 20 | 116 | 0 | 1.9 | 49.16 | 12 | 9042.35 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1230 | 17 | 0 | 0 | 670.31 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 19.68 | 9 | 0 | 0 | 29.04 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 5.88 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0.9 | 39 | 0.57 | 80 | 276 | 112 | 220 | 0 | 1063 | 300 | 54 | 5543.38 | 14585.73 | 105.98
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 115 | 62 | 262 | 55 | 35 | 90 | 0 | 0 | 305 | 0 | 17 | 327 | 0 | 0 | 11 | 143.42 | 11 | 22 | 0 | 380 | 94 | 158 | 42 | 0 | 0 | 0 | 22 | 36 | 24 | 25 | 3.42 | 219 | 92 | 0 | 1060 | 16 | 0 | 50 | 8 | 102 | 215 | 0 | 0 | 0 | 1160 | 18 | 150 | 0 | 0 | 305 | 280 | 44 | 47 | 188 | 34 | 50 | 65 | 101 | 68 | 8 | 88 | 68 | 43 | 64 | 14 | 283 | 398 | 150 | 40 | 38 | 144 | 10 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 8.06 | 116 | 0 | 0.9 | 45.72 | 12 | 8833.52 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1190 | 17 | 0 | 0 | 661.85 | 0 | 34 | 0 | 55 | 50 | 0 | 0 | 8 | 0 | 7.34 | 20 | 0 | 0 | 21.65 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 1.73 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1 | 0.56 | 64 | 271 | 113 | 220 | 0 | 1068 | 300 | 54 | 5447.93 | 14281.45 | 105.97
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 18 | 115 | 15 | 145 | 55 | 35 | 90 | 0 | 0 | 300 | 0 | 17 | 325 | 0 | 0 | 0 | 86 | 11 | 22 | 0 | 415 | 30 | 158 | 23 | 0 | 2 | 0 | 20 | 36 | 12 | 25 | 2.9 | 219 | 92 | 0 | 1060 | 17 | 0 | 38 | 8 | 96 | 213 | 0 | 0 | 0 | 1160 | 16 | 150 | 0 | 0 | 330 | 310 | 44 | 47 | 200 | 34 | 51 | 66 | 51 | 68 | 8 | 17 | 74 | 16 | 52 | 14 | 277 | 395 | 150 | 40 | 38 | 148 | 1 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 59 | 2.33 | 115 | 0 | 0 | 0.73 | 12 | 8381.96 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1160 | 17 | 0 | 0 | 582.85 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3.93 | 83 | 0 | 0 | 4.28 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 65 | 0.48 | 32 | 271 | 112 | 220 | 0 | 1005 | 300 | 54 | 5154.34 | 13536.3 | 105.97
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 43 | 95 | 15 | 145 | 55 | 35 | 90 | 0 | 0 | 410 | 0 | 35 | 325 | 0 | 0 | 0 | 51 | 10.5 | 22 | 0 | 420 | 17 | 50 | 15 | 0 | 5 | 0 | 20 | 36 | 24 | 25 | 1.98 | 220 | 51 | 0 | 1060 | 17 | 0 | 41 | 0 | 34 | 213 | 0 | 0 | 0 | 1187 | 12 | 150 | 0 | 0 | 318 | 290 | 44 | 46 | 198 | 34 | 51 | 66 | 49 | 68 | 8 | 17 | 70 | 8 | 41 | 14 | 276 | 400 | 150 | 40 | 38 | 154 | 7 | 8 | 0 | 52 | 0 | 139 | 0 | 100 | 0 | 8 | 0.38 | 16 | 0 | 0 | 0.22 | 2 | 8080.08 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1200 | 17 | 0 | 0 | 581.33 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3.16 | 59 | 0 | 0 | 9.96 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0.72 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5.2 | 103 | 0.06 | 32 | 307 | 113 | 220 | 0 | 1064 | 300 | 54 | 5322.43 | 13402.51 | 105.96
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 20 | 0 | 45 | 40 | 0 | 17 | 0 | 0 | 455 | 0 | 0 | 280 | 0 | 0 | 0 | 34 | 10.5 | 22 | 0 | 400 | 0 | 15 | 18 | 0 | 2 | 0 | 47 | 17 | 24 | 25 | 1 | 221 | 34 | 0 | 980 | 0 | 0 | 31 | 5 | 17 | 213 | 0 | 0 | 0 | 958 | 7 | 100 | 8 | 0 | 299 | 270 | 44 | 42 | 183 | 34 | 16 | 65 | 17 | 34 | 8 | 0 | 70 | 8 | 5 | 18 | 275 | 400 | 150 | 40 | 38 | 150 | 1 | 8 | 0 | 52 | 0 | 140 | 0 | 100 | 0 | 8 | 0.3 | 8 | 0 | 0.3 | 0.75 | 12 | 6955.85 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1160 | 0 | 0 | 0 | 613.56 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18.85 | 9 | 0 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0.64 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.9 | 8 | 0.04 | 0 | 206 | 113 | 220 | 0 | 990 | 300 | 0 | 4905.19 | 11861.04 | 105.96
17:00 | 0 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 21 | 15 | 95 | 41 | 35 | 90 | 0 | 0 | 400 | 0 | 12 | 281 | 0 | 0 | 2 | 68 | 10.5 | 0 | 0 | 405 | 2 | 50 | 22 | 0 | 1 | 0 | 51 | 19 | 24 | 25 | 0.14 | 222 | 17 | 0 | 1060 | 5 | 0 | 35 | 8 | 17 | 215 | 0 | 0 | 0 | 1040 | 1 | 50 | 36 | 0 | 277 | 275 | 44 | 44 | 186 | 33 | 22 | 65 | 16 | 39 | 8 | 17 | 68 | 8 | 1 | 22 | 275 | 400 | 150 | 40 | 38 | 152 | 0 | 8 | 0 | 52 | 0 | 138 | 0 | 100 | 0 | 16 | 1.5 | 45 | 0 | 0.1 | 0.15 | 12 | 7297.39 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 950 | 0 | 0 | 0 | 561.55 | 0 | 0 | 0 | 20 | 4 | 0 | 17 | 0 | 0 | 1.37 | 0 | 0 | 0 | 2.59 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0.2 | 0 | 0 | 35 | 2 | 15 | 0 | 0 | 0 | 0.1 | 13 | 0.03 | 4 | 283 | 112 | 220 | 0 | 987 | 300 | 5 | 4754.84 | 12052.23 | 105.95
18:00 | 0 | 18 | 24 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 8 | 75 | 15 | 95 | 15 | 55 | 115 | 0 | 0 | 380 | 0 | 55 | 293 | 0 | 0 | 0 | 123 | 10.5 | 22 | 0 | 440 | 13 | 60 | 43 | 0 | 0 | 34 | 54 | 54.36 | 36 | 38 | 0 | 222 | 20 | 0 | 1060 | 16 | 0 | 50 | 0 | 17 | 216 | 0 | 0 | 0 | 1224 | 0 | 61 | 80 | 0 | 329 | 295 | 44 | 47 | 202 | 33 | 52 | 65 | 28 | 69 | 0 | 17 | 52 | 16 | 0 | 23 | 273 | 400 | 150 | 40 | 39 | 142 | 0 | 8 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 56 | 0 | 48 | 0 | 0 | 0 | 12 | 8172.86 | 779 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1041 | 0 | 0 | 0 | 565.82 | 0 | 42 | 0 | 50 | 35 | 0 | 92 | 20 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1100 | 300 | 17 | 5106.82 | 13279.68 | 105.95
19:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 45 | 88 | 0 | 60 | 15 | 55 | 126 | 0 | 0 | 540 | 0 | 55 | 293 | 0 | 0 | 0 | 143.42 | 10.5 | 22 | 0 | 420 | 0 | 100 | 49 | 0 | 0 | 51 | 34 | 54.36 | 12 | 38 | 0 | 222 | 29 | 0 | 1060 | 16 | 0 | 50 | 5 | 49 | 218 | 0 | 0 | 0 | 1224 | 0 | 127 | 170 | 0 | 315 | 290 | 44 | 47 | 197 | 33 | 101 | 71 | 34 | 70 | 5 | 0 | 62 | 16 | 0 | 23 | 267 | 400 | 150 | 40 | 40 | 152 | 0 | 0 | 0 | 83 | 0 | 138 | 0 | 100 | 0 | 65 | 0 | 110 | 0 | 0 | 0 | 12 | 8653.28 | 730 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 2 | 0 | 0 | 601.75 | 0 | 42 | 0 | 35 | 35 | 0 | 95 | 38 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1100 | 300 | 54 | 5344.75 | 13998.03 | 105.94
19:30 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 54 | 70 | 0 | 30 | 15 | 17 | 126 | 0 | 0 | 563 | 0 | 55 | 302 | 0 | 0 | 0 | 105 | 10.5 | 22 | 0 | 530 | 0 | 50 | 51 | 0 | 0 | 51 | 15 | 54.36 | 0 | 38 | 0 | 222 | 17 | 2 | 1060 | 6 | 0 | 50 | 8 | 51 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 175 | 0 | 346 | 320 | 44 | 47 | 207 | 33 | 50 | 73 | 17 | 72 | 5 | 0 | 60 | 8 | 0 | 23 | 260 | 400 | 150 | 40 | 40 | 154 | 0 | 8 | 0 | 83 | 0 | 139 | 0 | 100 | 0 | 45 | 0 | 110 | 0 | 0 | 0 | 12 | 8597.86 | 730 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 0 | 0 | 650.78 | 0 | 42 | 0 | 35 | 0 | 0 | 95 | 38 | 8 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 1100 | 300 | 30 | 5323.98 | 13921.84
20:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 54 | 74 | 0 | 15 | 16 | 17 | 72 | 0 | 0 | 555 | 0 | 55 | 335 | 0 | 0 | 0 | 86 | 10.5 | 22 | 0 | 584 | 0 | 15 | 52 | 0 | 0 | 51 | 0 | 54.36 | 0 | 38 | 0 | 222 | 17 | 0 | 1060 | 0 | 0 | 50 | 8 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 184 | 0 | 354 | 345 | 44 | 47 | 212 | 33 | 16 | 72 | 17 | 71 | 5 | 0 | 68 | 8 | 0 | 0 | 263 | 400 | 150 | 40 | 40 | 155 | 0 | 10 | 0 | 84 | 0 | 141 | 0 | 100 | 0 | 45 | 0 | 95 | 0 | 0 | 0 | 12 | 8535.86 | 731 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 703.24 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 1100 | 300 | 0 | 5084.44 | 13620.3 | 105.94
21:00 | 0 | 8 | 51 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 54 | 53 | 0 | 45 | 44 | 30 | 162 | 0 | 0 | 580 | 0 | 55 | 305 | 0 | 0 | 0 | 105 | 10.5 | 22 | 0 | 550 | 0 | 100 | 54 | 0 | 0 | 51 | 0 | 54.36 | 0 | 38 | 0 | 222 | 17 | 5 | 1060 | 0 | 0 | 50 | 8 | 31 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 170 | 0 | 346 | 320 | 44 | 16 | 199 | 33 | 25 | 72 | 18 | 65 | 5 | 0 | 66 | 8 | 0 | 0 | 260 | 400 | 146 | 40 | 40 | 157 | 0 | 12 | 0 | 84 | 0 | 139 | 0 | 100 | 0 | 75 | 0 | 120 | 0 | 0 | 0 | 12 | 8734.86 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 708.63 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 1100 | 300 | 0 | 5165.83 | 13900.69 | 105.93
22:00 | 0 | 17 | 51 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 54 | 88 | 0 | 45 | 55 | 55 | 162 | 0 | 0 | 545 | 0 | 55 | 298 | 0 | 0 | 0 | 105 | 10.5 | 22 | 0 | 455 | 0 | 100 | 51 | 0 | 0 | 51 | 0 | 54.36 | 0 | 38 | 0 | 222 | 17 | 5 | 1060 | 0 | 0 | 50 | 8 | 51 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 138 | 0 | 330 | 305 | 44 | 10 | 211 | 33 | 50 | 72 | 37 | 73 | 5 | 0 | 68 | 8 | 0 | 0 | 265 | 400 | 146 | 40 | 40 | 158 | 0 | 14 | 0 | 84 | 0 | 138 | 0 | 100 | 0 | 75 | 0 | 120 | 0 | 0 | 0 | 12 | 8659.86 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 703.56 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 1100 | 300 | 0 | 5233.76 | 13893.62 | 105.93
23:00 | 0 | 17 | 51 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 54 | 88 | 0 | 45 | 50 | 55 | 162 | 0 | 0 | 490 | 0 | 55 | 297 | 0 | 0 | 0 | 105 | 10.5 | 22 | 0 | 450 | 0 | 100 | 51 | 0 | 0 | 51 | 0 | 54.36 | 0 | 38 | 0 | 222 | 17 | 5 | 1060 | 0 | 0 | 50 | 8 | 51 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 138 | 0 | 328 | 305 | 44 | 10 | 220 | 33 | 50 | 73 | 47 | 74 | 8 | 0 | 62 | 8 | 0 | 0 | 260 | 400 | 146 | 40 | 40 | 150 | 0 | 16 | 0 | 81 | 0 | 140 | 0 | 100 | 1 | 75 | 0 | 120 | 0 | 0 | 0 | 12 | 8588.86 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 721.88 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 116 | 220 | 0 | 1100 | 300 | 0 | 5250.08 | 13838.94 | 105.92
Total KWH | 0 | 585600 | 484320 | 0 | 0 | 0 | 0 | 0 | 8935200 | 0 | 0 | 0 | 952200 | 2202480 | 347040 | 3604309 | 1180622 | 680240 | 1944000 | 0 | 0 | 9566792 | 0 | 800403 | 7341812 | 0 | 0 | 119087 | 2522400 | 261000 | 464760 | 0 | 10618181.82 | 1403836 | 2205491 | 1019520 | 0 | 9600 | 602558 | 577175 | 660974 | 404160 | 687360 | 21602 | 5306389 | 1766392 | 229440 | 24603636.36 | 349600 | 0 | 1169280 | 195435 | 1878472 | 5026494 | 0 | 0 | 0 | 28276361 | 133110 | 3412363 | 1756364 | 0 | 8044800 | 7112000 | 1032784 | 824160 | 4946000 | 768168 | 1349760 | 1740330 | 1763040 | 1219680 | 176990 | 1071600 | 1530240 | 577843 | 456864 | 318240 | 6559000 | 9558800 | 3168000 | 952000 | 943320 | 3549109.09 | 59066 | 198192 | 0 | 1444800 | 0 | 3133000 | 0 | 2397560 | 57960 | 1322400 | 86605 | 2016000 | 0 | 7850 | 221060 | 282960 | 203196240.27 | 20493091 | 0 | 234720 | 0 | 0 | 0 | 0 | 0 | 0 | 208944 | 420480 | 28778180 | 106080 | 0 | 0 | 15491107 | 0 | 458457 | 0 | 816672 | 376416 | 0 | 305808 | 91684 | 39494 | 217368 | 426769 | 100114 | 0 | 219056 | 0 | 0 | 0 | 0 | 0 | 0 | 7607563 | 0 | 21720 | 0 | 0 | 1231233 | 71020 | 992832 | 0 | 16538 | 0 | 12167.76 | 463680 | 3490 | 1502112 | 7134000 | 2740000 | 5469670 | 0 | 26167273 | 7246545.46 | 922800 | 130387084.22 | 333583324.49

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14857.17 | MW | 11:00 Hr. | Energy Generated |  |  | 333.5833 |  | MKWHr.
| Day Peak Demand |  |  | 14883.3 | MW | 11:00 Hr. | Energy Unserverd |  |  | 6.79 |  | MKWHr.
| Evening Peak Generation |  |  | 13998.03 | MW | 19:00 Hr. | Energy Demand |  |  | 340.3733 |  | MKWHr.
| Evening Peak Demand |  |  | 13998.03 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.4 |  | °C
| Minimum Generation of the Day |  |  | 11861.04 | MW | 16:00 Hr. | Total Gas Supplied |  |  | 847.43 |  | MMCFD
| Maximum Generation of the Day |  |  | 15345.49 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.6474 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.1877 | 0 | 15.3036 | 0 | 0 | 0.11909 | 0 | 0 | 52.6104 | Gas | 116.5663 | Gas | 402920646.8722
| Chattogram Zone |  |  | 5.2559 | 52.88 | 12.9203 | 0 | 5.3064 | 0.15471 | 0 | 0.0096 | 76.5269 | Coal | 122.206 | Coal | 881698251.707
| Cumilla Zone |  |  | 26.4016 | 0 | 9.7125 | 0 | 0 | 0.45686 | 1.5302 | 0 | 38.1012 | HFO | 49.0031 | HFO | 1000349474.14
| Mymensingh Zone |  |  | 0 | 0 | 3.6793 | 0 | 0 | 0.31551 | 0 | 0 | 3.9948 | HSD | 0.016538 | HSD | 510693.44
| Sylhet Zone |  |  | 31.9038 | 0 | 0 | 0 | 0 | 0.059066 | 0 | 0 | 31.9628 | Hydro | 5.3064 | Hydro | 530638.9
| Khulna Zone |  |  | 0 | 28.7782 | 0.54974 | 0 | 0 | 0.42048 | 20.4931 | 0 | 50.2415 | Solar | 2.961 | Solar | 45969055.6532
| Barishal Zone |  |  | 8.2097 | 40.5478 | 2.4249 | 0 | 0 | 0.00349 | 0 | 0 | 51.1859 | Import | 37.5144 | Import | 218932455.84
| Rajshahi Zone |  |  | 7.6076 | 0 | 2.1886 | 0 | 0 | 0.88491 | 15.4911 | 0 | 26.1722 | Wind | 0.0096 | Wind | 142464
| Rangpur Zone |  |  | 0 | 0 | 2.2241 | 0.016538 | 0 | 0.54687 | 0 | 0 | 2.7875
| Total |  |  | 116.5663 | 122.206 | 49.0031 | 0.016538 | 5.3064 | 2.961 | 37.5144 | 0.0096 | 333.5833
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 402920646.8722 |  | Hydro | 530638.9
|  |  |  | Coal | 881698251.707 |  | Solar | 45969055.6532
|  |  |  | HFO | 1000349474.14 |  | Import | 218932455.84
|  |  |  | HSD | 510693.44 |  | Wind | 142464
[5 empty] | Total: | 255,10,53,680 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4931 | Peak Hr Flow | 730.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34326472.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.4911 | Peak Hr Flow | 601.75 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1341 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5302 | Peak Hr Flow | 62.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2037 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.5144 | Peak Hr Flow | 1393.75 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5481
|  |  |  | Chattogram |  | 0 |  | 1677
|  |  |  | Cumilla |  | 0 |  | 1268
|  |  |  | Mymensingh |  | 0 |  | 887
|  |  |  | Sylhet |  | 0 |  | 442
|  |  |  | Khulna |  | 0 |  | 1416
|  |  |  | Barishal |  | 0 |  | 454
|  |  |  | Rajshahi |  | 0 |  | 1231
|  |  |  | Rangpur |  | 0 |  | 728
|  |  |  | Total |  | 0 |  | 13584
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 193.5
|  |  |  | Total Unavailable Capacity |  |  |  | 493.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 17:53 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Annual Maintenance work
| 08:15 | 17:52 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Annual Maintenance work
| 08:40 | 16:52 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to Wall Painting
| 08:41 | 14:42 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Annual Maintenance work 2026
| 08:41 | 14:39 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Annual Maintenance work 2026
| 08:41 | 16:52 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to Wall painting
| 09:01 | 17:18 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph LT Project Work S/D Due to Fire Fighter
(CAF) Work
| 09:02 | 17:16 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph HT Project Work S/D Due to Fire Fighter
(CAF) Work
| 09:40 | 17:34 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance work.
| 11:11 | 16:48 | Mirsorai 400/230/33kV S/S Korerhat-2 Scheduled S/D
| 11:30 | 16:32 | Ishwardi-Pabna 132kV ckt Forced S/D from Pabna 132/33kV end. and from Ishurdi 132/33kV
end Due to Dismantling of scaffholding of Ghorashal-1
| 11:56 | 12:22 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to PBS 33kV Daulatpur
Feeder Fault
| 11:56 | 12:24 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF relays Due to PBS 33kV Daulatpur
Feeder Fault
| 12:00 |  | Day peak generation: 14586 MW
| 12:06 | 15:46 | Lakshmipur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS Maintenance purpose.
| 12:14 | 15:45 | Lakshmipur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS Maintenance purpose.
| 12:14 | 15:45 | Lakshmipur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS Maintenance purpose.
|  | 12:55 | Khulna (C) S/S Tr-3 405T HT is restored.
|  | 12:56 | Khulna (C) S/S Tr-3 405T LT is restored.
| 12:57 | 13:52 | Shahjadpur 132/33kV S/S T-3(425T) LT Tripped showing MCGG relays Due to 33 kV irrigation | [7 empty] | 24.0MW load
|  |  | Feeder fault | [7 empty] | interrup.
| 12:57 | 13:52 | Shahjadpur 132/33kV S/S T-3(425T) HT Tripped showing Siprotec relays Due to 33 kV | [7 empty] | 24.0MW load
|  |  | Irrigation Feeeder fault. | [7 empty] | interrup.
| 14:39 | 15:04 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Manikganj 132/33kV end showing General
Trip relays. and from Kabirpur 132/33kV end showing Distance Relay relays Due to Bad
weather
| 15:09 | 16:34 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance Relay
relays Due to Bad weather and from Tongi 230/132/33kV end showing Distance Relay relays.
| 15:10 | 15:32 | Savar 132/33kV S/S T-3 LT Tripped showing Over current relay relays Due to Dpbs-3 L-46
feeder fault
| 15:10 | 15:32 | Savar 132/33kV S/S T-4 LT Tripped showing Over current relay relays Due to Dpbs-3 L-46
feeder fault
|  | 15:40 | Chowmuhani 230/132/33kV S/S TR1 is restored.
|  | 15:41 | Rajbari 132/33kV S/S 132 kV Bus-II is restored.
|  | 15:41 | Rajbari 132/33kV S/S 132 kV Bus-II is restored.
|  | 16:08 | BIPTC S/S 20DF24 is restored.
| 16:46 | 22:50 | Bogura 230/132kV S/S T-03 LT Forced S/D Due to oil filling
| 16:46 | 22:50 | Bogura 230/132kV S/S T-03 HT Forced S/D Due to oil filling
| 17:54 | 17:59 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Tripped showing O/C & E/F relay. relays Due | [7 empty] | 9.0MW load
|  |  | to 33kV kalaroa feeder trip. | [7 empty] | interrup.
| 19:00 |  | Evening peak generation is 13999 MW.
|  | 19:02 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 is restored.
| 20:02 | 20:24 | Khulna(C )-Noapara 132kV Ckt-2 Tripped from Khulna (C) end showing Distance, zone-1,
12.9km, L-1 phase faulty-4.47kA relays Due to Heavy thundering
| 21:47 | 03:52 | Haripur-Madanganj 132kV Ckt-1 Forced S/D from Madanganj 132/33kV end Due to Redhot
maintenance and from Haripur 230/132kV end Due to Hight temperature maintenace.
| 21:49 | 03:56 | Madanganj 132/33kV S/S BUS Coupler Forced S/D Due to Redhot maintenance at 132kv Haripur
ckt-1
| 23:27 | 00:25 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to 33kV Red hot Maintanence of | [7 empty] | 60.0MW load
|  |  | Mouchak feeder | [7 empty] | interrup.
| 23:27 | 00:23 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D | [7 empty] | 60.0MW load
interrup.
| 00:50 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- GT
| 06:00 |  | Minimum Generation: 11286 MW.
| 06:20 |  | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end. and from
Kaliakoir 400/230/132kV end Due to NLDC
| 06:37 |  | Pabna 132/33kV S/S T-1 HT Tripped showing 51×3 51G INST Trip relays Due to T-1 এর | [7 empty] | 25.0MW load
|  |  | R-Phase এ Over Current এ Trip করে।কিন্তু ৩৩কেভি ব্রেকার ট্রিপ করে নাই। ১৩২ কেভি ব্রেকার | [7 empty] | interrup.
ট্রিপ করে।
| 06:53 |  | Ashuganj 230/132/33kV S/S TR-OAT-12 LT Scheduled S/D Due to Bus DS Allienment problem
| 06:56 |  | Ashuganj 230/132/33kV S/S TR-OAT-12 HT Scheduled S/D
| 07:03 |  | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to 33KV BUS DS Red hot under t-1 | [7 empty] | 65.0MW load
interrup.
| 07:04 |  | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to 33KV BUS DS Red hot under t-1 | [7 empty] | 65.0MW load
interrup.
| 07:10 |  | Madaripur 132/33kV S/S T-4 HT Scheduled S/D Due to High Temperature Maintenance
| 07:12 |  | Ashuganj 230/132/33kV S/S 132kv Busbar-1 Scheduled S/D Due to Tempareture issue
| 07:14 |  | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Protection
purpose work done by SPMD.
| 07:42 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Hot Spot maintenance
work on 132KV & 33KV CT Clamp.
| 07:43 |  | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to Hot Spot maintenance
work on 132KV & 33KV CT Clamp.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8935200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 1180622 | Fuel Shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 7341812 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | Machine Problem
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 347040 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 680240 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 800403 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10.5 | 261000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 464760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 484320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 3604309 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 2202480 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 585600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1944000 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 119087 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 45 | 952200 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 420 | 10618181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 540 | 9566792 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2522400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2279.92 | 52610446.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 5 | 195435 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133110 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1169280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5306389 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5026494 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 49 | 1878472 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 577175 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 602558 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 404160 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 229440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 49 | 1019520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 2205491 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 660974 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 29 | 1766392 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 687360 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 1403836 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 349600 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28276361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 9600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1060 | 24603636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3211.36 | 76526885.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 197 | 4946000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 315 | 8044800 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 7112000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 768168 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 47 | 824160 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 170 | 1756364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1032784 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 3412363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 318240 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 71 | 1740330 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 1763040 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1530240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 577843 | plant availability zero
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 5 | 176990 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 1071600 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 1219680 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1349760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456864 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1605 | 38101226
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 86605 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 110 | 2016000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 1322400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 221060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 282960 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 57960 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 187 | 3994835
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 59066 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 952000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 943320 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3549109.09 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 138 | 3133000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1444800 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2397560 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 198192 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 267 | 6559000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 150 | 3168000 | Gas Restrction
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9558800 | plant availability zero
Sylhet Area Total |  |  |  |  | 2325 | 1370 | 31962847.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 730 | 20493091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 234720 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 2 | 106080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 208944 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 420480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1212 | 28778180 | Average Gen
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1982 | 50241495
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 26167273 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 1502112 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2740000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7246545.46 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5469670 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 922800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7134000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3490 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2112 | 51185890.46
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 217368 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 42 | 458457 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 91684 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 278 | 7607563 | ramp limitation
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 100114 | Fuel Shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 39494 | Fuel Shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 305808 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 376416 | High Voltage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 816672 | High Voltage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 21720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 601.75 | 15491107 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 219056 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 426769 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1145.75 | 26172228
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 16538 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 992832 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 12167.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 1231233 | Bad Weather
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 71020 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 463680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 105 | 2787470.76
Eastern Grid Total |  |  |  |  | 16961.086 | 8653.28 | 203196240.27
Western Grid Total |  |  |  |  | 11731.125 | 5344.75 | 130387084.22
National Grid Total |  |  |  |  | 28692.211 | 13998.03 | 333583324.49
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9755.83 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3828.7 | MW
i) Dhaka area |  |  | 5481.02 |  | MW | i) Khulna area |  |  |  | 1416 | MW
ii) Chattogram area |  |  | 1677.4 |  | MW | ii) Barishal area |  |  |  | 453.5 | MW
iii) Cumilla area |  |  | 1268.41 |  | MW | iii) Rajshahi area |  |  |  | 1231.2 | MW
iv) Mymensingh area |  |  | 887 |  | MW | iv) Rangpur area |  |  |  | 728 | MW
v) Sylhet area |  |  | 442 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13584.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 25 | 16:00 | 72 | Hatirjheel | 82 | 12:00 | 143 | PHP | 12 | 18:00
2 | AKSML | 153.3 | 07:00 | 73 | Ishurdi | 71 | 11:00 | 144 | Pabna | 89 | 07:00
3 | Aftabnagar | 46 | 13:00 | 74 | Jaldhaka | 68 | 00:00 | 145 | Palashbari | 122 | 00:00
4 | Agargaon | 141 | 13:00 | 75 | Jamalpur | 123 | 00:00 | 146 | Panchagarh | 56 | 00:00
5 | Agrabad | 80 | 12:00 | 76 | Jashore | 123 | 12:00 | 147 | Patiya | 31 | 18:00
6 | Amnura | 27 | 00:00 | 77 | Jhenaidah | 89 | 01:00 | 148 | Patnitala | 29 | 02:00
7 | Araihazar | 102 | 11:00 | 78 | Joydebpur | 178 | 12:00 | 149 | Patuakhali | 68 | 03:00
8 | Ashuganj | 0.46 | 00:00 | 79 | Joypurhat | 50 | 03:00 | 150 | Payra | 32 | 21:00
9 | Ashuganj-230 | 98 | 01:00 | 80 | Juldah | 18 | 18:00 | 151 | Postogola | 63 | 00:00
10 | BSRM | 202 | 19:00 | 81 | KSRM | 25 | 12:00 | 152 | Pubail | 44 | 11:00
11 | Bagerhat | 87 | 04:00 | 82 | Kabirpur | 281 | 11:00 | 153 | Purbachal | 29 | 00:00
12 | Bajitpur | 86 | 00:00 | 83 | Kachua | 92 | 19:30 | 154 | Purbasadipur | 123 | 00:00
13 | Bakerganj | 13 | 21:00 | 84 | Kaliganj | 39 | 00:00 | 155 | Rahanpur | 38 | 04:00
14 | Bakulia | 105 | 18:30 | 85 | Kallyanpur | 111 | 00:00 | 156 | Rahim | 56 | 12:00
15 | Banani | 68 | 11:00 | 86 | Kalurghat | 42 | 15:00 | 157 | Rajbari | 83 | 00:00
16 | Bangabhaban | 20 | 11:00 | 87 | Kamrangirchar | 101 | 13:00 | 158 | Rajendrapur | 138 | 12:00
17 | Barapukuria | 53 | 00:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 105 | 01:00
18 | Barguna | 20 | 18:00 | 89 | Kasba | 36 | 22:00 | 160 | Rajshahi-230 | 101 | 12:00
19 | Barishal | 105 | 12:00 | 90 | Kazla | 131 | 13:00 | 161 | Ramganj | 112 | 22:00
20 | Barishal-230 | 98 | 18:00 | 91 | Keranigonj | 91 | 19:30 | 162 | Rampur | 47 | 23:00
21 | Baroaulia | 42 | 13:00 | 92 | Khagrachori | 36 | 18:00 | 163 | Rangamati | 16 | 18:00
22 | Baroirhat | 70 | 18:00 | 93 | Khulna | 66 | 00:00 | 164 | Rangpur | 116 | 19:00
23 | Bashundhara | 204 | 12:00 | 94 | Khulshi | 193 | 15:00 | 165 | Ruppur | 4.4 | 11:00
24 | BashundharaCement | 1 | 15:00 | 95 | Kishoreganj | 114 | 00:00 | 166 | SSM | 1 | 04:00
25 | Beanibazar | 82 | 18:00 | 96 | Kodda | 311 | 11:00 | 167 | Saidpur | 94 | 08:00
26 | Benapole | 66 | 00:00 | 97 | Kulaura | 55 | 18:00 | 168 | Santhia | 30 | 18:00
27 | Bhaluka | 156 | 12:00 | 98 | Kurigram | 60 | 07:00 | 169 | Satkhira | 125 | 01:00
28 | Bhandaria | 56 | 03:00 | 99 | Kushtia | 148 | 00:00 | 170 | Satmasjid | 108 | 13:00
29 | Bhangura | 33 | 07:00 | 100 | Laksam | 38 | 18:30 | 171 | Savar | 236 | 12:00
30 | Bheramara(GK) | 65 | 00:00 | 101 | Lakshmipur | 49 | 00:00 | 172 | SevenRings | 15.28 | 12:00
31 | Bhulta | 206 | 11:00 | 102 | Lalbag | 85 | 13:00 | 173 | ShahCement | 18 | 11:00
32 | Bog-Sherpur | 60 | 18:00 | 103 | Lalmonirhat | 51 | 00:00 | 174 | Shahjadpur | 77 | 12:00
33 | Bogura | 164 | 00:00 | 104 | MI_Cement | 18.2 | 15:00 | 175 | Shahjibazar | 129 | 03:00
34 | Borhanuddin | 74 | 03:00 | 105 | Madanganj | 54 | 18:00 | 176 | Shahmirpur | 60.5 | 01:00
35 | Brahmanbaria | 125 | 19:30 | 106 | Madaripur | 116 | 00:00 | 177 | Shariatpur | 103 | 00:00
36 | Cantonment | 134 | 13:00 | 107 | Madartek | 85 | 00:00 | 178 | Sherpur | 144 | 00:00
37 | Chandina | 21 | 01:00 | 108 | Madunaghat | 54 | 14:00 | 179 | Shikalbaha | 35 | 01:00
38 | Chandpur | 80 | 21:00 | 109 | Magura | 66 | 00:00 | 180 | Shitalakhya | 83 | 13:00
39 | Chandraghona | 34 | 18:00 | 110 | Mahasthangarh | 61 | 01:00 | 181 | Sholosohor | 51 | 15:00
40 | Chapai | 66 | 04:00 | 111 | Maijdee | 51 | 23:00 | 182 | Shomvuganj | 45 | 08:00
41 | Charfasson | 31 | 20:00 | 112 | Manikganj | 124 | 22:00 | 183 | Shyampur | 164 | 11:00
42 | Charsaidpur | 40 | 15:00 | 113 | Maniknagar | 70 | 00:00 | 184 | Siddhirganj | 138 | 12:00
43 | Chauddagram | 75 | 22:00 | 114 | Matarbari | 56 | 18:00 | 185 | Sirajganj | 106 | 12:00
44 | Chhatak | 34 | 04:00 | 115 | Matuail | 81 | 12:00 | 186 | Sitakunda | 38 | 15:00
45 | Chowmuhani | 166 | 18:00 | 116 | Metrorail_Motijheel | 20 | 14:00 | 187 | Sonargaon | 119 | 09:00
46 | Chuadanga | 119 | 00:00 | 117 | Metrorail_Uttara | 7 | 20:00 | 188 | Sreemongol | 74 | 16:00
47 | Coxsbazar | 146 | 19:00 | 118 | Millgate | 115 | 15:00 | 189 | Sreepur | 136 | 18:30
48 | Cumilla(N) | 146 | 12:00 | 119 | Mirpur | 155 | 12:00 | 190 | Srinagar | 49.1 | 00:00
49 | Cumilla(S) | 151 | 15:00 | 120 | Mirsorai | 67 | 14:00 | 191 | Sunamganj | 60 | 03:00
50 | Daganbhuiyan | 35 | 18:00 | 121 | Mirzapur | 52 | 13:00 | 192 | Sylhet | 137 | 18:00
51 | Daudkandi | 130 | 05:00 | 122 | Mithapukur | 64 | 00:00 | 193 | Sylhet_(South) | 57 | 18:00
52 | DhakaUniversity | 108 | 12:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 96 | 00:00 | 124 | Mogbazar | 72.2 | 11:00 | 195 | Tangail | 162 | 13:00
54 | Dhanmondi | 126 | 12:00 | 125 | Mongla | 42 | 15:00 | 196 | Taraganj | 29 | 18:00
55 | Dohazari | 108 | 04:00 | 126 | Monirampur | 25 | 00:00 | 197 | Tasnim | 43 | 15:00
56 | Faridpur | 184 | 00:00 | 127 | Motijheel | 49 | 12:00 | 198 | Thakurgaon | 93 | 00:00
57 | Fatullah | 123 | 15:00 | 128 | Muktagacha | 34 | 00:00 | 199 | Tongi | 155 | 18:00
58 | Fenchuganj | 44 | 18:00 | 129 | Munshiganj | 108 | 02:00 | 200 | Ullahpara | 36 | 00:00
59 | Feni | 117 | 18:00 | 130 | Muradnagar | 47 | 05:00 | 201 | Ullon | 46 | 18:00
60 | GPH | 78 | 19:00 | 131 | Mymensingh | 144 | 13:00 | 202 | Uttara | 95 | 12:00
61 | Ghatail | 78 | 00:00 | 132 | Nabinagar | 106 | 11:00 | 203 | UttaraNew | 58 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 96 | 04:00 | 204 | Zigatola | 86 | 00:00
63 | Ghorashal-230 | 101 | 12:00 | 134 | Narail | 61 | 00:00
64 | Goalpara | 42 | 00:00 | 135 | Narinda | 80 | 13:00
65 | Gollamari | 118 | 13:00 | 136 | Narshingdi | 175 | 00:00
66 | Gopalganj | 114 | 00:00 | 137 | Natore | 124 | 18:30
67 | Gulshan | 126 | 12:00 | 138 | Nawabganj | 45.8 | 02:00
68 | Halishahar | 133.5 | 15:00 | 139 | Netrakona | 133 | 00:00
69 | HaripurSBU | 135 | 19:00 | 140 | New | 84 | 15:00
70 | Hasnabad | 109 | 10:00 | 141 | Niamatpur | 54 | 00:00
71 | Hathazari | 100 | 18:00 | 142 | Noapara | 50 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15345.49 | 1267 |  | 16669.51
1:00 | 14244.44 | 1691 |  | 16011.44
2:00 | 14175.94 | 1557 |  | 15802.94
3:00 | 14003.21 | 985 |  | 15032.21
4:00 | 13909.63 | 274 |  | 14195.63
5:00 | 13568.39 | 45 |  | 13615.39
6:00 | 13464.85 | 32 |  | 13497.85
7:00 | 13697.77 | 198 |  | 13904.77
8:00 | 13749.11 | 124 |  | 13879.11
9:00 | 14061.93 | 40 |  | 14103.93
10:00 | 14269.68 | 25 |  | 14295.68
11:00 | 14857.17 | 25 |  | 14883.3
12:00 | 14585.73 | 130 |  | 14721.73
13:00 | 14281.45 | 124 |  | 14411.45
14:00 | 13536.3 | 61 |  | 13600.05
15:00 | 13402.51 | 71 |  | 13476.51
16:00 | 11861.04 | 15 |  | 11877.04
17:00 | 12052.23 | 0 |  | 12052.23
18:00 | 13279.68 | 0 |  | 13279.68
19:00 | 13998.03 | 0 |  | 13998.03
19:30 | 13921.84 | 29 |  | 13951.84
20:00 | 13620.3 | 29 |  | 13650.3
21:00 | 13900.69 | 39 |  | 13941.69
22:00 | 13893.62 | 29 |  | 13923.62
23:00 | 13838.94 | 29 |  | 13869.25
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9427.42 | 5918.07 | 15345.49 | DAILY GENERATION CURVE
00:30 | 9018.67 | 5776.295 | 14794.965
01:00 | 8609.92 | 5634.52 | 14244.44 | 08-10-2026
01:30 | 8604.42 | 5605.77 | 14210.19
02:00 | 8598.92 | 5577.02 | 14175.94
02:30 | 8538.17 | 5551.405 | 14089.575
03:00 | 8477.42 | 5525.79 | 14003.21
03:30 | 8459.42 | 5497 | 13956.42
04:00 | 8441.42 | 5468.21 | 13909.63
04:30 | 8308.21 | 5430.8 | 13739.01
05:00 | 8175 | 5393.39 | 13568.39
05:30 | 8164.67 | 5351.95 | 13516.62
06:00 | 8154.34 | 5310.51 | 13464.85
06:30 | 8162.31 | 5419 | 13581.31
07:00 | 8170.28 | 5527.49 | 13697.77
07:30 | 8150.44 | 5573 | 13723.44
08:00 | 8130.6 | 5618.51 | 13749.11
08:30 | 8241.26 | 5664.26 | 13905.52
09:00 | 8351.92 | 5710.01 | 14061.93
09:30 | 8444.7 | 5721.105 | 14165.805
10:00 | 8537.48 | 5732.2 | 14269.68
10:30 | 8781.745 | 5781.68 | 14563.425
11:00 | 9026.01 | 5831.16 | 14857.17
11:30 | 9034.18 | 5687.27 | 14721.45
12:00 | 9042.35 | 5543.38 | 14585.73
12:30 | 8937.935 | 5495.655 | 14433.59
13:00 | 8833.52 | 5447.93 | 14281.45
13:30 | 8607.74 | 5301.135 | 13908.875
14:00 | 8381.96 | 5154.34 | 13536.3
14:30 | 8231.02 | 5238.385 | 13469.405
15:00 | 8080.08 | 5322.43 | 13402.51
15:30 | 7517.965 | 5113.81 | 12631.775
16:00 | 6955.85 | 4905.19 | 11861.04
16:30 | 7126.62 | 4830.015 | 11956.635
17:00 | 7297.39 | 4754.84 | 12052.23
17:30 | 7735.125 | 4930.83 | 12665.955
18:00 | 8172.86 | 5106.82 | 13279.68
18:30 | 8413.07 | 5225.785 | 13638.855
19:00 | 8653.28 | 5344.75 | 13998.03
19:30 | 8597.86 | 5323.98 | 13921.84
20:00 | 8535.86 | 5084.44 | 13620.3
20:30 | 8635.36 | 5125.135 | 13760.495 |  | Executive Engineer
21:00 | 8734.86 | 5165.83 | 13900.69 |  | Network Operation Division
21:30 | 8697.36 | 5199.795 | 13897.155
22:00 | 8659.86 | 5233.76 | 13893.62
22:30 | 8624.36 | 5241.92 | 13866.28
23:00 | 8588.86 | 5250.08 | 13838.94

## En-Curve
QF-LDC-12
Date | 08-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3057 | 1774.5 | 849 | 0 | 72 | 692.87 | 220 | 5225.2 | 0 | 570.42 | 2834.5 | 50 | 0 | 0 | 1267 | DAILY ENERGY CURVE
00:30 | 3005 | 1744 | 884 | 0 | 71 | 661.095 | 217.5 | 5225.2 | 0 | 490.92 | 2471.25 | 25 | 0 | 0 | 1479 | 08-10-2026
01:00 | 2953 | 1713.5 | 919 | 0 | 70 | 629.32 | 215 | 5225.2 | 0 | 411.42 | 2108 | 0 | 0 | 0 | 1691
01:30 | 2951 | 1709 | 888 | 0 | 68 | 648.57 | 215 | 5225.2 | 0 | 393.92 | 2111.5 | 0 | 0 | 0 | 1624 | Energy Generated | 333.5833 |  | MKWHr
02:00 | 2949 | 1704.5 | 857 | 0 | 66 | 667.82 | 215 | 5225.2 | 0 | 376.42 | 2115 | 0 | 0 | 0 | 1557 | Energy not Served | 6.79 |  | MKWHr
02:30 | 2972 | 1697.75 | 817 | 0 | 66 | 666.205 | 215.5 | 5193.2 | 0 | 376.42 | 2085.5 | 0 | 0 | 0 | 1271 | Total Energy Requirement | 340.3733 |  | MKWHr
03:00 | 2995 | 1691 | 777 | 0 | 66 | 664.59 | 216 | 5161.2 | 0 | 376.42 | 2056 | 0 | 0 | 0 | 985
03:30 | 2997.5 | 1688.5 | 777 | 0 | 65 | 666.8 | 216 | 5153.7 | 0 | 362.92 | 2029 | 0 | 0 | 0 | 629.5
04:00 | 3000 | 1686 | 777 | 0 | 64 | 669.01 | 216 | 5146.2 | 0 | 349.42 | 2002 | 0 | 0 | 0 | 274
04:30 | 2992 | 1644.5 | 777 | 0 | 63 | 668.6 | 216.5 | 5153.7 | 0 | 314.21 | 1909.5 | 0 | 0 | 0 | 159.5
05:00 | 2984 | 1603 | 777 | 0 | 62 | 668.19 | 217 | 5161.2 | 0 | 279 | 1817 | 0 | 0 | 0 | 45
05:30 | 3059.5 | 1651.5 | 777 | 0 | 61 | 624.175 | 217.5 | 5102.7 | 0.745 | 255.5 | 1767 | 0 | 0 | 0 | 38.5
06:00 | 3135 | 1700 | 777 | 0 | 60 | 580.16 | 218 | 5044.2 | 1.49 | 232 | 1717 | 0 | 0 | 0 | 32
06:30 | 3126.5 | 1662 | 777 | 0 | 59 | 626.93 | 220 | 5040.7 | 52.18 | 215.5 | 1801.5 | 0 | 0 | 0 | 115
07:00 | 3118 | 1624 | 777 | 0 | 58 | 673.7 | 222 | 5037.2 | 102.87 | 199 | 1886 | 0 | 0 | 0 | 198
07:30 | 3072 | 1606 | 777.5 | 0 | 59 | 670.765 | 222 | 5029.1 | 178.075 | 199 | 1910 | 0 | 0 | 0 | 161
08:00 | 3026 | 1588 | 778 | 0 | 60 | 667.83 | 222 | 5021 | 253.28 | 199 | 1934 | 0 | 0 | 0 | 124
08:30 | 3048 | 1583.5 | 849.5 | 0 | 60 | 670.255 | 222 | 4964 | 332.765 | 217.5 | 1958 | 0 | 0 | 0 | 82
09:00 | 3070 | 1579 | 921 | 0 | 60 | 672.68 | 222 | 4907 | 412.25 | 236 | 1982 | 0 | 0 | 0 | 40
09:30 | 3089 | 1585 | 921 | 0 | 60 | 671.29 | 222 | 4949.5 | 432.515 | 249.5 | 1986 | 0 | 0 | 0 | 32.5
10:00 | 3108 | 1591 | 921 | 0 | 60 | 669.9 | 222 | 4992 | 452.78 | 263 | 1990 | 0 | 0 | 0 | 25
10:30 | 3164.5 | 1597 | 920.5 | 0 | 63 | 667.39 | 222 | 5076.5 | 455.325 | 324.71 | 2072.5 | 0 | 0 | 0 | 25
11:00 | 3221 | 1603 | 920 | 0 | 66 | 664.88 | 222 | 5161 | 457.87 | 386.42 | 2155 | 0 | 0 | 0 | 25
11:30 | 3207.5 | 1591 | 920.5 | 0 | 68 | 667.595 | 221 | 5125.5 | 386.435 | 375.42 | 2158.5 | 0 | 0 | 0 | 77.5
12:00 | 3194 | 1579 | 921 | 0 | 70 | 670.31 | 220 | 5090 | 315 | 364.42 | 2162 | 0 | 0 | 0 | 130
12:30 | 3151 | 1551.5 | 920.5 | 0 | 69 | 666.08 | 219.5 | 5069.5 | 277.59 | 336.42 | 2172.5 | 0 | 0 | 0 | 127
13:00 | 3108 | 1524 | 920 | 0 | 68 | 661.85 | 219 | 5049 | 240.18 | 308.42 | 2183 | 0 | 0 | 0 | 124
13:30 | 3133 | 1538 | 920 | 0 | 71 | 622.35 | 219 | 5002.5 | 241.815 | 242.71 | 1917.5 | 0 | 0 | 1 | 92.5
14:00 | 3158 | 1552 | 920 | 0 | 74 | 582.85 | 219 | 4956 | 243.45 | 177 | 1652 | 0 | 0 | 2 | 61
14:30 | 3144 | 1611.25 | 920 | 0 | 72 | 582.09 | 219.5 | 5037 | 254.565 | 159.5 | 1466 | 0 | 0 | 3.5 | 66
15:00 | 3130 | 1670.5 | 920 | 0 | 70 | 581.33 | 220 | 5118 | 265.68 | 142 | 1280 | 0 | 0 | 5 | 71
15:30 | 3070 | 1682.5 | 920.5 | 0 | 70 | 597.445 | 220.5 | 4856 | 178.33 | 137.5 | 895.5 | 0 | 0 | 3.5 | 43
16:00 | 3010 | 1694.5 | 921 | 0 | 70 | 613.56 | 221 | 4594 | 90.98 | 133 | 511 | 0 | 0 | 2 | 15
16:30 | 2980 | 1674.5 | 921 | 0 | 69 | 587.555 | 221.5 | 4607 | 61.58 | 164.5 | 668.5 | 0 | 0 | 1.5 | 7.5
17:00 | 2950 | 1654.5 | 921 | 0 | 68 | 561.55 | 222 | 4620 | 32.18 | 196 | 826 | 0 | 0 | 1 | 0
17:30 | 3006 | 1702 | 850 | 0 | 60 | 563.685 | 222 | 4826 | 16.09 | 346 | 1073.68 | 0 | 0 | 0.5 | 0
18:00 | 3062 | 1749.5 | 779 | 0 | 52 | 565.82 | 222 | 5032 | 0 | 496 | 1321.36 | 0 | 0 | 0 | 0
18:30 | 3044.5 | 1865 | 754.5 | 0 | 57 | 583.785 | 222 | 5117.5 | 0 | 519.71 | 1474.86 | 0 | 0 | 0 | 0
19:00 | 3027 | 1980.5 | 730 | 0 | 62 | 601.75 | 222 | 5203 | 0 | 543.42 | 1628.36 | 0 | 0 | 0 | 0
19:30 | 3130 | 2123.5 | 730 | 0 | 60 | 650.78 | 222 | 5225.2 | 0 | 464 | 1316.36 | 0 | 0 | 0 | 29
20:00 | 3245 | 2183.5 | 731 | 0 | 68 | 703.24 | 222 | 5225.2 | 0 | 182 | 1060.36 | 0 | 0 | 0 | 29
20:30 | 3202.5 | 2159.5 | 730.5 | 0 | 67 | 705.935 | 222 | 5225.2 | 0 | 198.5 | 1249.36 | 0 | 0 | 0 | 34
21:00 | 3160 | 2135.5 | 730 | 0 | 66 | 708.63 | 222 | 5225.2 | 0 | 215 | 1438.36 | 0 | 0 | 0 | 39
21:30 | 3131.5 | 2055.5 | 730 | 0 | 67 | 706.095 | 222 | 5225.2 | 0 | 219.5 | 1540.36 | 0 | 0 | 0 | 34
22:00 | 3103 | 1975.5 | 730 | 0 | 68 | 703.56 | 222 | 5225.2 | 0 | 224 | 1642.36 | 0 | 0 | 0 | 29
22:30 | 3102 | 1940 | 729.5 | 0 | 65 | 712.72 | 222 | 5225.2 | 0 | 224 | 1645.86 | 0 | 0 | 0 | 29
23:00 | 3101 | 1904.5 | 729 | 0 | 62 | 721.88 | 222 | 5225.2 | 0 | 224 | 1649.36 | 0 | 0 | 0 | 29
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 08-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 57 | 25 | 110 | 156 | 1056 | 432 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 57 | 20 | 96 | 136 | 1158 | 462
2:00 | 46 | 24 | 82 | 136 | 1106 | 492 |  | Import | 0
3:00 | 45 | 27 | 84 | 140 | 1140 | 450
4:00 | 43 | 24 | 94 | 142 | 1120 | 432 | Ishurdi-Ghorashal Ckt-2 | Export | 1970472.73
5:00 | 48 | 14 | 138 | 148 | 1182 | 418
6:00 | 50 | 15 | 136 | 146 | 1226 | 452 |  | Import | 0
7:00 | 38 | 8 | 130 | 144 | 1150 | 412
8:00 | 62 | 21 | 232 | 162 | 1210 | 478 | Sirajganj-Sreepur Ckt-1 | Export | 1145000
9:00 | 121 | 28 | 332 | 182 | 1442 | 546
10:00 | 121 | 27 | 322 | 176 | 1528 | 602 |  | Import | 0
11:00 | 130 | 38 | 354 | 188 | 1550 | 678
12:00 | 140 | 50 | 392 | 220 | 794 | 704 | Sirajganj-Sreepur Ckt-2 | Export | 1151000
13:00 | 157 | 52 | 382 | 202 | 1384 | 668
14:00 | 154 | 52 | 296 | 92 | 1490 | 668 |  | Import | 0
15:00 | 153 | 52 | 332 | 174 | 1552 | 642
16:00 | 91 | 0 | 124 | 64 | 1118 | 412 | Gopalganj-Aminbazar Ckt-1 | Export | 15010000
17:00 | 93 | -1 | 198 | 92 | 1288 | 448
18:00 | 69 | 16 | 146 | 134 | 1148 | 442 |  | Import | 0
18:30 | 52 | 14 | 124 | 136 | 1148 | 426
19:00 | 57 | 15 | 136 | 128 | 1148 | 418 | Gopalganj-Aminbazar Ckt-2 | Export | 15050000
19:30 | 73 | 23 | 90 | 98 | 1166 | 462
20:00 | 34 | 41 | 80 | 94 | 1072 | 432 |  | Import | 0
21:00 | 71 | 22 | 124 | 108 | 1120 | 422
22:00 | 71 | 16 | 140 | 108 | 1126 | 388 |  | Total Export | 34326472.73
23:00 | 73 | 16 | 140 | 106 | 1130 | 394 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 16:00 | 362 | 11:00 | Madunaghat | 402 | 08:00 | 394 | 15:00
Amtali | 413 | 17:00 | 407 | 11:00 | Meghnaghat | 393 | 17:00 | 372 | 11:00
Ashuganj | 400 | 0:00 | 377 | 11:00 | Mirsorai | 402 | 17:00 | 389 | 12:00
Bhulta | 395 | 16:00 | 368 | 11:00 | Payra | 414 | 16:00 | 409 | 09:00
Bibiana | 387 | 16:00 | 378 | 11:00 | Rahanpur | 407 | 12:00 | 400 | 10:00
BIPTC | 403 | 04:00 | 390 | 16:00 | Rampal | 400 | 16:00 | 305 | 23:00
Bogura | 400 | 17:00 | 386 | 10:00
Gopalganj | 397 | 16:00 | 382 | 11:00
Kaliakoir | 380 | 17:00 | 357 | 11:00
Korerhat | 402 | 17:00 | 388 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 17:00 | 217 | 11:00 | Hasnabad | 229 | 17:00 | 212 | 11:00
AKSML | 236 | 01:00 | 227 | 15:00 | Hathazari | 237 | 00:00 | 229 | 14:00
Aminbazar | 234 | 17:00 | 218 | 11:00 | Ishurdi | 236 | 16:00 | 224 | 10:00
Ashuganj | 231 | 19:00 | 219 | 12:00 | Jhenaidah | 229 | 19:30 | 215 | 10:00
Ashuganj-400 | 231 | 19:00 | 219 | 12:00 | Kachua | 230 | 17:00 | 221 | 15:00
Baghabari | 234 | 13:00 | 224 | 10:00 | Kaliakoir | 236 | 16:00 | 219 | 11:00
Barapukuria | 239 | 13:00 | 223 | 10:00 | Keranigonj | 230 | 17:00 | 213 | 11:00
Barapukuria-230 | 239 | 13:00 | 223 | 10:00 | Khulna(S) | 229 | 16:00 | 220 | 00:00
Barapukuria(N) | 240 | 13:00 | 225 | 10:00 | Korerhat | 229 | 17:00 | 221 | 15:00
Barishal | 227 | 17:00 | 222 | 12:00 | Madunaghat | 239 | 00:00 | 233 | 14:00
Bheramara | 233 | 02:00 | 221 | 10:00 | Madunaghat-400 | 241 | 08:00 | 234 | 15:00
Bhulta | 226 | 16:00 | 209 | 11:00 | Maniknagar | 223 | 17:00 | 207 | 11:00
Bibiana | 223 | 18:00 | 216 | 12:00 | Meghnaghat | 230 | 05:00 | 217 | 11:00
BIPTC | 236 | 02:00 | 222 | 10:00 | Meghnaghat-400 | 229 | 04:00 | 212 | 11:00
Birulia | 234 | 17:00 | 216 | 11:00 | Mirsorai | 233 | 17:00 | 225 | 15:00
Bogura | 242 | 13:00 | 233 | 07:00 | Naogaon | 229 | 13:00 | 217 | 07:00
Bogura-400 | 241 | 13:00 | 233 | 07:00 | Purbasadipur | 236 | 13:00 | 221 | 19:30
Borhanuddin | 231 | 17:00 | 226 | 11:00 | Rajshahi | 233 | 03:00 | 221 | 10:00
BSRM | 229 | 07:00 | 221 | 15:00 | Rampal | 228 | 16:00 | 219 | 00:00
Charfasson | 234 | 17:00 | 226 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 17:00 | 221 | 15:00 | Rampura | 225 | 16:00 | 207 | 11:00
Cumilla(N) | 225 | 17:00 | 213 | 12:00 | Shikalbaha | 241 | 00:00 | 232 | 15:00
Faridpur | 225 | 17:00 | 216 | 11:00 | Shyampur | 228 | 17:00 | 211 | 11:00
Fenchuganj | 227 | 19:30 | 219 | 12:00 | Siddhirganj | 225 | 20:00 | 212 | 10:00
Feni | 227 | 17:00 | 218 | 15:00 | Sirajgonj | 236 | 02:00 | 230 | 12:00
Ghorashal | 230 | 02:00 | 220 | 09:00 | Sreepur | 226 | 16:00 | 214 | 10:00
Ghorashal-230 | 228 | 16:00 | 207 | 10:00 | Tongi | 232 | 16:00 | 207 | 11:00
Gopalganj | 228 | 15:00 | 217 | 10:00
GPH | 235 | 00:00 | 227 | 15:00
Haripur | 225 | 17:00 | 209 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 16:00 | 127 | 11:00 | Madanganj | 135 | 16:00 | 124 | 11:00
Agargaon | 139 | 16:00 | 129 | 11:00 | Madaripur | 135 | 17:00 | 127 | 00:00
Agrabad | 136 | 00:00 | 130 | 15:00 | Madartek | 137 | 05:00 | 126 | 12:00
AKS | 135 | 00:00 | 129 | 14:00 | Madunaghat | 138 | 00:00 | 135 | 15:00
Aminbazar | 133 | 17:00 | 123 | 12:00 | Magura | 135 | 17:00 | 127 | 00:00
Amnura | 135 | 17:00 | 129 | 07:00 | Mahasthangarh | 140 | 13:00 | 130 | 20:00
Araihazar | 132 | 16:00 | 117 | 11:00 | Maijdee | 128 | 00:00 | 124 | 15:00
Ashuganj | 136 | 17:00 | 127 | 12:00 | Manikganj | 140 | 16:00 | 126 | 10:00
Ashuganj-230 | 140 | 16:00 | 133 | 10:00 | Maniknagar | 138 | 04:00 | 126 | 12:00
Bagerhat | 127 | 16:00 | 121 | 07:00 | Matarbari | 121 | 00:00 | 111 | 19:30
Bajitpur | 136 | 17:00 | 123 | 12:00 | Matuail | 134.7 | 17:00 | 124 | 11:00
Bakerganj | 133 | 17:00 | 128 | 20:00 | Metrorail_Motijheel | 138 | 04:00 | 126 | 12:00
Bakulia | 137 | 00:00 | 131 | 14:00 | Metrorail_Uttara | 139 | 16:00 | 122 | 12:00
Banani | 138 | 16:00 | 126 | 12:00 | Millgate | 140 | 16:00 | 123 | 12:00
Bangabhaban | 138 | 16:00 | 126 | 12:00 | Mirpur | 134 | 17:00 | 122 | 11:00
Barapukuria | 142 | 13:00 | 129 | 07:00 | Mirzapur | 137 | 16:00 | 126 | 10:00
Barguna | 132 | 03:00 | 128 | 20:00 | Mithapukur | 140 | 13:00 | 128 | 07:00
Barishal | 132 | 04:00 | 126 | 22:00 | MI_Cement | 133 | 04:00 | 122 | 11:00
Barishal-230 | 132 | 17:00 | 127 | 20:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 00:00 | 132 | 11:00 | Mogbazar | 140 | 17:00 | 125 | 12:00
Baroirhat | 132 | 00:00 | 128 | 11:00 | Mongla | 125 | 04:00 | 119 | 00:00
Bashundhara | 139 | 16:00 | 122 | 12:00 | Monirampur | 131 | 18:00 | 116 | 07:00
BashundharaCement | 135 | 16:00 | 124 | 11:00 | Motijheel | 138 | 16:00 | 126 | 12:00
Beanibazar | 124 | 04:00 | 119 | 12:00 | Muktagacha | 135 | 15:00 | 116 | 06:00
Benapole | 135 | 18:00 | 116 | 00:00 | Munshiganj | 134 | 17:00 | 123 | 11:00
Bhaluka | 135 | 16:00 | 124 | 10:00 | Muradnagar | 132 | 17:00 | 120 | 11:00
Bhandaria | 132 | 16:00 | 124 | 12:00 | Mymensingh | 136 | 15:00 | 119 | 07:00
Bhangura | 135 | 13:00 | 129 | 10:00 | Nabinagar | 143 | 16:00 | 121 | 11:00
Bheramara | 138 | 13:00 | 130 | 10:00 | Naogaon | 137 | 13:00 | 130 | 21:00
Bheramara(GK) | 137 | 13:00 | 130 | 10:00 | Narail | 134 | 13:00 | 125 | 00:00
Bhulta | 129 | 16:00 | 116 | 11:00 | Narinda | 138 | 04:00 | 126 | 12:00
Bhulta-400 | 132 | 15:00 | 119 | 11:00 | Narshingdi | 138 | 16:00 | 114 | 11:00
Birulia | 137 | 17:00 | 127 | 11:00 | Natore | 136 | 13:00 | 129 | 10:00
Bog-Sherpur | 139 | 13:00 | 131 | 10:00 | Nawabganj | 139 | 16:00 | 127 | 12:00
Bogura | 141 | 13:00 | 132 | 20:00 | Netrakona | 127 | 16:00 | 114 | 12:00
Bogura-230 | 141 | 13:00 | 134 | 07:00 | New | 142 | 16:00 | 126 | 10:00
Brahmanbaria | 135 | 18:00 | 124 | 11:00 | Niamatpur | 137 | 18:00 | 132 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 139 | 16:00 | 128 | 12:00 | Noapara | 131 | 17:00 | 121 | 00:00
Chandina | 132 | 17:00 | 124 | 11:00 | Pabna | 136 | 15:00 | 121 | 12:00
Chandpur | 135 | 00:00 | 128 | 15:00 | Palashbari | 139 | 13:00 | 126 | 06:00
Chandraghona | 138 | 00:00 | 134 | 15:00 | Panchagarh | 141 | 13:00 | 132 | 15:00
Chapai | 134 | 16:00 | 130 | 07:00 | Patiya | 135 | 00:00 | 129 | 15:00
Charsaidpur | 135 | 16:00 | 124 | 11:00 | Patnitala | 135 | 13:00 | 130 | 20:00
Chauddagram | 131 | 17:00 | 124 | 15:00 | Patuakhali | 132 | 03:00 | 127 | 22:00
Chhatak | 123 | 18:00 | 115 | 12:00 | Payra | 135 | 01:00 | 133 | 12:00
Chowmuhani | 129 | 17:00 | 124 | 15:00 | PHP | 132 | 00:00 | 127 | 15:00
Chuadanga | 136 | 18:00 | 125 | 00:00 | Postogola | 136 | 17:00 | 125 | 12"00
Coxsbazar | 121 | 10:00 | 116 | 19:00 | Pubail | 134 | 17:00 | 122 | 14:00
Cumilla(N) | 131 | 17:00 | 123 | 12:00 | Purbachal | 139 | 16:00 | 126 | 11:00
Cumilla(S) | 133 | 03:00 | 124 | 12:00 | Purbasadipur | 142 | 13:00 | 133 | 19:30
Daganbhuiyan | 130 | 00:00 | 125 | 15:00 | Rahanpur | 137 | 17:00 | 134 | 09:00
Daudkandi | 132 | 17:00 | 119 | 11:00 | Rahanpur-400 | 137 | 17:00 | 134 | 07:00
DhakaUniversity | 139 | 16:00 | 126 | 12:00 | Rahim | 135 | 17:00 | 124 | 11:00
Dhamrai | 142 | 16:00 | 123 | 11:00 | Rajbari | 128 | 16:00 | 122 | 00:00
Dhanmondi | 139 | 16:00 | 126 | 11:00 | Rajendrapur | 139 | 16:00 | 127 | 12:00
Dohazari | 132 | 00:00 | 125 | 14:00 | Rajshahi | 133 | 13:00 | 128 | 10:00
Faridpur | 131 | 16:00 | 124 | 11:00 | Rajshahi-230 | 134 | 13:00 | 128 | 20:00
Fatullah | 135 | 17:00 | 123 | 11:00 | Ramganj | 130 | 01:00 | 124 | 15:00
Fenchuganj | 134 | 19:30 | 128 | 12:00 | Rampur | 136 | 00:00 | 131 | 14:00
Feni | 131 | 07:00 | 125 | 15:00 | Rampura | 138 | 16:00 | 126 | 12:00
Feni-230 | 139 | 09:00 | 126 | 15:00 | Rangamati | 137 | 00:00 | 133 | 15:00
Ghatail | 133 | 15:00 | 119 | 07:00 | Rangpur | 138 | 13:00 | 125 | 08:00
Ghorashal | 138 | 16:00 | 127 | 11:00 | Ruppur | 138 | 13:00 | 132 | 10:00
Goalpara | 133 | 17:00 | 123 | 00:00 | Saidpur | 141 | 13:00 | 130 | 18:00
Gollamari | 134 | 17:00 | 124 | 07:00 | Santhia | 136 | 13:00 | 130 | 10:00
Gopalganj | 131 | 16:00 | 124 | 00:00 | Satkhira | 132 | 18:00 | 117 | 00:00
Gopalganj-400 | 133 | 16:00 | 128 | 10:00 | Satmasjid | 139 | 04:00 | 128 | 11:00
Gulshan | 139 | 16:00 | 126 | 12:00 | Savar | 133 | 17:00 | 122 | 11:00
Halishahar | 137 | 00:00 | 130 | 15:00 | SevenRings | 139 | 16:00 | 125 | 15:00
Haripur | 135 | 17:00 | 124 | 11:00 | ShahCement | 135 | 16:00 | 124 | 11:00
HaripurSBU | 135 | 18:00 | 124 | 11:00 | Shahjadpur | 132 | 04:00 | 130 | 00:00
Hasnabad | 135 | 22:00 | 124 | 11:00 | Shahjibazar | 134 | 19:00 | 124 | 12:00
Hathazari | 138 | 00:00 | 133 | 14:00 | Shahmirpur | 138 | 00:00 | 132 | 15:00
Hatirjheel | 139 | 17:00 | 126 | 12:00 | Shariatpur | 132 | 17:00 | 124 | 00:00
Ishurdi | 139 | 13:00 | 131 | 10:00 | Sherpur | 138 | 15:00 | 116 | 01:00
Jaldhaka | 140 | 13:00 | 127 | 00:00 | Shikalbaha | 126 | 00:00 | 122 | 16:00
Jamalpur | 139 | 21:00 | 120 | 07:00 | Shikalbaha-230 | 138 | 00:00 | 132 | 15:00
Jashore | 138 | 02:00 | 118 | 00:00 | Shitalakhya | 133 | 04:00 | 121.5 | 12:00
Jhenaidah | 139 | 17:00 | 130 | 10:00 | Sholosohor | 138 | 00:00 | 131 | 15:00
Jhenaidah-230 | 139 | 16:00 | 130 | 00:00 | Shomvuganj | 126 | 18:00 | 111 | 14:00
Joydebpur | 138 | 16:00 | 120 | 10:00 | Shyampur | 136 | 17:00 | 124 | 11:00
Joypurhat | 135 | 13:00 | 130 | 07:00 | Shyampur-230 | 137 | 18:30 | 124 | 11:00
Juldah | 137 | 00:00 | 133 | 14:00 | Siddhirganj | 135 | 16:00 | 124 | 11:00
Kabirpur | 141 | 16:00 | 119 | 12:00 | Sirajganj | 134 | 13:00 | 126 | 10:00
Kachua | 131 | 00:00 | 126 | 15:00 | Sitakunda | 137 | 00:00 | 132 | 15:00
Kaliakoir | 140 | 16:00 | 131 | 10:00 | Sonargaon | 134 | 16:00 | 121 | 12:00
Kaliganj | 138 | 17:00 | 128 | 10:00 | Sreemongol | 133 | 19:00 | 123 | 12:00
Kallyanpur | 133 | 17:00 | 122 | 11:00 | Sreepur | 138 | 16:00 | 129 | 09:00
Kalurghat | 138 | 00:00 | 134 | 15:00 | Srinagar | 139 | 16:00 | 127 | 12:00
Kamrangirchar | 140 | 17:00 | 119 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 18:00 | 112 | 14:00
Kasba | 132 | 17:00 | 120 | 11:00 | Sylhet | 124 | 05:00 | 120 | 11:00
Kazla | 139 | 02:00 | 126 | 12:00 | Sylhet_(South) | 126 | 03:00 | 121 | 12:00
Keranigonj | 140 | 17:00 | 128 | 11:00 | Tangail | 131 | 15:00 | 123 | 12:00
Khagrachori | 136 | 07:00 | 131 | 15:00 | Taraganj | 140 | 13:00 | 128 | 07:00
Khulna | 132 | 17:00 | 123 | 00:00 | Tasnim | 134 | 17:00 | 121 | 12:00
Khulna(S) | 133 | 16:00 | 125 | 00:00 | Thakurgaon | 142 | 12:00 | 132 | 15:00
Khulshi | 136 | 00:00 | 129 | 15:00 | TK | 137 | 17:00 | 134 | 15:00
Kishoreganj | 135 | 17:00 | 122 | 04:00 | Tongi | 143 | 16:00 | 126 | 11:00
Kodda | 140 | 16:00 | 120 | 15:00 | Ullahpara | 136 | 13:00 | 128 | 10:00
Korerhat | 134 | 00:00 | 130 | 13:00 | Ullon | 138 | 16:00 | 126 | 12:00
KSRM | 136 | 00:00 | 132 | 12:00 | Uttara | 137 | 04:00 | 122 | 11:00
Kulaura | 132 | 18:30 | 126 | 12:00 | UttaraNew | 139 | 16:00 | 122 | 12:00
Kurigram | 137 | 13:00 | 121 | 07:00 | Zigatola | 140 | 16:00 | 128 | 11:00
Kushtia | 137 | 13:00 | 129 | 10:00
Laksam | 131 | 16:00 | 125 | 14:00
Lakshmipur | 128 | 09:00 | 124 | 15:00
Lalbag | 139 | 16:00 | 127 | 12:00
Lalmonirhat | 133 | 17:00 | 124 | 07:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division