## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-10-2026 | during | 12-10-2026 | during | 12-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 364 | 412 | 412 | 412 | 389 | 389 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 310 | 335 | 335 | 319 | 319 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 125 | 133 | 133 | 30 | 143 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 10 | 24.75 | 24.75 | 10 | 10 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 47 | 52.19 | 52.19 | 24 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 262 | 295 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 97 | 115 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 480 | 584 | 584 | 526 | 526 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 445 | 400 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 51 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2369 | 2898.42 | 5557.55 | 5528.55 | 2732.09 | 3092.09
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 182 | 182 | 176 | 176 | 176 | 176 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 45 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 100 | 100 | 100 | 24 | 89 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 5 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 3 | 71 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.56 | 0 | 3.56 | 0 | 3.56 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 155 | 212 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 91 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 37 | 100 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 153 | 160 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1060 | 1060 | 1150 | 1150 | 1060 | 1060 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3452.56 | 3842.86 | 4091.52 | 4097.96 | 3457.56 | 3785.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 211 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 338 | 330 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 305 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 41.65 | 41.65 | 20 | 20 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.82 | 52.82 | 5 | 5 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 178 | 148 | 195 | 195 | 178 | 178 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 130 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 29 | 15 | 15 | 15 | 15 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 87 | 163 | 163 | 70 | 70 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 88 | 155 | 200 | 200 | 136 | 136 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 72 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 8 | 25 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 13 | 24.5 | 24.5 | 14 | 14 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 85 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 73 | 73 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1677 | 1874.2 | 2354.44 | 2280.44 | 1846 | 1853
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-10-2026 | during | 12-10-2026 | during | 12-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.82 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 169 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.38 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 277.3 | 297 | 663.6 | 591.5 | 280.1 | 294
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 40 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 139 | 138 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 81 | 81 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 8 | 8 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 388 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1261 | 1282 | 1304 | 1304 | 1244 | 1244
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 467 | 434 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 32 | 32 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 105 | 105 | 105 | 0 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1829.2 | 1846.2 | 3626.2 | 3536.2 | 2966.2 | 2908.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 64 | 110 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 119 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2229.84 | 2341.6 | 2378.6 | 2377.6 | 2266.6 | 2265.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 43.98 | 0 | 53.42 | 0 | 53.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 45 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 309 | 333 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 20 | 25 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8.5 | 50 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 60 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.45 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 544.03 | 739.8 | 748 | 748 | 680 | 680 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.38 | 0 | 63 | 0 | 63 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1230.34 | 1509 | 2554.11 | 2331.99 | 1537.73 | 1486.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 199 | 0 | 186.09 | 0 | 186.09 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 311 | 228 | 469.09 | 248 | 379.09 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 14637.24 | 16119.28 | 22999.11 | 22296.24 | 16709.37 | 17166.36
Forecast Scenario (12-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14950 |  | 1690.35 |  | 16720
|  |  |  | 1:00 | 14833 |  | 688 |  | 15553.4188
|  |  |  | 2:00 | 14666 |  | 10 |  | 14676.4712
|  |  |  | 3:00 | 14125 |  | 0 |  | 14125
|  |  |  | 4:00 | 13517 |  | 0 |  | 13517
|  |  |  | 5:00 | 13013 |  | 0 |  | 13013
|  |  |  | 6:00 | 12936 |  | 0 |  | 12936
|  |  |  | 7:00 | 13404 |  | 10 |  | 13414.4712
|  |  |  | 8:00 | 13564 |  | 10 |  | 13574.4712
|  |  |  | 9:00 | 13620 |  | 124.15 |  | 13750
|  |  |  | 10:00 | 13800 |  | 95.5 |  | 13900
|  |  |  | 11:00 | 14100 |  | 429.75 |  | 14550
|  |  |  | 12:00 | 14700 |  | 620.75 |  | 15350
|  |  |  | 13:00 | 15050 |  | 229.2 |  | 15290
|  |  |  | 14:00 | 14490 |  | 620.75 |  | 15140
|  |  |  | 15:00 | 14715 |  | 463.175 |  | 15200
|  |  |  | 16:00 | 14966 |  | 290.32 |  | 15270
|  |  |  | 17:00 | 14750 |  | 334.25 |  | 15100
|  |  |  | 18:00 | 15500 |  | 955 |  | 16500
|  |  |  | 18:30 | 15820 |  | 1031.4 |  | 16900
|  |  |  | 19:00 | 15945 |  | 959.775 |  | 16950
|  |  |  | 19:30 | 15962 |  | 991.29 |  | 17000
|  |  |  | 20:00 | 16120 |  | 888.15 |  | 17050
|  |  |  | 21:00 | 15959 |  | 516.655 |  | 16500
|  |  |  | 22:00 | 15822 |  | 408.74 |  | 16250
|  |  |  | 23:00 | 15425 |  | 644.625 |  | 16100
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 15350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 888.15
Probable Maximum Demand at Evening Peak: |  |  | 17050.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16120.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 337.35395 MKWHr. |  | 200 | 90 | 108 | 100 | 50 | 110 | 40 | 110 | 80 | 888
*** This report is generated digitally from Operation Information System (OIS) at 07:52 hrs on 12-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-10-2026 | [28 empty] | Date: | 11-10-2026 | [28 empty] | Date: | 11-10-2026 | [28 empty] | Date: | 11-10-2026 | [28 empty] | Date: | 11-10-2026 | [16 empty] | Date: | 11-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 53 | 54 | 115 | 56 | 295 | 52 | 55 | 158 | 0 | 0 | 430 | 0 | 55 | 296 | 0 | 0 | 0 | 105 | 10 | 22 | 0 | 425 | 94 | 214 | 55 | 0 | 4 | 34 | 43 | 36 | 24 | 38 | 0 | 182 | 82 | 7 | 1055 | 152 | 0 | 50 | 17 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 144 | 178 | 0 | 319 | 295 | 44 | 5 | 220 | 20 | 104 | 71 | 156 | 75 | 15 | 30 | 66 | 25 | 0 | 15 | 315 | 400 | 0 | 40 | 40 | 156 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 100 | 0 | 65 | 0 | 185 | 0 | 0 | 0 | 18 | 9558 | 294 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1168 | 0 | 0 | 0 | 698.54 | 0 | 40 | 0 | 35 | 113 | 0 | 51 | 30 | 25 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 137 | 5392.14 | 14950.14 | 105.39
01:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 54 | 115 | 41 | 295 | 49 | 55 | 152 | 0 | 0 | 425 | 0 | 55 | 290 | 0 | 0 | 0 | 86 | 10 | 22 | 0 | 410 | 90 | 68 | 57 | 0 | 3 | 34 | 43 | 36 | 12 | 38 | 0 | 180 | 92 | 17 | 960 | 145 | 0 | 50 | 8 | 105 | 219 | 0 | 0 | 0 | 1135 | 0 | 144 | 178 | 0 | 315 | 290 | 44 | 5 | 223 | 20 | 103 | 72 | 156 | 68 | 16 | 17 | 64 | 16 | 0 | 15 | 310 | 400 | 0 | 40 | 40 | 154 | 0 | 16 | 0 | 81 | 0 | 137 | 0 | 100 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 13 | 9012 | 478 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1212 | 0 | 0 | 0 | 689.36 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 0 | 16 | 23.7 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 90 | 5416.66 | 14428.66 | 105.38
02:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 35 | 54 | 110 | 14 | 245 | 0 | 35 | 146 | 0 | 0 | 415 | 0 | 55 | 306 | 0 | 0 | 0 | 51 | 10 | 22 | 0 | 450 | 34 | 69 | 33 | 0 | 1 | 34 | 37 | 0 | 0 | 38 | 0 | 180 | 92 | 22 | 850 | 102 | 0 | 25 | 0 | 105 | 221 | 0 | 0 | 0 | 1160 | 0 | 150 | 178 | 0 | 335 | 310 | 44 | 5 | 222 | 20 | 98 | 72 | 100 | 70 | 19 | 0 | 60 | 0 | 0 | 15 | 305 | 400 | 0 | 40 | 40 | 152 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 100 | 5 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8466 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 698.85 | 0 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 90 | 5148.45 | 13614.45 | 105.37
03:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 54 | 82 | 13 | 195 | 0 | 35 | 155 | 0 | 0 | 425 | 0 | 55 | 304 | 0 | 0 | 0 | 34 | 10 | 22 | 0 | 445 | 15 | 69 | 11 | 0 | 3 | 34 | 37 | 0 | 0 | 38 | 0 | 179 | 92 | 27 | 710 | 64 | 0 | 6 | 0 | 105 | 221 | 0 | 0 | 0 | 1160 | 0 | 150 | 178 | 0 | 330 | 305 | 44 | 5 | 221 | 20 | 104 | 72 | 98 | 0 | 19 | 0 | 62 | 0 | 0 | 16 | 310 | 400 | 0 | 40 | 40 | 155 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 100 | 17 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8108 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 699.89 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 90 | 5132.49 | 13240.49 | 105.36
04:00 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 54 | 53 | 0 | 145 | 0 | 35 | 152 | 0 | 0 | 425 | 0 | 55 | 300 | 0 | 0 | 0 | 17 | 10 | 22 | 0 | 425 | 0 | 69 | 0 | 0 | 1 | 34 | 37 | 0 | 0 | 38 | 0 | 179 | 92 | 29 | 710 | 30 | 0 | 6 | 0 | 105 | 220 | 0 | 0 | 0 | 1160 | 0 | 150 | 177 | 0 | 320 | 295 | 44 | 5 | 221 | 20 | 75 | 85 | 34 | 0 | 19 | 0 | 60 | 0 | 0 | 16 | 305 | 400 | 0 | 40 | 40 | 152 | 0 | 16 | 0 | 81 | 0 | 137 | 0 | 100 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 7763 | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 695.03 | 0 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 54 | 5100.83 | 12863.83 | 105.35
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 35 | 34 | 0 | 0 | 0 | 35 | 147 | 0 | 0 | 420 | 0 | 55 | 300 | 0 | 0 | 0 | 17 | 10 | 22 | 0 | 435 | 0 | 69 | 0 | 0 | 3 | 34 | 37 | 0 | 0 | 38 | 0 | 179 | 84 | 29 | 710 | 29 | 0 | 6 | 0 | 105 | 220 | 0 | 0 | 0 | 1160 | 0 | 150 | 178 | 0 | 320 | 300 | 44 | 5 | 222 | 20 | 68 | 110 | 0 | 0 | 19 | 0 | 58 | 0 | 0 | 16 | 300 | 400 | 0 | 40 | 40 | 150 | 0 | 16 | 0 | 81 | 0 | 137 | 0 | 100 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 7530 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 699.54 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 54 | 5043.34 | 12573.34 | 105.34
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 35 | 34 | 0 | 0 | 0 | 17 | 90 | 0 | 0 | 425 | 0 | 35 | 304 | 0 | 0 | 0 | 17 | 10 | 22 | 0 | 440 | 0 | 69 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 38 | 0.03 | 179 | 51 | 29 | 710 | 0 | 0 | 0 | 0 | 68 | 220 | 0 | 0 | 0 | 1160 | 0 | 150 | 178 | 0 | 340 | 310 | 44 | 5 | 221 | 20 | 54 | 110 | 0 | 0 | 19 | 0 | 56 | 0 | 0 | 16 | 305 | 400 | 0 | 40 | 40 | 154 | 0 | 16 | 0 | 81 | 0 | 139 | 0 | 100 | 0 | 59 | 0.14 | 67 | 0 | 0 | 0.13 | 12 | 7324.3 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 1234.2 | 0 | 0 | 0 | 700.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.01 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 54 | 5022.14 | 12346.44 | 105.33
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17 | 35 | 34 | 0 | 0 | 0 | 17 | 87 | 0 | 0 | 445 | 0 | 17 | 318 | 0 | 0 | 4 | 32 | 10 | 22 | 0 | 515 | 0 | 69 | 0 | 0 | 7 | 0 | 37 | 0 | 0 | 38 | 0.89 | 181 | 51 | 24 | 710 | 3 | 0 | 0 | 0 | 66 | 220 | 0 | 0 | 0 | 1224 | 5 | 147 | 178 | 0 | 349 | 325 | 44 | 5 | 218 | 20 | 51 | 84 | 0 | 0 | 8 | 0 | 52 | 0 | 16 | 16 | 320 | 400 | 0 | 40 | 40 | 159 | 2 | 8 | 0 | 81 | 0 | 137 | 0 | 100 | 0 | 59 | 3.33 | 67 | 0 | 0.3 | 8.19 | 12 | 7525.71 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1234.2 | 0 | 0 | 0 | 701.61 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7.7 | 12 | 26 | 0 | 7.68 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0.75 | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 0 | 0.9 | 30 | 0.08 | 32 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 54 | 5104.52 | 12630.23 | 105.32
08:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 35 | 34 | 0 | 15 | 0 | 19 | 35 | 0 | 0 | 445 | 0 | 17 | 311 | 0 | 0 | 12 | 51 | 9.5 | 22 | 0 | 480 | 0 | 70 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 37 | 1.77 | 181 | 56 | 8 | 710 | 22 | 0 | 12 | 0 | 85 | 219 | 0 | 0 | 0 | 1224 | 11 | 150 | 178 | 0 | 319 | 305 | 44 | 5 | 208 | 20 | 52 | 71 | 9 | 2 | 8 | 0 | 56 | 0 | 37 | 16 | 320 | 400 | 0 | 40 | 40 | 158 | 6 | 8 | 0 | 81 | 0 | 138 | 0 | 100 | 0 | 59 | 9.27 | 67 | 0 | 0.9 | 23.07 | 12 | 7522.51 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 1234.2 | 0 | 0 | 0 | 733.09 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 21.93 | 37 | 26 | 0 | 24.12 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 2.15 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 2.9 | 85 | 0.22 | 48 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5365.21 | 12887.72 | 105.31
09:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 35 | 34 | 0 | 30 | 0 | 35 | 35 | 0 | 0 | 435 | 0 | 17 | 295 | 0 | 0 | 21 | 51 | 9.5 | 21 | 0 | 400 | 0 | 100 | 0 | 0 | 0 | 0 | 36 | 1 | 0 | 37 | 2.69 | 182 | 73 | 2 | 855 | 51 | 0 | 18 | 0 | 102 | 219 | 0 | 0 | 0 | 1224 | 15 | 143 | 178 | 0 | 309 | 300 | 44 | 5 | 202 | 20 | 51 | 70 | 16 | 55 | 8 | 0 | 68 | 0 | 54 | 15 | 315 | 400 | 0 | 40 | 39 | 156 | 9 | 8 | 0 | 80 | 0 | 139 | 0 | 100 | 14 | 68 | 14.72 | 97 | 0 | 1.5 | 36.32 | 12 | 7813.73 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1234.2 | 0 | 0 | 0 | 705.59 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 37.51 | 64 | 26 | 0 | 40.87 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 3.65 | 0 | 0 | 0 | 25 | 34 | 0 | 0 | 0 | 4.7 | 140 | 0.4 | 64 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5499.52 | 13313.25 | 105.3
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 36 | 34 | 0 | 64 | 0 | 35 | 35 | 0 | 0 | 470 | 0 | 17 | 320 | 0 | 0 | 27 | 51 | 9.5 | 21 | 0 | 520 | 0 | 50 | 0 | 0 | 0 | 0 | 36 | 36 | 0 | 12 | 3.31 | 182 | 34 | 0 | 965 | 16 | 0 | 19 | 0 | 51 | 217 | 0 | 0 | 0 | 1224 | 18 | 80 | 178 | 0 | 334 | 310 | 44 | 5 | 191 | 20 | 51 | 30 | 16 | 73 | 14 | 0 | 70 | 0 | 66 | 15 | 320 | 394 | 0 | 40 | 39 | 155 | 11 | 0 | 0 | 80 | 0 | 138 | 0 | 100 | 17 | 68 | 20 | 106 | 0 | 1.9 | 42.9 | 12 | 7959.61 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1218 | 0 | 0 | 0 | 700.32 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 46.24 | 59 | 20 | 0 | 53.25 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 4.7 | 0 | 0 | 0 | 32 | 34 | 0 | 0 | 0 | 6 | 175 | 0.48 | 32 | 303 | 114 | 220 | 0 | 1170.6 | 300 | 17 | 5430.59 | 13390.2 | 105.29
11:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 50 | 62 | 0 | 205 | 22 | 35 | 35 | 0 | 0 | 500 | 0 | 17 | 300 | 0 | 0 | 32 | 51 | 10 | 21 | 0 | 410 | 20 | 130 | 0 | 0 | 0 | 0 | 34 | 36 | 0 | 37 | 3.59 | 182 | 51 | 0 | 1060 | 46 | 0 | 34 | 1 | 65 | 216 | 0 | 0 | 0 | 1224 | 18 | 90 | 178 | 0 | 302 | 290 | 44 | 5 | 202 | 20 | 51 | 40 | 37 | 73 | 14 | 0 | 79 | 0 | 73 | 15 | 315 | 395 | 0 | 41 | 39 | 154 | 12 | 8 | 0 | 80 | 0 | 139 | 0 | 100 | 17 | 69 | 20.92 | 106 | 0 | 2.1 | 51.8 | 12 | 8427.41 | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1234.2 | 0 | 0 | 0 | 640.21 | 0 | 0 | 0 | 40 | 12 | 0 | 8.5 | 0 | 0 | 48.58 | 74 | 20 | 0 | 59.66 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 5.39 | 0 | 0 | 35 | 35 | 34 | 0 | 0 | 0 | 6.8 | 194 | 0.29 | 48 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5546.23 | 13973.64 | 105.28
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 54 | 97 | 15 | 262 | 50 | 35 | 35 | 0 | 0 | 445 | 0 | 17 | 318 | 0 | 0 | 27 | 51 | 10 | 21 | 0 | 500 | 89 | 155 | 3 | 0 | 0 | 0 | 34 | 36 | 12 | 37 | 3.56 | 182 | 73 | 0 | 1060 | 153 | 0 | 45 | 8 | 105 | 215 | 0 | 0 | 0 | 1224 | 18 | 108 | 178 | 0 | 338 | 320 | 44 | 5 | 210 | 20 | 51 | 30 | 88 | 73 | 14 | 17 | 80 | 16 | 70 | 15 | 305 | 388 | 0 | 41 | 38 | 152 | 10 | 8 | 0 | 80 | 0 | 139 | 0 | 100 | 17 | 58 | 21.82 | 115 | 0 | 2.1 | 51.38 | 12 | 9036.86 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 78 | 1234.2 | 0 | 0 | 0 | 544.03 | 0 | 0 | 0 | 55 | 60 | 0 | 8.5 | 0 | 16 | 43.98 | 107 | 20 | 0 | 61.38 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 5.45 | 0 | 0 | 35 | 36 | 34 | 0 | 0 | 0 | 7 | 199 | 0.24 | 64 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5600.38 | 14637.24 | 105.27
13:00 | 0 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 54 | 114 | 70 | 295 | 55 | 35 | 35 | 0 | 0 | 460 | 0 | 17 | 304 | 0 | 0 | 28 | 143.42 | 10 | 21 | 0 | 460 | 102 | 155 | 28 | 0 | 0 | 0 | 33 | 36 | 36 | 37 | 3.43 | 181 | 73 | 0 | 1060 | 162 | 0 | 46 | 9 | 105 | 211 | 0 | 0 | 0 | 1224 | 18 | 130 | 178 | 0 | 319 | 305 | 44 | 5 | 200 | 20 | 51 | 30 | 127 | 73 | 13 | 73 | 82 | 28 | 68 | 22 | 315 | 388 | 0 | 39 | 37 | 153 | 10 | 8 | 0 | 79 | 0 | 138 | 0 | 100 | 17 | 58 | 20.4 | 115 | 0 | 1.9 | 41.19 | 18 | 9420.34 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 64 | 1234.2 | 0 | 0 | 0 | 517.35 | 0 | 0 | 0 | 55 | 100 | 0 | 8.5 | 0 | 52.2 | 23.7 | 66 | 20 | 0 | 40.64 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 4.89 | 0 | 0 | 95 | 34 | 32 | 0 | 0 | 0 | 6.6 | 188 | 0.49 | 64 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5627.17 | 15047.51 | 105.25
14:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 54 | 114 | 128 | 295 | 55 | 35 | 35 | 0 | 0 | 385 | 0 | 35 | 306 | 0 | 0 | 25 | 143.42 | 10 | 21 | 0 | 430 | 87 | 175 | 46 | 0 | 0 | 0 | 33 | 36 | 36 | 37 | 2.85 | 179 | 73 | 0 | 1060 | 160 | 0 | 50 | 25.5 | 105 | 212 | 0 | 0 | 0 | 1165 | 16 | 128 | 178 | 0 | 322 | 310 | 44 | 5 | 213 | 20 | 51 | 32 | 148 | 72 | 13 | 80 | 82 | 52.2 | 58 | 22 | 305 | 387 | 0 | 39 | 38 | 152 | 10 | 8 | 0 | 79 | 0 | 139 | 0 | 100 | 17 | 58 | 13.16 | 115 | 0 | 1.7 | 41.76 | 8 | 9441.59 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 59 | 1234.2 | 0 | 0 | 0 | 518.3 | 0 | 0 | 0 | 55 | 113 | 0 | 8 | 0 | 52.2 | 13.42 | 45 | 20 | 0 | 50.85 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 4.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 64 | 272 | 112 | 180 | 0 | 1100 | 300 | 54 | 5047.51 | 14489.1 | 105.25
15:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 54 | 114 | 111 | 295 | 55 | 35 | 35 | 0 | 0 | 385 | 0 | 35 | 310 | 0 | 0 | 18 | 143.42 | 10 | 21 | 0 | 490 | 90 | 177 | 46 | 0 | 0 | 0 | 33 | 36 | 36 | 37 | 2.05 | 178 | 73 | 0 | 1060 | 160 | 0 | 50 | 25.5 | 105 | 212 | 0 | 0 | 0 | 1160 | 12 | 134 | 178 | 0 | 333 | 310 | 44 | 5 | 188 | 20 | 51 | 31 | 153 | 73 | 13 | 80 | 84 | 43 | 43 | 20 | 325 | 385 | 0 | 39 | 38 | 152 | 7 | 8 | 0 | 80 | 0 | 137 | 0 | 100 | 17 | 58 | 12.16 | 115 | 0 | 1.2 | 22.97 | 18 | 9469.3 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 40 | 1180 | 0 | 0 | 0 | 520.82 | 0 | 0 | 0 | 55 | 113 | 0 | 8 | 0 | 52.2 | 30.52 | 55 | 20 | 0 | 35.2 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 2.16 | 0 | 0 | 0 | 22 | 12 | 0 | 0 | 0 | 4.3 | 118 | 0.34 | 64 | 260 | 112 | 220 | 0 | 1115 | 300 | 54 | 5245.54 | 14714.84 | 105.24
16:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 54 | 114 | 127 | 295 | 55 | 35 | 72 | 0 | 0 | 395 | 0 | 35 | 301 | 0 | 0 | 8 | 143.42 | 10 | 21 | 0 | 420 | 104 | 177 | 48 | 0 | 2 | 0 | 31 | 50 | 36 | 37 | 0 | 178 | 75 | 0 | 1060 | 162 | 0 | 50 | 25.5 | 105 | 211 | 0 | 0 | 0 | 1184 | 5 | 134 | 158 | 0 | 317 | 300 | 44 | 5 | 208 | 20 | 51 | 70 | 154 | 73 | 13 | 80 | 84 | 43 | 23 | 20 | 305 | 389 | 0 | 39 | 38 | 152 | 4 | 8 | 0 | 82 | 0 | 139 | 0 | 100 | 17 | 58 | 6.22 | 116 | 0 | 0.5 | 16.37 | 18 | 9482.01 | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 22 | 1195 | 0 | 0 | 0 | 514 | 0 | 34 | 0 | 100 | 113 | 0 | 8 | 0 | 52.2 | 16.18 | 30 | 20 | 0 | 17.98 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 1.55 | 0 | 0 | 91 | 12 | 70 | 0 | 0 | 0 | 2.3 | 63 | 0.17 | 96 | 307 | 113 | 220 | 0 | 1170.6 | 300 | 54 | 5483.98 | 14965.99 | 105.23
17:00 | 0 | 88 | 47 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 54 | 115 | 130 | 295 | 55 | 35 | 126 | 0 | 0 | 390 | 0 | 35 | 296 | 0 | 0 | 2 | 105 | 10 | 21 | 0 | 410 | 72 | 212 | 56 | 0 | 0 | 0 | 38 | 54.36 | 36 | 37 | 0.1 | 179 | 82 | 0 | 1060 | 90 | 0 | 50 | 25.5 | 105 | 213 | 0 | 0 | 0 | 1162 | 1 | 128 | 158 | 0 | 308 | 290 | 44 | 5 | 217 | 20 | 51 | 84 | 154 | 73 | 13 | 80 | 70 | 52.2 | 4 | 29 | 310 | 394 | 0 | 39 | 38 | 152 | 1 | 16 | 0 | 82 | 0 | 138 | 0 | 100 | 17 | 58 | 1.37 | 125 | 0 | 0.1 | 3.08 | 23 | 9428.71 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 5 | 1234.2 | 0 | 0 | 0 | 516.97 | 0 | 45 | 0 | 113 | 70 | 0 | 8 | 0 | 34 | 3.34 | 7 | 23 | 0 | 3.37 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0.25 | 0 | 0 | 111 | 2 | 70 | 0 | 0 | 0 | 0.7 | 14 | 0.04 | 96 | 277 | 114 | 180 | 0 | 1100 | 300 | 119 | 5320.87 | 14749.58 | 105.22
18:00 | 0 | 94 | 47 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 54 | 115 | 140 | 278 | 55 | 55 | 162 | 0 | 0 | 370 | 0 | 55 | 318 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 500 | 79 | 212 | 67 | 0 | 0 | 0 | 43 | 54.36 | 100 | 88 | 0 | 180 | 73 | 0 | 1060 | 97 | 0 | 50 | 25.5 | 105 | 213 | 0 | 0 | 0 | 1224 | 0 | 130 | 158 | 0 | 345 | 320 | 44 | 5 | 196 | 20 | 57 | 86 | 154 | 73 | 13 | 80 | 82 | 52.2 | 0 | 29 | 310 | 391 | 0 | 39 | 38 | 153 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 58 | 0 | 144 | 0 | 0 | 0 | 24 | 9907.48 | 467 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 581.57 | 0 | 45 | 0 | 113 | 90 | 0 | 50 | 18 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 119 | 5635.57 | 15543.05 | 105.21
19:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 115 | 125 | 295 | 55 | 55 | 162 | 0 | 0 | 395 | 0 | 55 | 298 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 410 | 105 | 212 | 68 | 0 | 0 | 34 | 43 | 54.36 | 100 | 100 | 0 | 181 | 88 | 0 | 1060 | 162 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 142 | 148 | 0 | 320 | 295 | 44 | 5 | 213 | 20 | 88 | 87 | 155 | 73 | 13 | 81 | 78 | 52.2 | 0 | 29 | 305 | 400 | 0 | 39 | 40 | 154 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 10049.48 | 387 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 700.21 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 34 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 119 | 5773.21 | 15822.69 | 105.2
19:30 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 54 | 54 | 115 | 132 | 295 | 55 | 55 | 162 | 0 | 0 | 402 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 434 | 108 | 212 | 70 | 0 | 0 | 34 | 45 | 54.36 | 100 | 100 | 0 | 182 | 91 | 0 | 1060 | 162 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 142 | 148 | 0 | 335 | 305 | 44 | 5 | 217 | 20 | 115 | 87 | 154 | 73 | 13 | 81 | 78 | 52.2 | 0 | 29 | 310 | 400 | 0 | 40 | 40 | 153 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 10165.48 | 387 | 0 | 33 | 2 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 694.75 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 38 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 119 | 5778.75 | 15944.23
20:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 115 | 141 | 295 | 55 | 55 | 162 | 0 | 0 | 390 | 0 | 55 | 303 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 430 | 109 | 212 | 70 | 0 | 0 | 34 | 45 | 54.36 | 100 | 100 | 0 | 182 | 92 | 2 | 1060 | 160 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 140 | 148 | 0 | 323 | 295 | 44 | 5 | 215 | 20 | 115 | 87 | 154 | 73 | 13 | 81 | 74 | 52.2 | 0 | 30 | 310 | 400 | 0 | 40 | 40 | 154 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 10130.48 | 387 | 0 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 729.1 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 39 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 119 | 5831.1 | 15961.58 | 105.19
21:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 115 | 125 | 295 | 55 | 55 | 162 | 0 | 0 | 400 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 480 | 107 | 212 | 71 | 0 | 0 | 34 | 45 | 54.36 | 100 | 100 | 0 | 182 | 91 | 5 | 1060 | 160 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 130 | 148 | 0 | 330 | 305 | 44 | 5 | 211 | 20 | 115 | 87 | 155 | 73 | 13 | 85 | 72 | 52.2 | 0 | 29 | 310 | 400 | 0 | 40 | 40 | 155 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 87 | 0 | 169 | 0 | 0 | 0 | 24 | 10194.48 | 434 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 739.8 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 38 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 119 | 5924.8 | 16119.28 | 105.18
22:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 54 | 54 | 115 | 126 | 295 | 55 | 55 | 90 | 0 | 0 | 400 | 0 | 55 | 303 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 425 | 107 | 212 | 72 | 0 | 0 | 34 | 45 | 54.36 | 100 | 100 | 0 | 182 | 91 | 2 | 1060 | 162 | 0 | 50 | 25.5 | 105 | 220 | 0 | 0 | 0 | 1224 | 0 | 135 | 148 | 0 | 320 | 295 | 44 | 5 | 212 | 20 | 106 | 88 | 155 | 74 | 13 | 81 | 72 | 52.2 | 0 | 30 | 308 | 400 | 0 | 40 | 39 | 156 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 24 | 10037.48 | 481 | 0 | 34 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 739.5 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 119 | 5922.3 | 15959.78 | 105.17
23:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 35 | 54 | 115 | 126 | 295 | 55 | 55 | 90 | 0 | 0 | 400 | 0 | 35 | 309 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 440 | 109 | 212 | 72 | 0 | 0 | 34 | 49 | 54.36 | 100 | 100 | 0 | 182 | 93 | 2 | 1060 | 80 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 137 | 108 | 0 | 334 | 310 | 44 | 5 | 220 | 20 | 79 | 89 | 156 | 74 | 13 | 80 | 72 | 52.2 | 0 | 30 | 305 | 400 | 0 | 40 | 39 | 155 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 88 | 0 | 164 | 0 | 0 | 0 | 24 | 9894.48 | 467 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 753.28 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 38 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 127 | 5928.08 | 15822.56 | 105.17
Total KWH | 0 | 1383360 | 777600 | 0 | 0 | 0 | 0 | 0 | 9295200 | 0 | 0 | 781920 | 1196280 | 2135232 | 1511040 | 4988073 | 807111 | 935806 | 2357280 | 0 | 0 | 10254346 | 0 | 930250 | 7435485 | 0 | 0 | 195221 | 2223600 | 237600 | 512280 | 0 | 11017272.73 | 1495418 | 3322036 | 815040 | 0 | 20640 | 377607 | 922368 | 721819 | 811200 | 1220160 | 24722 | 4355542 | 1898500 | 210240 | 22610909.09 | 2376945 | 0 | 855840 | 290412 | 2409563 | 4963036 | 0 | 0 | 0 | 28783633 | 131220 | 3248436 | 4014545 | 0 | 8303800 | 7546000 | 1002396 | 140160 | 5140000 | 493200 | 1697280 | 1682548 | 2479680 | 1306200 | 341290 | 967860 | 1676160 | 616651 | 517500 | 491200 | 7518000 | 9478200 | 0 | 944000 | 908520 | 3705300 | 85462 | 311904 | 0 | 1952640 | 0 | 3161000 | 0 | 2403960 | 321120 | 1594800 | 134776 | 2635200 | 0 | 13850 | 349000 | 408000 | 215182444.82 | 11145455 | 0 | 185280 | 168832 | 0 | 0 | 0 | 0 | 0 | 1414656 | 540720 | 29556360 | 0 | 0 | 0 | 15603814 | 0 | 560745 | 0 | 1329888 | 1828224 | 0 | 376784 | 207827 | 472642 | 313328 | 591420 | 527000 | 0 | 404256 | 0 | 0 | 0 | 0 | 0 | 0 | 7697890 | 0 | 35100 | 0 | 0 | 1232151 | 238999 | 1314892 | 0 | 0 | 0 | 41690.4 | 1237680 | 3187 | 1779648 | 7265000 | 2739000 | 5431040 | 0 | 28145454 | 7328000 | 1791600 | 131508562.4 | 346691007.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14637.24 | MW | 12:00 Hr. | Energy Generated |  |  | 346.691 |  | MKWHr.
| Day Peak Demand |  |  | 14782.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.826 |  | MKWHr.
| Evening Peak Generation |  |  | 16119.28 | MW | 21:00 Hr. | Energy Demand |  |  | 352.517 |  | MKWHr.
| Evening Peak Demand |  |  | 17108.23 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 12346.44 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 845.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 16119.28 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 8.472 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.7522 | 0 | 20.0276 | 0 | 0 | 0.19522 | 0 | 0 | 58.975 | Gas | 118.8409 | Gas | 411638467.4941
| Chattogram Zone |  |  | 5.1733 | 51.3945 | 17.5169 | 0 | 4.3555 | 0.15594 | 0 | 0.02064 | 78.6169 | Coal | 123.6894 | Coal | 895031490.7677
| Cumilla Zone |  |  | 28.6639 | 0 | 10.8073 | 0 | 0 | 0.5175 | 1.6762 | 0 | 41.6649 | HFO | 66.5011 | HFO | 1366983071.57
| Mymensingh Zone |  |  | 0 | 0 | 4.9591 | 0 | 0 | 0.49763 | 0 | 0 | 5.4567 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.3835 | 0 | 0 | 0 | 0 | 0.085462 | 0 | 0 | 30.469 | Hydro | 4.3555 | Hydro | 435554.2
| Khulna Zone |  |  | 0 | 29.5564 | 1.7688 | 0 | 0 | 0.54072 | 11.1455 | 0 | 43.0113 | Solar | 4.8581 | Solar | 78178050.088
| Barishal Zone |  |  | 8.17 | 42.7385 | 3.5712 | 0 | 0 | 0.003187 | 0 | 0 | 54.4829 | Import | 28.4254 | Import | 184580553.91
| Rajshahi Zone |  |  | 7.6979 | 0 | 5.3031 | 0 | 0 | 1.3441 | 15.6038 | 0 | 29.9489 | Wind | 0.02064 | Wind | 306297.6
| Rangpur Zone |  |  | 0 | 0 | 2.547 | 0 | 0 | 1.5184 | 0 | 0 | 4.0654
| Total |  |  | 118.8409 | 123.6894 | 66.5011 | 0 | 4.3555 | 4.8581 | 28.4254 | 0.02064 | 346.691
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 411638467.4941 |  | Hydro | 435554.2
|  |  |  | Coal | 895031490.7677 |  | Solar | 78178050.088
|  |  |  | HFO | 1366983071.57 |  | Import | 184580553.91
|  |  |  | HSD | 0 |  | Wind | 306297.6
[5 empty] | Total: | 293,71,53,485 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 36800 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.1455 | Peak Hr Flow | 434.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31252836.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.6038 | Peak Hr Flow | 739.80 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 978 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6762 | Peak Hr Flow | 72.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1965 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 28.4254 | Peak Hr Flow | 1245.80 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 83 |  | 5979
|  |  |  | Chattogram |  | 73 |  | 1607
|  |  |  | Cumilla |  | 111 |  | 1653
|  |  |  | Mymensingh |  | 60 |  | 1260
|  |  |  | Sylhet |  | 88 |  | 746
|  |  |  | Khulna |  | 80 |  | 1886
|  |  |  | Barishal |  | 42 |  | 534
|  |  |  | Rajshahi |  | 85 |  | 1557
|  |  |  | Rangpur |  | 10 |  | 880
|  |  |  | Total |  | 632 |  | 16102
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 143.5
|  |  |  | Total Unavailable Capacity |  |  |  | 443.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 16:24 | Panchagarh 132/33kV S/S T-1(407T) LT Scheduled S/D Due to Annual Maintenance
| 08:11 | 16:23 | Panchagarh 132/33kV S/S T-1(407T) HT Scheduled S/D Due to Annual Maintenance
| 08:37 | 11:07 | Mahasthangarh 132/33kV S/S 132KVMain bus 2 Scheduled S/D Due to Annual Maintenance
| 08:55 | 15:45 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Annual
Maintenance
| 09:04 | 15:37 | Sylhet_(South) 132/33kV S/S Sylhet (S)-Biyanibazar 132KV Ckt-1 Scheduled S/D Due to
Annual maintenance work.
|  | 09:05 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 09:06 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 09:07 | 09:55 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Forced S/D Due to 33kv Auxiliary-1 fuse | [7 empty] | 30.0MW load
|  |  | change. | [7 empty] | interrup.
| 09:07 | 09:55 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Forced S/D Due to 33kv Auxiliary-1 fuse
change.
| 09:12 | 14:26 | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Annual maintenance
| 09:12 | 15:59 | Chauddagram-Cumilla(S) 132 kV Ckt-2 Scheduled S/D from Cumilla(S) 132/33kV end Due to AM
and from Chauddagram 132/33kV end Due to Annual Maintenance
| 09:13 | 14:25 | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Annual Manintenance
| 09:25 | 15:47 | Beanibazar 132/33kV S/S 132 KV BUS-1 Scheduled S/D Due to Annual Maintenance line 1
| 09:33 | 17:39 | Korerhat 400/230/132kV S/S 400/132 KV ATR-2 (7203T) LT Project Work S/D Due to CAF WORK
| 09:34 | 17:37 | Korerhat 400/230/132kV S/S 400/132 KV ATR-2 (7203T) HT Project Work S/D Due to CAF WORK
| 09:58 | 12:14 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end Due to Project
work at Ishwardi End. and from Ishurdi 132/33kV end Due to Remove scaffolding work .
| 10:10 | 17:04 | Korerhat 400/230/132kV S/S Madunaghat-2 (C06) Project Work S/D Due to DFDR WORK
| 10:11 | 17:04 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-2 Project Work S/D
| 10:36 | 17:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Project Work S/D | [7 empty] | 18.0MW load
interrup.
| 10:37 | 17:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Project Work S/D | [7 empty] | 18.0MW load
interrup.
| 10:45 | 15:10 | Kachua 230/132/33kV S/S Laksam CKT-1 Project Work S/D Due to for SCADA integration
| 12:00 |  | Day Peak Generation: 14637 MW.
| 12:15 | 15:00 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end.
| 12:17 | 14:59 | Ishwardi-Rooppur 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end.
| 12:55 | 17:33 | Barapukuria S/S-P/S 230 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing
Siemens SIPROTEC 7SD87 relays Due to Line Differential Main1 Trip.
| 13:20 | 13:38 | Baroaulia-KSRM 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing 1. Trip Relay | [7 empty] | 10.0MW load
|  |  | K35 2. Trip Relay K34 relays Due to Null | [7 empty] | interrup. Baroaulia
132/33kV end
| 13:43 |  | Mithapukur-Palashbari 132kV Ckt-1 Tripped from Mithapukur 132/33kV end showing 21M2, | [7 empty] | 46.0MW load
|  |  | 86A, 86B relays Due to O/C & E/F Operated, Y-ph operated | [7 empty] | interrup.
Mithapukur 132/33kV
end
| 13:43 | 15:06 | Barapukuria(N)-Barapukuria P/S 230kV Ckt-2 Tripped from Barapukuria(N) 230kV end showing | [7 empty] | 163.0MW load
|  |  | Distance Relay(21) relays Due to Over current and Earth fault(50/51) | [7 empty] | interrup.
Barapukuria(N)
230kV end
| 13:43 | 14:32 | Barapukuria P/S-Bogura West 230kV Ckt-1 Tripped from Bogura 400/230kV end showing Main-1
and Main-2 relays Due to LA blast at Barapukuria Power Station.
| 13:43 | 15:05 | Barapukuria(N)-Bogura(west) 230kV Ckt-2 Tripped from Bogura 400/230kV end showing Main-1
and Main-2 relays Due to LA blast at Barapukuria Power Station.
| 13:44 | 15:02 | Barapukuria P/S-Purbasadipur 230 kV Ckt-2 Tripped from Purbasadipur 230/132/33kV end | [7 empty] | 90.0MW load
|  |  | showing Distance Relay relays Due to LA Blast in Boropukuria Power Plant | [7 empty] | interrup.
Purbasadipur
230/132/33kV end
| 13:44 | 14:45 | Barapukuria P/S-Purbasadipur 230 kV Ckt-1 Tripped from Purbasadipur 230/132/33kV end | [7 empty] | 90.0MW load
|  |  | showing Distance Relay relays Due to LA Blast in Boropukuria Power Plant | [7 empty] | interrup.
Purbasadipur
230/132/33kV end
| 13:45 | 15:06 | Barapukuria(N) -Bogura West (Old P/S-Bogura W) 230kV Ckt-2 Tripped from Barapukuria
230/132/33kV end showing ABB REL521, REL 511. relays Due to 230KV IBT -2 R phase LA blast
at power station end.
| 13:45 | 14:55 | Barapukuria S/S-P/S 230 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing | [7 empty] | 133.0MW load
|  |  | Siemens siprotec relays Due to 230KV IBT -02 R phase LA blast at power station end. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
|  | 14:35 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 14:38 | Barishal 230/132kV S/S T-4 LT is restored.
| 15:38 | 17:16 | Kachua 230/132/33kV S/S Laksam CKT-2 Project Work S/D
| 15:45 | 17:33 | Barapukuria S/S-P/S 230 kV Ckt-2 Forced S/D from Barapukuria 230/132/33kV end Due to
Emergency LA maintenance.
| 17:00 |  | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Bhulta 400/230/132kV end.
| 17:00 |  | Bhulta-Haripur 132 kV Ckt-2 Scheduled S/D from Bhulta 400/230/132kV end.
| 17:01 |  | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to One of the towers had tilted
earlier. Then it was strained using earthwire and stay insulator. Now the tower has
straightened itself out leaving the straining wires loose and very close to the current
carrying conductors.
| 17:02 |  | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Scheduled S/D Due to One of the
towers had tilted earlier. Then it was strained using earthwire and stay insulator. Now
the tower has straightened itself out leaving the straining wires loose and very close to
the current carrying conductors.
|  | 18:35 | Ishwardi-Santhia 132kV Ckt is restored.
|  | 21:29 | Dhaka University - Rampura 132kV ckt-1 is restored.
| 02:42 |  | TK chemical S/S 50/75 MVA T-1(405T) LT Tripped showing Over current relay relays Due to | [7 empty] | 2.0MW load
|  |  | Over current | [7 empty] | interrup.
| 03:22 |  | Khulshi-Madunaghat 132kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL-670
relays Due to B-phase conductor broken
| 03:51 |  | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance relay
relays Due to Distance trip 19.5
| 03:54 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance relay
62.3 km. Z 3/4.phase c relays.
| 07:10 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to High temp & Oil Leakage
maintenance
| 07:10 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to High temp & Oil leakage
Maintenance
| 07:24 |  | Hasnabad 132/33kV S/S 132kV Main Bus Scheduled S/D Due to Temperature Rise
| 07:26 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to
Temperature Rise
| 07:27 |  | Bogura South-Confidence 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to
Bus loop connecting
| 07:30 |  | Bogura 230/132kV S/S 132KV Main 1 Project Work S/D Due to conductor loop connect
| 07:50 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 230/132/33kV end
Due to RTU Works
| 07:54 |  | Ghorashal 230kV S/S TARFO-2 LT Tripped showing SIEMENS (Reyrolle) relays Due to Out Going | [7 empty] | 70.0MW load
|  |  | Fedder-2 Earth Fault. | [7 empty] | interrup.
| 08:00 |  | Panchagarh 132/33kV S/S T-1(407T) LT Scheduled S/D Due to For Annual Maintenance Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9295200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 807111 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7435485 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 781920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1511040 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935806 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 930250 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 237600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 512280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 47 | 777600 | Machine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4988073 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 2135232 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1383360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2357280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 195221 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1196280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 11017272.73 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 400 | 10254346 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2223600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2898.42 | 58974956.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 290412 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131220 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 855840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 182 | 4355542 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 4963036 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2409563 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 45 | 922368 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 377607 | Plant availability less
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 811200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 210240 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 71 | 815040 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24722 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 212 | 3322036 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 721819 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 1898500 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1220160 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1495418 | Machine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 160 | 2376945 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28783633 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 20640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1060 | 22610909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3842.86 | 78616850.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 211 | 5140000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 330 | 8303800 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 305 | 7546000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 493200 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 140160 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 148 | 4014545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1002396 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 3248436 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 491200 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 1682548 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 2479680 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1676160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 616651 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 341290 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 85 | 967860 | Fuel Shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1306200 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1697280 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 517500 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1874.2 | 41664906
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 134776 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 169 | 2635200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1594800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 349000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 408000 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 321120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 297 | 5456746
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 85462 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 944000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 908520 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3705300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 138 | 3161000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1952640 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403960 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 311904 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7518000 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9478200 | -
Sylhet Area Total |  |  |  |  | 2325 | 1282 | 30468986
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 434 | 11145455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 185280 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 168832 | Machine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel Shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1414656 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 540720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Machine Problem
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29556360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1846.2 | 43011303
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 28145454 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1779648 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2739000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7328000 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5431040 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 119 | 1791600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7265000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3187 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2341.6 | 54482929
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 313328 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 45 | 560745 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 207827 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 333 | 7697890 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 527000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 472642 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 376784 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1828224 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1329888 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 35100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 739.8 | 15603814 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 404256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 591420 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1509 | 29948918
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1314892 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41690.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1232151 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 238999 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1237680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 4065412.4
Eastern Grid Total |  |  |  |  | 16961.086 | 10194.48 | 215182444.82
Western Grid Total |  |  |  |  | 11731.125 | 5924.8 | 131508562.4
National Grid Total |  |  |  |  | 28692.211 | 16119.28 | 346691007.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-10-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10830.04 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4640 | MW
i) Dhaka area |  |  | 5895.65 |  | MW | i) Khulna area |  |  |  | 1806 | MW
ii) Chattogram area |  |  | 1533.9 |  | MW | ii) Barishal area |  |  |  | 491.6 | MW
iii) Cumilla area |  |  | 1542.49 |  | MW | iii) Rajshahi area |  |  |  | 1472.4 | MW
iv) Mymensingh area |  |  | 1200 |  | MW | iv) Rangpur area |  |  |  | 870 | MW
v) Sylhet area |  |  | 658 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15470.04 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 16 | 17:00 | 72 | Hatirjheel | 86 | 13:00 | 143 | PHP | 12 | 23:00
2 | AKSML | 138.1 | 10:00 | 73 | Ishurdi | 76 | 21:00 | 144 | Pabna | 104 | 18:00
3 | Aftabnagar | 44 | 12:00 | 74 | Jaldhaka | 70 | 18:00 | 145 | Palashbari | 123 | 19:00
4 | Agargaon | 125 | 13:00 | 75 | Jamalpur | 124 | 21:00 | 146 | Panchagarh | 64 | 18:30
5 | Agrabad | 82 | 15:00 | 76 | Jashore | 122 | 18:30 | 147 | Patiya | 30 | 18:00
6 | Amnura | 32 | 18:30 | 77 | Jhenaidah | 84 | 18:30 | 148 | Patnitala | 31 | 21:00
7 | Araihazar | 103 | 03:00 | 78 | Joydebpur | 164 | 16:00 | 149 | Patuakhali | 69.5 | 00:00
8 | Ashuganj | 0.53 | 23:00 | 79 | Joypurhat | 55 | 19:00 | 150 | Payra | 34 | 22:00
9 | Ashuganj-230 | 101 | 23:00 | 80 | Juldah | 21 | 22:00 | 151 | Postogola | 61 | 19:00
10 | BSRM | 197 | 05:00 | 81 | KSRM | 26 | 10:00 | 152 | Pubail | 48 | 12:00
11 | Bagerhat | 95 | 22:00 | 82 | Kabirpur | 269 | 17:00 | 153 | Purbachal | 31 | 18:00
12 | Bajitpur | 85 | 23:00 | 83 | Kachua | 92 | 00:00 | 154 | Purbasadipur | 122 | 18:30
13 | Bakerganj | 15 | 22:00 | 84 | Kaliganj | 40 | 18:30 | 155 | Rahanpur | 36 | 21:00
14 | Bakulia | 103 | 15:00 | 85 | Kallyanpur | 120 | 18:00 | 156 | Rahim | 47 | 16:00
15 | Banani | 66 | 13:00 | 86 | Kalurghat | 43 | 16:00 | 157 | Rajbari | 80 | 18:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 98 | 13:00 | 158 | Rajendrapur | 133 | 15:00
17 | Barapukuria | 56 | 18:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 126 | 14:00
18 | Barguna | 24 | 21:00 | 89 | Kasba | 39 | 21:00 | 160 | Rajshahi-230 | 79 | 01:00
19 | Barishal | 107 | 13:00 | 90 | Kazla | 116 | 19:30 | 161 | Ramganj | 108 | 00:00
20 | Barishal-230 | 110 | 21:00 | 91 | Keranigonj | 92 | 21:00 | 162 | Rampur | 50 | 21:00
21 | Baroaulia | 34 | 17:00 | 92 | Khagrachori | 38 | 18:00 | 163 | Rangamati | 16 | 12:00
22 | Baroirhat | 64 | 18:00 | 93 | Khulna | 62 | 13:00 | 164 | Rangpur | 120 | 18:30
23 | Bashundhara | 208 | 13:00 | 94 | Khulshi | 199 | 13:00 | 165 | Ruppur | 4.2 | 15:00
24 | BashundharaCement | 7 | 09:00 | 95 | Kishoreganj | 139 | 19:00 | 166 | SSM | 6 | 23:00
25 | Beanibazar | 74 | 00:00 | 96 | Kodda | 333 | 16:00 | 167 | Saidpur | 102 | 17:00
26 | Benapole | 71 | 13:00 | 97 | Kulaura | 54 | 21:00 | 168 | Santhia | 36 | 18:00
27 | Bhaluka | 149 | 21:00 | 98 | Kurigram | 60 | 19:00 | 169 | Satkhira | 131 | 21:00
28 | Bhandaria | 54 | 15:00 | 99 | Kushtia | 139 | 12:00 | 170 | Satmasjid | 105 | 18:00
29 | Bhangura | 36 | 20:00 | 100 | Laksam | 36 | 00:00 | 171 | Savar | 224 | 12:00
30 | Bheramara(GK) | 66 | 19:30 | 101 | Lakshmipur | 54 | 23:00 | 172 | SevenRings | 16.7 | 23:00
31 | Bhulta | 213 | 23:00 | 102 | Lalbag | 84 | 13:00 | 173 | ShahCement | 32 | 10:00
32 | Bog-Sherpur | 64 | 19:00 | 103 | Lalmonirhat | 54 | 18:00 | 174 | Shahjadpur | 77 | 19:00
33 | Bogura | 180 | 19:30 | 104 | MI_Cement | 11.6 | 01:00 | 175 | Shahjibazar | 137 | 21:00
34 | Borhanuddin | 72 | 00:00 | 105 | Madanganj | 54 | 00:00 | 176 | Shahmirpur | 58 | 17:00
35 | Brahmanbaria | 136 | 21:00 | 106 | Madaripur | 110 | 22:00 | 177 | Shariatpur | 97 | 18:00
36 | Cantonment | 130 | 13:00 | 107 | Madartek | 83 | 23:00 | 178 | Sherpur | 148 | 18:30
37 | Chandina | 24 | 18:00 | 108 | Madunaghat | 64 | 15:00 | 179 | Shikalbaha | 29 | 18:30
38 | Chandpur | 84 | 22:00 | 109 | Magura | 63 | 21:00 | 180 | Shitalakhya | 83.7 | 12:00
39 | Chandraghona | 33 | 21:00 | 110 | Mahasthangarh | 69 | 21:00 | 181 | Sholosohor | 52 | 15:00
40 | Chapai | 67 | 13:00 | 111 | Maijdee | 41 | 22:00 | 182 | Shomvuganj | 52 | 15:00
41 | Charfasson | 30 | 19:30 | 112 | Manikganj | 146 | 20:00 | 183 | Shyampur | 162 | 11:00
42 | Charsaidpur | 41 | 15:00 | 113 | Maniknagar | 88 | 13:00 | 184 | Siddhirganj | 135 | 12:00
43 | Chauddagram | 72 | 00:00 | 114 | Matarbari | 59 | 21:00 | 185 | Sirajganj | 122 | 19:00
44 | Chhatak | 40 | 00:00 | 115 | Matuail | 78 | 12:00 | 186 | Sitakunda | 33 | 18:00
45 | Chowmuhani | 158 | 21:00 | 116 | Metrorail_Motijheel | 18 | 11:00 | 187 | Sonargaon | 118 | 23:00
46 | Chuadanga | 112 | 21:00 | 117 | Metrorail_Uttara | 8 | 14:00 | 188 | Sreemongol | 77 | 00:00
47 | Coxsbazar | 145 | 01:00 | 118 | Millgate | 99 | 15:00 | 189 | Sreepur | 132 | 16:00
48 | Cumilla(N) | 162 | 18:30 | 119 | Mirpur | 158 | 18:00 | 190 | Srinagar | 51.9 | 21:00
49 | Cumilla(S) | 188 | 13:00 | 120 | Mirsorai | 49 | 10:00 | 191 | Sunamganj | 60 | 00:00
50 | Daganbhuiyan | 36 | 18:30 | 121 | Mirzapur | 47 | 19:30 | 192 | Sylhet | 139 | 18:30
51 | Daudkandi | 133 | 19:30 | 122 | Mithapukur | 59 | 20:00 | 193 | Sylhet_(South) | 63 | 14:00
52 | DhakaUniversity | 102 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 98 | 19:30 | 124 | Mogbazar | 71.2 | 15:00 | 195 | Tangail | 176 | 22:00
54 | Dhanmondi | 120 | 13:00 | 125 | Mongla | 46 | 16:00 | 196 | Taraganj | 29 | 16:00
55 | Dohazari | 113 | 22:00 | 126 | Monirampur | 23 | 22:00 | 197 | Tasnim | 44 | 17:00
56 | Faridpur | 181 | 19:00 | 127 | Motijheel | 55 | 13:00 | 198 | Thakurgaon | 103 | 18:30
57 | Fatullah | 122 | 12:00 | 128 | Muktagacha | 37 | 19:30 | 199 | Tongi | 170 | 13:00
58 | Fenchuganj | 44 | 22:00 | 129 | Munshiganj | 118 | 21:00 | 200 | Ullahpara | 42 | 18:00
59 | Feni | 110 | 18:00 | 130 | Muradnagar | 59 | 21:00 | 201 | Ullon | 34 | 00:00
60 | GPH | 2 | 16:00 | 131 | Mymensingh | 165 | 18:00 | 202 | Uttara | 98 | 13:00
61 | Ghatail | 90 | 19:30 | 132 | Nabinagar | 110 | 09:00 | 203 | UttaraNew | 54 | 14:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 112 | 21:00 | 204 | Zigatola | 86 | 00:00
63 | Ghorashal-230 | 106 | 15:00 | 134 | Narail | 58 | 18:00
64 | Goalpara | 39 | 21:00 | 135 | Narinda | 75 | 14:00
65 | Gollamari | 110 | 23:00 | 136 | Narshingdi | 179 | 02:00
66 | Gopalganj | 109 | 20:00 | 137 | Natore | 128 | 00:00
67 | Gulshan | 118 | 14:00 | 138 | Nawabganj | 51.3 | 21:00
68 | Halishahar | 152.5 | 16:00 | 139 | Netrakona | 131 | 22:00
69 | HaripurSBU | 133 | 09:00 | 140 | New | 82 | 12:00
70 | Hasnabad | 104 | 23:00 | 141 | Niamatpur | 66 | 20:00
71 | Hathazari | 99 | 21:00 | 142 | Noapara | 46 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14950.14 | 4 |  | 14954.32
1:00 | 14428.66 | 0 |  | 14428.66
2:00 | 13614.45 | 0 |  | 13614.45
3:00 | 13240.49 | 0 |  | 13240.49
4:00 | 12863.83 | 0 |  | 12863.83
5:00 | 12573.34 | 0 |  | 12573.34
6:00 | 12346.44 | 0 |  | 12346.44
7:00 | 12630.23 | 0 |  | 12630.23
8:00 | 12887.72 | 0 |  | 12887.72
9:00 | 13313.25 | 10 |  | 13323.25
10:00 | 13390.2 | 10 |  | 13400.2
11:00 | 13973.64 | 10 |  | 13983.64
12:00 | 14637.24 | 139 |  | 14782.24
13:00 | 15047.51 | 114 |  | 15166.51
14:00 | 14489.1 | 117 |  | 14611.1
15:00 | 14714.84 | 438 |  | 15172.84
16:00 | 14965.99 | 151 |  | 15123.99
17:00 | 14749.58 | 86 |  | 14839.58
18:00 | 15543.05 | 1001 |  | 16589.05
19:00 | 15822.69 | 1164 |  | 17038.69
19:30 | 15944.23 | 1114 |  | 17108.23
20:00 | 15961.58 | 1025 |  | 17032.58
21:00 | 16119.28 | 632 |  | 16779.28
22:00 | 15959.78 | 495 |  | 16476.78
23:00 | 15822.56 | 430 |  | 16271.56
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 11-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | -31 | 14 | 28 | 116 | 996 | 356 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | -2 | 1 | 88 | 98 | 1116 | 346
2:00 | 6 | 1 | 90 | 92 | 1132 | 322 |  | Import | 0
3:00 | 19 | 5 | 120 | 90 | 1222 | 322
4:00 | 36 | 12 | 154 | 100 | 1300 | 344 | Ishurdi-Ghorashal Ckt-2 | Export | 966836.36
5:00 | 49 | 22 | 150 | 100 | 1334 | 382
6:00 | 53 | 24 | 140 | 88 | 1358 | 424 |  | Import | 36800
7:00 | 41 | 25 | 92 | 104 | 1220 | 416
8:00 | 60 | 31 | 120 | 90 | 1322 | 450 | Sirajganj-Sreepur Ckt-1 | Export | 756000
9:00 | 105 | 50 | 230 | 110 | 1526 | 554
10:00 | 119 | 54 | 280 | 130 | 1566 | 620 |  | Import | 0
11:00 | 100 | 46 | 254 | 146 | 1456 | 652
12:00 | 79 | 45 | 170 | 168 | 1278 | 652 | Sirajganj-Sreepur Ckt-2 | Export | 760000
13:00 | 49 | 37 | 140 | 140 | 1248 | 630
14:00 | 66 | 41 | 100 | 150 | 1252 | 638 |  | Import | 0
15:00 | 80 | 47 | 244 | 166 | 1288 | 644
16:00 | 56 | 43 | 140 | 156 | 1272 | 584 | Gopalganj-Aminbazar Ckt-1 | Export | 14370000
17:00 | 38 | 41 | 100 | 160 | 1174 | 566
18:00 | 7 | 30 | 44 | 164 | 946 | 456 |  | Import | 0
18:30 | -4 | 22 | 8 | 136 | 930 | 440
19:00 | -11 | 25 | 16 | 136 | 944 | 446 | Gopalganj-Aminbazar Ckt-2 | Export | 14400000
19:30 | -10 | 25 | 36 | 160 | 908 | 442
20:00 | -6 | 26 | 50 | 156 | 922 | 428 |  | Import | 0
21:00 | 2 | 20 | 54 | 144 | 922 | 442
22:00 | 3 | 15 | 80 | 146 | 990 | 418 |  | Total Export | 31252836.36
23:00 | 9 | 20 | 102 | 146 | 1056 | 440 |  | Total Import | 36800
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9558 | 5392.14 | 14950.14 | DAILY GENERATION CURVE
00:30 | 9285 | 5404.4 | 14689.4
01:00 | 9012 | 5416.66 | 14428.66 | 11-10-2026
01:30 | 8739 | 5282.555 | 14021.555
02:00 | 8466 | 5148.45 | 13614.45
02:30 | 8287 | 5140.47 | 13427.47
03:00 | 8108 | 5132.49 | 13240.49
03:30 | 7935.5 | 5116.66 | 13052.16
04:00 | 7763 | 5100.83 | 12863.83
04:30 | 7646.5 | 5072.085 | 12718.585
05:00 | 7530 | 5043.34 | 12573.34
05:30 | 7427.15 | 5032.74 | 12459.89
06:00 | 7324.3 | 5022.14 | 12346.44
06:30 | 7425.005 | 5063.33 | 12488.335
07:00 | 7525.71 | 5104.52 | 12630.23
07:30 | 7524.11 | 5234.865 | 12758.975
08:00 | 7522.51 | 5365.21 | 12887.72
08:30 | 7668.12 | 5432.365 | 13100.485
09:00 | 7813.73 | 5499.52 | 13313.25
09:30 | 7886.67 | 5465.055 | 13351.725
10:00 | 7959.61 | 5430.59 | 13390.2
10:30 | 8193.51 | 5488.41 | 13681.92
11:00 | 8427.41 | 5546.23 | 13973.64
11:30 | 8732.135 | 5573.305 | 14305.44
12:00 | 9036.86 | 5600.38 | 14637.24
12:30 | 9228.6 | 5613.775 | 14842.375
13:00 | 9420.34 | 5627.17 | 15047.51
13:30 | 9430.965 | 5337.34 | 14768.305
14:00 | 9441.59 | 5047.51 | 14489.1
14:30 | 9455.445 | 5146.525 | 14601.97
15:00 | 9469.3 | 5245.54 | 14714.84
15:30 | 9475.655 | 5364.76 | 14840.415
16:00 | 9482.01 | 5483.98 | 14965.99
16:30 | 9455.36 | 5402.425 | 14857.785
17:00 | 9428.71 | 5320.87 | 14749.58
17:30 | 9668.095 | 5478.22 | 15146.315
18:00 | 9907.48 | 5635.57 | 15543.05
18:30 | 9978.48 | 5704.39 | 15682.87
19:00 | 10049.48 | 5773.21 | 15822.69
19:30 | 10165.48 | 5778.75 | 15944.23
20:00 | 10130.48 | 5831.1 | 15961.58
20:30 | 10162.48 | 5877.95 | 16040.43 |  | Executive Engineer
21:00 | 10194.48 | 5924.8 | 16119.28 |  | Network Operation Division
21:30 | 10115.98 | 5923.55 | 16039.53
22:00 | 10037.48 | 5922.3 | 15959.78
22:30 | 9965.98 | 5925.19 | 15891.17
23:00 | 9894.48 | 5928.08 | 15822.56

## En-Curve
QF-LDC-12
Date | 11-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2946 | 1924 | 294 | 0 | 66 | 698.54 | 182 | 5160.6 | 0 | 644 | 3031 | 0 | 0 | 4 | 4 | DAILY ENERGY CURVE
00:30 | 2938.5 | 1916 | 386 | 0 | 65 | 693.95 | 181 | 5122.6 | 11.85 | 576.5 | 2794.5 | 0 | 0 | 3.5 | 2 | 11-10-2026
01:00 | 2931 | 1908 | 478 | 0 | 64 | 689.36 | 180 | 5084.6 | 23.7 | 509 | 2558 | 0 | 0 | 3 | 0
01:30 | 2956.5 | 1923.5 | 478 | 0 | 62 | 694.105 | 180 | 5048.6 | 11.85 | 387.5 | 2277.5 | 0 | 0 | 2 | 0 | Energy Generated | 346.691 |  | MKWHr
02:00 | 2982 | 1939 | 478 | 0 | 60 | 698.85 | 180 | 5012.6 | 0 | 266 | 1997 | 0 | 0 | 1 | 0 | Energy not Served | 5.826 |  | MKWHr
02:30 | 2989 | 1948 | 478 | 0 | 61 | 699.37 | 179.5 | 4944.1 | 0 | 257.5 | 1869 | 0 | 0 | 2 | 0 | Total Energy Requirement | 352.517 |  | MKWHr
03:00 | 2996 | 1957 | 478 | 0 | 62 | 699.89 | 179 | 4875.6 | 0 | 249 | 1741 | 0 | 0 | 3 | 0
03:30 | 2994.5 | 1943.5 | 477.5 | 0 | 61 | 697.46 | 179 | 4878.7 | 0 | 221.5 | 1597 | 0 | 0 | 2 | 0
04:00 | 2993 | 1930 | 477 | 0 | 60 | 695.03 | 179 | 4881.8 | 0 | 194 | 1453 | 0 | 0 | 1 | 0
04:30 | 3006 | 1929.5 | 477.5 | 0 | 59 | 697.285 | 179 | 4881.8 | 0 | 186 | 1300.5 | 0 | 0 | 2 | 0
05:00 | 3019 | 1929 | 478 | 0 | 58 | 699.54 | 179 | 4881.8 | 0 | 178 | 1148 | 0 | 0 | 3 | 0
05:30 | 3046 | 1938.5 | 478 | 0 | 57 | 699.82 | 179 | 4881.8 | 0.27 | 137 | 1041 | 0 | 0 | 1.5 | 0
06:00 | 3073 | 1948 | 478 | 0 | 56 | 700.1 | 179 | 4881.8 | 0.54 | 96 | 934 | 0 | 0 | 0 | 0
06:30 | 3089.5 | 1993.5 | 478.5 | 0 | 54 | 700.855 | 180 | 4913.8 | 58.68 | 103.5 | 912.5 | 0 | 0 | 3.5 | 0
07:00 | 3106 | 2039 | 479 | 0 | 52 | 701.61 | 181 | 4945.8 | 116.82 | 111 | 891 | 0 | 0 | 7 | 0
07:30 | 3065.5 | 2012.75 | 479 | 0 | 54 | 717.35 | 181 | 4945.8 | 221.075 | 128 | 951 | 0 | 0 | 3.5 | 0
08:00 | 3025 | 1986.5 | 479 | 0 | 56 | 733.09 | 181 | 4945.8 | 325.33 | 145 | 1011 | 0 | 0 | 0 | 0
08:30 | 2997.5 | 1934 | 479.5 | 0 | 62 | 719.34 | 181.5 | 5018.3 | 426.845 | 144.5 | 1137 | 0 | 0 | 0 | 5
09:00 | 2970 | 1881.5 | 480 | 0 | 68 | 705.59 | 182 | 5090.8 | 528.36 | 144 | 1263 | 0 | 0 | 0 | 10
09:30 | 2966.5 | 1959 | 479.5 | 0 | 69 | 702.955 | 182 | 5135.7 | 586.07 | 141 | 1130 | 0 | 0 | 0 | 10
10:00 | 2963 | 2036.5 | 479 | 0 | 70 | 700.32 | 182 | 5180.6 | 643.78 | 138 | 997 | 0 | 0 | 0 | 10
10:30 | 2931 | 1997.75 | 479 | 0 | 74.5 | 670.265 | 182 | 5238.2 | 681.455 | 158.75 | 1269 | 0 | 0 | 0 | 10
11:00 | 2899 | 1959 | 479 | 0 | 79 | 640.21 | 182 | 5295.8 | 719.13 | 179.5 | 1541 | 0 | 0 | 0 | 10
11:30 | 2921.5 | 1970.5 | 473 | 0 | 79.5 | 592.12 | 182 | 5295.8 | 730.52 | 212 | 1848.5 | 0 | 0 | 0 | 74.5
12:00 | 2944 | 1982 | 467 | 0 | 80 | 544.03 | 182 | 5295.8 | 741.91 | 244.5 | 2156 | 0 | 0 | 0 | 139
12:30 | 2917.5 | 1974 | 467 | 0 | 81 | 530.69 | 181.5 | 5295.8 | 680.575 | 359.71 | 2354.6 | 0 | 0 | 0 | 126.5
13:00 | 2891 | 1966 | 467 | 0 | 82 | 517.35 | 181 | 5295.8 | 619.24 | 474.92 | 2553.2 | 0 | 0 | 0 | 114
13:30 | 2851 | 1888 | 467 | 0 | 82 | 517.825 | 180 | 5213.5 | 480.26 | 543.17 | 2545.55 | 0 | 0 | 0 | 115.5
14:00 | 2811 | 1810 | 467 | 0 | 82 | 518.3 | 179 | 5131.2 | 341.28 | 611.42 | 2537.9 | 0 | 0 | 0 | 117
14:30 | 2842 | 1870.5 | 467 | 0 | 83 | 519.56 | 178.5 | 5103.1 | 383.59 | 601.92 | 2552.8 | 0 | 0 | 0 | 277.5
15:00 | 2873 | 1931 | 467 | 0 | 84 | 520.82 | 178 | 5075 | 425.9 | 592.42 | 2567.7 | 0 | 0 | 0 | 438
15:30 | 2905 | 1882 | 466.5 | 0 | 84 | 517.41 | 178 | 5145.8 | 327.085 | 616.42 | 2717.2 | 0 | 0 | 1 | 294.5
16:00 | 2937 | 1833 | 466 | 0 | 84 | 514 | 178 | 5216.6 | 228.27 | 640.42 | 2866.7 | 0 | 0 | 2 | 151
16:30 | 2950 | 1812 | 466.5 | 0 | 77 | 515.485 | 178.5 | 5174.9 | 138.31 | 629.21 | 2914.88 | 0 | 0 | 1 | 118.5
17:00 | 2963 | 1791 | 467 | 0 | 70 | 516.97 | 179 | 5133.2 | 48.35 | 618 | 2963.06 | 0 | 0 | 0 | 86
17:30 | 3001 | 1847 | 467 | 0 | 76 | 549.27 | 179.5 | 5214.5 | 24.175 | 683.71 | 3104.16 | 0 | 0 | 0 | 543.5
18:00 | 3039 | 1903 | 467 | 0 | 82 | 581.57 | 180 | 5295.8 | 0 | 749.42 | 3245.26 | 0 | 0 | 0 | 1001
18:30 | 3026.5 | 1863.5 | 427 | 0 | 80 | 640.89 | 180.5 | 5295.8 | 0 | 786.42 | 3382.26 | 0 | 0 | 0 | 1082.5
19:00 | 3014 | 1824 | 387 | 0 | 78 | 700.21 | 181 | 5295.8 | 0 | 823.42 | 3519.26 | 0 | 0 | 0 | 1164
19:30 | 3051 | 1859 | 387 | 0 | 78 | 694.75 | 182 | 5295.8 | 0 | 833.42 | 3563.26 | 0 | 0 | 0 | 1114
20:00 | 3030 | 1846 | 387 | 0 | 74 | 729.1 | 182 | 5295.8 | 0 | 853.42 | 3564.26 | 0 | 0 | 0 | 1025
20:30 | 3044 | 1878 | 410.5 | 0 | 73 | 734.45 | 182 | 5295.8 | 0 | 858.92 | 3563.76 | 0 | 0 | 0 | 828.5
21:00 | 3058 | 1910 | 434 | 0 | 72 | 739.8 | 182 | 5295.8 | 0 | 864.42 | 3563.26 | 0 | 0 | 0 | 632
21:30 | 3047 | 1880.5 | 457.5 | 0 | 72 | 739.65 | 182 | 5295.8 | 0 | 864.42 | 3500.66 | 0 | 0 | 0 | 563.5
22:00 | 3036 | 1851 | 481 | 0 | 72 | 739.5 | 182 | 5295.8 | 0 | 864.42 | 3438.06 | 0 | 0 | 0 | 495
22:30 | 3050.5 | 1836.5 | 474 | 0 | 72 | 746.39 | 182 | 5295.8 | 0 | 862.42 | 3371.56 | 0 | 0 | 0 | 462.5
23:00 | 3065 | 1822 | 467 | 0 | 72 | 753.28 | 182 | 5295.8 | 0 | 860.42 | 3305.06 | 0 | 0 | 0 | 430
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 03:00 | 361 | 12:00 | Madunaghat | 404 | 04:00 | 394 | 11:00
Amtali | 411 | 02:00 | 406 | 11:00 | Meghnaghat | 394 | 03:00 | 371 | 12:00
Ashuganj | 394 | 04:00 | 380 | 12:00 | Mirsorai | 404 | 01:00 | 386 | 12:00
Bhulta | 397 | 03:00 | 369 | 12:00 | Payra | 413 | 04:00 | 408 | 11:00
Bibiana | 387 | 01:00 | 375 | 10:00 | Rahanpur | 408 | 15:00 | 396 | 12:00
BIPTC | 405 | 00:00 | 398 | 22:00 | Rampal | 400 | 05:00 | 387 | 12:00
Bogura | 402 | 15:00 | 386 | 18:30
Gopalganj | 394 | 04:00 | 380 | 12:00
Kaliakoir | 379 | 02:00 | 352 | 12:00
Korerhat | 403 | 03:00 | 383 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 03:00 | 215 | 12:00 | Hasnabad | 230 | 03:00 | 211 | 12:00
AKSML | 239 | 00:00 | 229 | 12:00 | Hathazari | 237 | 00:00 | 230 | 11:00
Aminbazar | 234 | 03:00 | 216 | 12:00 | Ishurdi | 235 | 05:00 | 223 | 12:00
Ashuganj | 232 | 05:00 | 219 | 12:00 | Jhenaidah | 227 | 05:00 | 211 | 21:00
Ashuganj-400 | 232 | 05:00 | 219 | 12:00 | Kachua | 230 | 01:00 | 222 | 12:00
Baghabari | 232 | 03:00 | 223 | 12:00 | Kaliakoir | 236 | 01:00 | 215 | 12:00
Barapukuria | 229 | 03:00 | 218 | 07:00 | Keranigonj | 231 | 03:00 | 212 | 12:00
Barapukuria-230 | 229 | 03:00 | 218 | 07:00 | Khulna(S) | 227 | 04:00 | 216 | 21:00
Barapukuria(N) | 231 | 23:00 | 219 | 18:30 | Korerhat | 230 | 03:00 | 219 | 12:00
Barishal | 228 | 04:00 | 222 | 12:00 | Madunaghat | 240 | 00:00 | 233 | 10:00
Bheramara | 234 | 05:00 | 221 | 12:00 | Madunaghat-400 | 242 | 00:00 | 235 | 11:00
Bhulta | 228 | 04:00 | 210 | 11:00 | Maniknagar | 224 | 03:00 | 208 | 11:00
Bibiana | 223 | 03:00 | 216 | 12:00 | Meghnaghat | 230 | 06:00 | 218 | 12:00
BIPTC | 236 | 05:00 | 221 | 12:00 | Meghnaghat-400 | 229 | 04:00 | 212 | 12:00
Birulia | 235 | 03:00 | 215 | 12:00 | Mirsorai | 236 | 01:00 | 225 | 11:00
Bogura | 239 | 14:00 | 229 | 12:00 | Naogaon | 227 | 15:00 | 212 | 21:00
Bogura-400 | 239 | 14:00 | 229 | 18:30 | Purbasadipur | 243 | 15:00 | 215 | 12:00
Borhanuddin | 229 | 03:00 | 226 | 11:00 | Rajshahi | 231 | 04:00 | 221 | 12:00
BSRM | 230 | 01:00 | 220 | 12:00 | Rampal | 227 | 04:00 | 216 | 21:00
Charfasson | 229 | 00:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 01:00 | 221 | 10:00 | Rampura | 227 | 04:00 | 208 | 11:00
Cumilla(N) | 226 | 06:00 | 213 | 11:00 | Shikalbaha | 242 | 18:30 | 232 | 10:00
Faridpur | 223 | 04:00 | 215 | 12:00 | Shyampur | 229 | 04:00 | 211 | 12:00
Fenchuganj | 226 | 05:00 | 219 | 12:00 | Siddhirganj | 226 | 02:00 | 210 | 12:00
Feni | 227 | 01:00 | 217 | 12:00 | Sirajgonj | 235 | 01:00 | 228 | 12:00
Ghorashal | 230 | 00:00 | 220 | 07:00 | Sreepur | 225 | 04:00 | 215 | 12:00
Ghorashal-230 | 225 | 00:00 | 201 | 12:00 | Tongi | 227 | 04:00 | 203 | 11:00
Gopalganj | 224 | 04:00 | 216 | 12:00
GPH | 237 | 00:00 | 228 | 12:00
Haripur | 227 | 04:00 | 210 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 122 | 11:00 | Madanganj | 133 | 00:00 | 125 | 11:00
Agargaon | 137 | 06:00 | 123 | 12:00 | Madaripur | 131 | 05:00 | 127 | 11:00
Agrabad | 137 | 04:00 | 131 | 10:00 | Madartek | 135 | 04:00 | 122 | 11:00
AKS | 135 | 05:00 | 130 | 11:00 | Madunaghat | 139 | 00:00 | 134 | 10:00
Aminbazar | 134 | 03:00 | 121 | 12:00 | Magura | 135 | 05:00 | 124 | 21:00
Amnura | 132 | 00:00 | 128 | 12:00 | Mahasthangarh | 138 | 15:00 | 130 | 18:30
Araihazar | 129 | 01:00 | 120 | 12:00 | Maijdee | 128 | 00:00 | 123 | 12:00
Ashuganj | 135 | 06:00 | 128 | 12:00 | Manikganj | 130 | 00:00 | 119 | 10:00
Ashuganj-230 | 138 | 03:00 | 132 | 12:00 | Maniknagar | 140 | 05:00 | 127 | 12:00
Bagerhat | 127 | 05:00 | 118 | 22:00 | Matarbari | 128 | 18:00 | 115 | 00:00
Bajitpur | 130 | 05:00 | 121 | 13:00 | Matuail | 135 | 02:00 | 125 | 11:00
Bakerganj | 134 | 17:00 | 130 | 10:00 | Metrorail_Motijheel | 140 | 05:00 | 127 | 12:00
Bakulia | 139 | 18:00 | 130 | 10:00 | Metrorail_Uttara | 134 | 03:00 | 119 | 12:00
Banani | 135 | 05:00 | 120 | 11:00 | Millgate | 138 | 03:00 | 121 | 12:00
Bangabhaban | 140 | 03:00 | 127 | 12:00 | Mirpur | 134 | 03:00 | 119 | 12:00
Barapukuria | 135 | 03:00 | 126 | 18:00 | Mirzapur | 132 | 00:00 | 124 | 09:00
Barguna | 134 | 17:00 | 129 | 12:00 | Mithapukur | 134 | 14:00 | 126 | 18:30
Barishal | 132 | 17:00 | 128 | 12:00 | MI_Cement | 136 | 03:00 | 121 | 12:00
Barishal-230 | 132 | 03:00 | 128 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 138 | 18:00 | 132 | 11:00 | Mogbazar | 138 | 02:00 | 123 | 11:00
Baroirhat | 133 | 19:00 | 127 | 11:00 | Mongla | 125 | 04:00 | 118 | 22:00
Bashundhara | 137 | 01:00 | 120 | 12:00 | Monirampur | 128 | 04:00 | 115 | 21:00
BashundharaCement | 133 | 00:00 | 125 | 11:00 | Motijheel | 140 | 03:00 | 127 | 12:00
Beanibazar | 125 | 06:00 | 118 | 12:00 | Muktagacha | 130 | 00:00 | 124 | 06:00
Benapole | 133 | 04:00 | 115 | 22:00 | Munshiganj | 134 | 02:00 | 124 | 12:00
Bhaluka | 128 | 02:00 | 122 | 12:00 | Muradnagar | 130 | 06:00 | 120 | 12:00
Bhandaria | 128 | 08:00 | 125 | 10:00 | Mymensingh | 133 | 00:00 | 116 | 12:00
Bhangura | 134 | 04:00 | 128 | 12:00 | Nabinagar | 135 | 04:00 | 118 | 12:00
Bheramara | 138 | 04:00 | 131 | 12:00 | Naogaon | 136 | 04:00 | 128 | 12:00
Bheramara(GK) | 137 | 05:00 | 130 | 12:00 | Narail | 135 | 05:00 | 123 | 21:00
Bhulta | 129 | 06:00 | 120 | 11:00 | Narinda | 140 | 05:00 | 127 | 12:00
Bhulta-400 | 131 | 03:00 | 121 | 11:00 | Narshingdi | 136 | 01:00 | 118 | 11:00
Birulia | 138 | 04:00 | 126 | 12:00 | Natore | 134 | 04:00 | 129 | 12:00
Bog-Sherpur | 137 | 14:00 | 131 | 11:00 | Nawabganj | 136 | 04:00 | 124 | 12:00
Bogura | 139 | 14:00 | 133 | 07:00 | Netrakona | 122 | 04:00 | 111 | 19:30
Bogura-230 | 139 | 14:00 | 133 | 12:00 | New | 139 | 00:00 | 121 | 12:00
Brahmanbaria | 134 | 06:00 | 126 | 12:00 | Niamatpur | 134 | 05:00 | 130 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 137 | 03:00 | 122 | 12:00 | Noapara | 130 | 04:00 | 121 | 21:00
Chandina | 131 | 04:00 | 124 | 11:00 | Pabna | 135 | 04:00 | 129 | 18:30
Chandpur | 135 | 00:00 | 129 | 10:00 | Palashbari | 135 | 15:00 | 125 | 18:30
Chandraghona | 139 | 00:00 | 135 | 11:00 | Panchagarh | 139 | 15:00 | 123 | 18:30
Chapai | 133 | 04:00 | 128 | 12:00 | Patiya | 138 | 18:00 | 130 | 10:00
Charsaidpur | 135 | 03:00 | 125 | 11:00 | Patnitala | 134 | 05:00 | 128 | 18:30
Chauddagram | 131 | 06:00 | 124 | 11:00 | Patuakhali | 135 | 17:00 | 129 | 12:00
Chhatak | 121 | 06:00 | 114 | 15:00 | Payra | 135 | 00:00 | 133 | 10:00
Chowmuhani | 129 | 01:00 | 124 | 12:00 | PHP | 133 | 04:00 | 126 | 12:00
Chuadanga | 135 | 04:00 | 123 | 21:00 | Postogola | 137 | 04:00 | 126 | 12:00
Coxsbazar | 121 | 09:00 | 116 | 14:00 | Pubail | 134 | 01:00 | 120 | 10:00
Cumilla(N) | 131 | 05:00 | 123 | 11:00 | Purbachal | 135 | 03:00 | 121 | 11:00
Cumilla(S) | 134 | 02:00 | 123 | 12:00 | Purbasadipur | 137 | 05:00 | 124 | 18:30
Daganbhuiyan | 131 | 01:00 | 125 | 11:00 | Rahanpur | 136 | 04:00 | 132 | 07:00
Daudkandi | 128 | 07:00 | 118 | 12:00 | Rahanpur-400 | 137 | 15:00 | 132 | 12:00
DhakaUniversity | 135 | 03:00 | 122 | 11:00 | Rahim | 135 | 02:00 | 125 | 13:00
Dhamrai | 135 | 03:00 | 120 | 12:00 | Rajbari | 129 | 22:00 | 122 | 21:00
Dhanmondi | 136 | 04:00 | 125.6 | 12:00 | Rajendrapur | 132 | 04:00 | 124 | 12:00
Dohazari | 135 | 18:00 | 125 | 12:00 | Rajshahi | 132 | 14:00 | 126 | 12:00
Faridpur | 130 | 06:00 | 125 | 11:00 | Rajshahi-230 | 133 | 04:00 | 128 | 12:00
Fatullah | 137 | 04:00 | 123 | 11:00 | Ramganj | 130 | 01:00 | 124 | 11:00
Fenchuganj | 132 | 05:00 | 128 | 18:00 | Rampur | 138 | 18:00 | 131 | 11:00
Feni | 133 | 04:00 | 126 | 12:00 | Rampura | 135 | 04:00 | 122 | 11:00
Feni-230 | 131 | 01:00 | 125 | 12:00 | Rangamati | 138 | 18:30 | 133 | 11:00
Ghatail | 129 | 00:00 | 121 | 07:00 | Rangpur | 133 | 03:00 | 123 | 18:30
Ghorashal | 136 | 00:00 | 124 | 07:00 | Ruppur | 137 | 05:00 | 130 | 21:00
Goalpara | 133 | 06:00 | 125 | 12:00 | Saidpur | 137 | 15:00 | 125 | 18:30
Gollamari | 132 | 06:00 | 124 | 21:00 | Santhia | 134 | 04:00 | 128 | 12:00
Gopalganj | 130 | 00:00 | 124 | 11:00 | Satkhira | 128 | 05:00 | 115 | 22:00
Gopalganj-400 | 132 | 04:00 | 128 | 11:00 | Satmasjid | 137 | 04:00 | 123 | 11:00
Gulshan | 134 | 04:00 | 122 | 11:00 | Savar | 132 | 01:00 | 119 | 12:00
Halishahar | 139 | 08:00 | 131 | 12:00 | SevenRings | 137 | 01:00 | 122 | 12:00
Haripur | 136 | 04:00 | 126 | 11:00 | ShahCement | 135 | 03:00 | 125 | 11:00
HaripurSBU | 135 | 04:00 | 126 | 11:00 | Shahjadpur | 135 | 01:00 | 129 | 12:00
Hasnabad | 136 | 01:00 | 124 | 13:00 | Shahjibazar | 133 | 06:00 | 126 | 12:00
Hathazari | 140 | 18:00 | 134 | 11:00 | Shahmirpur | 140 | 18:00 | 132 | 11:00
Hatirjheel | 135 | 04:00 | 122 | 11:00 | Shariatpur | 129 | 04:00 | 125 | 11:00
Ishurdi | 138 | 05:00 | 131 | 12:00 | Sherpur | 135 | 00:00 | 119 | 07:00
Jaldhaka | 132 | 05:00 | 123 | 16:00 | Shikalbaha | 129 | 18:00 | 122 | 12:00
Jamalpur | 137 | 00:00 | 122 | 07:00 | Shikalbaha-230 | 140 | 18:00 | 133 | 10:00
Jashore | 135 | 05:00 | 117 | 22:00 | Shitalakhya | 136 | 03:00 | 121 | 12:00
Jhenaidah | 138 | 05:00 | 127 | 21:00 | Sholosohor | 139 | 00:00 | 132 | 11:00
Jhenaidah-230 | 138 | 05:00 | 126 | 21:00 | Shomvuganj | 124 | 05:00 | 117 | 13:00
Joydebpur | 134 | 01:00 | 117 | 10:00 | Shyampur | 133 | 00:00 | 125 | 14:00
Joypurhat | 134 | 14:00 | 129 | 12:00 | Shyampur-230 | 137 | 03:00 | 124 | 11:00
Juldah | 141 | 18:00 | 131 | 12:00 | Siddhirganj | 136 | 03:00 | 125 | 12:00
Kabirpur | 136 | 03:00 | 117 | 11:00 | Sirajganj | 133 | 04:00 | 126 | 18:30
Kachua | 132 | 01:00 | 127 | 11:00 | Sitakunda | 138 | 00:00 | 133 | 11:00
Kaliakoir | 138 | 01:00 | 128 | 10:00 | Sonargaon | 133 | 00:00 | 123 | 13:00
Kaliganj | 137 | 05:00 | 126 | 21:00 | Sreemongol | 132 | 08:00 | 125 | 21:00
Kallyanpur | 133 | 03:00 | 120 | 12:00 | Sreepur | 135 | 04:00 | 128 | 12:00
Kalurghat | 139 | 00:00 | 9 | 04:00 | Srinagar | 135 | 04:00 | 124 | 12:00
Kamrangirchar | 136 | 05:00 | 118 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 119 | 06:00 | 112 | 14:00
Kasba | 130 | 06:00 | 1 | 01:00 | Sylhet | 124 | 04:00 | 121 | 12:00
Kazla | 140 | 04:00 | 126 | 13:00 | Sylhet_(South) | 126 | 06:00 | 121 | 14:00
Keranigonj | 137 | 04:00 | 124 | 12:00 | Tangail | 128 | 00:00 | 121 | 09:00
Khagrachori | 137 | 06:00 | 132 | 11:00 | Taraganj | 133 | 02:00 | 124 | 18:30
Khulna | 131 | 06:00 | 122 | 21:00 | Tasnim | 133 | 04:00 | 123 | 11:00
Khulna(S) | 132 | 04:00 | 123 | 21:00 | Thakurgaon | 140 | 15:00 | 125 | 18:30
Khulshi | 137 | 18:00 | 130 | 12:00 | TK | 138 | 01:00 | 135 | 00:00
Kishoreganj | 129 | 05:00 | 120 | 20:00 | Tongi | 140 | 04:00 | 125 | 11:00
Kodda | 134 | 18:00 | 118 | 10:00 | Ullahpara | 134 | 04:00 | 128 | 11:00
Korerhat | 135 | 00:00 | 129 | 11:00 | Ullon | 135 | 03:00 | 121 | 12:00
KSRM | 138 | 08:00 | 133 | 10:00 | Uttara | 137 | 01:00 | 121 | 12:00
Kulaura | 132 | 08:00 | 127 | 13:00 | UttaraNew | 134 | 03:00 | 119 | 12:00
Kurigram | 131 | 15:00 | 119 | 07:00 | Zigatola | 137 | 05:00 | 125 | 11:00
Kushtia | 136 | 06:00 | 127 | 21:00
Laksam | 131 | 01:00 | 127 | 10:00
Lakshmipur | 128 | 01:00 | 123 | 12:00
Lalbag | 135 | 01:00 | 123 | 12:00
Lalmonirhat | 130 | 15:00 | 121 | 18:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division