## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-10-2026 | during | 13-10-2026 | during | 13-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 412 | 412 | 412 | 389 | 389 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 319 | 335 | 335 | 322 | 322 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 125 | 133 | 133 | 30 | 143 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9 | 8.5 | 24.75 | 24.75 | 9 | 9 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 47 | 48 | 52.19 | 52.19 | 16 | 47 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 245 | 230 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 149 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 43 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 480 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 535 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 51 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2563 | 2974.92 | 5558.55 | 5528.55 | 2786.42 | 3186.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 19 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 182 | 176 | 176 | 176 | 176 | 176 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 214 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 86 | 90 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 19 | 48 | 24 | 54 | 24 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 34 | 34 | 34 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 88 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 30 | 60 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.67 | 0 | 3.56 | 0 | 3.56 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 90 | 213 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 37 | 88 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 30 | 108 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 20 | 160 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1180 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1060 | 1060 | 1150 | 1150 | 1060 | 1060 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3218.67 | 3819.86 | 4084.52 | 4103.96 | 3484.56 | 3785.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 208 | 205 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 339 | 334 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 342 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 36 | 41.65 | 41.65 | 20 | 20 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 15 | 15 | 52.82 | 52.82 | 15 | 15 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 108 | 107 | 195 | 195 | 108 | 108 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 117 | 140 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 28 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 89 | 163 | 163 | 91 | 91 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 48 | 128 | 200 | 200 | 136 | 136 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 72 | 78 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 17.75 | 17.75 | 13 | 13 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 24 | 100 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 72 | 74 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1654 | 1900.2 | 2364.69 | 2290.69 | 1867.2 | 1857.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-10-2026 | during | 13-10-2026 | during | 13-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 51 | 173 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 77 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 54.17 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 5 | 24 | 22 | 22 | 18 | 18 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 179.37 | 291 | 663.6 | 591.5 | 286.1 | 300
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 40 | 0 | 0 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 135 | 139 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 83 | 83 | 83 | 83 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 390 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1267 | 1291 | 1264 | 1264 | 1254 | 1254
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 469 | 294 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 32 | 32 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 26 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1184 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1756 | 1683.2 | 3294.2 | 3206.2 | 2739.2 | 2651.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1137 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 64 | 48 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 112 | 114 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 290 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 110 | 220 | 110 | GT-11 under shutdown for Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 137 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 301 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2178.39 | 2296.6 | 2378.6 | 2267.6 | 2266.6 | 2155.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.67 | 0 | 53.42 | 0 | 53.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 46 | 45 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 358 | 331 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 18 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8.5 | 51 | 0 | 0 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.62 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 751.76 | 693.67 | 748 | 748 | 680 | 680 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.29 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1482.84 | 1403.67 | 2467.11 | 2246.99 | 2047.73 | 1935.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 50 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 201 | 0 | 190.88 | 0 | 190.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 329 | 228 | 473.88 | 248 | 383.88 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 14628.27 | 15888.45 | 22549.15 | 21747.49 | 17115.69 | 17362.89
Forecast Scenario (13-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15420 |  | 1776.3 |  | 17280
|  |  |  | 1:00 | 14830 |  | 1575.75 |  | 16480
|  |  |  | 2:00 | 14670 |  | 1470.7 |  | 16210
|  |  |  | 3:00 | 14120 |  | 1757.2 |  | 15960
|  |  |  | 4:00 | 13520 |  | 2062.8 |  | 15680
|  |  |  | 5:00 | 13010 |  | 2234.7 |  | 15350
|  |  |  | 6:00 | 12940 |  | 1747.65 |  | 14770
|  |  |  | 7:00 | 13420 |  | 1079.15 |  | 14550
|  |  |  | 8:00 | 13560 |  | 764 |  | 14360
|  |  |  | 9:00 | 13520 |  | 955 |  | 14520
|  |  |  | 10:00 | 13850 |  | 830.85 |  | 14720
|  |  |  | 11:00 | 14220 |  | 735.35 |  | 14990
|  |  |  | 12:00 | 14630 |  | 1069.6 |  | 15750
|  |  |  | 13:00 | 15070 |  | 592.1 |  | 15690
|  |  |  | 14:00 | 15150 |  | 448.85 |  | 15620
|  |  |  | 15:00 | 15430 |  | 668.5 |  | 16130
|  |  |  | 16:00 | 15310 |  | 305.6 |  | 15630
|  |  |  | 17:00 | 15100 |  | 219.65 |  | 15330
|  |  |  | 18:00 | 15530 |  | 162.35 |  | 15700
|  |  |  | 18:30 | 15690 |  | 577.775 |  | 16295
|  |  |  | 19:00 | 15850 |  | 993.2 |  | 16890
|  |  |  | 19:30 | 15890 |  | 1098.25 |  | 17040
|  |  |  | 20:00 | 15960 |  | 849.95 |  | 16850
|  |  |  | 21:00 | 16120 |  | 764 |  | 16920
|  |  |  | 22:00 | 15960 |  | 592.1 |  | 16580
|  |  |  | 23:00 | 15820 |  | 840.4 |  | 16700
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 15750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 764
Probable Maximum Demand at Evening Peak: |  |  | 17040.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16120.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 353.01 MKWHr. |  | 100 | 60 | 90 | 150 | 40 | 100 | 50 | 100 | 74 | 764
*** This report is generated digitally from Operation Information System (OIS) at 08:52 hrs on 13-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-10-2026 | [28 empty] | Date: | 12-10-2026 | [28 empty] | Date: | 12-10-2026 | [28 empty] | Date: | 12-10-2026 | [28 empty] | Date: | 12-10-2026 | [16 empty] | Date: | 12-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 54 | 116 | 126 | 295 | 55 | 55 | 90 | 0 | 0 | 460 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 415 | 107 | 212 | 60 | 0 | 0 | 34 | 43 | 54.36 | 37 | 38 | 0 | 182 | 93 | 2 | 1060 | 18 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 142 | 108 | 0 | 310 | 285 | 44 | 5 | 190 | 20 | 54 | 89 | 158 | 68 | 13 | 81 | 70 | 52.2 | 0 | 30 | 310 | 400 | 0 | 40 | 39 | 156 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 17 | 88 | 0 | 164 | 0 | 0 | 0 | 24 | 9573.48 | 467 | 0 | 34 | 31 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 752.68 | 0 | 45 | 0 | 113 | 113 | 0 | 50 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 91 | 5851.48 | 15424.96 | 105.15
01:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 54 | 115 | 111 | 295 | 55 | 55 | 72 | 0 | 0 | 440 | 0 | 35 | 296 | 0 | 0 | 0 | 143.42 | 9 | 21 | 0 | 410 | 109 | 68 | 59 | 0 | 0 | 34 | 36 | 17 | 37 | 38 | 0 | 182 | 92 | 11 | 930 | 16 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 138 | 108 | 0 | 312 | 285 | 44 | 5 | 201 | 30 | 72 | 90 | 155 | 70 | 13 | 81 | 66 | 52.2 | 0 | 30 | 305 | 400 | 0 | 40 | 39 | 154 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 9080.12 | 470 | 0 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 759.5 | 0 | 47 | 0 | 55 | 113 | 0 | 0 | 38 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 91 | 5752.3 | 14832.42 | 105.14
02:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 54 | 115 | 111 | 295 | 55 | 55 | 72 | 0 | 0 | 440 | 0 | 35 | 298 | 0 | 0 | 0 | 143.42 | 9 | 21 | 0 | 415 | 107 | 68 | 58 | 0 | 0 | 34 | 29 | 17 | 37 | 38 | 0 | 180 | 91 | 15 | 810 | 18 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 133 | 108 | 0 | 317 | 290 | 44 | 5 | 191 | 30 | 89 | 90 | 156 | 73 | 13 | 86 | 64 | 52.2 | 0 | 30 | 310 | 400 | 0 | 40 | 39 | 152 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 8978.12 | 469 | 0 | 33 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 759.98 | 0 | 47 | 0 | 55 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 116 | 220 | 0 | 1170.6 | 300 | 91 | 5687.78 | 14665.9 | 105.13
03:00 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 54 | 115 | 0 | 295 | 55 | 55 | 72 | 0 | 0 | 440 | 0 | 35 | 309 | 0 | 0 | 0 | 51 | 9 | 21 | 0 | 440 | 92 | 68 | 58 | 0 | 1 | 34 | 29 | 17 | 0 | 38 | 0 | 180 | 74 | 21 | 780 | 18 | 0 | 50 | 17 | 95 | 221 | 0 | 0 | 0 | 1160 | 0 | 142 | 108 | 0 | 331 | 305 | 44 | 5 | 202 | 30 | 90 | 90 | 157 | 0 | 13 | 17 | 64 | 16 | 0 | 30 | 305 | 400 | 0 | 40 | 39 | 153 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 17 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 8495 | 469 | 0 | 28 | 24 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1230 | 0 | 0 | 0 | 756.59 | 0 | 47 | 0 | 55 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 1144 | 300 | 91 | 5629.59 | 14124.59 | 105.12
04:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 54 | 110 | 0 | 245 | 40 | 55 | 72 | 0 | 0 | 445 | 0 | 35 | 310 | 0 | 0 | 0 | 34 | 9 | 21 | 0 | 460 | 17 | 68 | 25 | 0 | 3 | 34 | 29 | 17 | 0 | 38 | 0 | 179 | 90 | 26 | 780 | 16 | 0 | 50 | 0 | 93 | 221 | 0 | 0 | 0 | 1160 | 0 | 137 | 108 | 0 | 336 | 310 | 44 | 5 | 202 | 30 | 72 | 90 | 120 | 0 | 13 | 17 | 60 | 0 | 0 | 30 | 305 | 400 | 0 | 40 | 39 | 154 | 0 | 16 | 0 | 84 | 0 | 137 | 0 | 100 | 17 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 8167 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1227 | 0 | 0 | 0 | 754.29 | 0 | 47 | 0 | 55 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 220 | 0 | 1126 | 300 | 54 | 5350.29 | 13517.29 | 105.11
05:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 54 | 86 | 0 | 95 | 0 | 55 | 72 | 0 | 0 | 475 | 0 | 35 | 310 | 0 | 0 | 0 | 34 | 9 | 21 | 0 | 440 | 0 | 68 | 14 | 0 | 2 | 34 | 29 | 17 | 0 | 38 | 0 | 179 | 91 | 26 | 780 | 16 | 0 | 38 | 0 | 90 | 220 | 0 | 0 | 0 | 1160 | 0 | 140 | 108 | 0 | 334 | 305 | 44 | 5 | 200 | 30 | 58 | 90 | 51 | 0 | 13 | 0 | 60 | 0 | 0 | 30 | 305 | 400 | 0 | 40 | 39 | 154 | 0 | 16 | 0 | 84 | 0 | 137 | 0 | 100 | 17 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 7797 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 759.95 | 0 | 47 | 0 | 55 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 276 | 115 | 220 | 0 | 1120 | 300 | 54 | 5215.95 | 13012.95 | 105.1
06:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 40 | 53 | 0 | 95 | 0 | 35 | 72 | 0 | 0 | 495 | 0 | 35 | 300 | 0 | 0 | 0 | 34 | 9 | 21 | 0 | 425 | 0 | 68 | 13 | 0 | 0 | 34 | 29 | 36 | 0 | 38 | 0.04 | 178 | 105 | 26 | 785 | 18 | 0 | 40 | 0 | 87 | 222 | 0 | 0 | 0 | 1150 | 0 | 142 | 108 | 0 | 318 | 295 | 44 | 5 | 195 | 30 | 51 | 91 | 47 | 0 | 13 | 0 | 58 | 0 | 0 | 31 | 310 | 400 | 0 | 40 | 39 | 155 | 0 | 16 | 0 | 84 | 0 | 137 | 0 | 100 | 17 | 59 | 0.05 | 68 | 0 | 0 | 0.09 | 18 | 7753.18 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 754.42 | 0 | 47 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 269 | 115 | 220 | 0 | 1131 | 300 | 54 | 5183.42 | 12936.6 | 105.9
07:00 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 54 | 35 | 53 | 22 | 145 | 4 | 0 | 72 | 0 | 0 | 500 | 0 | 35 | 315 | 0 | 0 | 5 | 51 | 9 | 21 | 0 | 500 | 3 | 68 | 16 | 0 | 0 | 0 | 29 | 36 | 0 | 38 | 0.71 | 179 | 110 | 23 | 785 | 18 | 0 | 42 | 1 | 91 | 220 | 0 | 0 | 0 | 1165 | 5 | 142 | 108 | 0 | 347 | 320 | 44 | 5 | 209 | 30 | 51 | 89 | 59 | 0 | 13 | 0 | 54 | 0.1 | 17 | 31 | 315 | 400 | 0 | 40 | 39 | 158 | 2 | 16 | 0 | 84 | 0 | 138 | 0 | 100 | 17 | 59 | 4 | 68 | 0 | 0.4 | 9.95 | 18 | 8047.16 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 13.86 | 1230 | 0 | 0 | 0 | 758.29 | 0 | 47 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 7.69 | 14 | 25 | 0 | 8.68 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0.8 | 0 | 0 | 34 | 6 | 34 | 0 | 0 | 0 | 0.9 | 35 | 0.08 | 64 | 298 | 115 | 220 | 0 | 1143 | 290 | 54 | 5374.3 | 13421.46 | 105.8
08:00 | 0 | 26 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 35 | 88 | 30 | 215 | 30 | 0 | 72 | 0 | 0 | 485 | 0 | 17 | 300 | 0 | 0 | 14 | 68 | 8.5 | 21 | 0 | 400 | 30 | 68 | 30 | 0 | 0 | 0 | 29 | 36 | 0 | 37 | 1.45 | 181 | 110 | 8 | 785 | 16 | 0 | 47 | 12 | 87 | 220 | 0 | 0 | 0 | 1160 | 7 | 142 | 108 | 0 | 300 | 280 | 44 | 12 | 185 | 27 | 51 | 88 | 96 | 2 | 13 | 30 | 52 | 34 | 39 | 31 | 305 | 400 | 0 | 40 | 39 | 154 | 6 | 16 | 0 | 84 | 0 | 137 | 0 | 100 | 17 | 58 | 0 | 68 | 0 | 1 | 26.59 | 18 | 8125.54 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 36.29 | 1225 | 0 | 0 | 0 | 754.13 | 0 | 47 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 24.37 | 43 | 25 | 0 | 26.18 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 2.32 | 0 | 0 | 35 | 16 | 34 | 0 | 0 | 0 | 1.9 | 92 | 0.24 | 64 | 269 | 115 | 220 | 0 | 1128 | 290 | 54 | 5438.43 | 13563.97 | 105.7
09:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 35 | 88 | 15 | 245 | 30 | 17 | 72 | 0 | 0 | 435 | 0 | 17 | 282 | 0 | 0 | 22 | 51 | 8.5 | 21 | 0 | 420 | 27 | 68 | 30 | 0 | 0 | 0 | 29 | 36 | 0 | 37 | 2.62 | 182 | 110 | 0 | 780 | 16 | 0 | 50 | 17 | 88 | 219 | 0 | 0 | 0 | 1160 | 8 | 138 | 108 | 0 | 290 | 245 | 44 | 15 | 194 | 32 | 51 | 87 | 51 | 43 | 13 | 17 | 64 | 16 | 56 | 31 | 300 | 400 | 0 | 40 | 39 | 142 | 9 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 17 | 58 | 16 | 95 | 0 | 1.6 | 39.59 | 18 | 8077.31 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 1185 | 0 | 0 | 0 | 738.17 | 0 | 46 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 39.56 | 70 | 25 | 0 | 42.18 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 3.88 | 0 | 0 | 35 | 26 | 34 | 0 | 0 | 0 | 4.9 | 144 | 0.41 | 64 | 271 | 114 | 220 | 0 | 1114 | 290 | 54 | 5440.1 | 13517.41 | 105.6
10:00 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 54 | 35 | 52 | 15 | 245 | 49 | 35 | 72 | 0 | 0 | 435 | 0 | 17 | 299 | 0 | 0 | 28 | 51 | 9 | 21 | 0 | 410 | 27 | 68 | 30 | 0 | 0 | 0 | 27 | 36 | 36 | 37 | 3.33 | 182 | 110 | 0 | 930 | 16 | 0 | 50 | 17 | 87 | 218 | 0 | 0 | 0 | 1160 | 8 | 122 | 108 | 0 | 288 | 230 | 44 | 15 | 192 | 32 | 51 | 86 | 46 | 71 | 13 | 17 | 58 | 16 | 67 | 30 | 300 | 398 | 0 | 40 | 39 | 135 | 10 | 16 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 58 | 20.35 | 95 | 0 | 2 | 49.47 | 18 | 8288.15 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 77 | 1182 | 0 | 0 | 0 | 754.44 | 0 | 45 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 50.49 | 89 | 25 | 0 | 55.18 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 4.99 | 0 | 0 | 35 | 33 | 34 | 0 | 0 | 0 | 6.1 | 183 | 0.57 | 64 | 272 | 114 | 220 | 0 | 1116 | 290 | 54 | 5563.77 | 13851.92 | 105.05
11:00 | 0 | 34 | 47 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 54 | 35 | 52 | 15 | 245 | 55 | 35 | 72 | 0 | 0 | 440 | 0 | 35 | 322 | 0 | 0 | 30 | 51 | 9 | 21 | 0 | 430 | 28 | 68 | 30 | 0 | 0 | 0 | 20 | 36 | 37 | 37 | 3.14 | 182 | 110 | 0 | 1060 | 16 | 0 | 50 | 17 | 88 | 215 | 0 | 0 | 0 | 1160 | 10 | 117 | 108 | 0 | 320 | 250 | 44 | 15 | 196 | 33 | 51 | 86 | 48 | 73 | 13 | 17 | 66 | 16 | 73 | 30 | 310 | 395 | 0 | 40 | 39 | 138 | 10 | 16 | 0 | 82 | 0 | 136 | 0 | 100 | 17 | 58 | 22 | 95 | 0 | 2.2 | 54.71 | 18 | 8623.05 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 87 | 1180 | 0 | 0 | 0 | 751.65 | 0 | 45 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 58.4 | 76 | 25 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 5.49 | 0 | 0 | 35 | 36 | 34 | 0 | 0 | 0 | 6.8 | 199 | 0.61 | 64 | 270 | 114 | 220 | 0 | 1128 | 290 | 54 | 5601.81 | 14224.86 | 105.04
12:00 | 0 | 34 | 47 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 43 | 52 | 15 | 245 | 55 | 35 | 72 | 0 | 0 | 535 | 0 | 35 | 321 | 0 | 0 | 32 | 51 | 9 | 21 | 0 | 500 | 30 | 90 | 30 | 0 | 0 | 0 | 19 | 36 | 37 | 37 | 3.67 | 182 | 110 | 0 | 1060 | 20 | 0 | 50 | 19 | 86 | 211 | 0 | 0 | 0 | 1180 | 18 | 117 | 108 | 0 | 339 | 310 | 44 | 15 | 208 | 30 | 51 | 85 | 48 | 72 | 13 | 24 | 72 | 16 | 72 | 30 | 315 | 390 | 0 | 40 | 38 | 141 | 10 | 16 | 0 | 82 | 0 | 135 | 0 | 100 | 17 | 28 | 22 | 51 | 0 | 2.2 | 54.17 | 5 | 8882.04 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 88 | 1184 | 0 | 0 | 0 | 751.76 | 0 | 46 | 0 | 55 | 0 | 0 | 8.5 | 0 | 0 | 58.67 | 108 | 25 | 0 | 66.29 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 5.62 | 0 | 0 | 35 | 36 | 50 | 0 | 0 | 0 | 7 | 201 | 0.39 | 64 | 301 | 112 | 220 | 0 | 1137 | 290 | 54 | 5746.23 | 14628.27 | 105.04
13:00 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 54 | 82 | 60 | 195 | 55 | 35 | 72 | 0 | 0 | 500 | 0 | 35 | 320 | 0 | 0 | 30 | 86 | 9 | 14 | 0 | 445 | 80 | 152 | 30 | 0 | 0 | 0 | 19 | 36 | 37 | 37 | 3.23 | 221 | 110 | 0 | 1060 | 85 | 0 | 50 | 0 | 88 | 211 | 0 | 0 | 0 | 1224 | 0 | 118 | 108 | 0 | 336 | 310 | 44 | 15 | 202 | 31 | 51 | 86 | 75 | 73 | 13 | 34 | 64 | 16 | 68 | 27 | 305 | 387 | 0 | 39 | 38 | 137 | 10 | 16 | 0 | 82 | 0 | 137 | 0 | 100 | 17 | 58 | 21 | 110 | 0 | 1.4 | 51.28 | 18 | 9158.91 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 89 | 1234.2 | 0 | 0 | 0 | 764.48 | 0 | 46 | 0 | 55 | 0 | 0 | 8.5 | 0 | 0 | 54.87 | 103 | 25 | 0 | 60.29 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 5.2 | 0 | 0 | 115 | 35 | 70 | 0 | 0 | 0 | 6.6 | 190 | 0.37 | 48 | 270 | 112 | 220 | 0 | 1170.6 | 290 | 54 | 5915.11 | 15074.02 | 105.03
14:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 54 | 110 | 60 | 195 | 55 | 35 | 72 | 0 | 0 | 485 | 0 | 35 | 317 | 0 | 0 | 26 | 86 | 9 | 21 | 0 | 455 | 99 | 157 | 30 | 0 | 2 | 0 | 19 | 36 | 37 | 37 | 2.99 | 220 | 110 | 0 | 1060 | 98 | 0 | 50 | 6 | 87 | 210 | 0 | 0 | 0 | 1224 | 18 | 122 | 108 | 0 | 334 | 310 | 44 | 15 | 203 | 30 | 51 | 85 | 102 | 71 | 13 | 34 | 72 | 52.2 | 57 | 27 | 315 | 392 | 0 | 38 | 38 | 141 | 10 | 16 | 0 | 81 | 0 | 137 | 0 | 100 | 17 | 58 | 18.37 | 115 | 0 | 1.8 | 44.52 | 18 | 9278.88 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 73 | 1234.2 | 0 | 0 | 0 | 759.75 | 0 | 46 | 0 | 55 | 9 | 0 | 8.5 | 0 | 0 | 48.13 | 88 | 25 | 0 | 49.29 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 4.56 | 0 | 0 | 115 | 30 | 93 | 0 | 0 | 0 | 5.7 | 162 | 0.49 | 32 | 275 | 112 | 220 | 0 | 1170.6 | 290 | 54 | 5872.22 | 15151.1 | 105.02
15:00 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 130 | 60 | 230 | 55 | 35 | 72 | 0 | 0 | 500 | 0 | 35 | 315 | 0 | 0 | 20 | 123 | 9 | 20 | 0 | 500 | 107 | 158 | 40 | 0 | 4 | 0 | 18 | 36 | 37 | 38 | 1.98 | 215 | 110 | 0 | 1060 | 134 | 0 | 50 | 25.5 | 88 | 210 | 0 | 0 | 0 | 1224 | 9 | 130 | 108 | 0 | 343 | 320 | 44 | 15 | 207 | 29 | 51 | 85 | 113 | 71 | 13 | 70 | 72 | 52.2 | 43 | 27 | 315 | 387 | 0 | 38 | 38 | 147 | 7 | 16 | 0 | 81 | 0 | 138 | 0 | 99 | 17 | 58 | 13.47 | 115 | 0 | 1.3 | 32.91 | 18 | 9546.36 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 44 | 1234.2 | 0 | 0 | 0 | 753.04 | 0 | 45 | 0 | 113 | 81 | 0 | 8.5 | 0 | 0 | 34.07 | 65 | 18 | 0 | 34.27 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 3.26 | 0 | 0 | 115 | 23 | 107 | 0 | 0 | 0 | 4.2 | 124 | 0.34 | 32 | 294 | 112 | 220 | 0 | 1170.6 | 290 | 54 | 5880.48 | 15426.84 | 105.02
16:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 141 | 60 | 230 | 55 | 35 | 144 | 0 | 0 | 515 | 0 | 35 | 311 | 0 | 0 | 11 | 123 | 9 | 20 | 0 | 530 | 109 | 158 | 48 | 0 | 2 | 0 | 18 | 36 | 37 | 38 | 1.15 | 127 | 110 | 0 | 1060 | 162 | 0 | 50 | 25.5 | 88 | 211 | 0 | 0 | 0 | 1224 | 8 | 130 | 108 | 0 | 349 | 335 | 44 | 15 | 211 | 23 | 51 | 85 | 103 | 71 | 13 | 70 | 70 | 52.2 | 22 | 27 | 320 | 388 | 0 | 39 | 38 | 149 | 4 | 16 | 0 | 81 | 0 | 137 | 0 | 99 | 17 | 49 | 7.41 | 115 | 0 | 0.7 | 16.83 | 0 | 9557.79 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 22 | 1234.2 | 0 | 0 | 0 | 760.2 | 0 | 45 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 19.39 | 36 | 18 | 0 | 18.25 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.6 | 0 | 0 | 115 | 13 | 106 | 0 | 0 | 0 | 2.5 | 69 | 0.21 | 32 | 294 | 106 | 220 | 0 | 1170.6 | 290 | 54 | 5756.45 | 15314.24 | 105.02
17:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 54 | 149 | 86 | 230 | 55 | 35 | 162 | 0 | 0 | 505 | 0 | 55 | 317 | 0 | 0 | 2 | 143.42 | 8.5 | 20 | 0 | 425 | 107 | 208 | 56 | 0 | 0 | 0 | 18 | 54.36 | 37 | 38 | 0.1 | 128 | 110 | 0 | 1060 | 53 | 0 | 50 | 25.5 | 88 | 212 | 0 | 0 | 0 | 1224 | 0 | 124 | 108 | 0 | 325 | 300 | 44 | 15 | 195 | 26 | 40 | 86 | 102 | 71 | 13 | 95 | 68 | 52.2 | 4 | 27 | 320 | 400 | 0 | 39 | 38 | 150 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 99 | 17 | 58 | 1.46 | 124 | 0 | 0.1 | 3.15 | 2 | 9432.79 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 7 | 1234.2 | 0 | 0 | 0 | 756.91 | 0 | 45 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 3.75 | 8 | 20 | 0 | 3.53 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0.24 | 0 | 0 | 115 | 3 | 113 | 0 | 0 | 0 | 0.6 | 13 | 0.04 | 32 | 272 | 108 | 220 | 0 | 1170.6 | 290 | 100 | 5663.37 | 15096.16 | 105.01
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 17 | 54 | 149 | 126 | 230 | 55 | 55 | 162 | 0 | 0 | 460 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 510 | 109 | 213 | 43 | 0 | 0 | 22 | 41 | 54.36 | 76 | 88 | 0 | 174 | 110 | 0 | 1060 | 77 | 0 | 50 | 25.5 | 88 | 211 | 0 | 0 | 0 | 1224 | 0 | 127 | 107 | 0 | 347 | 320 | 44 | 15 | 210 | 32 | 50 | 87 | 104 | 73 | 13 | 85 | 82 | 52.2 | 0 | 27 | 310 | 396 | 0 | 40 | 39 | 151 | 0 | 16 | 0 | 82 | 0 | 137 | 0 | 100 | 3 | 58 | 0 | 135 | 0 | 0 | 0 | 22 | 9851.98 | 469 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 751.69 | 0 | 45 | 0 | 113 | 113 | 0 | 8.5 | 18 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 297 | 108 | 220 | 0 | 1170.6 | 300 | 100 | 5681.99 | 15533.97 | 105.01
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 54 | 149 | 125 | 230 | 55 | 55 | 162 | 0 | 0 | 510 | 0 | 55 | 318 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 510 | 107 | 213 | 56 | 0 | 0 | 51 | 48 | 54.36 | 88 | 88 | 0 | 175 | 110 | 0 | 1060 | 160 | 0 | 50 | 25.5 | 90 | 213 | 0 | 0 | 0 | 1224 | 0 | 134 | 107 | 0 | 335 | 305 | 44 | 15 | 203 | 32 | 106 | 89 | 114 | 73 | 13 | 95 | 78 | 52.2 | 0 | 27 | 320 | 400 | 0 | 40 | 40 | 152 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 17 | 77 | 0 | 162 | 0 | 0 | 0 | 24 | 10217.98 | 290 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 753.73 | 0 | 45 | 0 | 113 | 113 | 0 | 45 | 39 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 296 | 114 | 220 | 0 | 1170.6 | 300 | 137 | 5635.53 | 15853.51 | 105
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 149 | 125 | 230 | 55 | 55 | 162 | 0 | 0 | 500 | 0 | 55 | 319 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 480 | 108 | 213 | 60 | 0 | 0 | 51 | 48 | 54.36 | 88 | 88 | 0 | 176 | 110 | 0 | 1060 | 160 | 0 | 50 | 25.5 | 90 | 214 | 0 | 0 | 0 | 1224 | 0 | 140 | 107 | 0 | 334 | 342 | 44 | 15 | 205 | 36 | 115 | 89 | 128 | 74 | 13 | 100 | 78 | 52.2 | 0 | 28 | 320 | 400 | 0 | 40 | 40 | 153 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 17 | 77 | 0 | 173 | 0 | 0 | 0 | 24 | 10276.98 | 294 | 0 | 24 | 26 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 693.67 | 0 | 45 | 0 | 113 | 113 | 0 | 51 | 39 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 137 | 5611.47 | 15888.45
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 54 | 149 | 125 | 230 | 55 | 55 | 162 | 0 | 0 | 505 | 0 | 55 | 319 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 450 | 107 | 213 | 61 | 0 | 0 | 51 | 48 | 54.36 | 88 | 88 | 0 | 221 | 110 | 0 | 1060 | 162 | 0 | 50 | 25.5 | 90 | 215 | 0 | 0 | 0 | 1224 | 0 | 139 | 108 | 0 | 327 | 342 | 44 | 15 | 200 | 33 | 115 | 88 | 122 | 73 | 13 | 100 | 76 | 52.2 | 0 | 28 | 315 | 400 | 0 | 40 | 40 | 153 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 77 | 0 | 173 | 0 | 0 | 0 | 24 | 10267.98 | 293 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 671.57 | 0 | 45 | 0 | 113 | 113 | 0 | 51 | 40 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 137 | 5599.37 | 15867.35 | 105
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 149 | 125 | 230 | 55 | 55 | 162 | 0 | 0 | 500 | 0 | 55 | 319 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 490 | 109 | 213 | 60 | 0 | 0 | 51 | 48 | 54.36 | 100 | 88 | 0 | 221 | 110 | 5 | 1060 | 16 | 0 | 50 | 25.5 | 90 | 217 | 0 | 0 | 0 | 1224 | 0 | 135 | 108 | 0 | 334 | 342 | 44 | 15 | 203 | 33 | 115 | 88 | 135 | 74 | 13 | 95 | 74 | 52.2 | 0 | 29 | 310 | 400 | 0 | 40 | 40 | 156 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 17 | 77 | 0 | 173 | 0 | 0 | 0 | 24 | 10188.98 | 293 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 760 | 0 | 45 | 0 | 95 | 113 | 0 | 51 | 39 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 137 | 5659.8 | 15848.78 | 104.99
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 54 | 149 | 126 | 230 | 55 | 55 | 162 | 0 | 0 | 505 | 0 | 55 | 319 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 490 | 107 | 212 | 59 | 0 | 0 | 51 | 48 | 54.36 | 100 | 88 | 0 | 222 | 110 | 2 | 1060 | 16 | 0 | 50 | 25.5 | 90 | 218 | 0 | 0 | 0 | 1224 | 0 | 130 | 108 | 0 | 338 | 342 | 44 | 15 | 205 | 33 | 109 | 88 | 138 | 74 | 13 | 99 | 72 | 52.2 | 0 | 21 | 320 | 400 | 0 | 40 | 40 | 156 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 100 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 10154.98 | 293 | 0 | 24 | 30 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 759.42 | 0 | 45 | 0 | 113 | 113 | 0 | 51 | 39 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 90 | 5631.22 | 15786.2 | 104.99
23:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 17 | 54 | 149 | 126 | 230 | 55 | 55 | 108 | 0 | 0 | 500 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 510 | 107 | 212 | 52 | 0 | 0 | 51 | 48 | 54.36 | 100 | 88 | 0 | 222 | 110 | 2 | 1060 | 58 | 0 | 50 | 25.5 | 90 | 219 | 0 | 0 | 0 | 1170 | 0 | 140 | 108 | 0 | 338 | 342 | 44 | 15 | 207 | 33 | 109 | 88 | 137 | 74 | 13 | 99 | 72 | 52.2 | 0 | 22 | 310 | 400 | 0 | 40 | 40 | 156 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 27 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 10107.98 | 334 | 0 | 24 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 756.12 | 0 | 45 | 0 | 113 | 113 | 0 | 51 | 31 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 114 | 220 | 0 | 1170.6 | 300 | 90 | 5655.92 | 15763.9 | 104.98
Total KWH | 0 | 1658880 | 782400 | 0 | 0 | 0 | 0 | 0 | 9316800 | 0 | 0 | 777960 | 1187280 | 2667888 | 1535040 | 5425407 | 1129294 | 933598 | 2354400 | 0 | 0 | 11678313 | 0 | 929714 | 7515776 | 0 | 0 | 217275 | 2389200 | 209400 | 480960 | 0 | 11076363.64 | 1806545 | 3116291 | 991680 | 0 | 12960 | 506458 | 747185 | 919561 | 912960 | 1166400 | 24957 | 4522096 | 2566800 | 167520 | 22909090.91 | 1393382 | 0 | 1192320 | 403124.4 | 2218872 | 5158312 | 0 | 0 | 0 | 28532724 | 75330 | 3189890 | 2626182 | 0 | 8264600 | 7458000 | 1033924 | 305280 | 4941000 | 735552 | 1674240 | 2098170 | 2507520 | 1291920 | 320180 | 1318980 | 1623360 | 798864 | 511018 | 681696 | 7512000 | 9562400 | 0 | 943000 | 917760 | 3609327.27 | 84710 | 400464 | 0 | 1979520 | 0 | 3144000 | 0 | 2404410 | 441000 | 1468800 | 142984 | 2560800 | 0 | 13650 | 378500 | 443280 | 218997498.22 | 10403636 | 0 | 248640 | 227840 | 0 | 0 | 0 | 0 | 0 | 1635984 | 575280 | 29360000 | 0 | 0 | 0 | 17940701 | 0 | 1111707 | 0 | 1890048 | 1816128 | 0 | 340912 | 232319 | 0 | 396688 | 732800 | 480393 | 0 | 426000 | 0 | 0 | 0 | 0 | 0 | 0 | 8427200 | 0 | 37500 | 0 | 0 | 1978033 | 259151 | 1843056 | 0 | 0 | 0 | 46072.32 | 1406880 | 3825 | 1354560 | 7026000 | 2724000 | 5437700 | 0 | 27905454 | 7156363.64 | 1842000 | 135266870.96 | 354264369.18

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14628.27 | MW | 12:00 Hr. | Energy Generated |  |  | 354.2644 |  | MKWHr.
| Day Peak Demand |  |  | 14767.27 | MW | 12:00 Hr. | Energy Unserverd |  |  | 10.905 |  | MKWHr.
| Evening Peak Generation |  |  | 15888.45 | MW | 19:30 Hr. | Energy Demand |  |  | 365.1694 |  | MKWHr.
| Evening Peak Demand |  |  | 17807.45 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.9 |  | °C
| Minimum Generation of the Day |  |  | 12936.6 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 862.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 15888.45 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 8.634 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.2776 | 0 | 21.7711 | 0 | 0 | 0.21727 | 0 | 0 | 62.2659 | Gas | 120.4481 | Gas | 416069324.4172
| Chattogram Zone |  |  | 5.3258 | 51.4418 | 17.9416 | 0 | 4.5221 | 0.10029 | 0 | 0.01296 | 79.3446 | Coal | 122.8896 | Coal | 889002240.5931
| Cumilla Zone |  |  | 27.7829 | 0 | 11.4631 | 0 | 0 | 0.51102 | 1.6234 | 0 | 41.3804 | HFO | 71.0912 | HFO | 1466929315.122
| Mymensingh Zone |  |  | 0 | 0 | 4.9139 | 0 | 0 | 0.53513 | 0 | 0 | 5.449 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.4729 | 0 | 0 | 0 | 0 | 0.08471 | 0 | 0 | 30.5576 | Hydro | 4.5221 | Hydro | 452209.6
| Khulna Zone |  |  | 0 | 29.36 | 2.1125 | 0 | 0 | 0.57528 | 10.4036 | 0 | 42.4514 | Solar | 5.3326 | Solar | 85939394.8924
| Barishal Zone |  |  | 8.1617 | 42.0878 | 3.1966 | 0 | 0 | 0.003825 | 0 | 0 | 53.4499 | Import | 29.9677 | Import | 200120289.45
| Rajshahi Zone |  |  | 8.4272 | 0 | 5.8715 | 0 | 0 | 1.593 | 17.9407 | 0 | 33.8324 | Wind | 0.01296 | Wind | 192326.4
| Rangpur Zone |  |  | 0 | 0 | 3.8211 | 0 | 0 | 1.7121 | 0 | 0 | 5.5332
| Total |  |  | 120.4481 | 122.8896 | 71.0912 | 0 | 4.5221 | 5.3326 | 29.9677 | 0.01296 | 354.2644
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416069324.4172 |  | Hydro | 452209.6
|  |  |  | Coal | 889002240.5931 |  | Solar | 85939394.8924
|  |  |  | HFO | 1466929315.122 |  | Import | 200120289.45
|  |  |  | HSD | 0 |  | Wind | 192326.4
[5 empty] | Total: | 305,87,05,100 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 150454.55 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.4036 | Peak Hr Flow | 294.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31682436.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.9407 | Peak Hr Flow | 693.67 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 814 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6234 | Peak Hr Flow | 78.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1837 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 29.9677 | Peak Hr Flow | 1065.67 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 410 |  | 6286
|  |  |  | Chattogram |  | 176 |  | 1717
|  |  |  | Cumilla |  | 172 |  | 1664
|  |  |  | Mymensingh |  | 233 |  | 1397
|  |  |  | Sylhet |  | 138 |  | 776
|  |  |  | Khulna |  | 261 |  | 1993
|  |  |  | Barishal |  | 96 |  | 527
|  |  |  | Rajshahi |  | 198 |  | 1655
|  |  |  | Rangpur |  | 152 |  | 1036
|  |  |  | Total |  | 1836 |  | 17051
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-2 |  |  | 40
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 403.5
|  |  |  | Total Unavailable Capacity |  |  |  | 703.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 17:33 | Panchagarh 132/33kV S/S T-1(407T) LT Scheduled S/D Due to For Annual Maintenance Work
| 08:01 | 17:32 | Panchagarh 132/33kV S/S T-1(407T) HT Scheduled S/D Due to For Annual Maintenance Work
| 08:15 | 17:36 | Bog-Sherpur 132/33kV S/S Main Bus-1 Scheduled S/D Due to Annual Maintenance
| 08:21 | 09:16 | Kushtia 132/33kV S/S T-3 LT Project Work S/D
| 08:22 | 09:10 | Kushtia 132/33kV S/S T-3 HT Project Work S/D
|  | 08:32 | TK chemical S/S 50/75 MVA T-1(405T) LT is restored.
| 08:45 | 16:36 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Annual
Maintenance
| 08:46 | 16:31 | Sylhet_(South) 132/33kV S/S Sylhet (S)-Biyanibazar 132KV Ckt-1 Scheduled S/D Due to
Annual Maintenance Work
|  | 09:09 | Ghorashal 230kV S/S TARFO-2 LT is restored.
| 09:14 | 17:44 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| 09:48 | 13:45 | Kachua 230/132/33kV S/S ATR-1 LT Project Work S/D Due to scada integration
| 09:51 | 13:45 | Kachua 230/132/33kV S/S ATR-1 HT Project Work S/D Due to scada integration
| 10:02 | 16:18 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Project Work S/D Due to
Project Work
| 10:02 | 16:22 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Project Work S/D Due to
Project Work
| 10:45 | 12:42 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Red maintenance by PBS L-22 | [7 empty] | 120.0MW load
interrup.
| 10:53 | 17:36 | Korerhat 400/230/132kV S/S BSRM-1 (D17) Project Work S/D Due to DFDR WORK
| 10:53 | 17:36 | Korerhat 400/230/132kV S/S BSRM-1 (D17) Project Work S/D Due to DFDR WORK
| 11:09 | 11:18 | Sherpur 132/33kV S/S Transformer- 02 LT Tripped showing IDMT-O/C relays Due to SPBD -02 | [7 empty] | 27.0MW load
|  |  | 33 KV feeder Fault. | [7 empty] | interrup.
| 11:09 | 11:19 | Sherpur 132/33kV S/S Transformer- 01 LT Tripped showing IDMT-O/C relays Due to SPBD -02 | [7 empty] | 26.0MW load
|  |  | 33 KV feeder Fault. | [7 empty] | interrup.
| 11:09 | 11:19 | Sherpur 132/33kV S/S Transformer- 01 HT Tripped showing IDMT-O/C relays Due to SPBD -02 | [7 empty] | 27.0MW load
|  |  | 33 KV feeder Fault. | [7 empty] | interrup.
| 12:09 | 13:14 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Hot spot | [7 empty] | 35.0MW load
interrup.
| 12:09 | 13:14 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Hot spot | [7 empty] | 35.0MW load
interrup.
|  | 12:23 | Bogura 230/132kV S/S 132KV Main 1 is restored.
|  | 12:32 | Hasnabad 230/132kV S/S AUTO TR-3 LT is restored.
|  | 12:32 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 12:42 | Kodda 132/33kV S/S Tr-5 (446T) LT is restored.
| 12:45 |  | Bogura 230/132kV S/S 132KV Main 2 Project Work S/D Due to 132kV Shabgram Bus Loop
Connection.
|  | 12:56 | Bogura South-Confidence 132 kV Ckt-2 is restored.
| 13:03 | 15:22 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Maitenance work 132 kv end.
| 13:03 | 15:22 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Maintenance work 132 kv end.
| 13:47 | 18:09 | Kachua 230/132/33kV S/S ATR-2 HT Project Work S/D Due to SCADA integration
| 13:48 | 18:10 | Kachua 230/132/33kV S/S ATR-2 LT Project Work S/D Due to SCADA integration
| 14:41 | 21:27 | Chowmuhani 230/132/33kV S/S Korerhat-04 Project Work S/D Due to Shutdown taken by
Korerhat ss
| 14:46 | 21:27 | Korerhat 400/230/132kV S/S Chowmuhani-4 (D09) Project Work S/D Due to DFDR
| 15:22 | 17:40 | Barapukuria S/S-P/S 230 kV Ckt-2 Forced S/D from Barapukuria 230/132/33kV end Due to LA
change for R-phase
|  | 15:25 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
|  | 16:33 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
|  | 16:34 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 17:05 | 18:03 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to 33 kv bus red ho removing | [7 empty] | 9.0MW load
interrup.
| 17:07 | 18:04 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to 33 kv bus red ho removing | [7 empty] | 9.0MW load
interrup.
|  | 17:09 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation: 15888 MW.
| 00:36 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 06:30 | 07:49 | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to 33kV N5 Feeder Red hot | [7 empty] | 15.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 06:31 | 07:48 | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to 33kV N5 Feeder Red hot | [7 empty] | 15.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:07 |  | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
| 07:08 |  | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance
| 07:30 |  | Bog-Sherpur 132/33kV S/S Main Bus-2 Scheduled S/D Due to Annual Maintenance
| 07:30 |  | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to Redhot maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9316800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1129294 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 319 | 7515776 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 777960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1535040 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 933598 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 929714 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8.5 | 209400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 480960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 782400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 230 | 5425407 | Fuel Shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2667888 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1658880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2354400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 217275 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1187280 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 11076363.64 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 500 | 11678313 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2389200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2974.92 | 62265948.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 403124.4 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 75330 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1192320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 176 | 4522096 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5158312 | ps availability is less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 2218872 | Machine Problem
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 747185 | Fuel Shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 506458 | ps availability is less
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 912960 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 167520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 60 | 991680 | Machine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24957 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 213 | 3116291 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 919561 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2566800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1166400 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 1806545 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 160 | 1393382 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28532724 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1060 | 22909090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3819.86 | 79344568.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 205 | 4941000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 334 | 8264600 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 342 | 7458000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 735552 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 15 | 305280 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 107 | 2626182 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1033924 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 3189890 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 681696 | ps availability is less
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2098170 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 128 | 2507520 | Machine Problem
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1623360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 798864 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 320180 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1318980 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 1291920 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1674240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 511018 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1900.2 | 41380376
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 142984 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 173 | 2560800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1468800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 378500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 443280 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 441000 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 674.21 | 291 | 5449014
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 84710 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 943000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 917760 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3609327.27 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3144000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1979520 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2404410 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 400464 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7512000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under Maintenance
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9562400 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1291 | 30557591.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 294 | 10403636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 248640 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 26 | 227840 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1635984 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 575280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29360000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1683.2 | 42451380
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 27905454 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 1354560 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 114 | 2724000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7156363.64 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5437700 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1842000 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7026000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3825 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2296.6 | 53449902.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 396688 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 45 | 1111707 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 232319 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 331 | 8427200 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 480393 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 340912 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1816128 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1890048 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 37500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 693.67 | 17940701 | Machine Problem
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 426000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 732800 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1403.67 | 33832396
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1843056 | Fuel Shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46072.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1978033 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 259151 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1406880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 5533192.32
Eastern Grid Total |  |  |  |  | 16961.086 | 10276.98 | 218997498.22
Western Grid Total |  |  |  |  | 11731.125 | 5611.47 | 135266870.96
National Grid Total |  |  |  |  | 28692.211 | 15888.45 | 354264369.18
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-10-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10710.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4503 | MW
i) Dhaka area |  |  | 5875.52 |  | MW | i) Khulna area |  |  |  | 1731.5 | MW
ii) Chattogram area |  |  | 1541.2 |  | MW | ii) Barishal area |  |  |  | 430.9 | MW
iii) Cumilla area |  |  | 1491.53 |  | MW | iii) Rajshahi area |  |  |  | 1456.6 | MW
iv) Mymensingh area |  |  | 1164 |  | MW | iv) Rangpur area |  |  |  | 884 | MW
v) Sylhet area |  |  | 638 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15213.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 19:00 | 72 | Hatirjheel | 90 | 15:00 | 143 | PHP | 13 | 03:00
2 | AKSML | 155.7 | 03:00 | 73 | Ishurdi | 75 | 15:00 | 144 | Pabna | 94 | 17:00
3 | Aftabnagar | 46 | 13:00 | 74 | Jaldhaka | 64 | 21:00 | 145 | Palashbari | 114 | 23:00
4 | Agargaon | 136 | 13:00 | 75 | Jamalpur | 126 | 18:30 | 146 | Panchagarh | 63 | 18:00
5 | Agrabad | 84 | 16:00 | 76 | Jashore | 127 | 18:30 | 147 | Patiya | 30 | 00:00
6 | Amnura | 33 | 21:00 | 77 | Jhenaidah | 89 | 18:30 | 148 | Patnitala | 31 | 18:30
7 | Araihazar | 107 | 23:00 | 78 | Joydebpur | 169 | 19:30 | 149 | Patuakhali | 70 | 18:30
8 | Ashuganj | 0.58 | 23:00 | 79 | Joypurhat | 57 | 21:00 | 150 | Payra | 36 | 21:00
9 | Ashuganj-230 | 105 | 00:00 | 80 | Juldah | 21 | 16:00 | 151 | Postogola | 63 | 19:00
10 | BSRM | 200 | 17:00 | 81 | KSRM | 36 | 13:00 | 152 | Pubail | 49 | 11:00
11 | Bagerhat | 83 | 02:00 | 82 | Kabirpur | 278 | 16:00 | 153 | Purbachal | 32 | 18:00
12 | Bajitpur | 85 | 00:00 | 83 | Kachua | 88 | 03:00 | 154 | Purbasadipur | 114 | 20:00
13 | Bakerganj | 14.2 | 03:00 | 84 | Kaliganj | 39 | 19:00 | 155 | Rahanpur | 33 | 18:00
14 | Bakulia | 107 | 18:00 | 85 | Kallyanpur | 120 | 00:00 | 156 | Rahim | 51 | 07:00
15 | Banani | 70 | 13:00 | 86 | Kalurghat | 43 | 10:00 | 157 | Rajbari | 83 | 18:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 101 | 13:00 | 158 | Rajendrapur | 134 | 18:00
17 | Barapukuria | 60 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 116 | 00:00
18 | Barguna | 22 | 02:00 | 89 | Kasba | 36 | 23:00 | 160 | Rajshahi-230 | 98 | 13:00
19 | Barishal | 107 | 12:00 | 90 | Kazla | 129 | 12:00 | 161 | Ramganj | 100 | 02:00
20 | Barishal-230 | 98 | 22:00 | 91 | Keranigonj | 94 | 21:00 | 162 | Rampur | 80 | 09:00
21 | Baroaulia | 45 | 14:00 | 92 | Khagrachori | 36 | 18:00 | 163 | Rangamati | 20 | 18:00
22 | Baroirhat | 60 | 00:00 | 93 | Khulna | 65 | 13:00 | 164 | Rangpur | 122 | 19:00
23 | Bashundhara | 217 | 13:00 | 94 | Khulshi | 203 | 15:00 | 165 | Ruppur | 4.6 | 15:00
24 | BashundharaCement | 7 | 01:00 | 95 | Kishoreganj | 144 | 20:00 | 166 | SSM | 11 | 03:00
25 | Beanibazar | 74 | 23:00 | 96 | Kodda | 314 | 17:00 | 167 | Saidpur | 95 | 14:00
26 | Benapole | 65 | 22:00 | 97 | Kulaura | 54 | 18:30 | 168 | Santhia | 34 | 18:00
27 | Bhaluka | 144 | 16:00 | 98 | Kurigram | 60 | 07:00 | 169 | Satkhira | 126 | 00:00
28 | Bhandaria | 52 | 00:00 | 99 | Kushtia | 139 | 12:00 | 170 | Satmasjid | 111 | 14:00
29 | Bhangura | 34 | 13:00 | 100 | Laksam | 38 | 18:00 | 171 | Savar | 236 | 16:00
30 | Bheramara(GK) | 61 | 21:00 | 101 | Lakshmipur | 55 | 19:30 | 172 | SevenRings | 21.47 | 12:00
31 | Bhulta | 219 | 00:00 | 102 | Lalbag | 86 | 13:00 | 173 | ShahCement | 30 | 12:00
32 | Bog-Sherpur | 62 | 00:00 | 103 | Lalmonirhat | 54 | 18:00 | 174 | Shahjadpur | 84 | 18:30
33 | Bogura | 189 | 18:30 | 104 | MI_Cement | 10.2 | 00:00 | 175 | Shahjibazar | 138 | 00:00
34 | Borhanuddin | 70 | 02:00 | 105 | Madanganj | 59 | 21:00 | 176 | Shahmirpur | 55 | 17:00
35 | Brahmanbaria | 136 | 20:00 | 106 | Madaripur | 96 | 21:00 | 177 | Shariatpur | 105 | 20:00
36 | Cantonment | 136 | 13:00 | 107 | Madartek | 85 | 23:00 | 178 | Sherpur | 146 | 18:30
37 | Chandina | 21 | 00:00 | 108 | Madunaghat | 63 | 18:00 | 179 | Shikalbaha | 33 | 19:30
38 | Chandpur | 80 | 02:00 | 109 | Magura | 65 | 18:30 | 180 | Shitalakhya | 84 | 12:00
39 | Chandraghona | 38 | 13:00 | 110 | Mahasthangarh | 72 | 23:00 | 181 | Sholosohor | 55 | 18:00
40 | Chapai | 69 | 01:00 | 111 | Maijdee | 37 | 02:00 | 182 | Shomvuganj | 46 | 00:00
41 | Charfasson | 31 | 18:30 | 112 | Manikganj | 126 | 02:00 | 183 | Shyampur | 152 | 00:00
42 | Charsaidpur | 40 | 00:00 | 113 | Maniknagar | 90 | 13:00 | 184 | Siddhirganj | 136 | 18:00
43 | Chauddagram | 74 | 18:00 | 114 | Matarbari | 59 | 00:00 | 185 | Sirajganj | 124 | 18:30
44 | Chhatak | 39 | 00:00 | 115 | Matuail | 80 | 10:00 | 186 | Sitakunda | 40 | 18:30
45 | Chowmuhani | 155 | 23:00 | 116 | Metrorail_Motijheel | 21 | 16:00 | 187 | Sonargaon | 118 | 01:00
46 | Chuadanga | 109 | 21:00 | 117 | Metrorail_Uttara | 9 | 13:00 | 188 | Sreemongol | 81 | 02:00
47 | Coxsbazar | 144 | 19:00 | 118 | Millgate | 100 | 16:00 | 189 | Sreepur | 138 | 16:00
48 | Cumilla(N) | 151 | 18:00 | 119 | Mirpur | 163 | 18:00 | 190 | Srinagar | 54 | 21:00
49 | Cumilla(S) | 166 | 18:30 | 120 | Mirsorai | 48 | 04:00 | 191 | Sunamganj | 60 | 02:00
50 | Daganbhuiyan | 37 | 22:00 | 121 | Mirzapur | 47 | 12:00 | 192 | Sylhet | 146 | 14:00
51 | Daudkandi | 135 | 00:00 | 122 | Mithapukur | 58 | 17:00 | 193 | Sylhet_(South) | 65 | 18:00
52 | DhakaUniversity | 100 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 96 | 02:00 | 124 | Mogbazar | 68 | 18:00 | 195 | Tangail | 174 | 22:00
54 | Dhanmondi | 121 | 13:00 | 125 | Mongla | 47 | 10:00 | 196 | Taraganj | 29 | 17:00
55 | Dohazari | 111 | 21:00 | 126 | Monirampur | 23 | 18:00 | 197 | Tasnim | 45 | 23:00
56 | Faridpur | 186 | 18:30 | 127 | Motijheel | 56 | 13:00 | 198 | Thakurgaon | 106 | 19:00
57 | Fatullah | 126 | 10:00 | 128 | Muktagacha | 38 | 19:30 | 199 | Tongi | 158 | 21:00
58 | Fenchuganj | 45 | 19:00 | 129 | Munshiganj | 113 | 18:00 | 200 | Ullahpara | 35 | 19:00
59 | Feni | 110 | 23:00 | 130 | Muradnagar | 49 | 01:00 | 201 | Ullon | 34 | 00:00
60 | GPH | 1 | 00:00 | 131 | Mymensingh | 173 | 19:30 | 202 | Uttara | 101 | 18:00
61 | Ghatail | 91 | 17:00 | 132 | Nabinagar | 106 | 08:00 | 203 | UttaraNew | 59 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 115 | 20:00 | 204 | Zigatola | 81 | 13:00
63 | Ghorashal-230 | 103 | 00:00 | 134 | Narail | 57.5 | 23:00
64 | Goalpara | 39 | 00:00 | 135 | Narinda | 81.5 | 13:00
65 | Gollamari | 112 | 13:00 | 136 | Narshingdi | 193 | 02:00
66 | Gopalganj | 100 | 18:30 | 137 | Natore | 130 | 19:30
67 | Gulshan | 130 | 13:00 | 138 | Nawabganj | 52.3 | 22:00
68 | Halishahar | 154.5 | 16:00 | 139 | Netrakona | 141 | 22:00
69 | HaripurSBU | 135 | 20:00 | 140 | New | 88 | 12:00
70 | Hasnabad | 110 | 23:00 | 141 | Niamatpur | 68 | 22:00
71 | Hathazari | 92 | 00:00 | 142 | Noapara | 43 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15424.96 | 775 |  | 16234.96
1:00 | 14832.42 | 688 |  | 15551.42
2:00 | 14665.9 | 10 |  | 14676.35
3:00 | 14124.59 | 0 |  | 14124.59
4:00 | 13517.29 | 0 |  | 13517.29
5:00 | 13012.95 | 0 |  | 13012.95
6:00 | 12936.6 | 0 |  | 12936.6
7:00 | 13421.46 | 10 |  | 13431.46
8:00 | 13563.97 | 10 |  | 13573.97
9:00 | 13517.41 | 15 |  | 13533.09
10:00 | 13851.92 | 15 |  | 13867.92
11:00 | 14224.86 | 106 |  | 14335.63
12:00 | 14628.27 | 133 |  | 14767.27
13:00 | 15074.02 | 178 |  | 15260.03
14:00 | 15151.1 | 203 |  | 15363.1
15:00 | 15426.84 | 184 |  | 15618.84
16:00 | 15314.24 | 230 |  | 15554.24
17:00 | 15096.16 | 225 |  | 15331.16
18:00 | 15533.97 | 1105 |  | 16688.97
19:00 | 15853.51 | 1624 |  | 17550.51
19:30 | 15888.45 | 1836 |  | 17807.45
20:00 | 15867.35 | 1516 |  | 17451.35
21:00 | 15848.78 | 1375 |  | 17285.78
22:00 | 15786.2 | 1317 |  | 17162.2
23:00 | 15763.9 | 1186 |  | 17002.9
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9573.48 | 5851.48 | 15424.96 | DAILY GENERATION CURVE
00:30 | 9326.8 | 5801.89 | 15128.69
01:00 | 9080.12 | 5752.3 | 14832.42 | 12-10-2026
01:30 | 9029.12 | 5720.04 | 14749.16
02:00 | 8978.12 | 5687.78 | 14665.9
02:30 | 8736.56 | 5658.685 | 14395.245
03:00 | 8495 | 5629.59 | 14124.59
03:30 | 8331 | 5489.94 | 13820.94
04:00 | 8167 | 5350.29 | 13517.29
04:30 | 7982 | 5283.12 | 13265.12
05:00 | 7797 | 5215.95 | 13012.95
05:30 | 7775.09 | 5199.685 | 12974.775
06:00 | 7753.18 | 5183.42 | 12936.6
06:30 | 7900.17 | 5278.86 | 13179.03
07:00 | 8047.16 | 5374.3 | 13421.46
07:30 | 8086.35 | 5406.365 | 13492.715
08:00 | 8125.54 | 5438.43 | 13563.97
08:30 | 8101.425 | 5439.265 | 13540.69
09:00 | 8077.31 | 5440.1 | 13517.41
09:30 | 8182.73 | 5501.935 | 13684.665
10:00 | 8288.15 | 5563.77 | 13851.92
10:30 | 8455.6 | 5582.79 | 14038.39
11:00 | 8623.05 | 5601.81 | 14224.86
11:30 | 8752.545 | 5674.02 | 14426.565
12:00 | 8882.04 | 5746.23 | 14628.27
12:30 | 9020.475 | 5830.67 | 14851.145
13:00 | 9158.91 | 5915.11 | 15074.02
13:30 | 9218.895 | 5893.665 | 15112.56
14:00 | 9278.88 | 5872.22 | 15151.1
14:30 | 9412.62 | 5876.35 | 15288.97
15:00 | 9546.36 | 5880.48 | 15426.84
15:30 | 9552.075 | 5818.465 | 15370.54
16:00 | 9557.79 | 5756.45 | 15314.24
16:30 | 9495.29 | 5709.91 | 15205.2
17:00 | 9432.79 | 5663.37 | 15096.16
17:30 | 9642.385 | 5672.68 | 15315.065
18:00 | 9851.98 | 5681.99 | 15533.97
18:30 | 10034.98 | 5658.76 | 15693.74
19:00 | 10217.98 | 5635.53 | 15853.51
19:30 | 10276.98 | 5611.47 | 15888.45
20:00 | 10267.98 | 5599.37 | 15867.35
20:30 | 10228.48 | 5629.585 | 15858.065 |  | Executive Engineer
21:00 | 10188.98 | 5659.8 | 15848.78 |  | Network Operation Division
21:30 | 10171.98 | 5645.51 | 15817.49
22:00 | 10154.98 | 5631.22 | 15786.2
22:30 | 10131.48 | 5643.57 | 15775.05
23:00 | 10107.98 | 5655.92 | 15763.9

## En-Curve
QF-LDC-12
Date | 12-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2961 | 1863 | 467 | 0 | 70 | 752.68 | 182 | 5295.8 | 0 | 856.42 | 2977.06 | 0 | 0 | 0 | 775 | DAILY ENERGY CURVE
00:30 | 2972 | 1851 | 468.5 | 0 | 68 | 756.09 | 182 | 5230.8 | 0 | 821.42 | 2778.88 | 0 | 0 | 0 | 731.5 | 12-10-2026
01:00 | 2983 | 1839 | 470 | 0 | 66 | 759.5 | 182 | 5165.8 | 0 | 786.42 | 2580.7 | 0 | 0 | 0 | 688
01:30 | 2985 | 1845 | 469.5 | 0 | 65 | 759.74 | 181 | 5105.8 | 0 | 761.92 | 2576.2 | 0 | 0 | 0 | 349 | Energy Generated | 354.2644 |  | MKWHr
02:00 | 2987 | 1851 | 469 | 0 | 64 | 759.98 | 180 | 5045.8 | 0 | 737.42 | 2571.7 | 0 | 0 | 0 | 10 | Energy not Served | 10.905 |  | MKWHr
02:30 | 3017.5 | 1864.5 | 469 | 0 | 64 | 758.285 | 180 | 4983.4 | 0 | 613.71 | 2444.35 | 0 | 0 | 0.5 | 5 | Total Energy Requirement | 365.1694 |  | MKWHr
03:00 | 3048 | 1878 | 469 | 0 | 64 | 756.59 | 180 | 4921 | 0 | 490 | 2317 | 0 | 0 | 1 | 0
03:30 | 3065 | 1894 | 469 | 0 | 62 | 755.44 | 179.5 | 4910.5 | 0 | 372.5 | 2111 | 0 | 0 | 2 | 0
04:00 | 3082 | 1910 | 469 | 0 | 60 | 754.29 | 179 | 4900 | 0 | 255 | 1905 | 0 | 0 | 3 | 0
04:30 | 3077 | 1915 | 469 | 0 | 60 | 757.12 | 179 | 4877 | 0 | 239 | 1689.5 | 0 | 0 | 2.5 | 0
05:00 | 3072 | 1920 | 469 | 0 | 60 | 759.95 | 179 | 4854 | 0 | 223 | 1474 | 0 | 0 | 2 | 0
05:30 | 3053 | 1925.5 | 469 | 0 | 59 | 757.185 | 178.5 | 4854.5 | 0.09 | 223.5 | 1453.5 | 0 | 0 | 1 | 0
06:00 | 3034 | 1931 | 469 | 0 | 58 | 754.42 | 178 | 4855 | 0.18 | 224 | 1433 | 0 | 0 | 0 | 0
06:30 | 3081 | 1973.5 | 469 | 0 | 56 | 756.355 | 178.5 | 4883 | 65.625 | 244 | 1472.05 | 0 | 0 | 0 | 5
07:00 | 3128 | 2016 | 469 | 0 | 54 | 758.29 | 179 | 4911 | 131.07 | 264 | 1511.1 | 0 | 0 | 0 | 10
07:30 | 3049.5 | 1947.25 | 469 | 0 | 53 | 756.21 | 180 | 4884 | 234.205 | 293 | 1626.55 | 0 | 0 | 0 | 10
08:00 | 2971 | 1878.5 | 469 | 0 | 52 | 754.13 | 181 | 4857 | 337.34 | 322 | 1742 | 0 | 0 | 0 | 10
08:30 | 2900.5 | 1852 | 469 | 0 | 58 | 746.15 | 181.5 | 4828.5 | 441.54 | 301 | 1762.5 | 0 | 0 | 0 | 12.5
09:00 | 2830 | 1825.5 | 469 | 0 | 64 | 738.17 | 182 | 4800 | 545.74 | 280 | 1783 | 0 | 0 | 0 | 15
09:30 | 2832 | 1817.25 | 469 | 0 | 61 | 746.305 | 182 | 4875 | 616.61 | 281 | 1804.5 | 0 | 0 | 0 | 15
10:00 | 2834 | 1809 | 469 | 0 | 58 | 754.44 | 182 | 4950 | 687.48 | 282 | 1826 | 0 | 0 | 0 | 15
10:30 | 2892.5 | 1827.5 | 469.5 | 0 | 62 | 753.045 | 182 | 5019 | 711.845 | 282 | 1839 | 0 | 0 | 0 | 60.5
11:00 | 2951 | 1846 | 470 | 0 | 66 | 751.65 | 182 | 5088 | 736.21 | 282 | 1852 | 0 | 0 | 0 | 106
11:30 | 3017.5 | 1932.5 | 469.5 | 0 | 69 | 751.705 | 182 | 5120 | 760.61 | 286.25 | 1837.5 | 0 | 0 | 0 | 119.5
12:00 | 3084 | 2019 | 469 | 0 | 72 | 751.76 | 182 | 5152 | 785.01 | 290.5 | 1823 | 0 | 0 | 0 | 133
12:30 | 3084 | 1963.5 | 469.5 | 0 | 68 | 758.12 | 201.5 | 5200.4 | 757.125 | 338 | 2011 | 0 | 0 | 0 | 155.5
13:00 | 3084 | 1908 | 470 | 0 | 64 | 764.48 | 221 | 5248.8 | 729.24 | 385.5 | 2199 | 0 | 0 | 0 | 178
13:30 | 3076.5 | 1915.5 | 469.5 | 0 | 68 | 762.115 | 220.5 | 5251.3 | 684.545 | 405 | 2258.6 | 0 | 0 | 1 | 190.5
14:00 | 3069 | 1923 | 469 | 0 | 72 | 759.75 | 220 | 5253.8 | 639.85 | 424.5 | 2318.2 | 0 | 0 | 2 | 203
14:30 | 3070 | 1955.5 | 469 | 0 | 72 | 756.395 | 217.5 | 5263.3 | 550.325 | 448.5 | 2483.45 | 0 | 0 | 3 | 193.5
15:00 | 3071 | 1988 | 469 | 0 | 72 | 753.04 | 215 | 5272.8 | 460.8 | 472.5 | 2648.7 | 0 | 0 | 4 | 184
15:30 | 3073 | 2014 | 469.5 | 0 | 71 | 756.62 | 171 | 5272.8 | 356.92 | 476.5 | 2706.2 | 0 | 0 | 3 | 207
16:00 | 3075 | 2040 | 470 | 0 | 70 | 760.2 | 127 | 5272.8 | 253.04 | 480.5 | 2763.7 | 0 | 0 | 2 | 230
16:30 | 3051 | 1982.75 | 469.5 | 0 | 69 | 758.555 | 127.5 | 5261.8 | 151.505 | 523.21 | 2809.38 | 0 | 0 | 1 | 227.5
17:00 | 3027 | 1925.5 | 469 | 0 | 68 | 756.91 | 128 | 5250.8 | 49.97 | 565.92 | 2855.06 | 0 | 0 | 0 | 225
17:30 | 3055.5 | 1941 | 469 | 0 | 75 | 754.3 | 151 | 5268.3 | 24.985 | 645.42 | 2930.56 | 0 | 0 | 0 | 665
18:00 | 3084 | 1956.5 | 469 | 0 | 82 | 751.69 | 174 | 5285.8 | 0 | 724.92 | 3006.06 | 0 | 0 | 0 | 1105
18:30 | 3077 | 1987.5 | 379.5 | 0 | 80 | 752.71 | 174.5 | 5285.3 | 0 | 784.17 | 3173.06 | 0 | 0 | 0 | 1364.5
19:00 | 3070 | 2018.5 | 290 | 0 | 78 | 753.73 | 175 | 5284.8 | 0 | 843.42 | 3340.06 | 0 | 0 | 0 | 1624
19:30 | 3115 | 1979.5 | 294 | 0 | 78 | 693.67 | 176 | 5295.8 | 0 | 856.42 | 3400.06 | 0 | 0 | 0 | 1836
20:00 | 3094 | 1950.5 | 293 | 0 | 76 | 671.57 | 221 | 5295.8 | 0 | 871.42 | 3394.06 | 0 | 0 | 0 | 1516
20:30 | 3100 | 1969.5 | 293 | 0 | 75 | 715.785 | 221 | 5295.8 | 0 | 866.92 | 3321.06 | 0 | 0 | 0 | 1445.5
21:00 | 3106 | 1988.5 | 293 | 0 | 74 | 760 | 221 | 5295.8 | 0 | 862.42 | 3248.06 | 0 | 0 | 0 | 1375
21:30 | 3110 | 1994.5 | 293 | 0 | 73 | 759.71 | 221.5 | 5295.8 | 0 | 858.42 | 3211.56 | 0 | 0 | 0 | 1346
22:00 | 3114 | 2000.5 | 293 | 0 | 72 | 759.42 | 222 | 5295.8 | 0 | 854.42 | 3175.06 | 0 | 0 | 0 | 1317
22:30 | 3116.5 | 2003 | 313.5 | 0 | 72 | 757.77 | 222 | 5268.8 | 0 | 846.42 | 3175.06 | 0 | 0 | 0 | 1251.5
23:00 | 3119 | 2005.5 | 334 | 0 | 72 | 756.12 | 222 | 5241.8 | 0 | 838.42 | 3175.06 | 0 | 0 | 0 | 1186
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 12-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 13 | 15 | 110 | 156 | 1138 | 400 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 14 | 16 | 110 | 110 | 1160 | 368
2:00 | 20 | 13 | 154 | 106 | 1222 | 356 |  | Import | 0
3:00 | 32 | 11 | 204 | 126 | 1282 | 376
4:00 | 34 | 7 | 212 | 120 | 1158 | 342 | Ishurdi-Ghorashal Ckt-2 | Export | 948436.36
5:00 | 53 | 17 | 208 | 106 | 1290 | 362
6:00 | 56 | 20 | 196 | 100 | 1304 | 376 |  | Import | 125454.55
7:00 | 26 | 9 | 120 | 94 | 1194 | 352
8:00 | 31 | 4 | 160 | 84 | 1292 | 386 | Sirajganj-Sreepur Ckt-1 | Export | 915000
9:00 | 68 | 18 | 240 | 100 | 1464 | 452
10:00 | 89 | 25 | 280 | 122 | 1468 | 506 |  | Import | 13000
11:00 | 79 | 24 | 256 | 124 | 1352 | 482
12:00 | 88 | 38 | 280 | 158 | 1394 | 564 | Sirajganj-Sreepur Ckt-2 | Export | 919000
13:00 | 69 | 28 | 210 | 146 | 1322 | 550
14:00 | 61 | 38 | 200 | 146 | 1284 | 542 |  | Import | 12000
15:00 | 70 | 51 | 220 | 180 | 1270 | 580
16:00 | 70 | 52 | 210 | 170 | 1268 | 582 | Gopalganj-Aminbazar Ckt-1 | Export | 14430000
17:00 | 59 | 46 | 150 | 140 | 1300 | 558
18:00 | 38 | 40 | 150 | 160 | 1094 | 490 |  | Import | 0
18:30 | -29 | 27 | -10 | 136 | 856 | 422
19:00 | -27 | 36 | -6 | 140 | 882 | 418 | Gopalganj-Aminbazar Ckt-2 | Export | 14470000
19:30 | -24 | 39 | -20 | 154 | 858 | 432
20:00 | -29 | 40 | -20 | 154 | 830 | 412 |  | Import | 0
21:00 | -28 | 33 | -16 | 142 | 850 | 410
22:00 | -21 | 33 | 8 | 148 | 866 | 400 |  | Total Export | 31682436.36
23:00 | -14 | 29 | 30 | 146 | 916 | 386 |  | Total Import | 150454.55
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 04:00 | 368 | 15:00 | Madunaghat | 405 | 02:00 | 397 | 12:00
Amtali | 412 | 03:00 | 407 | 12:00 | Meghnaghat | 395 | 04:00 | 379 | 12:00
Ashuganj | 405 | 6:00 | 382 | 13:00 | Mirsorai | 405 | 08:00 | 393 | 12:00
Bhulta | 397 | 04:00 | 374 | 12:00 | Payra | 414 | 06:00 | 409 | 12:00
Bibiana | 388 | 05:00 | 377 | 15:00 | Rahanpur | 408 | 03:00 | 395 | 12:00
BIPTC | 404 | 03:00 | 396 | 16:00 | Rampal | 399 | 03:00 | 387 | 12:00
Bogura | 403 | 03:00 | 385 | 12:00
Gopalganj | 396 | 03:00 | 384 | 12:00
Kaliakoir | 380 | 01:00 | 360 | 12:00
Korerhat | 403 | 02:00 | 391 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 04:00 | 221 | 12:00 | Hasnabad | 229 | 07:00 | 217 | 11:00
AKSML | 240 | 01:00 | 231 | 13:00 | Hathazari | 239 | 08:00 | 233 | 12:00
Aminbazar | 236 | 08:00 | 223 | 15:00 | Ishurdi | 236 | 03:00 | 223 | 13:00
Ashuganj | 231 | 03:00 | 220 | 12:00 | Jhenaidah | 227 | 06:00 | 213 | 13:00
Ashuganj-400 | 231 | 3:00 | 220 | 12:00 | Kachua | 231 | 01:00 | 222 | 13:00
Baghabari | 234 | 05:00 | 223 | 12:00 | Kaliakoir | 237 | 01:00 | 222 | 12:00
Barapukuria | 234 | 04:00 | 219 | 11:00 | Keranigonj | 232 | 04:00 | 218 | 12:00
Barapukuria-230 | 234 | 4:00 | 218 | 12:00 | Khulna(S) | 228 | 06:00 | 218 | 13:00
Barapukuria(N) | 238 | 03:00 | 221 | 11:00 | Korerhat | 234 | 04:00 | 222 | 13:00
Barishal | 228 | 02:00 | 223 | 12:00 | Madunaghat | 240 | 04:00 | 234 | 15:00
Bheramara | 235 | 03:00 | 222 | 13:00 | Madunaghat-400 | 242 | 01:00 | 237 | 12:00
Bhulta | 228 | 04:00 | 213 | 12:00 | Maniknagar | 226 | 03:00 | 212 | 12:00
Bibiana | 224 | 06:00 | 217 | 15:00 | Meghnaghat | 234 | 03:00 | 220 | 16:00
BIPTC | 236 | 03:00 | 221 | 13:00 | Meghnaghat-400 | 229 | 03:00 | 217 | 12:00
Birulia | 236 | 04:00 | 221 | 12:00 | Mirsorai | 235 | 06:00 | 228 | 12:00
Bogura | 240 | 03:00 | 229 | 12:00 | Naogaon | 229 | 03:00 | 210 | 13:00
Bogura-400 | 240 | 03:00 | 228 | 12:00 | Purbasadipur | 235 | 02:00 | 217 | 11:00
Borhanuddin | 230 | 06:00 | 227 | 12:00 | Rajshahi | 233 | 03:00 | 220 | 13:00
BSRM | 231 | 01:00 | 224 | 12:00 | Rampal | 227 | 03:00 | 218 | 13:00
Charfasson | 231 | 06:00 | 227 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 231 | 01:00 | 224 | 12:00 | Rampura | 227 | 04:00 | 211 | 12:00
Cumilla(N) | 227 | 08:00 | 216 | 13:00 | Shikalbaha | 241 | 00:00 | 235 | 12:00
Faridpur | 224 | 03:00 | 217 | 15:00 | Shyampur | 230 | 04:00 | 216 | 12:00
Fenchuganj | 227 | 06:00 | 220 | 12:00 | Siddhirganj | 229 | 05:00 | 215 | 12:00
Feni | 229 | 08:00 | 220 | 12:00 | Sirajgonj | 237 | 05:00 | 229 | 12:00
Ghorashal | 230 | 01:00 | 220 | 10:00 | Sreepur | 226 | 06:00 | 214 | 12:00
Ghorashal-230 | 227 | 01:00 | 207 | 12:00 | Tongi | 229 | 01:00 | 210 | 15:00
Gopalganj | 225 | 06:00 | 218 | 12:00
GPH | 236 | 08:00 | 232 | 01:00
Haripur | 227 | 03:00 | 214 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 124 | 12:00 | Madanganj | 136 | 07:00 | 129 | 12:00
Agargaon | 137 | 03:00 | 126 | 12:00 | Madaripur | 132 | 07:00 | 126 | 13:00
Agrabad | 138 | 18:00 | 132 | 11:00 | Madartek | 136 | 05:00 | 124 | 12:00
AKS | 135 | 00:00 | 131 | 11:00 | Madunaghat | 139 | 04:00 | 135 | 11:00
Aminbazar | 135 | 03:00 | 126 | 15:00 | Magura | 135 | 05:00 | 125 | 13:00
Amnura | 134 | 02:00 | 126 | 13:00 | Mahasthangarh | 137 | 03:00 | 129 | 12:00
Araihazar | 127 | 04:00 | 118 | 12:00 | Maijdee | 130 | 08:00 | 125 | 13:00
Ashuganj | 136 | 06:00 | 128 | 12:00 | Manikganj | 134 | 00:00 | 127 | 15:00
Ashuganj-230 | 137 | 03:00 | 133 | 12:00 | Maniknagar | 141 | 04:00 | 129 | 13:00
Bagerhat | 125 | 09:00 | 118 | 13:00 | Matarbari | 122 | 09:00 | 115 | 00:00
Bajitpur | 129 | 05:00 | 122 | 12:00 | Matuail | 137 | 03:00 | 130 | 14:00
Bakerganj | 133 | 01:00 | 130 | 15:00 | Metrorail_Motijheel | 141 | 04:00 | 129 | 13:00
Bakulia | 138 | 18:30 | 132 | 12:00 | Metrorail_Uttara | 139 | 04:00 | 124 | 12:00
Banani | 136 | 03:00 | 122 | 12:00 | Millgate | 139 | 03:00 | 124 | 15:00
Bangabhaban | 141 | 04:00 | 128 | 13:00 | Mirpur | 135 | 04:00 | 124 | 12:00
Barapukuria | 137 | 03:00 | 126 | 12:00 | Mirzapur | 134 | 00:00 | 125 | 12:00
Barguna | 133 | 05:00 | 130 | 13:00 | Mithapukur | 135 | 03:00 | 125 | 11:00
Barishal | 133 | 05:00 | 129 | 13:00 | MI_Cement | 136 | 04:00 | 130 | 11:00
Barishal-230 | 133 | 03:00 | 129 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 00:00 | 132 | 12:00 | Mogbazar | 138 | 04:00 | 125 | 12:00
Baroirhat | 135 | 02:00 | 129 | 13:00 | Mongla | 125 | 09:00 | 118 | 13:00
Bashundhara | 138 | 02:00 | 123 | 15:00 | Monirampur | 127 | 09:00 | 117 | 22:00
BashundharaCement | 136 | 07:00 | 129 | 13:00 | Motijheel | 141 | 04:00 | 128 | 13:00
Beanibazar | 125 | 06:00 | 117 | 15:00 | Muktagacha | 131 | 00:00 | 117 | 12:00
Benapole | 133 | 05:00 | 117 | 13:00 | Munshiganj | 135 | 02:00 | 127 | 14:00
Bhaluka | 130 | 04:00 | 120 | 12:00 | Muradnagar | 130 | 06:00 | 119 | 13:00
Bhandaria | 130 | 06:00 | 125 | 15:00 | Mymensingh | 133 | 00:00 | 115 | 13:00
Bhangura | 136 | 06:00 | 127 | 11:00 | Nabinagar | 134 | 03:00 | 123 | 12:00
Bheramara | 138 | 03:00 | 130 | 13:00 | Naogaon | 138 | 03:00 | 126 | 13:00
Bheramara(GK) | 137 | 02:00 | 131 | 11:00 | Narail | 134 | 04:00 | 125 | 22:00
Bhulta | 123 | 08:00 | 119 | 10:00 | Narinda | 141 | 4:00 | 129 | 13:00
Bhulta-400 | 128 | 04:00 | 119 | 12:00 | Narshingdi | 132 | 01:00 | 119 | 12:00
Birulia | 138 | 04:00 | 129 | 12:00 | Natore | 135 | 06:00 | 127 | 13:00
Bog-Sherpur | 138 | 03:00 | 129 | 13:00 | Nawabganj | 137 | 04:00 | 128 | 12:00
Bogura | 138 | 04:00 | 131 | 13:00 | Netrakona | 121 | 08:00 | 110 | 14:00
Bogura-230 | 140 | 03:00 | 132 | 12:00 | New | 137 | 00:00 | 127 | 12:00
Brahmanbaria | 133 | 06:00 | 126 | 12:00 | Niamatpur | 134 | 04:00 | 128 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 137 | 03:00 | 126 | 12:00 | Noapara | 129 | 03:00 | 122 | 13:00
Chandina | 132 | 06:00 | 124 | 13:00 | Pabna | 134 | 02:00 | 127 | 11:00
Chandpur | 135 | 01:00 | 130 | 11:00 | Palashbari | 132 | 04:00 | 126 | 07:00
Chandraghona | 139 | 00:00 | 136 | 11:00 | Panchagarh | 139 | 03:00 | 122 | 11:00
Chapai | 133 | 04:00 | 130 | 00:00 | Patiya | 136 | 18:30 | 130 | 19:30
Charsaidpur | 137 | 03:00 | 128 | 12:00 | Patnitala | 134 | 06:00 | 127 | 13:00
Chauddagram | 131 | 08:00 | 125 | 13:00 | Patuakhali | 134 | 06:00 | 130 | 12:00
Chhatak | 122 | 05:00 | 114 | 15:00 | Payra | 135 | 08:00 | 133 | 12:00
Chowmuhani | 130 | 01:00 | 126 | 12:00 | PHP | 133 | 01:00 | 128 | 13:00
Chuadanga | 136 | 06:00 | 123 | 00:00 | Postogola | 133 | 00:00 | 128 | 06:00
Coxsbazar | 122 | 12:00 | 117 | 00:00 | Pubail | 134 | 00:00 | 123 | 12:00
Cumilla(N) | 132 | 08:00 | 124 | 13:00 | Purbachal | 136 | 04:00 | 123 | 12:00
Cumilla(S) | 132 | 05:00 | 125 | 13:00 | Purbasadipur | 137 | 03:00 | 124 | 12:00
Daganbhuiyan | 132 | 01:00 | 127 | 12:00 | Rahanpur | 136 | 04:00 | 125 | 06:00
Daudkandi | 130 | 03:00 | 116 | 13:00 | Rahanpur-400 | 137 | 03:00 | 131 | 13:00
DhakaUniversity | 136 | 03:00 | 124 | 12:00 | Rahim | 136 | 06:00 | 129 | 12:00
Dhamrai | 135 | 03:00 | 124 | 14:00 | Rajbari | 128 | 06:00 | 123 | 14:00
Dhanmondi | 138 | 05:00 | 129 | 12:00 | Rajendrapur | 132 | 01:00 | 124 | 12:00
Dohazari | 133 | 18:30 | 125 | 15:00 | Rajshahi | 132 | 01:00 | 125 | 13:00
Faridpur | 129 | 03:00 | 126 | 13:00 | Rajshahi-230 | 134 | 03:00 | 125 | 13:00
Fatullah | 137 | 03:00 | 127 | 12:00 | Ramganj | 131 | 01:00 | 126 | 12:00
Fenchuganj | 133 | 06:00 | 128 | 15:00 | Rampur | 137 | 01:00 | 131 | 12:00
Feni | 131 | 04:00 | 127 | 12:00 | Rampura | 136 | 03:00 | 124 | 12:00
Feni-230 | 133 | 08:00 | 127 | 13:00 | Rangamati | 138 | 02:00 | 134 | 11:00
Ghatail | 128 | 05:00 | 117 | 12:00 | Rangpur | 132 | 04:00 | 123 | 12:00
Ghorashal | 133 | 00:00 | 125 | 13:00 | Ruppur | 137 | 18:00 | 130 | 13:00
Goalpara | 132 | 03:00 | 125 | 13:00 | Saidpur | 133 | 02:00 | 124 | 12:00
Gollamari | 131 | 09:00 | 124 | 12:00 | Santhia | 135 | 06:00 | 129 | 13:00
Gopalganj | 132 | 03:00 | 125 | 12:00 | Satkhira | 127 | 06:00 | 118 | 13:00
Gopalganj-400 | 133 | 03:00 | 129 | 12:00 | Satmasjid | 136 | 03:00 | 125 | 13:00
Gulshan | 136 | 04:00 | 124 | 12:00 | Savar | 132 | 00:00 | 123 | 12:00
Halishahar | 138 | 01:00 | 132 | 12:00 | SevenRings | 137 | 03:00 | 124 | 13:00
Haripur | 137 | 04:00 | 129 | 12:00 | ShahCement | 137 | 03:00 | 128 | 12:00
HaripurSBU | 138 | 06:00 | 128 | 11:00 | Shahjadpur | 134 | 16:00 | 130 | 11:00
Hasnabad | 137 | 05:00 | 128 | 12:00 | Shahjibazar | 133 | 08:00 | 125 | 13:00
Hathazari | 139 | 08:00 | 132 | 00:00 | Shahmirpur | 138 | 01:00 | 133 | 11:00
Hatirjheel | 136 | 03:00 | 124 | 12:00 | Shariatpur | 130 | 05:00 | 125 | 13:00
Ishurdi | 138 | 03:00 | 130 | 13:00 | Sherpur | 131 | 00:00 | 116 | 12:00
Jaldhaka | 130 | 02:00 | 121 | 12:00 | Shikalbaha | 128 | 01:00 | 122 | 12:00
Jamalpur | 135 | 00:00 | 116 | 12:00 | Shikalbaha-230 | 139 | 02:00 | 134 | 12:00
Jashore | 135 | 06:00 | 118 | 13:00 | Shitalakhya | 136 | 04:00 | 126 | 16:00
Jhenaidah | 138 | 05:00 | 128 | 13:00 | Sholosohor | 138 | 00:00 | 132 | 12:00
Jhenaidah-230 | 138 | 06:00 | 128 | 13:00 | Shomvuganj | 126 | 06:00 | 116 | 13:00
Joydebpur | 135 | 01:00 | 121 | 12:00 | Shyampur | 135 | 02:00 | 128 | 12:00
Joypurhat | 135 | 04:00 | 126 | 13:00 | Shyampur-230 | 138 | 06:00 | 130 | 12:00
Juldah | 138 | 00:00 | 133 | 12:00 | Siddhirganj | 137 | 03:00 | 130 | 15:00
Kabirpur | 138 | 00:00 | 120 | 15:00 | Sirajganj | 134 | 03:00 | 125 | 13:00
Kachua | 132 | 01:00 | 127 | 13:00 | Sitakunda | 138 | 01:00 | 134 | 12:00
Kaliakoir | 139 | 00:00 | 131 | 12:00 | Sonargaon | 133 | 19:30 | 127 | 12:00
Kaliganj | 137 | 06:00 | 127 | 13:00 | Sreemongol | 131 | 07:00 | 125 | 02:00
Kallyanpur | 133 | 07:00 | 125 | 12:00 | Sreepur | 135 | 06:00 | 125 | 12:00
Kalurghat | 139 | 01:00 | 135 | 12:00 | Srinagar | 136 | 05:00 | 128 | 12:00
Kamrangirchar | 137 | 02:00 | 121 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | 140 | 1:00 | 135 | 16:00 | Sunamganj | 119 | 07:00 | 114 | 00:00
Kasba | 129 | 05:00 | 118 | 13:00 | Sylhet | 125 | 07:00 | 121 | 12:00
Kazla | 141 | 04:00 | 129 | 12:00 | Sylhet_(South) | 126 | 06:00 | 121 | 15:00
Keranigonj | 137 | 03:00 | 128 | 12:00 | Tangail | 130 | 00:00 | 120 | 12:00
Khagrachori | 137 | 01:00 | 133 | 11:00 | Taraganj | 132 | 02:00 | 123 | 12:00
Khulna | 130 | 09:00 | 122 | 13:00 | Tasnim | 135 | 05:00 | 127 | 12:00
Khulna(S) | 132 | 06:00 | 124 | 13:00 | Thakurgaon | 141 | 03:00 | 123 | 11:00
Khulshi | 137 | 01:00 | 130 | 12:00 | TK | 139 | 18:00 | 135 | 00:00
Kishoreganj | 128 | 04:00 | 119 | 13:00 | Tongi | 140 | 01:00 | 127 | 15:00
Kodda | 137 | 00:00 | 122 | 11:00 | Ullahpara | 135 | 02:00 | 127 | 13:00
Korerhat | 136 | 07:00 | 131 | 12:00 | Ullon | 135 | 01:00 | 124 | 12:00
KSRM | 139 | 00:00 | 132 | 13:00 | Uttara | 139 | 03:00 | 123 | 15:00
Kulaura | 132 | 08:00 | 127 | 12:00 | UttaraNew | 139 | 04:00 | 124 | 12:00
Kurigram | 130 | 09:00 | 120 | 07:00 | Zigatola | 138 | 05:00 | 128 | 13:00
Kushtia | 137 | 04:00 | 129 | 13:00
Laksam | 132 | 09:00 | 126 | 13:00
Lakshmipur | 129 | 08:00 | 124 | 13:00
Lalbag | 136 | 08:00 | 127 | 12:00
Lalmonirhat | 129 | 06:00 | 121 | 18:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division