## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-10-2026 | during | 14-10-2026 | during | 14-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 404 | 406 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 317 | 335 | 335 | 329 | 329 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 85 | 122 | 133 | 133 | 30 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 5 | 24.75 | 24.75 | 9 | 9 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 47 | 48 | 52.19 | 52.19 | 16 | 47 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 210 | 295 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 114 | 133 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 540 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 410 | 560 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 110 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2600 | 3127.42 | 5558.55 | 5528.55 | 2836.42 | 3218.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 81 | 111 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 43 | 24 | 50 | 24 | 50 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 | 34 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 100 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 2 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 57 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.75 | 0 | 3.66 | 0 | 3.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 155 | 212 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 68 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 22 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 162 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 17 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1060 | 1080 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3122.75 | 3780.86 | 4093.62 | 4095.96 | 3566.66 | 3850.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 194 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 347 | 338 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 320 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 300 | 300 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 35 | 41.65 | 41.65 | 33 | 33 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 15 | 15 | 52.82 | 52.82 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 108 | 148 | 195 | 195 | 50 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 123 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 7 | 15 | 20 | 20 | 20 | 20 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 163 | 163 | 90 | 90 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 31 | 155 | 200 | 200 | 136 | 136 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 76 | 80 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 13 | 17.75 | 17.75 | 0 | 0 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 101 | 108 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 74 | 73 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 115 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 0 | 0 | 0 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1764 | 1870.2 | 2675.69 | 2673.69 | 2066.2 | 2078.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-10-2026 | during | 14-10-2026 | during | 14-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.1 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 163 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 87 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 54.15 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22 | 18 | 18 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 291.45 | 291 | 663.6 | 591.5 | 286.1 | 300
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 28 | 40 | 40 | 40 | 40 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 136 | 136 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 83 | 83 | 83 | 83 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 276 | 312 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 146 | 74 | 280 | 280 | 280 | 280 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 388 | 395 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1355 | 1336 | 1604 | 1604 | 1534 | 1534
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 469 | 294 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 25 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1877.2 | 1662.2 | 3296.2 | 3204.2 | 2731.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 48 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 107 | 113 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 220 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 124 | 0 | 0 | 0 | 0 | Station shutdown for GT-11& STG Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 137 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2207.1 | 2215.6 | 2078.6 | 2157.6 | 1963.6 | 1962.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 60.41 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 45 | 43 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 281 | 266 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 5 | 51 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 60 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.99 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 754.93 | 752.61 | 748 | 748 | 748 | 748 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.86 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1444.19 | 1402.61 | 2569.11 | 2346.99 | 1568.53 | 1517.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 105 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 73 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 208 | 0 | 186.25 | 0 | 186.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 423.9 | 228 | 469.25 | 248 | 379.25 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 15085.59 | 15913.89 | 23008.62 | 22450.49 | 16931.96 | 17337.69
Forecast Scenario (14-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15180 |  | 1747.65 |  | 17010
|  |  |  | 1:00 | 14455 |  | 1968 |  | 16515.733
|  |  |  | 2:00 | 14289 |  | 1752 |  | 16123.555
|  |  |  | 3:00 | 13899 |  | 1713 |  | 15692.7173
|  |  |  | 4:00 | 13743 |  | 1624 |  | 15443.5236
|  |  |  | 5:00 | 13618 |  | 148 |  | 13772.9738
|  |  |  | 6:00 | 13515 |  | 31 |  | 13547.4607
|  |  |  | 7:00 | 13797 |  | 10 |  | 13807.4712
|  |  |  | 8:00 | 13750 |  | 716.25 |  | 14500
|  |  |  | 9:00 | 13840 |  | 630.3 |  | 14500
|  |  |  | 10:00 | 14000 |  | 553.9 |  | 14580
|  |  |  | 11:00 | 14470 |  | 362.9 |  | 14850
|  |  |  | 12:00 | 15090 |  | 534.8 |  | 15650
|  |  |  | 13:00 | 15080 |  | 649.4 |  | 15760
|  |  |  | 14:00 | 15140 |  | 525.25 |  | 15690
|  |  |  | 15:00 | 15090 |  | 1079.15 |  | 16220
|  |  |  | 16:00 | 15070 |  | 725.8 |  | 15830
|  |  |  | 17:00 | 15050 |  | 630.3 |  | 15710
|  |  |  | 18:00 | 15430 |  | 487.05 |  | 15940
|  |  |  | 18:30 | 15620 |  | 988.425 |  | 16655
|  |  |  | 19:00 | 15820 |  | 1413.4 |  | 17300
|  |  |  | 19:30 | 15950 |  | 1384.75 |  | 17400
|  |  |  | 20:00 | 15870 |  | 1260.6 |  | 17190
|  |  |  | 21:00 | 15850 |  | 1375.2 |  | 17290
|  |  |  | 22:00 | 15790 |  | 1107.8 |  | 16950
|  |  |  | 23:00 | 15760 |  | 1337 |  | 17160
Probable Maximum Temperature: |  |  | 36.5 °C
Probable Maximum Demand at Day Peak: |  |  | 15650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1384.75
Probable Maximum Demand at Evening Peak: |  |  | 17400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15950.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 353.55 MKWHr. |  | 220 | 150 | 200 | 165 | 50 | 200 | 50 | 220 | 130 | 1385
*** This report is generated digitally from Operation Information System (OIS) at 10:01 hrs on 14-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-10-2026 | [28 empty] | Date: | 13-10-2026 | [28 empty] | Date: | 13-10-2026 | [28 empty] | Date: | 13-10-2026 | [28 empty] | Date: | 13-10-2026 | [16 empty] | Date: | 13-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17 | 54 | 149 | 126 | 230 | 55 | 55 | 72 | 0 | 0 | 510 | 0 | 35 | 320 | 0 | 0 | 0 | 143.42 | 8.5 | 22 | 0 | 475 | 107 | 212 | 50 | 0 | 0 | 51 | 48 | 35 | 25 | 25 | 0 | 222 | 110 | 4 | 1060 | 90 | 0 | 50 | 25.5 | 90 | 0 | 0 | 0 | 0 | 1087 | 0 | 143 | 108 | 0 | 320 | 342 | 44 | 15 | 201 | 33 | 74 | 88 | 139 | 68 | 13 | 98 | 70 | 52.2 | 0 | 22 | 320 | 400 | 0 | 40 | 40 | 156 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 35 | 78 | 0 | 174 | 0 | 0 | 0 | 24 | 9522.62 | 327 | 0 | 23 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 754.94 | 0 | 45 | 0 | 113 | 113 | 0 | 51 | 30 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 91 | 5657.74 | 15180.36 | 104.98
01:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 35 | 54 | 137 | 126 | 230 | 55 | 55 | 72 | 0 | 0 | 495 | 0 | 35 | 325 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 450 | 107 | 68 | 0 | 0 | 0 | 51 | 36 | 18 | 25 | 25 | 0 | 222 | 110 | 12 | 960 | 88 | 0 | 50 | 25.5 | 91 | 0 | 0 | 0 | 0 | 1162 | 0 | 147 | 108 | 0 | 323 | 342 | 44 | 15 | 199 | 33 | 78 | 88 | 139 | 73 | 13 | 102 | 68 | 52.2 | 0 | 16 | 310 | 400 | 15 | 40 | 39 | 155 | 0 | 16 | 0 | 83 | 0 | 139 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 9141.62 | 328 | 0 | 23 | 26 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 749.22 | 0 | 45 | 0 | 55 | 50 | 0 | 0 | 30 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 91 | 5473.02 | 14614.64 | 104.95
02:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 35 | 54 | 132 | 126 | 213 | 55 | 55 | 72 | 0 | 0 | 495 | 0 | 35 | 325 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 430 | 109 | 68 | 0 | 0 | 0 | 51 | 29 | 18 | 25 | 25 | 0 | 220 | 110 | 18 | 860 | 48 | 0 | 50 | 17 | 105 | 0 | 0 | 0 | 0 | 1224 | 0 | 140 | 108 | 0 | 321 | 342 | 44 | 15 | 197 | 33 | 87 | 88 | 138 | 68 | 13 | 114 | 66 | 52.2 | 0 | 16 | 305 | 400 | 100 | 40 | 39 | 156 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 22 | 9107.12 | 327 | 0 | 23 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 750.61 | 0 | 45 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 54 | 5413.41 | 14520.53 | 104.94
03:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 35 | 54 | 132 | 110 | 147 | 55 | 55 | 72 | 0 | 0 | 490 | 0 | 35 | 329 | 0 | 0 | 0 | 143.42 | 8.5 | 19 | 0 | 450 | 107 | 68 | 0 | 0 | 0 | 51 | 29 | 18 | 25 | 25 | 0 | 219 | 110 | 23 | 700 | 16 | 0 | 50 | 0 | 105 | 0 | 0 | 0 | 0 | 1224 | 0 | 137 | 108 | 0 | 298 | 342 | 44 | 15 | 183 | 33 | 88 | 88 | 139 | 18 | 13 | 114 | 64 | 52.2 | 0 | 16 | 305 | 400 | 246 | 40 | 39 | 155 | 0 | 16 | 0 | 52 | 0 | 137 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 8863.12 | 328 | 0 | 23 | 26 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1234.2 | 0 | 0 | 0 | 759.33 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 54 | 5411.13 | 14274.25 | 104.92
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 35 | 55 | 132 | 80 | 147 | 55 | 55 | 72 | 0 | 0 | 475 | 0 | 35 | 324 | 0 | 0 | 0 | 86 | 8.5 | 19 | 0 | 510 | 60 | 68 | 0 | 0 | 0 | 51 | 29 | 18 | 0 | 25 | 0 | 218 | 110 | 26 | 700 | 16 | 0 | 45 | 0 | 105 | 0 | 0 | 0 | 0 | 1160 | 0 | 145 | 108 | 0 | 336 | 342 | 44 | 15 | 204 | 33 | 79 | 90 | 138 | 0 | 13 | 8 | 62 | 0 | 0 | 16 | 256 | 400 | 276 | 40 | 39 | 152 | 0 | 16 | 0 | 52 | 0 | 137 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 8449.5 | 394 | 0 | 23 | 24 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 0 | 0 | 0 | 758.77 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 54 | 5361.57 | 13811.07 | 104.9
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 35 | 54 | 110 | 45 | 110 | 30 | 55 | 72 | 0 | 0 | 490 | 0 | 35 | 325 | 0 | 0 | 0 | 51 | 8.5 | 19 | 0 | 480 | 35 | 68 | 0 | 0 | 0 | 51 | 29 | 18 | 0 | 25 | 0 | 219 | 100 | 26 | 700 | 17 | 0 | 50 | 0 | 85 | 0 | 0 | 0 | 0 | 1160 | 0 | 100 | 108 | 0 | 332 | 342 | 44 | 15 | 207 | 33 | 54 | 90 | 68 | 0 | 13 | 0 | 62 | 0 | 0 | 16 | 260 | 400 | 276 | 40 | 39 | 155 | 0 | 16 | 0 | 52 | 0 | 135 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 8087.5 | 469 | 0 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 0 | 0 | 0 | 758.13 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 115 | 220 | 0 | 1170.6 | 300 | 54 | 5320.93 | 13408.43 | 104.9
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 35 | 54 | 96 | 45 | 110 | 30 | 35 | 72 | 0 | 0 | 495 | 0 | 35 | 329 | 0 | 0 | 0 | 51 | 8.5 | 19 | 0 | 450 | 35 | 68 | 0 | 0 | 0 | 51 | 29 | 35 | 0 | 25 | 0.01 | 219 | 68 | 26 | 705 | 16 | 0 | 50 | 0 | 68 | 0 | 0 | 0 | 0 | 1160 | 0 | 100 | 108 | 0 | 325 | 342 | 44 | 15 | 195 | 33 | 52 | 90 | 68 | 0 | 13 | 0 | 58 | 0 | 0 | 16 | 264 | 400 | 276 | 40 | 39 | 156 | 0 | 16 | 0 | 52 | 0 | 138 | 0 | 100 | 35 | 59 | 0.1 | 67 | 0 | 0 | 0.15 | 24 | 7984.76 | 469 | 0 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 0 | 0 | 0 | 740 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0.02 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 263 | 115 | 220 | 0 | 1155 | 300 | 54 | 5258.29 | 13243.05 | 104.88
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 17 | 54 | 96 | 50 | 110 | 30 | 0 | 72 | 0 | 0 | 500 | 0 | 17 | 326 | 0 | 0 | 6 | 68 | 8.5 | 19 | 0 | 490 | 48 | 68 | 0 | 0 | 0 | 51 | 29 | 35 | 0 | 25 | 0.49 | 218 | 75 | 26 | 705 | 40 | 0 | 50 | 0 | 83 | 0 | 0 | 0 | 0 | 1192 | 4 | 103 | 105 | 0 | 338 | 320 | 44 | 15 | 206 | 33 | 55 | 89 | 84 | 0 | 9 | 0 | 60 | 0 | 8 | 16 | 263 | 400 | 276 | 40 | 39 | 159 | 2 | 16 | 0 | 52 | 0 | 138 | 0 | 100 | 35 | 59 | 4.5 | 67 | 0 | 0.4 | 10.36 | 24 | 8123.25 | 469 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 38 | 13 | 1234.2 | 0 | 0 | 0 | 742.02 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 9.71 | 16 | 0 | 0 | 11.68 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 1.03 | 0 | 0 | 74 | 6 | 105 | 0 | 0 | 0 | 0.7 | 35 | 0.07 | 16 | 307 | 115 | 220 | 0 | 1170.6 | 300 | 54 | 5466.01 | 13589.26 | 104.84
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 17 | 54 | 105 | 45 | 145 | 30 | 0 | 72 | 0 | 0 | 390 | 0 | 17 | 324 | 0 | 0 | 15 | 68 | 7 | 19 | 0 | 425 | 53 | 68 | 0 | 0 | 0 | 0 | 29 | 35 | 12 | 25 | 0.96 | 220 | 92 | 11 | 708 | 88 | 0 | 48 | 7 | 68 | 0 | 0 | 0 | 0 | 1168 | 0 | 115 | 107 | 0 | 339 | 342 | 44 | 15 | 205 | 30 | 53 | 89 | 102 | 2 | 0 | 17 | 64 | 16 | 35 | 16 | 275 | 400 | 151 | 40 | 39 | 153 | 6 | 16 | 0 | 52 | 0 | 138 | 0 | 100 | 35 | 59 | 11.18 | 67 | 0 | 1.2 | 26.29 | 24 | 8007.63 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 38 | 1234.2 | 0 | 0 | 0 | 739.91 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 27.73 | 48 | 0 | 0 | 31.18 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 2.81 | 0 | 0 | 70 | 17 | 106 | 0 | 0 | 0 | 3.1 | 94 | 0.22 | 16 | 266 | 114 | 220 | 0 | 1170.6 | 300 | 54 | 5561.75 | 13569.38 | 104.83
09:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 54 | 114 | 15 | 145 | 30 | 17 | 72 | 0 | 0 | 395 | 0 | 17 | 326 | 0 | 0 | 24 | 68 | 5 | 19 | 0 | 405 | 35 | 100 | 0 | 0 | 0 | 0 | 29 | 35 | 12 | 25 | 1.75 | 221 | 85 | 3 | 850 | 52 | 0 | 39 | 8 | 68 | 0 | 0 | 0 | 0 | 1160 | 15 | 127 | 107 | 0 | 319 | 342 | 44 | 15 | 191 | 33 | 54 | 88 | 85 | 55 | 0 | 17 | 62 | 16 | 56 | 8 | 282 | 400 | 146 | 40 | 40 | 155 | 9 | 16 | 0 | 52 | 0 | 137 | 0 | 100 | 0 | 59 | 16.52 | 114 | 0 | 1.7 | 39.9 | 24 | 8167.87 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 61 | 1234.2 | 0 | 0 | 0 | 750.69 | 0 | 45 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 42.93 | 76 | 0 | 0 | 49.18 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 4.31 | 0 | 0 | 70 | 27 | 107 | 0 | 0 | 0 | 4.9 | 152 | 0.4 | 16 | 244 | 113 | 220 | 0 | 1170.6 | 300 | 54 | 5673.21 | 13841.08 | 104.82
10:00 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 17 | 54 | 114 | 15 | 95 | 30 | 35 | 72 | 0 | 0 | 400 | 0 | 35 | 317 | 0 | 0 | 30 | 68 | 5 | 18 | 0 | 480 | 17 | 100 | 0 | 0 | 0 | 0 | 28 | 35 | 37 | 25 | 3.67 | 221 | 68 | 2 | 960 | 16 | 0 | 24 | 8 | 68 | 0 | 0 | 0 | 0 | 1165 | 18 | 122 | 108 | 0 | 328 | 342 | 44 | 15 | 202 | 33 | 53 | 88 | 17 | 73 | 0 | 17 | 68 | 8 | 66 | 8 | 275 | 395 | 146 | 40 | 40 | 155 | 10 | 16 | 0 | 52 | 0 | 137 | 0 | 100 | 0 | 59 | 20 | 125 | 0 | 2.2 | 48.94 | 22 | 8292.81 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 83 | 1234.2 | 0 | 0 | 0 | 752.25 | 0 | 45 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 54.45 | 97 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 5.33 | 0 | 0 | 35 | 33 | 107 | 0 | 0 | 0 | 6 | 183 | 0.51 | 16 | 248 | 113 | 220 | 0 | 1170.6 | 300 | 54 | 5702.34 | 13995.15 | 104.82
11:00 | 0 | 35 | 49 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 54 | 114 | 15 | 95 | 33 | 35 | 72 | 0 | 0 | 405 | 0 | 35 | 317 | 0 | 0 | 32 | 51 | 5 | 14 | 0 | 500 | 17 | 128 | 0 | 0 | 0 | 0 | 38 | 35 | 37 | 25 | 3.7 | 221 | 68 | 0 | 1060 | 16 | 0 | 27 | 8 | 73 | 80 | 0 | 0 | 0 | 1224 | 18 | 122 | 108 | 0 | 337 | 342 | 44 | 15 | 208 | 33 | 54 | 85 | 17 | 73 | 5 | 52 | 70 | 8 | 76 | 8 | 279 | 390 | 146 | 39 | 38 | 155 | 10 | 16 | 0 | 52 | 0 | 137 | 0 | 100 | 5 | 59 | 21.62 | 116 | 0 | 2.2 | 53.77 | 22 | 8661.29 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 90 | 1234.2 | 0 | 0 | 0 | 754.16 | 0 | 44 | 0 | 55 | 35 | 0 | 0 | 0 | 0 | 60.05 | 108 | 0 | 0 | 66.36 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 5.9 | 0 | 0 | 35 | 32 | 106 | 0 | 0 | 0 | 6.7 | 204 | 0.55 | 32 | 307 | 113 | 220 | 0 | 1170.6 | 300 | 54 | 5810.52 | 14471.81 | 104.81
12:00 | 0 | 52 | 47 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 54 | 114 | 85 | 210 | 55 | 35 | 72 | 0 | 0 | 410 | 0 | 35 | 315 | 0 | 0 | 32 | 110 | 5 | 18 | 0 | 530 | 22 | 155 | 0 | 0 | 0 | 0 | 38 | 36 | 37 | 25 | 3.75 | 221 | 68 | 0 | 1060 | 16 | 0 | 30 | 8 | 90 | 81 | 0 | 0 | 0 | 1224 | 8 | 123 | 108 | 0 | 347 | 342 | 44 | 15 | 211 | 33 | 53 | 85 | 31 | 74 | 8 | 101 | 76 | 34 | 72 | 7 | 276 | 388 | 146 | 39 | 39 | 153 | 10 | 16 | 0 | 52 | 0 | 136 | 0 | 100 | 17 | 59 | 22.1 | 115 | 0 | 2.2 | 54.15 | 22 | 9133.2 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 89 | 1234.2 | 0 | 0 | 0 | 754.93 | 0 | 45 | 0 | 55 | 60 | 0 | 5 | 0 | 0 | 60.41 | 110 | 0 | 0 | 66.86 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 5.99 | 0 | 0 | 73 | 31 | 105 | 0 | 0 | 0 | 6.9 | 208 | 0.5 | 48 | 307 | 107 | 220 | 0 | 1170.6 | 300 | 54 | 5952.39 | 15085.59 | 104.81
13:00 | 0 | 96 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 54 | 132 | 96 | 225 | 55 | 35 | 72 | 0 | 0 | 385 | 0 | 35 | 316 | 0 | 0 | 31 | 143.42 | 5 | 18 | 0 | 460 | 57 | 155 | 11 | 0 | 0 | 0 | 37 | 36 | 37 | 25 | 3.53 | 221 | 74 | 0 | 1060 | 16 | 0 | 36 | 9 | 105 | 81 | 0 | 0 | 0 | 1224 | 4 | 128 | 108 | 0 | 303 | 342 | 44 | 15 | 191 | 33 | 54 | 84 | 100 | 72 | 9 | 114 | 72 | 52.2 | 67 | 13 | 285 | 394 | 96 | 39 | 39 | 151 | 9 | 16 | 0 | 79 | 0 | 139 | 0 | 100 | 17 | 59 | 21.43 | 115 | 0 | 2.1 | 49.99 | 24 | 9215.67 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 84 | 1234.2 | 0 | 0 | 0 | 743.18 | 0 | 38 | 0 | 55 | 90 | 0 | 8.3 | 0 | 0 | 54.69 | 107 | 0 | 0 | 62.86 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 5.55 | 0 | 0 | 95 | 34 | 55 | 0 | 0 | 0 | 6.5 | 198 | 0.3 | 48 | 307 | 107 | 180 | 0 | 1170.6 | 300 | 54 | 5862.18 | 15077.85 | 104.8
14:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 54 | 132 | 106 | 225 | 55 | 35 | 72 | 0 | 0 | 405 | 0 | 35 | 310 | 0 | 0 | 27 | 143.42 | 5 | 18 | 0 | 505 | 97 | 155 | 45 | 0 | 0 | 0 | 37 | 36 | 37 | 25 | 3.12 | 221 | 71 | 0 | 1060 | 16 | 0 | 44 | 17 | 105 | 81 | 0 | 0 | 0 | 1162 | 0 | 123 | 108 | 0 | 328 | 342 | 44 | 15 | 210 | 32 | 54 | 84 | 122 | 73 | 13 | 107 | 76 | 52.2 | 57 | 14 | 295 | 381 | 85 | 39 | 38 | 151 | 9 | 16 | 0 | 80 | 0 | 138 | 0 | 100 | 17 | 59 | 18.37 | 115 | 0 | 1.7 | 43.55 | 20 | 9332.36 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 69 | 1234.2 | 0 | 0 | 0 | 760.31 | 0 | 38 | 0 | 55 | 90 | 0 | 8.3 | 0 | 0 | 45.87 | 94 | 0 | 0 | 54.56 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 4.84 | 0 | 0 | 100 | 31 | 34 | 0 | 0 | 0 | 5.5 | 170 | 0.48 | 48 | 307 | 107 | 220 | 0 | 1170.6 | 300 | 54 | 5811.66 | 15144.02 | 104.8
15:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 54 | 132 | 106 | 225 | 55 | 35 | 72 | 0 | 0 | 455 | 0 | 35 | 312 | 0 | 0 | 20 | 143.42 | 5 | 18 | 0 | 410 | 107 | 155 | 50 | 0 | 1 | 0 | 30 | 36 | 37 | 24 | 0.56 | 218 | 91 | 0 | 1060 | 16 | 0 | 42 | 17 | 105 | 81 | 0 | 0 | 0 | 1224 | 0 | 114 | 143 | 0 | 310 | 342 | 33 | 15 | 197 | 32 | 58 | 84 | 137 | 70 | 13 | 103 | 82 | 52.2 | 42 | 14 | 303 | 390 | 85 | 39 | 38 | 151 | 7 | 16 | 0 | 81 | 0 | 139 | 0 | 100 | 17 | 59 | 13.8 | 115 | 0 | 1.4 | 32.52 | 24 | 9338.9 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 48 | 1234.2 | 0 | 0 | 0 | 740.84 | 0 | 36 | 0 | 113 | 110 | 0 | 8.5 | 0 | 0 | 38.12 | 67 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 3.58 | 0 | 0 | 115 | 23 | 34 | 0 | 0 | 0 | 4.1 | 125 | 0.33 | 48 | 307 | 107 | 220 | 0 | 1170.6 | 300 | 54 | 5754.03 | 15092.93 | 104.79
16:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 127 | 106 | 260 | 55 | 35 | 126 | 0 | 0 | 415 | 0 | 35 | 311 | 0 | 0 | 12 | 142 | 5 | 18 | 0 | 480 | 107 | 159 | 50 | 0 | 6 | 0 | 30 | 36 | 37 | 24 | 0.51 | 218 | 109 | 0 | 1060 | 16 | 0 | 42 | 17 | 105 | 81 | 0 | 0 | 0 | 1224 | 6 | 105 | 145 | 0 | 337 | 330 | 33 | 15 | 208 | 34 | 40 | 84 | 138 | 72 | 13 | 114 | 80 | 52.2 | 22 | 7 | 310 | 390 | 85 | 39 | 36 | 151 | 4 | 16 | 0 | 80 | 0 | 138 | 0 | 100 | 17 | 58 | 8.26 | 115 | 0 | 0.6 | 17.75 | 24 | 9443.32 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 27 | 1234.2 | 0 | 0 | 0 | 745.95 | 0 | 36 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 22.11 | 42 | 0 | 0 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 1.96 | 0 | 0 | 115 | 13 | 34 | 0 | 0 | 0 | 2.2 | 72 | 0.19 | 59 | 307 | 107 | 220 | 0 | 1170.6 | 300 | 54 | 5630.51 | 15073.83 | 104.79
17:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 54 | 115 | 107 | 270 | 55 | 35 | 162 | 0 | 0 | 450 | 0 | 55 | 314 | 0 | 0 | 1 | 143.42 | 5 | 18 | 0 | 395 | 109 | 208 | 47 | 0 | 7 | 0 | 34 | 54.36 | 37 | 24 | 0 | 218 | 110 | 0 | 1060 | 16 | 0 | 50 | 17 | 105 | 121 | 0 | 0 | 0 | 1224 | 0 | 109 | 147 | 0 | 295 | 342 | 33 | 15 | 184 | 32 | 34 | 85 | 137 | 72 | 13 | 114 | 76 | 52.2 | 6 | 14 | 320 | 398 | 74 | 40 | 38 | 151 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 100 | 17 | 58 | 1.68 | 116 | 0 | 0.1 | 3.03 | 24 | 9526.79 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 5 | 1234.2 | 0 | 0 | 0 | 745.09 | 0 | 37 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 3.52 | 8 | 0 | 0 | 3.53 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0.22 | 0 | 0 | 115 | 3 | 42 | 0 | 0 | 0 | 0.4 | 15 | 0.04 | 64 | 307 | 105 | 220 | 0 | 1170.6 | 300 | 100 | 5527.1 | 15053.89 | 104.78
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 54 | 129 | 107 | 295 | 55 | 55 | 162 | 0 | 0 | 405 | 0 | 55 | 311 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 525 | 107 | 208 | 56 | 0 | 0 | 0 | 39 | 54.36 | 100 | 78 | 0 | 218 | 110 | 0 | 1080 | 112 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 0 | 148 | 0 | 344 | 335 | 44 | 15 | 213 | 34 | 40 | 86 | 138 | 72 | 13 | 114 | 82 | 52.2 | 0 | 15 | 320 | 393 | 74 | 39 | 37 | 152 | 0 | 0 | 0 | 82 | 0 | 137 | 0 | 100 | 17 | 58 | 0 | 122 | 0 | 0 | 0 | 24 | 9906.48 | 328 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 742.38 | 0 | 38 | 0 | 113 | 113 | 0 | 33 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 106 | 220 | 0 | 1170.6 | 300 | 119 | 5521.18 | 15427.66 | 104.78
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 54 | 54 | 132 | 122 | 295 | 55 | 55 | 162 | 0 | 0 | 525 | 0 | 55 | 317 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 490 | 107 | 212 | 67 | 0 | 7 | 34 | 39 | 54.36 | 100 | 67 | 0 | 219 | 110 | 0 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 36 | 148 | 0 | 340 | 342 | 44 | 15 | 204 | 34 | 115 | 86 | 145 | 72 | 13 | 114 | 78 | 52.2 | 0 | 15 | 310 | 395 | 74 | 40 | 28 | 153 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 24 | 10299.48 | 294 | 0 | 28 | 12 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 754.51 | 0 | 38 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 114 | 150 | 0 | 1170.6 | 300 | 137 | 5517.31 | 15816.79 | 104.77
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 54 | 133 | 122 | 295 | 55 | 55 | 162 | 0 | 0 | 560 | 0 | 55 | 317 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 540 | 107 | 212 | 57 | 0 | 17 | 34 | 43 | 54.36 | 100 | 68 | 0 | 219 | 110 | 2 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 80 | 148 | 0 | 338 | 320 | 44 | 15 | 194 | 35 | 115 | 85 | 155 | 73 | 13 | 108 | 80 | 52.2 | 0 | 15 | 312 | 395 | 74 | 40 | 28 | 152 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 10405.48 | 294 | 0 | 24 | 25 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 752.61 | 0 | 43 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 113 | 124 | 0 | 1170.6 | 300 | 137 | 5508.41 | 15913.89
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 54 | 54 | 132 | 122 | 280 | 55 | 55 | 162 | 0 | 0 | 555 | 0 | 55 | 317 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 520 | 109 | 212 | 58 | 0 | 3 | 34 | 44 | 54.36 | 100 | 69 | 0 | 220 | 110 | 2 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 103 | 147 | 0 | 300 | 320 | 44 | 15 | 198 | 36 | 115 | 86 | 155 | 72 | 13 | 108 | 80 | 52.2 | 0 | 15 | 310 | 395 | 74 | 40 | 30 | 153 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 100 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 10350.48 | 294 | 0 | 24 | 50 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 753.35 | 0 | 46 | 0 | 113 | 113 | 0 | 51 | 40 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 114 | 110 | 0 | 1170.6 | 300 | 137 | 5526.15 | 15876.63 | 104.77
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 54 | 133 | 124 | 280 | 55 | 55 | 162 | 0 | 0 | 545 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 420 | 109 | 212 | 69 | 0 | 62 | 34 | 43 | 54.36 | 100 | 70 | 0 | 221 | 110 | 4 | 1080 | 160 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 132 | 128 | 0 | 294 | 255 | 44 | 15 | 219 | 36 | 115 | 88 | 157 | 73 | 13 | 114 | 76 | 52.2 | 0 | 15 | 310 | 400 | 74 | 40 | 30 | 155 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 88 | 0 | 163 | 0 | 0 | 0 | 24 | 10296.48 | 293 | 0 | 22 | 45 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 756.22 | 0 | 47 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 110 | 0 | 1170.6 | 300 | 137 | 5522.02 | 15818.5 | 104.76
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 54 | 54 | 133 | 124 | 280 | 55 | 55 | 162 | 0 | 0 | 510 | 0 | 55 | 314 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 550 | 109 | 212 | 67 | 0 | 30 | 34 | 43 | 54.36 | 100 | 88 | 0 | 221 | 110 | 4 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 144 | 128 | 0 | 315 | 280 | 44 | 15 | 212 | 33 | 115 | 88 | 156 | 73 | 13 | 114 | 74 | 52.2 | 0 | 15 | 308 | 400 | 74 | 40 | 30 | 155 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 100 | 17 | 91 | 0 | 163 | 0 | 0 | 0 | 24 | 10393.48 | 294 | 0 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 760.78 | 0 | 47 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 114 | 110 | 0 | 1170.6 | 300 | 90 | 5476.58 | 15870.06 | 104.76
23:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 35 | 54 | 133 | 124 | 279 | 55 | 55 | 126 | 0 | 0 | 430 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 390 | 107 | 196 | 64 | 0 | 4 | 34 | 43 | 54.36 | 88 | 88 | 0 | 222 | 110 | 4 | 1080 | 117 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 150 | 128 | 0 | 293 | 255 | 44 | 15 | 195 | 36 | 108 | 70 | 156 | 73 | 13 | 114 | 74 | 52.2 | 0 | 15 | 304 | 400 | 85 | 40 | 30 | 156 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 75 | 17 | 88 | 0 | 163 | 0 | 0 | 0 | 24 | 9871.48 | 337 | 0 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 760.14 | 0 | 47 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 110 | 0 | 1170.6 | 300 | 90 | 5541.94 | 15413.42 | 104.75
Total KWH | 0 | 1892160 | 510240 | 0 | 0 | 0 | 0 | 0 | 9835200 | 0 | 0 | 778320 | 1298520 | 2981088 | 2166720 | 4905022 | 1166617 | 935683 | 2357280 | 0 | 0 | 11098237 | 0 | 930135 | 7671340 | 0 | 0 | 232811 | 2810400 | 148800 | 443880 | 0 | 11444090.91 | 2011036 | 3309491 | 643200 | 0 | 133920 | 558224 | 827731 | 914518 | 1011840 | 887040 | 18606 | 5289080 | 2378600 | 191520 | 22741818.18 | 1520509 | 0 | 1100160 | 332694 | 2345163 | 1515810 | 0 | 0 | 0 | 28718179 | 85185 | 2858690 | 2910545 | 0 | 8242000 | 7954000 | 979132 | 377280 | 4974000 | 800712 | 1671360 | 2055621 | 2814240 | 1310400 | 263540 | 1902660 | 1684800 | 864341 | 500354 | 314368 | 7089000 | 9435500 | 3187000 | 942000 | 879960 | 3703418.18 | 85338 | 387024 | 0 | 1691520 | 0 | 3128000 | 0 | 2374280 | 540000 | 1566000 | 157118 | 2668800 | 0 | 15750 | 382440 | 572160 | 221424219.27 | 9512727 | 0 | 265440 | 332288 | 0 | 0 | 0 | 0 | 0 | 1793808 | 588960 | 29665450 | 0 | 0 | 0 | 17875107 | 0 | 1052087 | 0 | 1909920 | 1989696 | 0 | 367632 | 238805 | 0 | 419512 | 788810 | 218367 | 0 | 471008 | 0 | 0 | 0 | 0 | 0 | 0 | 7309818 | 0 | 41280 | 0 | 0 | 2196477 | 255349 | 2198179 | 0 | 0 | 0 | 46830.48 | 1448640 | 3696 | 1024512 | 7156000 | 2741000 | 4770270 | 0 | 28261818 | 7242181.82 | 1725600 | 133911268.3 | 355335487.57

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15085.59 | MW | 12:00 Hr. | Energy Generated |  |  | 355.3355 |  | MKWHr.
| Day Peak Demand |  |  | 15090.59 | MW | 12:00 Hr. | Energy Unserverd |  |  | 18.458 |  | MKWHr.
| Evening Peak Generation |  |  | 15913.89 | MW | 19:30 Hr. | Energy Demand |  |  | 373.7935 |  | MKWHr.
| Evening Peak Demand |  |  | 17860.89 | MW | 19:30 Hr. | Maximum Temperature |  |  | 36.5 |  | °C
| Minimum Generation of the Day |  |  | 13243.05 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 854.68 |  | MMCFD
| Maximum Generation of the Day |  |  | 15913.89 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 8.7484 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6415 | 0 | 22.7322 | 0 | 0 | 0.23281 | 0 | 0 | 63.6065 | Gas | 118.5445 | Gas | 408841398.2703
| Chattogram Zone |  |  | 1.7073 | 51.46 | 17.8402 | 0 | 5.2891 | 0.10379 | 0 | 0.13392 | 76.5343 | Coal | 123.7854 | Coal | 895826045.7308
| Cumilla Zone |  |  | 28.5568 | 0 | 11.7361 | 0 | 0 | 0.50035 | 1.6848 | 0 | 42.478 | HFO | 72.9682 | HFO | 1515614786.23
| Mymensingh Zone |  |  | 0 | 0 | 5.347 | 0 | 0 | 0.55531 | 0 | 0 | 5.9023 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.8177 | 0 | 0 | 0 | 0 | 0.085338 | 0 | 0 | 32.903 | Hydro | 5.2891 | Hydro | 528908
| Khulna Zone |  |  | 0 | 29.6654 | 2.3915 | 0 | 0 | 0.58896 | 9.5127 | 0 | 42.1587 | Solar | 5.5417 | Solar | 89175426.3536
| Barishal Zone |  |  | 7.5113 | 42.66 | 2.7501 | 0 | 0 | 0.003696 | 0 | 0 | 52.9251 | Import | 29.0726 | Import | 196647466.2
| Rajshahi Zone |  |  | 7.3098 | 0 | 5.7765 | 0 | 0 | 1.7206 | 17.8751 | 0 | 32.682 | Wind | 0.13392 | Wind | 1987372.8
| Rangpur Zone |  |  | 0 | 0 | 4.3947 | 0 | 0 | 1.7508 | 0 | 0 | 6.1455
| Total |  |  | 118.5445 | 123.7854 | 72.9682 | 0 | 5.2891 | 5.5417 | 29.0726 | 0.13392 | 355.3355
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 408841398.2703 |  | Hydro | 528908
|  |  |  | Coal | 895826045.7308 |  | Solar | 89175426.3536
|  |  |  | HFO | 1515614786.23 |  | Import | 196647466.2
|  |  |  | HSD | 0 |  | Wind | 1987372.8
[5 empty] | Total: | 310,86,21,403 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 243509.09 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 9.5127 | Peak Hr Flow | 294.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 30457200 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.8751 | Peak Hr Flow | 752.61 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 742 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.6848 | Peak Hr Flow | 80.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1937 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 29.0726 | Peak Hr Flow | 1126.61 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 244 |  | 6286
|  |  |  | Chattogram |  | 171 |  | 1604
|  |  |  | Cumilla |  | 270 |  | 1702
|  |  |  | Mymensingh |  | 182 |  | 1407
|  |  |  | Sylhet |  | 147 |  | 790
|  |  |  | Khulna |  | 283 |  | 2029
|  |  |  | Barishal |  | 146 |  | 583
|  |  |  | Rajshahi |  | 255 |  | 1702
|  |  |  | Rangpur |  | 165 |  | 1014
|  |  |  | Total |  | 1863 |  | 17117
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Karnaphuli Hydro PP Unit-5 |  |  | 50
[7 empty] | 5 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 488.5
|  |  |  | Total Unavailable Capacity |  |  |  | 788.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 17:21 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to For Annual Maintenance Work
| 08:20 | 13:03 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Purbasadipur 230/132/33kV end
Due to EPVL side RTU equipment installation work
| 08:20 | 17:20 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to For Annual Maintenance work
| 08:24 | 16:59 | Shariatpur 132/33kV S/S Main Bus - 1 Scheduled S/D Due to Annual Maintenance work .
| 09:36 | 16:52 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
maintenance work
| 09:47 | 13:46 | Madunaghat-Meghnaghat 400kV Ckt-1 Project Work S/D from Meghnaghat 400/230kV end Due to
For Project Work.
| 09:51 | 13:45 | Korerhat 400/230/132kV S/S Meghnaghat-1 (C04) Project Work S/D Due to For project work
| 10:05 |  | Thakurgaon 132/33kV S/S RPC Indoor-2 Scheduled S/D Due to Annual Maintenance
| 10:40 | 15:48 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to DS alignment adjust.
| 10:40 | 15:45 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to DS alignment adjust.
| 10:59 |  | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D Due to 33kV sreenagar feeder DS plate &
finger change.
| 11:28 | 15:27 | Bogura 230/132kV S/S T-01 LT Project Work S/D
| 11:28 | 15:26 | Bogura 230/132kV S/S T-01 HT Project Work S/D
| 12:00 |  | Day Peak Generation: 15085 MW.
| 13:13 | 14:18 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to Oil leakage under main tank &
conservator connection pipe
| 13:13 | 14:18 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to Oil leakage under main tank &
conservator connection pipe
| 13:16 | 15:44 | Thakurgaon-Thakurgaon EPV 132kV Ckt-2 Scheduled S/D from Thakurgaon 132/33kV end.
| 14:20 | 18:07 | Korerhat 400/230/132kV S/S 400/230 KV ATR-3 (7103T) LT Project Work S/D Due to For
project work
| 14:21 | 18:06 | Korerhat 400/230/132kV S/S 400/230 KV ATR-3 (7103T) HT Project Work S/D Due to For
project work
| 14:23 | 16:01 | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to Oil leakage under main tank &
conservator connection pipe
| 14:23 | 16:01 | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to Oil leakage under main tank &
conservator connection pipe
| 14:29 | 18:16 | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to DFDR testing
witness work at Korerhat end
| 14:30 | 18:15 | Korerhat 400/230/132kV S/S Feni-1 (D06) Project Work S/D Due to For project work
|  | 14:56 | Chandpur 132/33kV S/S 412T (T-2) HT is restored.
|  | 15:50 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 15:52 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
| 16:07 | 18:10 | Thakurgaon-Thakurgaon EPV 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due to
According to the instruction of ALDC, Bogura.
|  | 16:35 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
|  | 16:55 | Bogura 230/132kV S/S 132KV Main 2 is restored.
| 17:41 | 21:24 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kV Nabinagar Feeder Red hot
Maintanence
|  | 17:48 | Bog-Sherpur 132/33kV S/S Main Bus-2 is restored.
| 18:28 |  | At Bogura 230/132 kV grid s/s, Sabgram ckt-1 bay was charged for the first time.
| 18:34 | 21:25 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kV Nabinagar Feeder Red hot
Maintenance
| 19:20 |  | At Bogura 230/132 kV grid s/s, Sabgram ckt-2 bay was charged for the first time.
| 19:30 |  | Evening peak generation is 15914 MW.
| 19:42 |  | Bhola Nutan Biddut BD LTD Forced Shutdown with remarks:- GT-11
| 19:42 |  | Bhola Nutan Biddut BD LTD GT-1 Shutdown with remarks:- GT11 was shut down at 19:42 hrs.
on October 13, 2026.
| 00:00 |  | Bhola Nutan Biddut BD LTD ST Shutdown with remarks:- STG was shutdown.
| 00:00 |  | Bhola Nutan Biddut BD LTD Shutdown with remarks:- GT12
| 00:12 |  | Bhola Nutan Biddut BD LTD GT-2 Shutdown with remarks:- GT-12 was shutdown
| 06:00 |  | Minimum Generation: 13515 MW.
| 06:34 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to None
| 06:35 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to None
| 07:07 |  | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end.
| 07:08 |  | Bhandaria 132/33kV S/S Transformer-2 LT Scheduled S/D Due to annual maintenance
| 07:09 |  | Bhandaria 132/33kV S/S Transformer-2 HT Scheduled S/D Due to annual maintenance
| 07:13 |  | Barapukuria-Saidpur 132 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end Due
to 230 KV Barapukuria (N)- Rangpur line stringing work by G2G project
| 07:14 |  | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to G2G
Project work.
| 07:15 |  | Barapukuria-Saidpur 132 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end Due
to 230 KV Barapukuria (N)- Rangpur line stringing work by G2G project and from Saidpur
132/33kV end Due to G2G project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 406 | 9835200 | Machine Problem
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1166617 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7671340 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 778320 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 2166720 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935683 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 930135 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 148800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 443880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 510240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4905022 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2981088 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1892160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2357280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 232811 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1298520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 540 | 11444090.91 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 560 | 11098237 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2810400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 3127.42 | 63606543.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 332694 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 85185 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1100160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5289080 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 111 | 1515810 | STG Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2345163 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 827731 | Fuel Shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 558224 | Fuel Shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1011840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 191520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 57 | 643200 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18606 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 212 | 3309491 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 914518 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2378600 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 68 | 887040 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2011036 | Machine Problem
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 162 | 1520509 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28718179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 17 | 133920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 22741818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3780.86 | 76534324.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 194 | 4974000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 338 | 8242000 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 7954000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 800712 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 15 | 377280 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 148 | 2910545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 979132 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 2858690 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 314368 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2055621 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 2814240 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 80 | 1684800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 864341 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 263540 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1902660 | Machine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1310400 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1671360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 500354 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1870.2 | 42478043
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 157118 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2668800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1566000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 382440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 572160 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 540000 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 674.21 | 291 | 5902268
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 85338 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 942000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 879960 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3703418.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 136 | 3128000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1691520 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2374280 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 387024 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 312 | 7089000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 74 | 3187000 | plant availability zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 395 | 9435500 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1336 | 32903040.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 294 | 9512727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 265440 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 332288 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1793808 | Machine Problem
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 588960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29665450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1662.2 | 42158673
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 28261818 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1024512 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 113 | 2741000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7242181.82 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 124 | 4770270 | Machine Problem
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1725600 | Machine Problem
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7156000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3696 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2215.6 | 52925077.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 419512 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 1052087 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 238805 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 266 | 7309818 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 218367 | Fuel Shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 367632 | plant availability zero
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1989696 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1909920 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 41280 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 752.61 | 17875107 | U1 under maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 471008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 788810 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1402.61 | 32682042
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2198179 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46830.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2196477 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 255349 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1448640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 6145475.48
Eastern Grid Total |  |  |  |  | 16961.086 | 10405.48 | 221424219.27
Western Grid Total |  |  |  |  | 11731.125 | 5508.41 | 133911268.3
National Grid Total |  |  |  |  | 28692.211 | 15913.89 | 355335487.57
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-10-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10775.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4478.5 | MW
i) Dhaka area |  |  | 6042.14 |  | MW | i) Khulna area |  |  |  | 1746 | MW
ii) Chattogram area |  |  | 1433 |  | MW | ii) Barishal area |  |  |  | 436.9 | MW
iii) Cumilla area |  |  | 1432.15 |  | MW | iii) Rajshahi area |  |  |  | 1446.6 | MW
iv) Mymensingh area |  |  | 1225 |  | MW | iv) Rangpur area |  |  |  | 849 | MW
v) Sylhet area |  |  | 643 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15253.79 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 16 | 19:30 | 72 | Hatirjheel | 83 | 11:00 | 143 | PHP | 9 | 11:00
2 | AKSML | 162 | 17:00 | 73 | Ishurdi | 73 | 12:00 | 144 | Pabna | 99 | 21:00
3 | Aftabnagar | 48 | 18:00 | 74 | Jaldhaka | 66 | 20:00 | 145 | Palashbari | 116 | 18:00
4 | Agargaon | 139 | 13:00 | 75 | Jamalpur | 145 | 19:00 | 146 | Panchagarh | 65 | 18:30
5 | Agrabad | 82 | 16:00 | 76 | Jashore | 134 | 20:00 | 147 | Patiya | 31 | 21:00
6 | Amnura | 33 | 05:00 | 77 | Jhenaidah | 95 | 18:00 | 148 | Patnitala | 32 | 21:00
7 | Araihazar | 101 | 08:00 | 78 | Joydebpur | 173 | 19:00 | 149 | Patuakhali | 65.5 | 21:00
8 | Ashuganj | 0.55 | 00:00 | 79 | Joypurhat | 55 | 20:00 | 150 | Payra | 32 | 22:00
9 | Ashuganj-230 | 103 | 00:00 | 80 | Juldah | 20 | 12:00 | 151 | Postogola | 65 | 13:00
10 | BSRM | 204 | 04:00 | 81 | KSRM | 26 | 18:00 | 152 | Pubail | 51 | 19:00
11 | Bagerhat | 85 | 20:00 | 82 | Kabirpur | 268 | 16:00 | 153 | Purbachal | 33 | 18:00
12 | Bajitpur | 98 | 19:00 | 83 | Kachua | 86 | 14:00 | 154 | Purbasadipur | 108 | 13:00
13 | Bakerganj | 14 | 22:00 | 84 | Kaliganj | 40 | 19:30 | 155 | Rahanpur | 36 | 19:00
14 | Bakulia | 108 | 15:00 | 85 | Kallyanpur | 117 | 19:00 | 156 | Rahim | 40 | 08:00
15 | Banani | 70 | 11:00 | 86 | Kalurghat | 44 | 10:00 | 157 | Rajbari | 80 | 21:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 102 | 13:00 | 158 | Rajendrapur | 150 | 19:00
17 | Barapukuria | 51 | 13:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 130 | 18:00
18 | Barguna | 22 | 23:00 | 89 | Kasba | 34 | 03:00 | 160 | Rajshahi-230 | 102 | 12:00
19 | Barishal | 108 | 12:00 | 90 | Kazla | 133 | 13:00 | 161 | Ramganj | 96 | 22:00
20 | Barishal-230 | 90 | 03:00 | 91 | Keranigonj | 104 | 19:00 | 162 | Rampur | 48 | 01:00
21 | Baroaulia | 45 | 09:00 | 92 | Khagrachori | 36 | 14:00 | 163 | Rangamati | 17 | 19:00
22 | Baroirhat | 62 | 18:00 | 93 | Khulna | 65 | 13:00 | 164 | Rangpur | 118 | 18:00
23 | Bashundhara | 218 | 18:00 | 94 | Khulshi | 195 | 12:00 | 165 | Ruppur | 4.4 | 10:00
24 | BashundharaCement | 1 | 10:00 | 95 | Kishoreganj | 129 | 00:00 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 72 | 20:00 | 96 | Kodda | 313 | 12:00 | 167 | Saidpur | 92 | 08:00
26 | Benapole | 67 | 18:30 | 97 | Kulaura | 52 | 21:00 | 168 | Santhia | 38 | 18:00
27 | Bhaluka | 138 | 15:00 | 98 | Kurigram | 62 | 07:00 | 169 | Satkhira | 137 | 20:00
28 | Bhandaria | 56 | 04:00 | 99 | Kushtia | 141 | 12:00 | 170 | Satmasjid | 111 | 13:00
29 | Bhangura | 37 | 18:00 | 100 | Laksam | 37 | 02:00 | 171 | Savar | 222 | 15:00
30 | Bheramara(GK) | 59 | 21:00 | 101 | Lakshmipur | 49 | 01:00 | 172 | SevenRings | 20.12 | 07:00
31 | Bhulta | 222 | 17:00 | 102 | Lalbag | 83 | 19:00 | 173 | ShahCement | 33 | 23:00
32 | Bog-Sherpur | 64 | 18:00 | 103 | Lalmonirhat | 50 | 18:00 | 174 | Shahjadpur | 89 | 18:00
33 | Bogura | 188 | 18:30 | 104 | MI_Cement | 11 | 19:30 | 175 | Shahjibazar | 136 | 21:00
34 | Borhanuddin | 73 | 03:00 | 105 | Madanganj | 55 | 11:00 | 176 | Shahmirpur | 62 | 18:00
35 | Brahmanbaria | 138 | 22:00 | 106 | Madaripur | 99 | 18:00 | 177 | Shariatpur | 91 | 21:00
36 | Cantonment | 150 | 13:00 | 107 | Madartek | 90 | 23:00 | 178 | Sherpur | 156 | 19:30
37 | Chandina | 23 | 18:30 | 108 | Madunaghat | 60 | 01:00 | 179 | Shikalbaha | 24 | 00:00
38 | Chandpur | 78 | 19:30 | 109 | Magura | 64 | 22:00 | 180 | Shitalakhya | 85.6 | 13:00
39 | Chandraghona | 33 | 19:00 | 110 | Mahasthangarh | 65 | 18:30 | 181 | Sholosohor | 57 | 16:00
40 | Chapai | 71 | 12:00 | 111 | Maijdee | 35 | 04:00 | 182 | Shomvuganj | 43 | 11:00
41 | Charfasson | 31 | 20:00 | 112 | Manikganj | 150 | 21:00 | 183 | Shyampur | 152 | 00:00
42 | Charsaidpur | 39 | 05:00 | 113 | Maniknagar | 90 | 13:00 | 184 | Siddhirganj | 136 | 18:00
43 | Chauddagram | 71 | 03:00 | 114 | Matarbari | 55 | 07:00 | 185 | Sirajganj | 128 | 18:30
44 | Chhatak | 35 | 05:00 | 115 | Matuail | 82 | 15:00 | 186 | Sitakunda | 31 | 00:00
45 | Chowmuhani | 162 | 21:00 | 116 | Metrorail_Motijheel | 16 | 09:00 | 187 | Sonargaon | 120 | 09:00
46 | Chuadanga | 110 | 22:00 | 117 | Metrorail_Uttara | 9 | 17:00 | 188 | Sreemongol | 71 | 22:00
47 | Coxsbazar | 146 | 17:00 | 118 | Millgate | 103 | 12:00 | 189 | Sreepur | 144 | 19:30
48 | Cumilla(N) | 147 | 00:00 | 119 | Mirpur | 162 | 18:00 | 190 | Srinagar | 51.6 | 19:00
49 | Cumilla(S) | 161 | 15:00 | 120 | Mirsorai | 36 | 11:00 | 191 | Sunamganj | 58 | 14:00
50 | Daganbhuiyan | 35 | 19:30 | 121 | Mirzapur | 47 | 21:00 | 192 | Sylhet | 146 | 19:30
51 | Daudkandi | 129 | 04:00 | 122 | Mithapukur | 62 | 07:00 | 193 | Sylhet_(South) | 60 | 18:30
52 | DhakaUniversity | 98 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 96 | 11:00 | 124 | Mogbazar | 67.5 | 12:00 | 195 | Tangail | 174 | 23:00
54 | Dhanmondi | 111 | 13:00 | 125 | Mongla | 44 | 19:00 | 196 | Taraganj | 27 | 11:00
55 | Dohazari | 111 | 05:00 | 126 | Monirampur | 23 | 23:00 | 197 | Tasnim | 47 | 17:00
56 | Faridpur | 178 | 21:00 | 127 | Motijheel | 57 | 13:00 | 198 | Thakurgaon | 105 | 18:30
57 | Fatullah | 126 | 15:00 | 128 | Muktagacha | 43 | 19:00 | 199 | Tongi | 170 | 19:30
58 | Fenchuganj | 41 | 00:00 | 129 | Munshiganj | 122 | 19:00 | 200 | Ullahpara | 35 | 12:00
59 | Feni | 109 | 00:00 | 130 | Muradnagar | 48 | 04:00 | 201 | Ullon | 38 | 23:00
60 | GPH | 1 | 00:00 | 131 | Mymensingh | 170 | 19:00 | 202 | Uttara | 106 | 18:00
61 | Ghatail | 105 | 19:00 | 132 | Nabinagar | 110 | 18:00 | 203 | UttaraNew | 61 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 112 | 18:30 | 204 | Zigatola | 80 | 18:00
63 | Ghorashal-230 | 93 | 19:30 | 134 | Narail | 63 | 18:00
64 | Goalpara | 39 | 18:00 | 135 | Narinda | 79.5 | 13:00
65 | Gollamari | 112 | 13:00 | 136 | Narshingdi | 174 | 22:00
66 | Gopalganj | 107 | 18:00 | 137 | Natore | 128 | 18:30
67 | Gulshan | 130 | 13:00 | 138 | Nawabganj | 51.5 | 21:00
68 | Halishahar | 151 | 15:00 | 139 | Netrakona | 137 | 00:00
69 | HaripurSBU | 137 | 11:00 | 140 | New | 86 | 12:00
70 | Hasnabad | 107 | 21:00 | 141 | Niamatpur | 69 | 18:00
71 | Hathazari | 88 | 00:00 | 142 | Noapara | 41 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15180.36 | 1682 |  | 16938.05
1:00 | 14614.64 | 1610 |  | 16296.64
2:00 | 14520.53 | 1460 |  | 16046.53
3:00 | 14274.25 | 882 |  | 15196.25
4:00 | 13811.07 | 35 |  | 13848.07
5:00 | 13408.43 | 30 |  | 13439.43
6:00 | 13243.05 | 30 |  | 13274.05
7:00 | 13589.26 | 10 |  | 13599.26
8:00 | 13569.38 | 25 |  | 13595.38
9:00 | 13841.08 | 15 |  | 13857.08
10:00 | 13995.15 | 15 |  | 14011.15
11:00 | 14471.81 | 0 |  | 14471.81
12:00 | 15085.59 | 5 |  | 15090.59
13:00 | 15077.85 | 351 |  | 15444.65
14:00 | 15144.02 | 342 |  | 15501.41
15:00 | 15092.93 | 998 |  | 16135.93
16:00 | 15073.83 | 1008 |  | 16126.83
17:00 | 15053.89 | 870 |  | 15962.89
18:00 | 15427.66 | 1739 |  | 17244.92
19:00 | 15816.79 | 1504 |  | 17388.79
19:30 | 15913.89 | 1863 |  | 17860.89
20:00 | 15876.63 | 1445 |  | 17386.63
21:00 | 15818.5 | 1380 |  | 17260.5
22:00 | 15870.06 | 1281 |  | 17209.06
23:00 | 15413.42 | 1741 |  | 17232.42
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 13-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 2 | 16 | 62 | 116 | 1132 | 366 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | -9 | 10 | 32 | 82 | 1112 | 314
2:00 | -9 | 11 | 50 | 88 | 1094 | 302 |  | Import | 0
3:00 | 0 | 14 | 80 | 90 | 1110 | 310
4:00 | 28 | 8 | 140 | 100 | 1222 | 378 | Ishurdi-Ghorashal Ckt-2 | Export | 883200
5:00 | 48 | 7 | 180 | 102 | 1274 | 362
6:00 | 53 | 12 | 170 | 108 | 1284 | 388 |  | Import | 232509.09
7:00 | 29 | 7 | 110 | 114 | 1176 | 400
8:00 | 62 | 10 | 180 | 100 | 1366 | 410 | Sirajganj-Sreepur Ckt-1 | Export | 710000
9:00 | 103 | 27 | 280 | 112 | 1554 | 498
10:00 | 106 | 37 | 270 | 124 | 1492 | 602 |  | Import | 5000
11:00 | 100 | 45 | 250 | 152 | 1494 | 646
12:00 | 73 | 40 | 220 | 170 | 1412 | 634 | Sirajganj-Sreepur Ckt-2 | Export | 714000
13:00 | 66 | 37 | 0 | 0 | 1326 | 604
14:00 | 51 | 26 | 170 | 152 | 1306 | 530 |  | Import | 6000
15:00 | 64 | 39 | 180 | 146 | 1332 | 570
16:00 | 70 | 45 | 180 | 146 | 1394 | 606 | Gopalganj-Aminbazar Ckt-1 | Export | 14050000
17:00 | 46 | 34 | 130 | 140 | 1340 | 566
18:00 | -24 | 30 | 6 | 150 | 914 | 452 |  | Import | 0
18:30 | -41 | 29 | -50 | 140 | 800 | 398
19:00 | -37 | 29 | -4 | 176 | 820 | 440 | Gopalganj-Aminbazar Ckt-2 | Export | 14100000
19:30 | -44 | 24 | -6 | 176 | 792 | 438
20:00 | -38 | 27 | 10 | 170 | 792 | 418 |  | Import | 0
21:00 | -42 | 24 | 2 | 164 | 740 | 402
22:00 | -31 | 28 | 10 | 166 | 742 | 414 |  | Total Export | 30457200
23:00 | -26 | 19 | 30 | 126 | 858 | 364 |  | Total Import | 243509.09
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9522.62 | 5657.74 | 15180.36 | DAILY GENERATION CURVE
00:30 | 9332.12 | 5565.38 | 14897.5
01:00 | 9141.62 | 5473.02 | 14614.64 | 13-10-2026
01:30 | 9124.37 | 5443.215 | 14567.585
02:00 | 9107.12 | 5413.41 | 14520.53
02:30 | 8985.12 | 5412.27 | 14397.39
03:00 | 8863.12 | 5411.13 | 14274.25
03:30 | 8656.31 | 5386.35 | 14042.66
04:00 | 8449.5 | 5361.57 | 13811.07
04:30 | 8268.5 | 5341.25 | 13609.75
05:00 | 8087.5 | 5320.93 | 13408.43
05:30 | 8036.13 | 5289.61 | 13325.74
06:00 | 7984.76 | 5258.29 | 13243.05
06:30 | 8054.005 | 5362.15 | 13416.155
07:00 | 8123.25 | 5466.01 | 13589.26
07:30 | 8065.44 | 5513.88 | 13579.32
08:00 | 8007.63 | 5561.75 | 13569.38
08:30 | 8087.75 | 5617.48 | 13705.23
09:00 | 8167.87 | 5673.21 | 13841.08
09:30 | 8230.34 | 5687.775 | 13918.115
10:00 | 8292.81 | 5702.34 | 13995.15
10:30 | 8477.05 | 5756.43 | 14233.48
11:00 | 8661.29 | 5810.52 | 14471.81
11:30 | 8897.245 | 5881.455 | 14778.7
12:00 | 9133.2 | 5952.39 | 15085.59
12:30 | 9174.435 | 5907.285 | 15081.72
13:00 | 9215.67 | 5862.18 | 15077.85
13:30 | 9274.015 | 5836.92 | 15110.935
14:00 | 9332.36 | 5811.66 | 15144.02
14:30 | 9335.63 | 5782.845 | 15118.475
15:00 | 9338.9 | 5754.03 | 15092.93
15:30 | 9391.11 | 5692.27 | 15083.38
16:00 | 9443.32 | 5630.51 | 15073.83
16:30 | 9485.055 | 5578.805 | 15063.86
17:00 | 9526.79 | 5527.1 | 15053.89
17:30 | 9716.635 | 5524.14 | 15240.775
18:00 | 9906.48 | 5521.18 | 15427.66
18:30 | 10102.98 | 5519.245 | 15622.225
19:00 | 10299.48 | 5517.31 | 15816.79
19:30 | 10405.48 | 5508.41 | 15913.89
20:00 | 10350.48 | 5526.15 | 15876.63
20:30 | 10323.48 | 5524.085 | 15847.565 |  | Executive Engineer
21:00 | 10296.48 | 5522.02 | 15818.5 |  | Network Operation Division
21:30 | 10344.98 | 5499.3 | 15844.28
22:00 | 10393.48 | 5476.58 | 15870.06
22:30 | 10132.48 | 5509.26 | 15641.74
23:00 | 9871.48 | 5541.94 | 15413.42

## En-Curve
QF-LDC-12
Date | 13-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2886 | 1994.5 | 327 | 0 | 70 | 754.94 | 222 | 5158.8 | 0 | 802.42 | 2964.7 | 0 | 0 | 0 | 1682 | DAILY ENERGY CURVE
00:30 | 2903 | 1971.5 | 327.5 | 0 | 69 | 752.08 | 222 | 5146.3 | 0 | 767.42 | 2738.7 | 0 | 0 | 0 | 1646 | 13-10-2026
01:00 | 2920 | 1948.5 | 328 | 0 | 68 | 749.22 | 222 | 5133.8 | 0 | 732.42 | 2512.7 | 0 | 0 | 0 | 1610
01:30 | 2963.5 | 1939.5 | 327.5 | 0 | 67 | 749.915 | 221 | 5114.8 | 0 | 714.42 | 2469.95 | 0 | 0 | 0 | 1535 | Energy Generated | 355.3355 |  | MKWHr
02:00 | 3007 | 1930.5 | 327 | 0 | 66 | 750.61 | 220 | 5095.8 | 0 | 696.42 | 2427.2 | 0 | 0 | 0 | 1460 | Energy not Served | 18.458 |  | MKWHr
02:30 | 3064.5 | 1924.5 | 327.5 | 0 | 65 | 754.97 | 219.5 | 5015.8 | 0 | 689.42 | 2336.2 | 0 | 0 | 0 | 1171 | Total Energy Requirement | 373.7935 |  | MKWHr
03:00 | 3122 | 1918.5 | 328 | 0 | 64 | 759.33 | 219 | 4935.8 | 0 | 682.42 | 2245.2 | 0 | 0 | 0 | 882
03:30 | 3168 | 1916.5 | 361 | 0 | 63 | 759.05 | 218.5 | 4903.8 | 0 | 557.21 | 2095.6 | 0 | 0 | 0 | 458.5
04:00 | 3214 | 1914.5 | 394 | 0 | 62 | 758.77 | 218 | 4871.8 | 0 | 432 | 1946 | 0 | 0 | 0 | 35
04:30 | 3212 | 1910.5 | 431.5 | 0 | 62 | 758.45 | 218.5 | 4850.3 | 0 | 386 | 1780.5 | 0 | 0 | 0 | 32.5
05:00 | 3210 | 1906.5 | 469 | 0 | 62 | 758.13 | 219 | 4828.8 | 0 | 340 | 1615 | 0 | 0 | 0 | 30
05:30 | 3203 | 1896.5 | 469 | 0 | 60 | 749.065 | 219 | 4823 | 0.175 | 340 | 1566 | 0 | 0 | 0 | 30
06:00 | 3196 | 1886.5 | 469 | 0 | 58 | 740 | 219 | 4817.2 | 0.35 | 340 | 1517 | 0 | 0 | 0 | 30
06:30 | 3193 | 1906.5 | 469 | 0 | 59 | 741.01 | 218.5 | 4863 | 64.645 | 342.5 | 1559 | 0 | 0 | 0 | 20
07:00 | 3190 | 1926.5 | 469 | 0 | 60 | 742.02 | 218 | 4908.8 | 128.94 | 345 | 1601 | 0 | 0 | 0 | 10
07:30 | 3126.5 | 1830.25 | 469 | 0 | 62 | 740.965 | 219 | 4877.8 | 243.305 | 321.5 | 1689 | 0 | 0 | 0 | 17.5
08:00 | 3063 | 1734 | 469 | 0 | 64 | 739.91 | 220 | 4846.8 | 357.67 | 298 | 1777 | 0 | 0 | 0 | 25
08:30 | 3037.5 | 1726 | 469 | 0 | 63 | 745.3 | 220.5 | 4902.8 | 469.63 | 269 | 1802.5 | 0 | 0 | 0 | 20
09:00 | 3012 | 1718 | 469 | 0 | 62 | 750.69 | 221 | 4958.8 | 581.59 | 240 | 1828 | 0 | 0 | 0 | 15
09:30 | 3005.5 | 1754 | 469.5 | 0 | 65 | 751.47 | 221 | 5018.3 | 651.845 | 243.5 | 1738 | 0 | 0 | 0 | 15
10:00 | 2999 | 1790 | 470 | 0 | 68 | 752.25 | 221 | 5077.8 | 722.1 | 247 | 1648 | 0 | 0 | 0 | 15
10:30 | 3031.5 | 1804 | 469.5 | 0 | 69 | 753.205 | 221 | 5186.8 | 756.475 | 251 | 1691 | 0 | 0 | 0 | 7.5
11:00 | 3064 | 1818 | 469 | 0 | 70 | 754.16 | 221 | 5295.8 | 790.85 | 255 | 1734 | 0 | 0 | 0 | 0
11:30 | 3059 | 1836.5 | 469 | 0 | 73 | 754.545 | 221 | 5295.8 | 786.855 | 364.5 | 1918.5 | 0 | 0 | 0 | 2.5
12:00 | 3054 | 1855 | 469 | 0 | 76 | 754.93 | 221 | 5295.8 | 782.86 | 474 | 2103 | 0 | 0 | 0 | 5
12:30 | 2996 | 1805 | 469 | 0 | 74 | 749.055 | 221 | 5295.8 | 761.905 | 499.36 | 2210.6 | 0 | 0 | 0 | 178
13:00 | 2938 | 1755 | 469 | 0 | 72 | 743.18 | 221 | 5295.8 | 740.95 | 524.72 | 2318.2 | 0 | 0 | 0 | 351
13:30 | 2935.5 | 1815 | 469 | 0 | 74 | 751.745 | 221 | 5264.8 | 687.97 | 534.72 | 2357.2 | 0 | 0 | 0 | 346.5
14:00 | 2933 | 1875 | 469 | 0 | 76 | 760.31 | 221 | 5233.8 | 634.99 | 544.72 | 2396.2 | 0 | 0 | 0 | 342
14:30 | 2922.5 | 1869 | 469 | 0 | 79 | 750.575 | 219.5 | 5264.8 | 549.58 | 531.82 | 2462.2 | 0 | 0 | 0.5 | 670
15:00 | 2912 | 1863 | 469 | 0 | 82 | 740.84 | 218 | 5295.8 | 464.17 | 518.92 | 2528.2 | 0 | 0 | 1 | 998
15:30 | 2925.5 | 1882 | 469 | 0 | 81 | 743.395 | 218 | 5295.8 | 369.275 | 514.71 | 2581.2 | 0 | 0 | 3.5 | 1003
16:00 | 2939 | 1901 | 469 | 0 | 80 | 745.95 | 218 | 5295.8 | 274.38 | 510.5 | 2634.2 | 0 | 0 | 6 | 1008
16:30 | 2934 | 1882.5 | 469 | 0 | 78 | 745.52 | 218 | 5295.8 | 162.45 | 526.21 | 2745.88 | 0 | 0 | 6.5 | 939
17:00 | 2929 | 1864 | 469 | 0 | 76 | 745.09 | 218 | 5295.8 | 50.52 | 541.92 | 2857.56 | 0 | 0 | 7 | 870
17:30 | 2955.5 | 1905.5 | 398.5 | 0 | 79 | 743.735 | 218 | 5305.8 | 25.26 | 609.67 | 2996.31 | 0 | 0 | 3.5 | 1304.5
18:00 | 2982 | 1947 | 328 | 0 | 82 | 742.38 | 218 | 5315.8 | 0 | 677.42 | 3135.06 | 0 | 0 | 0 | 1739
18:30 | 2987.5 | 1958.5 | 311 | 0 | 80 | 748.445 | 218.5 | 5315.8 | 0 | 730.92 | 3268.06 | 0 | 0 | 3.5 | 1621.5
19:00 | 2993 | 1970 | 294 | 0 | 78 | 754.51 | 219 | 5315.8 | 0 | 784.42 | 3401.06 | 0 | 0 | 7 | 1504
19:30 | 2958 | 2032 | 294 | 0 | 80 | 752.61 | 219 | 5315.8 | 0 | 802.42 | 3443.06 | 0 | 0 | 17 | 1863
20:00 | 2933 | 1991 | 294 | 0 | 80 | 753.35 | 220 | 5315.8 | 0 | 833.42 | 3453.06 | 0 | 0 | 3 | 1445
20:30 | 2916 | 1928.5 | 293.5 | 0 | 78 | 754.785 | 220.5 | 5315.8 | 0 | 829.92 | 3478.06 | 0 | 0 | 32.5 | 1412.5
21:00 | 2899 | 1866 | 293 | 0 | 76 | 756.22 | 221 | 5315.8 | 0 | 826.42 | 3503.06 | 0 | 0 | 62 | 1380
21:30 | 2906.5 | 1912.5 | 293.5 | 0 | 75 | 758.5 | 221 | 5315.8 | 0 | 819.92 | 3495.56 | 0 | 0 | 46 | 1330.5
22:00 | 2914 | 1959 | 294 | 0 | 74 | 760.78 | 221 | 5315.8 | 0 | 813.42 | 3488.06 | 0 | 0 | 30 | 1281
22:30 | 2867.5 | 1837.5 | 315.5 | 0 | 74 | 760.46 | 221.5 | 5315.8 | 0 | 813.42 | 3419.06 | 0 | 0 | 17 | 1511
23:00 | 2821 | 1716 | 337 | 0 | 74 | 760.14 | 222 | 5315.8 | 0 | 813.42 | 3350.06 | 0 | 0 | 4 | 1741
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 02:00 | 363 | 11:00 | Madunaghat | 406 | 02:00 | 395 | 12:00
Amtali | 411 | 01:00 | 406 | 12:00 | Meghnaghat | 397 | 03:00 | 372 | 12:00
Ashuganj | 396 | 03:00 | 381 | 11:00 | Mirsorai | 408 | 03:00 | 393 | 11:00
Bhulta | 400 | 03:00 | 368 | 12:00 | Payra | 413 | 04:00 | 407 | 12:00
Bibiana | 388 | 01:00 | 379 | 11:00 | Rahanpur | 408 | 03:00 | 396 | 11:00
BIPTC | 407 | 03:00 | 396 | 16:00 | Rampal | 398 | 02:00 | 387 | 12:00
Bogura | 403 | 03:00 | 387 | 11:00
Gopalganj | 396 | 03:00 | 381 | 11:00
Kaliakoir | 381 | 03:00 | 356 | 11:00
Korerhat | 405 | 08:00 | 393 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 02:00 | 217 | 12:00 | Hasnabad | 231 | 04:00 | 213 | 12:00
AKSML | 240 | 03:00 | 231 | 11:00 | Hathazari | 239 | 07:00 | 223 | 06:00
Aminbazar | 237 | 02:00 | 219 | 11:00 | Ishurdi | 235 | 03:00 | 222 | 11:00
Ashuganj | 230 | 04:00 | 218 | 13:00 | Jhenaidah | 225 | 03:00 | 213 | 19:30
Ashuganj-400 | 230 | 04:00 | 218 | 13:00 | Kachua | 232 | 01:00 | 223 | 11:00
Baghabari | 233 | 03:00 | 224 | 12:00 | Kaliakoir | 237 | 03:00 | 218 | 11:00
Barapukuria | 237 | 03:00 | 222 | 11:00 | Keranigonj | 233 | 03:00 | 214 | 12:00
Barapukuria-230 | 237 | 03:00 | 222 | 11:00 | Khulna(S) | 227 | 06:00 | 217 | 22:00
Barapukuria(N) | 238 | 03:00 | 224 | 11:00 | Korerhat | 230 | 00:00 | 223 | 11:00
Barishal | 226 | 00:00 | 222 | 11:00 | Madunaghat | 242 | 01:00 | 138 | 15:00
Bheramara | 235 | 03:00 | 222 | 07:00 | Madunaghat-400 | 244 | 02:00 | 236 | 12:00
Bhulta | 230 | 03:00 | 209 | 12:00 | Maniknagar | 255 | 08:00 | 208 | 12:00
Bibiana | 225 | 03:00 | 217 | 12:00 | Meghnaghat | 234 | 03:00 | 216 | 12:00
BIPTC | 235 | 03:00 | 1 | 12:00 | Meghnaghat-400 | 231 | 03:00 | 213 | 12:00
Birulia | 237 | 03:00 | 217 | 12:00 | Mirsorai | 237 | 01:00 | 228 | 11:00
Bogura | 240 | 03:00 | 230 | 11:00 | Naogaon | 227 | 03:00 | 211 | 12:00
Bogura-400 | 239 | 03:00 | 229 | 11:00 | Purbasadipur | 235 | 04:00 | 220 | 11:00
Borhanuddin | 229 | 00:00 | 226 | 11:00 | Rajshahi | 230 | 00:00 | 220 | 11:00
BSRM | 233 | 02:00 | 224 | 11:00 | Rampal | 226 | 03:00 | 217 | 22:00
Charfasson | 230 | 08:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 233 | 03:00 | 224 | 11:00 | Rampura | 229 | 03:00 | 207 | 11:00
Cumilla(N) | 228 | 02:00 | 213 | 12:00 | Shikalbaha | 243 | 02:00 | 235 | 11:00
Faridpur | 223 | 02:00 | 216 | 11:00 | Shyampur | 232 | 03:00 | 212 | 12:00
Fenchuganj | 226 | 07:00 | 219 | 12:00 | Siddhirganj | 225 | 07:00 | 211 | 12:00
Feni | 230 | 02:00 | 220 | 11:00 | Sirajgonj | 239 | 06:00 | 229 | 11:00
Ghorashal | 230 | 01:00 | 220 | 00:00 | Sreepur | 228 | 03:00 | 215 | 11:00
Ghorashal-230 | 226 | 03:00 | 201 | 11:00 | Tongi | 225 | 00:00 | 207 | 11:00
Gopalganj | 224 | 02:00 | 216 | 12:00
GPH | 233 | 01:00 | 230 | 08:00
Haripur | 229 | 03:00 | 210 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 122 | 12:00 | Madanganj | 136 | 00:00 | 127 | 12:00
Agargaon | 137 | 02:00 | 124 | 11:00 | Madaripur | 131 | 00:00 | 128 | 11:00
Agrabad | 137 | 00:00 | 132 | 11:00 | Madartek | 137 | 03:00 | 121 | 12:00
AKS | 136 | 18:00 | 131 | 11:00 | Madunaghat | 140 | 00:00 | 135 | 11:00
Aminbazar | 136 | 03:00 | 124 | 11:00 | Magura | 133 | 05:00 | 125 | 18:00
Amnura | 132 | 00:00 | 127 | 07:00 | Mahasthangarh | 137 | 03:00 | 130 | 12:00
Araihazar | 128 | 02:00 | 116 | 12:00 | Maijdee | 130 | 01:00 | 126 | 11:00
Ashuganj | 136 | 02:00 | 127 | 12:00 | Manikganj | 166 | 02:00 | 126 | 12:00
Ashuganj-230 | 137 | 01:00 | 132 | 11:00 | Maniknagar | 141 | 02:00 | 126 | 12:00
Bagerhat | 126 | 00:00 | 119 | 22:00 | Matarbari | 131 | 19:30 | 115 | 17:00
Bajitpur | 129 | 01:00 | 12 | 04:00 | Matuail | 138.8 | 06:00 | 127 | 12:00
Bakerganj | 133 | 00:00 | 130 | 11:00 | Metrorail_Motijheel | 141 | 03:00 | 126 | 12:00
Bakulia | 140 | 18:00 | 131 | 12:00 | Metrorail_Uttara | 139 | 02:00 | 121 | 11:00
Banani | 137 | 03:00 | 120 | 12:00 | Millgate | 138 | 01:00 | 122 | 11:00
Bangabhaban | 141 | 04:00 | 126 | 12:00 | Mirpur | 135 | 03:00 | 124 | 13:00
Barapukuria | 139 | 03:00 | 128 | 13:00 | Mirzapur | 135 | 00:00 | 127 | 11:00
Barguna | 133 | 17:00 | 129 | 12:00 | Mithapukur | 136 | 03:00 | 126 | 13:00
Barishal | 131 | 00:00 | 127 | 11:00 | MI_Cement | 136 | 02:00 | 122.3 | 12:00
Barishal-230 | 131 | 00:00 | 128 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 138 | 03:00 | 133 | 11:00 | Mogbazar | 138 | 01:00 | 123 | 12:00
Baroirhat | 133 | 00:00 | 129 | 12:00 | Mongla | 126 | 00:00 | 120 | 14:00
Bashundhara | 139 | 02:00 | 121 | 12:00 | Monirampur | 126 | 06:00 | 114 | 19:30
BashundharaCement | 136 | 01:00 | 127 | 12:00 | Motijheel | 141 | 04:00 | 126 | 12:00
Beanibazar | 124 | 04:00 | 119 | 14:00 | Muktagacha | 132 | 00:00 | 119 | 07:00
Benapole | 131 | 05:00 | 116 | 22:00 | Munshiganj | 139 | 03:00 | 125 | 12:00
Bhaluka | 132 | 01:00 | 122 | 11:00 | Muradnagar | 127 | 02:00 | 117 | 12:00
Bhandaria | 129 | 08:00 | 124 | 11:00 | Mymensingh | 134 | 23:00 | 116 | 13:00
Bhangura | 134 | 02:00 | 127 | 13:00 | Nabinagar | 135 | 01:00 | 123 | 16:00
Bheramara | 138 | 03:00 | 131 | 07:00 | Naogaon | 137 | 03:00 | 127 | 12:00
Bheramara(GK) | 137 | 02:00 | 131 | 10:00 | Narail | 132 | 05:00 | 124 | 18:00
Bhulta | 124 | 02:00 | 118 | 11:00 | Narinda | 141 | 02:00 | 126 | 12:00
Bhulta-400 | 129 | 03:00 | 117 | 12:00 | Narshingdi | 132 | 01:00 | 115 | 12:00
Birulia | 138 | 03:00 | 126 | 12:00 | Natore | 134 | 03:00 | 128 | 11:00
Bog-Sherpur | 138 | 03:00 | 130 | 12:00 | Nawabganj | 137 | 04:00 | 125 | 12:00
Bogura | 138 | 02:00 | 133 | 11:00 | Netrakona | 121 | 03:00 | 110 | 12:00
Bogura-230 | 140 | 03:00 | 133 | 11:00 | New | 139 | 01:00 | 123 | 11:00
Brahmanbaria | 133 | 02:00 | 125 | 12:00 | Niamatpur | 134 | 03:00 | 130 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 02:00 | 122 | 12:00 | Noapara | 129 | 06:00 | 121 | 22:00
Chandina | 131 | 01:00 | 123 | 12:00 | Pabna | 135 | 03:00 | 128 | 11:00
Chandpur | 136 | 01:00 | 129 | 11:00 | Palashbari | 135 | 03:00 | 125 | 12:00
Chandraghona | 139 | 00:00 | 136 | 12:00 | Panchagarh | 141 | 03:00 | 125 | 11:00
Chapai | 132 | 11:00 | 130 | 13:00 | Patiya | 138 | 18:00 | 130 | 11:00
Charsaidpur | 137 | 01:00 | 126 | 12:00 | Patnitala | 132 | 04:00 | 127 | 12:00
Chauddagram | 132 | 01:00 | 125 | 11:00 | Patuakhali | 134 | 00:00 | 130 | 12:00
Chhatak | 121 | 06:00 | 115 | 12:00 | Payra | 135 | 00:00 | 133 | 12:00
Chowmuhani | 131 | 02:00 | 125 | 11:00 | PHP | 134 | 01:00 | 128 | 11:00
Chuadanga | 132 | 03:00 | 123 | 22:00 | Postogola | 137 | 01:00 | 17 | 04:00
Coxsbazar | 130 | 21:00 | 117 | 17:00 | Pubail | 135 | 03:00 | 119 | 11:00
Cumilla(N) | 131 | 01:00 | 122 | 12:00 | Purbachal | 137 | 03:00 | 120 | 12:00
Cumilla(S) | 133 | 01:00 | 123 | 12:00 | Purbasadipur | 137 | 03:00 | 126 | 11:00
Daganbhuiyan | 133 | 02:00 | 127 | 11:00 | Rahanpur | 136 | 03:00 | 132 | 11:00
Daudkandi | 124 | 02:00 | 114 | 12:00 | Rahanpur-400 | 137 | 03:00 | 132 | 11:00
DhakaUniversity | 137 | 02:00 | 122 | 12:00 | Rahim | 138 | 01:00 | 127 | 12:00
Dhamrai | 136 | 02:00 | 125 | 16:00 | Rajbari | 127 | 03:00 | 122 | 11:00
Dhanmondi | 139 | 02:00 | 127 | 12:00 | Rajendrapur | 134 | 01:00 | 124 | 11:00
Dohazari | 136 | 15:00 | 126 | 11:00 | Rajshahi | 132 | 00:00 | 125 | 14:00
Faridpur | 130 | 05:00 | 125 | 11:00 | Rajshahi-230 | 132 | 00:00 | 126 | 11:00
Fatullah | 138 | 03:00 | 124 | 11:00 | Ramganj | 132 | 01:00 | 125 | 11:00
Fenchuganj | 133 | 03:00 | 128 | 13:00 | Rampur | 138 | 18:00 | 131 | 11:00
Feni | 133 | 01:00 | 126 | 11:00 | Rampura | 137 | 03:00 | 122 | 11:00
Feni-230 | 134 | 02:00 | 128 | 11:00 | Rangamati | 139 | 18:00 | 134 | 11:00
Ghatail | 130 | 00:00 | 118 | 19:00 | Rangpur | 133 | 02:00 | 125 | 12:00
Ghorashal | 134 | 00:00 | 123 | 11:00 | Ruppur | 136 | 00:00 | 130 | 10:00
Goalpara | 132 | 06:00 | 123 | 22:00 | Saidpur | 136 | 03:00 | 127 | 11:00
Gollamari | 131 | 06:00 | 124 | 21:00 | Santhia | 134 | 00:00 | 129 | 19:30
Gopalganj | 132 | 01:00 | 125 | 11:00 | Satkhira | 126 | 06:00 | 115 | 22:00
Gopalganj-400 | 133 | 02:00 | 128 | 11:00 | Satmasjid | 136 | 03:00 | 122 | 13:00
Gulshan | 134 | 03:00 | 121 | 12:00 | Savar | 133 | 00:00 | 124 | 11:00
Halishahar | 139 | 18:00 | 132 | 11:00 | SevenRings | 137 | 03:00 | 121 | 11:00
Haripur | 140 | 02:00 | 128 | 12:00 | ShahCement | 137 | 01:00 | 126 | 12:00
HaripurSBU | 140 | 03:00 | 129 | 11:00 | Shahjadpur | 134 | 01:00 | 131 | 07:00
Hasnabad | 137 | 05:00 | 125 | 12:00 | Shahjibazar | 131 | 01:00 | 125 | 11:00
Hathazari | 140 | 18:00 | 135 | 11:00 | Shahmirpur | 141 | 18:00 | 133 | 11:00
Hatirjheel | 137 | 02:00 | 122 | 12:00 | Shariatpur | 130 | 05:00 | 125 | 11:00
Ishurdi | 138 | 03:00 | 131 | 11:00 | Sherpur | 133 | 00:00 | 119 | 07:00
Jaldhaka | 134 | 03:00 | 123 | 11:00 | Shikalbaha | 130 | 18:00 | 122 | 11:00
Jamalpur | 136 | 00:00 | 121 | 07:00 | Shikalbaha-230 | 141 | 18:00 | 133 | 11:00
Jashore | 133 | 03:00 | 117 | 22:00 | Shitalakhya | 136 | 02:00 | 122 | 12:00
Jhenaidah | 135 | 05:00 | 128 | 22:00 | Sholosohor | 139 | 00:00 | 133 | 10:00
Jhenaidah-230 | 136 | 03:00 | 128 | 19:30 | Shomvuganj | 125 | 03:00 | 114 | 13:00
Joydebpur | 135 | 01:00 | 117 | 10:00 | Shyampur | 134 | 05:00 | 126 | 12:00
Joypurhat | 134 | 03:00 | 128 | 14:00 | Shyampur-230 | 139 | 02:00 | 127 | 12:00
Juldah | 138 | 00:00 | 132 | 11:00 | Siddhirganj | 139 | 01:00 | 127 | 12:00
Kabirpur | 140 | 00:00 | 118 | 11:00 | Sirajganj | 134 | 03:00 | 126 | 19:30
Kachua | 133 | 02:00 | 126 | 11:00 | Sitakunda | 139 | 03:00 | 134 | 11:00
Kaliakoir | 139 | 23:00 | 134 | 15:00 | Sonargaon | 138 | 04:00 | 126 | 12:00
Kaliganj | 134 | 03:00 | 127 | 13:00 | Sreemongol | 130 | 01:00 | 124 | 12:00
Kallyanpur | 133 | 01:00 | 122 | 12:00 | Sreepur | 135 | 01:00 | 126 | 11:00
Kalurghat | 140 | 01:00 | 135 | 11:00 | Srinagar | 136 | 04:00 | 125 | 12:00
Kamrangirchar | 138 | 03:00 | 119 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 118 | 01:00 | 112 | 13:00
Kasba | 126 | 02:00 | 116 | 12:00 | Sylhet | 124 | 01:00 | 120 | 13:00
Kazla | 141 | 05:00 | 125 | 13:00 | Sylhet_(South) | 126 | 06:00 | 121 | 14:00
Keranigonj | 138 | 03:00 | 126 | 12:00 | Tangail | 130 | 00:00 | 123 | 13:00
Khagrachori | 139 | 18:00 | 132 | 12:00 | Taraganj | 135 | 03:00 | 126 | 11:00
Khulna | 129 | 05:00 | 122 | 13:00 | Tasnim | 138 | 03:00 | 125 | 12:00
Khulna(S) | 131 | 06:00 | 124 | 22:00 | Thakurgaon | 141 | 02:00 | 125 | 11:00
Khulshi | 136 | 00:00 | 130 | 11:00 | TK | 140 | 00:00 | 135 | 11:00
Kishoreganj | 128 | 03:00 | 119 | 12:00 | Tongi | 137 | 00:00 | 125 | 11:00
Kodda | 138 | 00:00 | 118 | 11:00 | Ullahpara | 134 | 00:00 | 128 | 12:00
Korerhat | 135 | 00:00 | 132 | 11:00 | Ullon | 136 | 01:00 | 123 | 12:00
KSRM | 139 | 00:00 | 133 | 11:00 | Uttara | 136 | 01:00 | 120 | 11:00
Kulaura | 131 | 02:00 | 127 | 11:00 | UttaraNew | 139 | 02:00 | 121 | 11:00
Kurigram | 133 | 03:00 | 123 | 16:00 | Zigatola | 138 | 03:00 | 125 | 13:00
Kushtia | 134 | 00:00 | 128 | 12:00
Laksam | 132 | 01:00 | 126 | 11:00
Lakshmipur | 130 | 02:00 | 125 | 11:00
Lalbag | 137 | 04:00 | 125 | 12:00
Lalmonirhat | 130 | 04:00 | 123 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division