## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-10-2026 | during | 15-10-2026 | during | 15-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 371 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 52 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 303 | 335 | 335 | 317 | 317 | FGNO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 109 | 124 | 133 | 133 | 30 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5.6 | 5 | 24.75 | 24.75 | 5.5 | 5.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 21 | 22 | 22 | 18 | 18 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 48 | 52.19 | 52.19 | 16 | 47 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 246 | 295 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 104 | 132 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 435 | 370 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 445 | 325 | 583 | 583 | 450 | 450 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2634.02 | 2652.42 | 5558.55 | 5528.55 | 2599.92 | 2981.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 43 | 220 | 215 | 215 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 89 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 29 | 41 | 24 | 54 | 24 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 100 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 45 | 64 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.95 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 158 | 203 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 91 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 100 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 80 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 162 | 163 | 163 | 88 | 88 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 760 | 930 | 1224 | 1224 | 845 | 845 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1080 | 1080 | 1150 | 1150 | 1080 | 1080 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2815.95 | 3607.86 | 4095.71 | 4164.96 | 3071.75 | 3422.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 202 | 137 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 345 | 280 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 230 | 342.01 | 342.01 | 280 | 280 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 33 | 60 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 36 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 145 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 7 | 14 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 75 | 75 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 155 | 144 | 200 | 200 | 136 | 136 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 78 | 74 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 17.75 | 17.75 | 13 | 13 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 108 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 65 | 70 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 110 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 36 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1752.2 | 1542.2 | 2737.69 | 2685.69 | 1912.2 | 1924.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-10-2026 | during | 15-10-2026 | during | 15-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.97 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 164 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 87 | 105 | 105 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 54 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22 | 22 | 22
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 291.97 | 310 | 663.6 | 591.5 | 290.1 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 135 | 137 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 13 | 83 | 83 | 83 | 83 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 77 | 75 | 75 | 75 | 75 | 75 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 252 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 397 | 390 | 390 | 390 | 390
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 394 | 399 | 383 | 383 | 383 | 383
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1466 | 1513 | 1669 | 1669 | 1609 | 1609
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 469 | 302 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 18 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 86 | 0 | 86 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1878.2 | 1674.2 | 3290.2 | 3204.2 | 2725.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 27 | 64 | 110 | 110 | 48 | 64 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 114 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 250 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Under maint
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 118 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1922.2 | 2073.6 | 2158.6 | 2157.6 | 1995.6 | 2010.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 32.64 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 37 | 42 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 310 | 235 | 413.79 | 413.79 | 300 | 300 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 34 | 34 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 6 | 50 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 50 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.29 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 757.21 | 754.66 | 748 | 748 | 748 | 748 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1423.14 | 1371.66 | 2569.11 | 2346.99 | 1496.12 | 1445
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 201 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 392.8 | 387 | 483 | 248 | 393 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 14576.48 | 15131.94 | 23225.46 | 22596.49 | 16092.89 | 16573.78
Forecast Scenario (15-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15160 |  | 2559.4 |  | 17840
|  |  |  | 1:00 | 14460 |  | 2502.1 |  | 17080
|  |  |  | 2:00 | 14290 |  | 2330.2 |  | 16730
|  |  |  | 3:00 | 13900 |  | 2406.6 |  | 16420
|  |  |  | 4:00 | 13740 |  | 2301.55 |  | 16150
|  |  |  | 5:00 | 13620 |  | 2167.85 |  | 15890
|  |  |  | 6:00 | 13520 |  | 1461.15 |  | 15050
|  |  |  | 7:00 | 13800 |  | 1146 |  | 15000
|  |  |  | 8:00 | 13710 |  | 800 |  | 14510
|  |  |  | 9:00 | 13610 |  | 150 |  | 13760
|  |  |  | 10:00 | 13850 |  | 170 |  | 14020
|  |  |  | 11:00 | 14340 |  | 180 |  | 14520
|  |  |  | 12:00 | 14580 |  | 950 |  | 15530
|  |  |  | 13:00 | 14490 |  | 1508.9 |  | 16070
|  |  |  | 14:00 | 14420 |  | 1422.95 |  | 15910
|  |  |  | 15:00 | 14380 |  | 1795.4 |  | 16260
|  |  |  | 16:00 | 14110 |  | 1613.95 |  | 15800
|  |  |  | 17:00 | 14110 |  | 1432.5 |  | 15610
|  |  |  | 18:00 | 14820 |  | 1031.4 |  | 15900
|  |  |  | 18:30 | 14930 |  | 1609.175 |  | 16615
|  |  |  | 19:00 | 15050 |  | 1700 |  | 16750
|  |  |  | 19:30 | 15090 |  | 1650 |  | 16740
|  |  |  | 20:00 | 15110 |  | 1600 |  | 16710
|  |  |  | 21:00 | 15820 |  | 1500 |  | 17320
|  |  |  | 22:00 | 15870 |  | 1900 |  | 17770
|  |  |  | 23:00 | 15410 |  | 2200 |  | 17610
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 15530.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 17320.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15820.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 346.17 MKWHr. |  | 280 | 120 | 220 | 250 | 80 | 180 | 50 | 170 | 150 | 1500
*** This report is generated digitally from Operation Information System (OIS) at 09:25 hrs on 15-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-10-2026 | [28 empty] | Date: | 14-10-2026 | [28 empty] | Date: | 14-10-2026 | [28 empty] | Date: | 14-10-2026 | [28 empty] | Date: | 14-10-2026 | [16 empty] | Date: | 14-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 54 | 134 | 124 | 279 | 55 | 55 | 108 | 0 | 0 | 445 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 5 | 18 | 0 | 440 | 107 | 212 | 54 | 0 | 14 | 34 | 43 | 35 | 25 | 25 | 0 | 222 | 110 | 4 | 1080 | 18 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 143 | 128 | 0 | 303 | 260 | 44 | 15 | 203 | 36 | 81 | 70 | 155 | 67 | 13 | 114 | 72 | 52.2 | 0 | 8 | 306 | 400 | 182 | 40 | 30 | 156 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 78 | 17 | 88 | 0 | 163 | 0 | 0 | 0 | 24 | 9705.12 | 338 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 759.1 | 0 | 47 | 0 | 113 | 113 | 0 | 51 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 28 | 0 | 1170.6 | 300 | 90 | 5458.9 | 15164.02 | 104.75
01:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 54 | 133 | 110 | 248 | 55 | 55 | 72 | 0 | 0 | 440 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 109 | 68 | 59 | 0 | 19 | 34 | 29 | 18 | 25 | 25 | 0 | 222 | 110 | 14 | 930 | 16 | 0 | 50 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 145 | 128 | 0 | 300 | 260 | 44 | 15 | 198 | 37 | 72 | 70 | 155 | 73 | 13 | 114 | 68 | 52.2 | 0 | 8 | 285 | 400 | 255 | 40 | 30 | 155 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 75 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 9232.62 | 327 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 756.02 | 0 | 46 | 0 | 55 | 50 | 0 | 0 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 90 | 5222.82 | 14455.44 | 104.74
02:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 54 | 133 | 110 | 197 | 55 | 55 | 72 | 0 | 0 | 430 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 480 | 107 | 68 | 57 | 0 | 0 | 34 | 29 | 18 | 25 | 25 | 0 | 221 | 110 | 20 | 780 | 18 | 0 | 48 | 25.5 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 147 | 68 | 90 | 300 | 260 | 44 | 15 | 199 | 37 | 82 | 70 | 156 | 73 | 13 | 114 | 66 | 52.2 | 0 | 8 | 262 | 400 | 330 | 40 | 30 | 155 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 75 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 22 | 9103.62 | 374 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 756.8 | 0 | 46 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 54 | 5184.6 | 14288.22 | 104.73
03:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 54 | 133 | 110 | 148 | 55 | 55 | 72 | 0 | 0 | 450 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 500 | 107 | 68 | 57 | 0 | 0 | 34 | 29 | 18 | 25 | 25 | 0 | 220 | 110 | 3 | 780 | 16 | 0 | 50 | 17 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 142 | 68 | 90 | 315 | 270 | 44 | 15 | 187 | 37 | 87 | 70 | 155 | 0 | 13 | 114 | 62 | 52.2 | 0 | 8 | 253 | 400 | 350 | 40 | 30 | 157 | 0 | 16 | 0 | 83 | 0 | 138 | 0 | 76 | 14 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 9063.12 | 374 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 762.19 | 0 | 46 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 116 | 0 | 0 | 800 | 300 | 54 | 4835.39 | 13898.51 | 104.72
04:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 35 | 54 | 133 | 110 | 148 | 55 | 55 | 72 | 0 | 0 | 460 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 480 | 109 | 68 | 60 | 0 | 0 | 34 | 29 | 18 | 25 | 25 | 0 | 218 | 110 | 16 | 780 | 16 | 0 | 50 | 17 | 105 | 111 | 0 | 0 | 0 | 1224 | 0 | 145 | 63 | 6 | 295 | 260 | 44 | 15 | 211 | 37 | 69 | 70 | 156 | 0 | 13 | 114 | 64 | 52.2 | 0 | 8 | 250 | 400 | 367 | 40 | 30 | 157 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 75 | 17 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 8893.12 | 373 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 760.53 | 0 | 46 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 0 | 0 | 800 | 300 | 54 | 4848.73 | 13741.85 | 104.71
05:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 54 | 133 | 110 | 148 | 55 | 55 | 72 | 0 | 0 | 450 | 0 | 55 | 305 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 465 | 107 | 68 | 58 | 0 | 0 | 34 | 29 | 18 | 25 | 25 | 0 | 218 | 110 | 21 | 780 | 18 | 0 | 50 | 17 | 105 | 111 | 0 | 0 | 0 | 1160 | 0 | 150 | 63 | 10 | 305 | 260 | 44 | 15 | 222 | 33 | 55 | 70 | 155 | 0 | 13 | 114 | 62 | 52.2 | 0 | 8 | 246 | 400 | 367 | 40 | 30 | 154 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 78 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8801.12 | 373 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1231 | 0 | 0 | 0 | 759.17 | 0 | 49 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 117 | 0 | 0 | 800 | 300 | 54 | 4817.17 | 13618.29 | 104.7
06:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 35 | 54 | 131 | 110 | 148 | 54 | 35 | 72 | 0 | 0 | 465 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 92 | 68 | 58 | 0 | 0 | 34 | 29 | 35 | 25 | 25 | 0.01 | 218 | 110 | 26 | 780 | 16 | 0 | 49 | 17 | 105 | 111 | 0 | 0 | 0 | 1160 | 0 | 143 | 63 | 15 | 305 | 260 | 44 | 15 | 222 | 29 | 51 | 70 | 155 | 0 | 13 | 114 | 58 | 52.2 | 0 | 8 | 250 | 400 | 333 | 40 | 30 | 157 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 78 | 17 | 58 | 0 | 68 | 0 | 0 | 0 | 24 | 8768.13 | 374 | 0 | 19 | 28 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1212 | 0 | 0 | 0 | 764.25 | 0 | 49 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 117 | 0 | 0 | 800 | 300 | 54 | 4747.25 | 13515.38 | 104.69
07:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 54 | 95 | 110 | 148 | 50 | 0 | 72 | 0 | 0 | 460 | 0 | 55 | 305 | 0 | 0 | 5 | 143.42 | 5.5 | 18 | 0 | 470 | 95 | 68 | 54 | 0 | 1 | 34 | 29 | 35 | 25 | 25 | 0.42 | 218 | 98 | 25 | 780 | 112 | 0 | 46 | 17 | 105 | 111 | 0 | 0 | 0 | 1160 | 0 | 142 | 65 | 22 | 313 | 270 | 44 | 15 | 221 | 9 | 51 | 70 | 156 | 0 | 13 | 107 | 56 | 52.2 | 5 | 8 | 249 | 400 | 333 | 40 | 30 | 157 | 1 | 16 | 0 | 11 | 0 | 137 | 0 | 77 | 17 | 63 | 2.66 | 68 | 0 | 0.4 | 9 | 24 | 8782.6 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 15 | 1200 | 0 | 0 | 0 | 765.4 | 0 | 49 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 10.19 | 17 | 0 | 0 | 10.53 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 1.02 | 0 | 0 | 115 | 6 | 34 | 0 | 0 | 0 | 0.7 | 33 | 0 | 16 | 276 | 116 | 0 | 0 | 1170.6 | 250 | 54 | 5014.44 | 13797.04 | 104.68
08:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 54 | 89 | 111 | 148 | 48 | 0 | 72 | 0 | 0 | 455 | 0 | 55 | 300 | 0 | 0 | 14 | 143.42 | 5.5 | 18 | 0 | 460 | 91 | 68 | 52 | 0 | 2 | 34 | 29 | 35 | 25 | 25 | 0.56 | 179 | 93 | 8 | 780 | 162 | 0 | 46 | 17 | 105 | 111 | 0 | 0 | 0 | 860 | 5 | 143 | 65 | 20 | 330 | 305 | 36 | 15 | 195 | 9 | 51 | 75 | 156 | 4 | 13 | 105 | 62 | 52.2 | 15 | 8 | 243 | 400 | 333 | 40 | 30 | 155 | 4 | 16 | 0 | 11 | 0 | 137 | 0 | 76 | 17 | 63 | 10.24 | 68 | 0 | 1 | 25.18 | 24 | 8507.1 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 1234.2 | 0 | 0 | 0 | 765.63 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 27.08 | 51 | 0 | 0 | 30.53 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 2.72 | 0 | 0 | 115 | 19 | 34 | 0 | 0 | 0 | 2.9 | 93 | 0.12 | 16 | 307 | 116 | 0 | 0 | 1170.6 | 220 | 54 | 5203.78 | 13710.88 | 104.67
09:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 54 | 89 | 92 | 148 | 48 | 17 | 72 | 0 | 0 | 460 | 0 | 35 | 302 | 0 | 0 | 17 | 86 | 5.5 | 18 | 0 | 455 | 53 | 115 | 47 | 0 | 2 | 0 | 29 | 35 | 25 | 25 | 0.66 | 220 | 68 | 0 | 780 | 147 | 0 | 46 | 17 | 90 | 111 | 0 | 0 | 0 | 737 | 8 | 145 | 55 | 28 | 330 | 305 | 36 | 15 | 193 | 9 | 51 | 75 | 156 | 68 | 13 | 70 | 64 | 34 | 21 | 8 | 245 | 400 | 331 | 40 | 30 | 156 | 9 | 16 | 0 | 11 | 0 | 137 | 0 | 77 | 17 | 59 | 16.16 | 114 | 0 | 1.6 | 37.79 | 24 | 8312.71 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 62 | 1210 | 0 | 0 | 0 | 756.4 | 0 | 48 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 41.16 | 79 | 0 | 0 | 46.03 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 4.09 | 0 | 0 | 70 | 26 | 34 | 0 | 0 | 0 | 4.8 | 140 | 0.16 | 16 | 247 | 115 | 0 | 0 | 1170.6 | 220 | 54 | 5295.24 | 13607.95 | 104.66
10:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17 | 54 | 89 | 92 | 148 | 49 | 35 | 72 | 0 | 0 | 460 | 0 | 17 | 310 | 0 | 0 | 26 | 86 | 5.5 | 18 | 0 | 475 | 53 | 115 | 45 | 0 | 17 | 0 | 29 | 35 | 25 | 25 | 1.38 | 221 | 68 | 0 | 920 | 89 | 0 | 46 | 17 | 68 | 111 | 0 | 0 | 0 | 740 | 20 | 143 | 26 | 31 | 349 | 300 | 36 | 10 | 190 | 32 | 51 | 51 | 120 | 72 | 13 | 34 | 66 | 34 | 43 | 8 | 248 | 395 | 331 | 40 | 29 | 155 | 10 | 16 | 0 | 11 | 0 | 137 | 0 | 77 | 17 | 59 | 20 | 113 | 0 | 2 | 47.63 | 24 | 8421.51 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 78 | 1202 | 0 | 0 | 0 | 762.5 | 0 | 39 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 50.16 | 100 | 0 | 0 | 55.03 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 4.88 | 0 | 0 | 70 | 32 | 34 | 0 | 0 | 0 | 6 | 176 | 0.59 | 16 | 290 | 115 | 0 | 0 | 1170.6 | 220 | 54 | 5427.76 | 13849.27 | 104.66
11:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 17 | 54 | 89 | 98 | 246 | 53 | 35 | 72 | 0 | 0 | 475 | 0 | 17 | 311 | 0 | 0 | 29 | 86 | 5.5 | 18 | 0 | 475 | 53 | 155 | 45 | 0 | 6 | 0 | 29 | 35 | 25 | 25 | 2.43 | 221 | 74 | 0 | 1080 | 35 | 0 | 46 | 17 | 82 | 40 | 0 | 0 | 0 | 740 | 20 | 143 | 16 | 32 | 340 | 270 | 36 | 10 | 212 | 32 | 51 | 50 | 124 | 70 | 13 | 70 | 76 | 36 | 71 | 7 | 260 | 393 | 331 | 40 | 29 | 154 | 10 | 16 | 0 | 11 | 0 | 136 | 0 | 77 | 17 | 59 | 18.28 | 115 | 0 | 2.2 | 53.17 | 22 | 8749.58 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 88 | 1234.2 | 0 | 0 | 0 | 761.37 | 0 | 39 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 56.44 | 110 | 0 | 0 | 61.03 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 4.88 | 0 | 0 | 111 | 36 | 34 | 0 | 0 | 0 | 6.7 | 198 | 0.61 | 16 | 307 | 113 | 0 | 0 | 1170.6 | 220 | 54 | 5593.83 | 14343.41 | 104.64
12:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 54 | 104 | 109 | 246 | 52 | 35 | 72 | 0 | 0 | 445 | 0 | 17 | 317 | 0 | 0 | 30 | 143.42 | 5.6 | 18 | 0 | 435 | 80 | 158 | 45 | 0 | 0 | 0 | 29 | 35 | 25 | 25 | 1.95 | 221 | 91 | 0 | 1080 | 35 | 0 | 46 | 17 | 105 | 43 | 0 | 0 | 0 | 760 | 19 | 145 | 16 | 33 | 345 | 320 | 36 | 10 | 202 | 30 | 51 | 50 | 155 | 65 | 13 | 108 | 78 | 52.2 | 36 | 7 | 265 | 394 | 334 | 40 | 30 | 154 | 10 | 16 | 0 | 11 | 0 | 135 | 0 | 77 | 17 | 65 | 21.97 | 114 | 0 | 2 | 54 | 18 | 8960.14 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 90 | 1234.2 | 0 | 0 | 0 | 757.21 | 0 | 37 | 0 | 55 | 50 | 0 | 6 | 0 | 0 | 32.64 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 5.29 | 0 | 0 | 115 | 36 | 34 | 0 | 0 | 0 | 6.8 | 201 | 0.6 | 27 | 307 | 113 | 0 | 0 | 1170.6 | 250 | 54 | 5616.34 | 14576.48 | 104.64
13:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 54 | 113 | 109 | 246 | 53 | 35 | 72 | 0 | 0 | 415 | 0 | 17 | 301 | 0 | 0 | 16 | 143.42 | 5.5 | 18 | 0 | 430 | 107 | 158 | 45 | 0 | 0 | 0 | 29 | 35 | 25 | 25 | 2.44 | 221 | 96 | 0 | 1080 | 35 | 0 | 46 | 17 | 105 | 61 | 0 | 0 | 0 | 765 | 14 | 142 | 8 | 31 | 334 | 305 | 36 | 9 | 192 | 33 | 51 | 50 | 155 | 69 | 13 | 114 | 78 | 52.2 | 53 | 7 | 275 | 394 | 334 | 39 | 30 | 153 | 10 | 16 | 0 | 11 | 0 | 136 | 0 | 77 | 17 | 57 | 21.17 | 114 | 0 | 2.1 | 31.47 | 18 | 8827.3 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 84 | 1234.2 | 0 | 0 | 0 | 759.73 | 0 | 37 | 0 | 55 | 50 | 0 | 8.5 | 0 | 0 | 52.78 | 106 | 0 | 0 | 59.35 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 5.22 | 0 | 0 | 115 | 34 | 34 | 0 | 0 | 0 | 6.4 | 191 | 0.6 | 32 | 307 | 113 | 0 | 0 | 1170.6 | 300 | 54 | 5666.38 | 14493.68 | 104.63
14:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 54 | 118 | 110 | 246 | 52 | 35 | 72 | 0 | 0 | 400 | 0 | 17 | 314 | 0 | 0 | 22 | 143.42 | 5.5 | 18 | 0 | 435 | 109 | 158 | 52 | 0 | 0 | 0 | 29 | 35 | 25 | 25 | 1.96 | 221 | 93 | 0 | 1080 | 35 | 0 | 46 | 17 | 105 | 59 | 0 | 0 | 0 | 761 | 17 | 143 | 8 | 38 | 350 | 325 | 44 | 0 | 210 | 10 | 51 | 40 | 156 | 69 | 5 | 114 | 84 | 52.2 | 48 | 14 | 280 | 388 | 335 | 39 | 28 | 153 | 9 | 16 | 0 | 11 | 0 | 137 | 0 | 77 | 17 | 64 | 16.47 | 115 | 0 | 1.7 | 44.69 | 18 | 8886.94 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 71 | 1234.2 | 0 | 0 | 0 | 765.2 | 0 | 37 | 0 | 55 | 50 | 0 | 8.5 | 0 | 0 | 33.1 | 91 | 0 | 0 | 29.35 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 4.67 | 0 | 0 | 115 | 30 | 34 | 0 | 0 | 0 | 5.5 | 162 | 0.47 | 32 | 307 | 113 | 0 | 0 | 1170.6 | 300 | 54 | 5536.59 | 14423.53 | 104.63
15:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 54 | 132 | 124 | 246 | 30 | 35 | 72 | 0 | 0 | 365 | 0 | 17 | 315 | 0 | 0 | 13 | 143.42 | 5.5 | 18 | 0 | 395 | 107 | 158 | 47 | 0 | 5 | 0 | 29 | 35 | 25 | 25 | 0.81 | 220 | 105 | 0 | 1080 | 35 | 0 | 46 | 17 | 95 | 51 | 0 | 0 | 0 | 845 | 9 | 143 | 8 | 45 | 342 | 320 | 44 | 0 | 201 | 10 | 51 | 40 | 156 | 70 | 5 | 114 | 84 | 52.2 | 42 | 14 | 310 | 385 | 335 | 39 | 28 | 152 | 7 | 16 | 0 | 11 | 0 | 137 | 0 | 77 | 17 | 67 | 12.99 | 115 | 0 | 1.2 | 33.37 | 18 | 8867.49 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 51 | 1234.2 | 0 | 0 | 0 | 759.49 | 0 | 43 | 0 | 113 | 69 | 0 | 8.5 | 0 | 0 | 25.98 | 69 | 0 | 0 | 37.08 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 3.17 | 0 | 0 | 115 | 23 | 34 | 0 | 0 | 0 | 4 | 122 | 0.34 | 32 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 54 | 5515.36 | 14382.85 | 104.62
16:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 54 | 131 | 123 | 246 | 30 | 35 | 72 | 0 | 0 | 345 | 0 | 17 | 316 | 0 | 0 | 8 | 143.42 | 5.5 | 18 | 0 | 385 | 107 | 158 | 36 | 0 | 3 | 0 | 40 | 35 | 25 | 25 | 1.05 | 219 | 94 | 0 | 1080 | 35 | 0 | 46 | 17 | 93 | 51 | 0 | 0 | 0 | 845 | 7 | 143 | 8 | 15 | 344 | 330 | 44 | 0 | 185 | 10 | 51 | 35 | 153 | 69 | 13 | 114 | 82 | 52.2 | 22 | 18 | 330 | 385 | 394 | 39 | 28 | 150 | 4 | 16 | 0 | 20 | 0 | 137 | 0 | 0 | 17 | 67 | 7.2 | 115 | 0 | 0.6 | 17.13 | 18 | 8743.1 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 28 | 1234.2 | 0 | 0 | 0 | 759.96 | 0 | 43 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 14.84 | 41 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 1.45 | 0 | 0 | 115 | 12 | 36 | 0 | 0 | 0 | 2.4 | 65 | 0.09 | 32 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 54 | 5363.04 | 14106.14 | 104.61
17:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 54 | 131 | 123 | 280 | 30 | 35 | 162 | 0 | 0 | 335 | 0 | 17 | 305 | 0 | 0 | 2 | 143.42 | 5.5 | 21 | 0 | 355 | 109 | 208 | 39 | 0 | 2 | 0 | 41 | 54.36 | 25 | 25 | 0.51 | 218 | 93 | 0 | 1080 | 35 | 0 | 50 | 25.5 | 90 | 77 | 0 | 0 | 0 | 845 | 1 | 147 | 8 | 13 | 304 | 300 | 36 | 0 | 165 | 10 | 51 | 35 | 138 | 71 | 13 | 110 | 72 | 52.2 | 4 | 21 | 320 | 394 | 399 | 39 | 29 | 151 | 0 | 16 | 0 | 33 | 0 | 137 | 0 | 0 | 17 | 67 | 1.1 | 115 | 0 | 0.1 | 2.75 | 18 | 8808.44 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 7 | 1234.2 | 0 | 0 | 0 | 761.11 | 0 | 42 | 0 | 113 | 113 | 0 | 8.5 | 0 | 0 | 2.12 | 9 | 0 | 0 | 2.31 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0.17 | 0 | 0 | 115 | 2 | 48 | 0 | 0 | 0 | 0.4 | 11 | 0.05 | 48 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 100 | 5301.46 | 14109.9 | 104.61
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 54 | 131 | 123 | 294 | 30 | 55 | 162 | 0 | 0 | 330 | 0 | 35 | 306 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 360 | 109 | 208 | 47 | 0 | 0 | 0 | 41 | 54.36 | 100 | 100 | 0 | 219 | 105 | 0 | 1080 | 108 | 0 | 50 | 25.5 | 102 | 214 | 0 | 0 | 0 | 845 | 0 | 147 | 0 | 15 | 300 | 250 | 36 | 0 | 157 | 10 | 115 | 50 | 139 | 70 | 13 | 114 | 86 | 52.2 | 0 | 21 | 295 | 394 | 354 | 40 | 29 | 152 | 0 | 16 | 0 | 13 | 0 | 138 | 0 | 70 | 17 | 68 | 0 | 120 | 0 | 0 | 0 | 18 | 9370.48 | 464 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 753.35 | 0 | 42 | 0 | 113 | 113 | 0 | 8.5 | 10 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 115 | 0 | 65 | 0 | 130 | 0 | 0 | 0 | 0 | 48 | 307 | 109 | 0 | 0 | 1170.6 | 300 | 118 | 5444.65 | 14815.13 | 104.6
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 54 | 132 | 123 | 295 | 30 | 55 | 162 | 0 | 0 | 320 | 0 | 55 | 313 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 350 | 107 | 215 | 62 | 0 | 0 | 30 | 41 | 54.36 | 100 | 100 | 0 | 220 | 93 | 3 | 1080 | 163 | 0 | 50 | 25.5 | 105 | 213 | 0 | 0 | 0 | 920 | 0 | 150 | 0 | 45 | 280 | 230 | 36 | 0 | 146 | 0 | 115 | 50 | 139 | 70 | 13 | 114 | 74 | 52.2 | 0 | 21 | 285 | 394 | 354 | 40 | 30 | 153 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 75 | 17 | 86 | 0 | 162 | 0 | 0 | 0 | 12 | 9564.48 | 294 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 759.17 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 40 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 118 | 5482.97 | 15047.45 | 104.6
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 54 | 54 | 132 | 123 | 295 | 30 | 55 | 162 | 0 | 0 | 325 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 370 | 107 | 215 | 62 | 0 | 0 | 34 | 41 | 54.36 | 100 | 100 | 0 | 220 | 95 | 0 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 214 | 0 | 0 | 0 | 930 | 0 | 150 | 0 | 55 | 280 | 230 | 44 | 0 | 145 | 0 | 115 | 50 | 140 | 70 | 13 | 114 | 76 | 52.2 | 0 | 21 | 270 | 394 | 354 | 40 | 30 | 154 | 0 | 16 | 0 | 13 | 0 | 137 | 0 | 75 | 21 | 86 | 0 | 155 | 0 | 0 | 0 | 24 | 9594.48 | 294 | 0 | 18 | 30 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 756.64 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 40 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 118 | 5493.44 | 15087.92
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 54 | 54 | 132 | 123 | 295 | 30 | 55 | 162 | 0 | 0 | 335 | 0 | 35 | 303 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 355 | 109 | 220 | 63 | 0 | 0 | 34 | 41 | 54.36 | 100 | 100 | 0 | 221 | 101 | 0 | 1080 | 162 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 933 | 0 | 150 | 0 | 55 | 280 | 230 | 44 | 0 | 145 | 0 | 115 | 50 | 137 | 71 | 13 | 114 | 74 | 52.2 | 0 | 14 | 265 | 399 | 364 | 40 | 30 | 154 | 0 | 16 | 0 | 13 | 0 | 136 | 0 | 70 | 28 | 86 | 0 | 164 | 0 | 0 | 0 | 21 | 9595.48 | 294 | 0 | 18 | 43 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 761.54 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 40 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 109 | 0 | 0 | 1170.6 | 300 | 118 | 5515.34 | 15110.82 | 104.6
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 54 | 54 | 132 | 124 | 295 | 30 | 55 | 162 | 0 | 0 | 325 | 0 | 55 | 303 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 370 | 107 | 203 | 64 | 0 | 0 | 51 | 41 | 54.36 | 100 | 100 | 0 | 221 | 110 | 0 | 1080 | 162 | 0 | 50 | 25.5 | 89 | 220 | 0 | 0 | 0 | 930 | 0 | 150 | 0 | 60 | 280 | 230 | 44 | 0 | 137 | 0 | 110 | 50 | 144 | 70 | 13 | 114 | 74 | 52.2 | 0 | 14 | 252 | 399 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 13 | 0 | 137 | 0 | 75 | 35 | 87 | 0 | 164 | 0 | 0 | 0 | 24 | 9625.48 | 302 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 754.66 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 38 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 115 | 0 | 107 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 114 | 0 | 0 | 1170.6 | 300 | 118 | 5506.46 | 15131.94 | 104.59
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 54 | 54 | 132 | 109 | 295 | 30 | 55 | 162 | 0 | 0 | 330 | 0 | 55 | 302 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 360 | 107 | 200 | 67 | 0 | 0 | 51 | 41 | 54.36 | 100 | 100 | 0 | 221 | 109 | 0 | 1080 | 160 | 0 | 50 | 25.5 | 95 | 222 | 0 | 0 | 0 | 935 | 0 | 144 | 0 | 55 | 280 | 230 | 44 | 0 | 130 | 0 | 110 | 50 | 153 | 70 | 13 | 114 | 76 | 52.2 | 0 | 14 | 240 | 400 | 397 | 40 | 30 | 156 | 0 | 16 | 0 | 13 | 0 | 137 | 0 | 70 | 35 | 87 | 0 | 164 | 0 | 0 | 0 | 0 | 9546.48 | 301 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 755.2 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 38 | 8 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 115 | 0 | 57 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 114 | 0 | 0 | 1170.6 | 300 | 100 | 5442 | 14988.48 | 104.59
23:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 44 | 54 | 128 | 125 | 295 | 30 | 55 | 162 | 0 | 0 | 325 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 5 | 21 | 0 | 325 | 107 | 200 | 60 | 0 | 0 | 51 | 41 | 54.36 | 100 | 100 | 0 | 222 | 96 | 2 | 1080 | 72 | 0 | 50 | 25.5 | 105 | 222 | 0 | 0 | 0 | 935 | 0 | 150 | 0 | 60 | 280 | 220 | 44 | 0 | 129 | 0 | 99 | 51 | 139 | 71 | 13 | 114 | 80 | 52.2 | 0 | 15 | 240 | 400 | 396 | 40 | 30 | 155 | 0 | 16 | 0 | 13 | 0 | 139 | 0 | 75 | 35 | 87 | 0 | 164 | 0 | 0 | 0 | 0 | 9361.48 | 301 | 0 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 760.65 | 0 | 42 | 0 | 113 | 113 | 0 | 50 | 38 | 8 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 115 | 0 | 56 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 100 | 5438.45 | 14799.93 | 104.58
Total KWH | 0 | 2059200 | 524160 | 0 | 0 | 0 | 0 | 0 | 9208800 | 0 | 0 | 778320 | 1297440 | 2909808 | 2734560 | 5353145 | 1064344 | 935072 | 2360160 | 0 | 0 | 9732228 | 0 | 930026 | 7426912 | 0 | 0 | 189076 | 3315600 | 128400 | 465480 | 0 | 10309545.45 | 2418764 | 3377236 | 1290240 | 0 | 61920 | 525416 | 793520 | 912707 | 1018560 | 1024320 | 13797 | 5306387 | 2418800 | 137280 | 23214545.46 | 1717891 | 0 | 1172640 | 477909 | 2432145 | 2857705 | 0 | 0 | 0 | 22958179 | 116775 | 3499345 | 853090.9 | 781000 | 7892100 | 6732000 | 934272 | 181440 | 4472000 | 416160 | 1677120 | 1307849 | 3562560 | 1290240 | 289670 | 2586660 | 1733760 | 1197461 | 353364 | 278912 | 6424000 | 9490400 | 8442000 | 946000 | 714360 | 3716591 | 76888 | 400896 | 0 | 550080 | 0 | 3132000 | 0 | 1697640 | 484560 | 1617600 | 145728 | 2652000 | 0 | 13850 | 366130 | 467520 | 217346259.81 | 9548364 | 0 | 201120 | 326016 | 0 | 0 | 0 | 0 | 0 | 2098080 | 591120 | 29498180 | 0 | 0 | 0 | 18342909 | 0 | 1045928 | 0 | 1910784 | 1905024 | 0 | 365392 | 248176 | 45974 | 349176 | 803990 | 267080 | 0 | 408752 | 0 | 0 | 0 | 0 | 0 | 0 | 7060582 | 0 | 37380 | 0 | 0 | 2672894 | 251822 | 1626739 | 0 | 999022.5 | 0 | 45602.76 | 1392480 | 3571 | 858144 | 7244000 | 2720000 | 3260 | 0 | 26821818 | 6949818.18 | 1754400 | 128397598.44 | 345743858.25

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14576.48 | MW | 12:00 Hr. | Energy Generated |  |  | 345.7439 |  | MKWHr.
| Day Peak Demand |  |  | 15576.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 34.386 |  | MKWHr.
| Evening Peak Generation |  |  | 15131.94 | MW | 21:00 Hr. | Energy Demand |  |  | 380.1299 |  | MKWHr.
| Evening Peak Demand |  |  | 18315.94 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.4 |  | °C
| Minimum Generation of the Day |  |  | 13515.38 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 791.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 15164.02 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 9.2042 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.2714 | 0 | 24.2618 | 0 | 0 | 0.18908 | 0 | 0 | 61.7223 | Gas | 109.4237 | Gas | 370761054.6465
| Chattogram Zone |  |  | 2.995 | 46.1727 | 19.5801 | 0 | 5.3064 | 0.13057 | 0 | 0.06192 | 74.2467 | Coal | 116.6865 | Coal | 845459412.3984
| Cumilla Zone |  |  | 23.8596 | 0 | 14.0923 | 0 | 0 | 0.35336 | 1.7338 | 0 | 40.039 | HFO | 78.4817 | HFO | 1648749968.99
| Mymensingh Zone |  |  | 0 | 0 | 5.2217 | 0 | 0 | 0.52571 | 0 | 0 | 5.7474 | HSD | 0.99902 | HSD | 30849814.8
| Sylhet Zone |  |  | 35.514 | 0 | 0 | 0 | 0 | 0.076888 | 0 | 0 | 35.5909 | Hydro | 5.3064 | Hydro | 530638.7
| Khulna Zone |  |  | 0 | 29.4982 | 2.6252 | 0 | 0 | 0.59112 | 9.5484 | 0 | 42.2629 | Solar | 5.1595 | Solar | 84030857.3832
| Barishal Zone |  |  | 2.7233 | 41.0156 | 2.6125 | 0 | 0 | 0.003571 | 0 | 0 | 46.355 | Import | 29.625 | Import | 201002662.65
| Rajshahi Zone |  |  | 7.0606 | 0 | 5.7884 | 0 | 0 | 1.5993 | 18.3429 | 0 | 32.7911 | Wind | 0.06192 | Wind | 918892.8
| Rangpur Zone |  |  | 0 | 0 | 4.2996 | 0.99902 | 0 | 1.6899 | 0 | 0 | 6.9886
| Total |  |  | 109.4237 | 116.6865 | 78.4817 | 0.99902 | 5.3064 | 5.1595 | 29.625 | 0.06192 | 345.7439
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 370761054.6465 |  | Hydro | 530638.7
|  |  |  | Coal | 845459412.3984 |  | Solar | 84030857.3832
|  |  |  | HFO | 1648749968.99 |  | Import | 201002662.65
|  |  |  | HSD | 30849814.8 |  | Wind | 918892.8
[5 empty] | Total: | 318,23,03,302 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 71927.27 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 9.5484 | Peak Hr Flow | 302.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26250909.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.3429 | Peak Hr Flow | 754.66 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1052 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7338 | Peak Hr Flow | 74.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1661 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 29.625 | Peak Hr Flow | 1130.66 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 566 |  | 6449
|  |  |  | Chattogram |  | 174 |  | 1635
|  |  |  | Cumilla |  | 435 |  | 1701
|  |  |  | Mymensingh |  | 459 |  | 1501
|  |  |  | Sylhet |  | 189 |  | 801
|  |  |  | Khulna |  | 470 |  | 2033
|  |  |  | Barishal |  | 195 |  | 591
|  |  |  | Rajshahi |  | 380 |  | 1754
|  |  |  | Rangpur |  | 179 |  | 992
|  |  |  | Total |  | 3047 |  | 17457
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 438.5
|  |  |  | Total Unavailable Capacity |  |  |  | 738.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:13 | 16:57 | Shariatpur 132/33kV S/S Main Bus - 2 Scheduled S/D Due to Annual Maintenance work
| 08:22 | 14:16 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Annual Maintenence Works.
| 08:24 | 14:15 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Annual Maintenence Works.
| 08:42 | 16:13 | Saidpur 132/33kV S/S TR-2 (404T) LT Scheduled S/D Due to Annual maintenance
| 08:44 | 16:12 | Saidpur 132/33kV S/S TR-2 (404T) HT Scheduled S/D Due to Annual maintenance
| 08:47 | 11:58 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to Pbs maintenance work. | [7 empty] | 75.0MW load
interrup.
| 08:47 | 11:58 | Ghorashal 230kV S/S TARFO-2 LT Scheduled S/D Due to Pbs maintenance work. | [7 empty] | 75.0MW load
interrup.
|  | 08:51 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 08:52 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 08:56 | 10:57 | Madunaghat-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end Due to
shutdown taken by korerhat ss
| 09:07 | 10:57 | Korerhat 400/230/132kV S/S Meghnaghat-2 (C05) Project Work S/D Due to For project work
| 09:25 | 16:47 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Annual Maintenance
| 09:26 | 16:46 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Annual Maintenance
| 09:34 |  | Manirampur-Satkhira 132kV Ckt-1 Project Work S/D from Satkhira 132/33kV end.
| 10:05 | 18:07 | Mirsorai 400/230/33kV S/S ATR-1 HT Scheduled S/D Due to CAF Work
| 10:05 | 18:08 | Mirsorai 400/230/33kV S/S ATR-1 LT Scheduled S/D Due to CAF work
| 10:05 | 14:10 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Annual
Maintenance
|  | 10:08 | Chandpur 132/33kV S/S 412T (T-2) LT is restored.
| 10:55 | 13:53 | Benapole 132/33kV S/S Transformer-1(416T) LT Scheduled S/D Due to LT Bushing clamp
(R-Phase & Y-Phase) Red hot maintenance work.
| 10:56 | 13:52 | Benapole 132/33kV S/S Transformer-1(416T) HT Scheduled S/D Due to LT Bushing clamp
(R-Phase & Y-Phase) Red hot maintenance work.
| 10:59 | 20:51 | Korerhat 400/230/132kV S/S BSRM-2 (D05) Project Work S/D Due to Project work completed
| 11:00 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to Project Work
Korerhat End.
| 11:08 | 20:39 | Korerhat 400/230/132kV S/S 400/230 KV ATR-3 (7103T) LT Project Work S/D Due to For
project work
| 11:09 | 20:38 | Korerhat 400/230/132kV S/S 400/230 KV ATR-3 (7103T) HT Project Work S/D Due to For
project work
| 11:24 | 17:43 | Korerhat 400/230/132kV S/S Mirsharai-1 (C09) Project Work S/D Due to For project work
| 11:39 | 14:11 | Araihazar 132/33kV S/S T-1 HT Project Work S/D Due to Red hot showing at R phase of CT
| 12:00 |  | Day Peak Generation: 14577 MW.
| 12:51 | 13:34 | Gollamari 132/33kV S/S Tr-1 LT Tripped showing 33kV incomer (F51) Backup Protection -1 | [7 empty] | 108.0MW load
|  |  | relays Due to Due to 33 kv Rupsha feeder CT Burn | [7 empty] | interrup.
| 12:51 | 13:35 | Gollamari 132/33kV S/S Tr-2 LT Tripped showing 33kV Incomer ( F51) Backup protection | [7 empty] | 108.0MW load
|  |  | Relay-1 relays Due to Due to 33 kv Rupsha feeder CT Burn | [7 empty] | interrup.
| 14:29 | 17:08 | Chapai 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to 33 kv bus pt change
| 14:30 | 17:07 | Chapai 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to 33 kv bus pt change
| 15:34 | 16:22 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Bukhloz Oil leakage
Maintenance
| 15:34 | 16:23 | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Bukhloz Oil leakage
Maintenance
| 15:34 | 16:22 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Bukhloz Oil leakage
Maintenance
| 15:44 |  | Sylhet 225 MW CCPP Tripped with remarks:- GT
| 15:44 |  | Sylhet 225 MW CCPP GT Tripped with remarks:- None
|  | 16:35 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 16:38 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 17:02 | Barapukuria-Saidpur 132 kV Ckt-2 is restored.
| 17:04 |  | Sylhet 225 MW CCPP GT Synchronized with remarks:- None
| 17:04 |  | Sylhet 225 MW CCPP Synchronized with remarks:- GT
| 21:00 |  | Evening peak generation is 15132 MW.
| 21:32 | 23:04 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kV BUS Section Isolator Red hot | [7 empty] | 70.0MW load
interrup.
| 21:32 | 23:04 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kV BUS Section Isolator Red hot | [7 empty] | 70.0MW load
interrup.
|  | 21:34 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
| 21:36 | 01:20 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Tripped showing Seprotec relays Due
to 230kV LA Blast Y-Phase
| 21:36 | 01:15 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Tripped showing Seprotec relays Due
to 230kV LA Blast Y-Phase
|  | 22:33 | Barapukuria-Saidpur 132 kV Ckt-1 is restored.
|  | 22:36 | Barapukuria-Rangpur 132 kV Ckt-2 is restored.
|  | 23:03 | Rangpur-Saidpur 132kV Ckt-2 is restored.
| 05:00 |  | Minimum generation is 13447 MW.
| 07:03 |  | Meghnaghat 400/230kV S/S ATR - 2 HT Scheduled S/D Due to For maintenance work
| 07:03 |  | Meghnaghat 400/230kV S/S ATR - 2 LT Scheduled S/D Due to For maintenance work
| 07:32 |  | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance Work
| 07:32 |  | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance Work
| 07:37 |  | Bhandaria 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance
| 07:37 |  | Bhandaria 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance
| 07:48 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to T1 B-Bus DS maintainance.
| 07:48 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to T1 B-Bus DS maintainance.
| 07:55 |  | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to High temperature maintenance.
| 07:55 |  | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to High temperature maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 371 | 9208800 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 1064344 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 303 | 7426912 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 778320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 124 | 2734560 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935072 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 930026 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 128400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 465480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 524160 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 5353145 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2909808 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2059200 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2360160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 189076 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1297440 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 370 | 10309545.45 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 325 | 9732228 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3315600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2652.42 | 61722276.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 477909 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 116775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1172640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5306387 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 2857705 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 89 | 2432145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 41 | 793520 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 525416 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1018560 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 137280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 64 | 1290240 | Machine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 203 | 3377236 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 912707 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2418800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1024320 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2418764 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 162 | 1717891 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 930 | 22958179 | Coal Shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 61920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 23214545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3607.86 | 74246736.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 137 | 4472000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7892100 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 6732000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 60 | 781000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 416160 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 181440 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 853090.9 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 934272 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 3499345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 14 | 278912 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1307849 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 144 | 3562560 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 74 | 1733760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1197461 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 289670 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2586660 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 1290240 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 110 | 1677120 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 353364 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1542.2 | 40039003.9
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 145728 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2652000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1617600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 366130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 467520 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 484560 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 310 | 5747388
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 76888 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 946000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714360 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3716591 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 137 | 3132000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 13 | 550080 | Gas Shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 75 | 1697640 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 400896 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 252 | 6424000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 397 | 8442000 | Gas Shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 399 | 9490400 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1513 | 35590855
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 302 | 9548364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 18 | 201120 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 326016 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 2098080 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 591120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29498180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1674.2 | 42262880
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 26821818 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 858144 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 114 | 2720000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 6949818.18 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 3260 | Under Maintenance
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 118 | 1754400 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7244000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3571 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2073.6 | 46355011.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 349176 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 42 | 1045928 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 248176 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 235 | 7060582 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 267080 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 45974 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 365392 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1905024 | Fuel Shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1910784 | Fuel Shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 37380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 754.66 | 18342909 | Unit1 Under Maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 408752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 803990 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1371.66 | 32791147
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 999022.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance, Plant Availability Zero
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 1626739 | Fuel Shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45602.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2672894 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 251822 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1392480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 387 | 6988560.26
Eastern Grid Total |  |  |  |  | 16961.086 | 9625.48 | 217346259.81
Western Grid Total |  |  |  |  | 11731.125 | 5506.46 | 128397598.44
National Grid Total |  |  |  |  | 28692.211 | 15131.94 | 345743858.25
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-10-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10264.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4146.3 | MW
i) Dhaka area |  |  | 5883.48 |  | MW | i) Khulna area |  |  |  | 1563 | MW
ii) Chattogram area |  |  | 1461.1 |  | MW | ii) Barishal area |  |  |  | 395.9 | MW
iii) Cumilla area |  |  | 1265.58 |  | MW | iii) Rajshahi area |  |  |  | 1374.4 | MW
iv) Mymensingh area |  |  | 1042 |  | MW | iv) Rangpur area |  |  |  | 813 | MW
v) Sylhet area |  |  | 612 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14410.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 10:00 | 72 | Hatirjheel | 86 | 13:00 | 143 | PHP | 11 | 15:00
2 | AKSML | 153 | 04:00 | 73 | Ishurdi | 69 | 00:00 | 144 | Pabna | 90 | 00:00
3 | Aftabnagar | 48 | 13:00 | 74 | Jaldhaka | 61 | 19:30 | 145 | Palashbari | 110 | 05:00
4 | Agargaon | 142 | 13:00 | 75 | Jamalpur | 113 | 22:00 | 146 | Panchagarh | 69 | 18:30
5 | Agrabad | 74 | 11:00 | 76 | Jashore | 143 | 18:30 | 147 | Patiya | 25 | 19:30
6 | Amnura | 36 | 08:00 | 77 | Jhenaidah | 79 | 22:00 | 148 | Patnitala | 33 | 18:30
7 | Araihazar | 103 | 06:00 | 78 | Joydebpur | 178 | 21:00 | 149 | Patuakhali | 60.5 | 05:00
8 | Ashuganj | 0.63 | 23:00 | 79 | Joypurhat | 55 | 00:00 | 150 | Payra | 30 | 00:00
9 | Ashuganj-230 | 95 | 22:00 | 80 | Juldah | 20 | 22:00 | 151 | Postogola | 67 | 23:00
10 | BSRM | 206 | 00:00 | 81 | KSRM | 30 | 04:00 | 152 | Pubail | 49 | 11:00
11 | Bagerhat | 79 | 08:00 | 82 | Kabirpur | 254 | 08:00 | 153 | Purbachal | 33 | 18:00
12 | Bajitpur | 93 | 00:00 | 83 | Kachua | 80 | 06:00 | 154 | Purbasadipur | 110 | 00:00
13 | Bakerganj | 13 | 01:00 | 84 | Kaliganj | 38 | 18:00 | 155 | Rahanpur | 30 | 03:00
14 | Bakulia | 99 | 21:00 | 85 | Kallyanpur | 126 | 19:30 | 156 | Rahim | 53 | 10:00
15 | Banani | 73.4 | 12:00 | 86 | Kalurghat | 42 | 09:00 | 157 | Rajbari | 70.5 | 00:00
16 | Bangabhaban | 17 | 10:00 | 87 | Kamrangirchar | 99 | 13:00 | 158 | Rajendrapur | 119 | 09:00
17 | Barapukuria | 52 | 11:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 112 | 18:30
18 | Barguna | 22 | 00:00 | 89 | Kasba | 33 | 05:00 | 160 | Rajshahi-230 | 90 | 20:00
19 | Barishal | 92 | 11:00 | 90 | Kazla | 133 | 13:00 | 161 | Ramganj | 92 | 05:00
20 | Barishal-230 | 90 | 02:00 | 91 | Keranigonj | 103 | 11:00 | 162 | Rampur | 44 | 18:00
21 | Baroaulia | 50 | 11:00 | 92 | Khagrachori | 32 | 18:00 | 163 | Rangamati | 16 | 12:00
22 | Baroirhat | 59 | 20:00 | 93 | Khulna | 81 | 14:00 | 164 | Rangpur | 106 | 15:00
23 | Bashundhara | 211 | 13:00 | 94 | Khulshi | 189 | 17:00 | 165 | Ruppur | 4.6 | 15:00
24 | BashundharaCement | 1 | 16:00 | 95 | Kishoreganj | 126 | 00:00 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 68 | 20:00 | 96 | Kodda | 307 | 10:00 | 167 | Saidpur | 91 | 08:00
26 | Benapole | 65 | 23:00 | 97 | Kulaura | 51 | 20:00 | 168 | Santhia | 30 | 00:00
27 | Bhaluka | 145 | 17:00 | 98 | Kurigram | 60 | 07:00 | 169 | Satkhira | 121 | 19:00
28 | Bhandaria | 60 | 18:00 | 99 | Kushtia | 128 | 07:00 | 170 | Satmasjid | 114 | 18:00
29 | Bhangura | 34 | 00:00 | 100 | Laksam | 37 | 18:30 | 171 | Savar | 205 | 18:00
30 | Bheramara(GK) | 57 | 07:00 | 101 | Lakshmipur | 48 | 03:00 | 172 | SevenRings | 6.34 | 03:00
31 | Bhulta | 222 | 23:00 | 102 | Lalbag | 86 | 18:00 | 173 | ShahCement | 32 | 01:00
32 | Bog-Sherpur | 64 | 07:00 | 103 | Lalmonirhat | 51 | 19:30 | 174 | Shahjadpur | 73 | 11:00
33 | Bogura | 207 | 21:00 | 104 | MI_Cement | 9.9 | 01:00 | 175 | Shahjibazar | 125 | 18:30
34 | Borhanuddin | 66 | 00:00 | 105 | Madanganj | 50 | 11:00 | 176 | Shahmirpur | 60 | 22:00
35 | Brahmanbaria | 123 | 00:00 | 106 | Madaripur | 92 | 05:00 | 177 | Shariatpur | 83 | 04:00
36 | Cantonment | 152 | 13:00 | 107 | Madartek | 90 | 22:00 | 178 | Sherpur | 146 | 21:00
37 | Chandina | 27 | 11:00 | 108 | Madunaghat | 54 | 16:00 | 179 | Shikalbaha | 26.5 | 19:30
38 | Chandpur | 74 | 05:00 | 109 | Magura | 58 | 00:00 | 180 | Shitalakhya | 89.4 | 13:00
39 | Chandraghona | 33 | 15:00 | 110 | Mahasthangarh | 70 | 00:00 | 181 | Sholosohor | 50 | 12:00
40 | Chapai | 65 | 21:00 | 111 | Maijdee | 33 | 02:00 | 182 | Shomvuganj | 45 | 05:00
41 | Charfasson | 28 | 01:00 | 112 | Manikganj | 126 | 21:00 | 183 | Shyampur | 162 | 13:00
42 | Charsaidpur | 39 | 01:00 | 113 | Maniknagar | 90 | 12:00 | 184 | Siddhirganj | 142 | 12:00
43 | Chauddagram | 63 | 04:00 | 114 | Matarbari | 50 | 22:00 | 185 | Sirajganj | 132 | 18:30
44 | Chhatak | 33 | 00:00 | 115 | Matuail | 82 | 23:00 | 186 | Sitakunda | 32 | 20:00
45 | Chowmuhani | 147 | 03:00 | 116 | Metrorail_Motijheel | 18 | 18:00 | 187 | Sonargaon | 126 | 10:00
46 | Chuadanga | 104 | 19:30 | 117 | Metrorail_Uttara | 8 | 18:00 | 188 | Sreemongol | 68 | 21:00
47 | Coxsbazar | 137 | 12:00 | 118 | Millgate | 104 | 15:00 | 189 | Sreepur | 136 | 11:00
48 | Cumilla(N) | 144 | 00:00 | 119 | Mirpur | 174 | 18:00 | 190 | Srinagar | 42.5 | 02:00
49 | Cumilla(S) | 172 | 18:00 | 120 | Mirsorai | 34 | 09:00 | 191 | Sunamganj | 53 | 06:00
50 | Daganbhuiyan | 35 | 00:00 | 121 | Mirzapur | 44 | 11:00 | 192 | Sylhet | 128 | 00:00
51 | Daudkandi | 128 | 05:00 | 122 | Mithapukur | 58 | 00:00 | 193 | Sylhet_(South) | 74 | 19:00
52 | DhakaUniversity | 108 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 110 | 15:00 | 124 | Mogbazar | 72.5 | 20:00 | 195 | Tangail | 170 | 12:00
54 | Dhanmondi | 128 | 13:00 | 125 | Mongla | 42 | 18:00 | 196 | Taraganj | 28 | 17:00
55 | Dohazari | 95 | 05:00 | 126 | Monirampur | 23 | 18:00 | 197 | Tasnim | 47 | 18:30
56 | Faridpur | 165 | 00:00 | 127 | Motijheel | 59 | 13:00 | 198 | Thakurgaon | 113 | 18:30
57 | Fatullah | 116 | 18:00 | 128 | Muktagacha | 38 | 14:00 | 199 | Tongi | 168 | 11:00
58 | Fenchuganj | 40 | 00:00 | 129 | Munshiganj | 103 | 04:00 | 200 | Ullahpara | 33 | 00:00
59 | Feni | 100 | 19:30 | 130 | Muradnagar | 44 | 03:00 | 201 | Ullon | 39 | 00:00
60 | GPH | 2 | 16:00 | 131 | Mymensingh | 151 | 20:00 | 202 | Uttara | 101 | 13:00
61 | Ghatail | 86 | 07:00 | 132 | Nabinagar | 110 | 08:00 | 203 | UttaraNew | 62 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 111 | 13:00 | 204 | Zigatola | 84 | 12:00
63 | Ghorashal-230 | 93 | 05:00 | 134 | Narail | 54 | 00:00
64 | Goalpara | 36 | 01:00 | 135 | Narinda | 70 | 18:00
65 | Gollamari | 108 | 12:00 | 136 | Narshingdi | 185 | 18:00
66 | Gopalganj | 97 | 07:00 | 137 | Natore | 123 | 07:00
67 | Gulshan | 136 | 13:00 | 138 | Nawabganj | 57.1 | 21:00
68 | Halishahar | 149 | 16:00 | 139 | Netrakona | 126 | 05:00
69 | HaripurSBU | 132 | 07:00 | 140 | New | 88 | 09:00
70 | Hasnabad | 102 | 23:00 | 141 | Niamatpur | 66 | 00:00
71 | Hathazari | 87 | 19:00 | 142 | Noapara | 40 | 07:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15164.02 | 2078 |  | 17335.53
1:00 | 14455.44 | 1968 |  | 16512.44
2:00 | 14288.22 | 1752 |  | 16119.22
3:00 | 13898.51 | 1713 |  | 15688.51
4:00 | 13741.85 | 1624 |  | 15438.85
5:00 | 13618.29 | 148 |  | 13773.29
6:00 | 13515.38 | 31 |  | 13547.38
7:00 | 13797.04 | 20 |  | 13818.04
8:00 | 13710.88 | 20 |  | 13731.88
9:00 | 13607.95 | 25 |  | 13633.95
10:00 | 13849.27 | 0 |  | 13849.27
11:00 | 14343.41 | 44 |  | 14389.41
12:00 | 14576.48 | 957 |  | 15576.48
13:00 | 14493.68 | 1152 |  | 15697.68
14:00 | 14423.53 | 1331 |  | 15814.53
15:00 | 14382.85 | 2036 |  | 16510.85
16:00 | 14106.14 | 1873 |  | 16063.14
17:00 | 14109.9 | 1886 |  | 16080.9
18:00 | 14815.13 | 2374 |  | 17296.13
19:00 | 15047.45 | 2552 |  | 17714.45
19:30 | 15087.92 | 2580 |  | 17783.92
20:00 | 15110.82 | 2649 |  | 17878.82
21:00 | 15131.94 | 3047 |  | 18315.94
22:00 | 14988.48 | 2395 |  | 17491.48
23:00 | 14799.93 | 2711 |  | 17632.93
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9705.12 | 5458.9 | 15164.02 | DAILY GENERATION CURVE
00:30 | 9468.87 | 5340.86 | 14809.73
01:00 | 9232.62 | 5222.82 | 14455.44 | 14-10-2026
01:30 | 9168.12 | 5203.71 | 14371.83
02:00 | 9103.62 | 5184.6 | 14288.22
02:30 | 9083.37 | 5009.995 | 14093.365
03:00 | 9063.12 | 4835.39 | 13898.51
03:30 | 8978.12 | 4842.06 | 13820.18
04:00 | 8893.12 | 4848.73 | 13741.85
04:30 | 8847.12 | 4832.95 | 13680.07
05:00 | 8801.12 | 4817.17 | 13618.29
05:30 | 8784.625 | 4782.21 | 13566.835
06:00 | 8768.13 | 4747.25 | 13515.38
06:30 | 8775.365 | 4880.845 | 13656.21
07:00 | 8782.6 | 5014.44 | 13797.04
07:30 | 8644.85 | 5109.11 | 13753.96
08:00 | 8507.1 | 5203.78 | 13710.88
08:30 | 8409.905 | 5249.51 | 13659.415
09:00 | 8312.71 | 5295.24 | 13607.95
09:30 | 8367.11 | 5361.5 | 13728.61
10:00 | 8421.51 | 5427.76 | 13849.27
10:30 | 8585.545 | 5510.795 | 14096.34
11:00 | 8749.58 | 5593.83 | 14343.41
11:30 | 8854.86 | 5605.085 | 14459.945
12:00 | 8960.14 | 5616.34 | 14576.48
12:30 | 8893.72 | 5641.36 | 14535.08
13:00 | 8827.3 | 5666.38 | 14493.68
13:30 | 8857.12 | 5601.485 | 14458.605
14:00 | 8886.94 | 5536.59 | 14423.53
14:30 | 8877.215 | 5525.975 | 14403.19
15:00 | 8867.49 | 5515.36 | 14382.85
15:30 | 8805.295 | 5439.2 | 14244.495
16:00 | 8743.1 | 5363.04 | 14106.14
16:30 | 8775.77 | 5332.25 | 14108.02
17:00 | 8808.44 | 5301.46 | 14109.9
17:30 | 9089.46 | 5373.055 | 14462.515
18:00 | 9370.48 | 5444.65 | 14815.13
18:30 | 9467.48 | 5463.81 | 14931.29
19:00 | 9564.48 | 5482.97 | 15047.45
19:30 | 9594.48 | 5493.44 | 15087.92
20:00 | 9595.48 | 5515.34 | 15110.82
20:30 | 9610.48 | 5510.9 | 15121.38 |  | Executive Engineer
21:00 | 9625.48 | 5506.46 | 15131.94 |  | Network Operation Division
21:30 | 9585.98 | 5474.23 | 15060.21
22:00 | 9546.48 | 5442 | 14988.48
22:30 | 9453.98 | 5440.225 | 14894.205
23:00 | 9361.48 | 5438.45 | 14799.93

## En-Curve
QF-LDC-12
Date | 14-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2949 | 1701 | 338 | 0 | 72 | 759.1 | 222 | 5315.8 | 0 | 759.42 | 3033.7 | 0 | 0 | 14 | 2078 | DAILY ENERGY CURVE
00:30 | 2978.5 | 1688.75 | 332.5 | 0 | 70 | 757.56 | 222 | 5240.8 | 0 | 719.42 | 2783.7 | 0 | 0 | 16.5 | 2023 | 14-10-2026
01:00 | 3008 | 1676.5 | 327 | 0 | 68 | 756.02 | 222 | 5165.8 | 0 | 679.42 | 2533.7 | 0 | 0 | 19 | 1968
01:30 | 3087 | 1643 | 350.5 | 0 | 67 | 756.41 | 221.5 | 5090.8 | 0 | 660.42 | 2485.7 | 0 | 0 | 9.5 | 1860 | Energy Generated | 345.7439 |  | MKWHr
02:00 | 3166 | 1609.5 | 374 | 0 | 66 | 756.8 | 221 | 5015.8 | 0 | 641.42 | 2437.7 | 0 | 0 | 0 | 1752 | Energy not Served | 34.386 |  | MKWHr
02:30 | 3206 | 1617.5 | 374 | 0 | 64 | 759.495 | 220.5 | 4830.5 | 0 | 641.42 | 2379.95 | 0 | 0 | 0 | 1732.5 | Total Energy Requirement | 380.1299 |  | MKWHr
03:00 | 3246 | 1625.5 | 374 | 0 | 62 | 762.19 | 220 | 4645.2 | 0 | 641.42 | 2322.2 | 0 | 0 | 0 | 1713
03:30 | 3210.5 | 1587 | 373.5 | 0 | 63 | 761.36 | 219 | 4645.2 | 0 | 641.42 | 2319.2 | 0 | 0 | 0 | 1668.5
04:00 | 3175 | 1548.5 | 373 | 0 | 64 | 760.53 | 218 | 4645.2 | 0 | 641.42 | 2316.2 | 0 | 0 | 0 | 1624
04:30 | 3185 | 1535 | 373 | 0 | 63 | 759.85 | 218 | 4596.6 | 0 | 639.92 | 2309.7 | 0 | 0 | 0 | 886
05:00 | 3195 | 1521.5 | 373 | 0 | 62 | 759.17 | 218 | 4548 | 0 | 638.42 | 2303.2 | 0 | 0 | 0 | 148
05:30 | 3190 | 1532.5 | 373.5 | 0 | 60 | 761.71 | 218 | 4538 | 0.005 | 628.42 | 2264.7 | 0 | 0 | 0 | 89.5
06:00 | 3185 | 1543.5 | 374 | 0 | 58 | 764.25 | 218 | 4528 | 0.01 | 618.42 | 2226.2 | 0 | 0 | 0 | 31
06:30 | 3182.5 | 1546 | 351 | 0 | 57 | 764.825 | 218 | 4682.3 | 58.465 | 594.92 | 2200.7 | 0 | 0 | 0.5 | 25.5
07:00 | 3180 | 1548.5 | 328 | 0 | 56 | 765.4 | 218 | 4836.6 | 116.92 | 571.42 | 2175.2 | 0 | 0 | 1 | 20
07:30 | 3189.5 | 1524.5 | 328 | 0 | 59 | 765.515 | 198.5 | 4704.2 | 219.625 | 571.42 | 2192.2 | 0 | 0 | 1.5 | 20
08:00 | 3199 | 1500.5 | 328 | 0 | 62 | 765.63 | 179 | 4571.8 | 322.33 | 571.42 | 2209.2 | 0 | 0 | 2 | 20
08:30 | 3187.5 | 1493 | 398.5 | 0 | 63 | 761.015 | 199.5 | 4468.2 | 418.39 | 481.21 | 2187.1 | 0 | 0 | 2 | 22.5
09:00 | 3176 | 1485.5 | 469 | 0 | 64 | 756.4 | 220 | 4364.6 | 514.45 | 391 | 2165 | 0 | 0 | 2 | 25
09:30 | 3191 | 1479.5 | 469 | 0 | 65 | 759.45 | 220.5 | 4453.6 | 593.56 | 398.5 | 2089 | 0 | 0 | 9.5 | 12.5
10:00 | 3206 | 1473.5 | 469 | 0 | 66 | 762.5 | 221 | 4542.6 | 672.67 | 406 | 2013 | 0 | 0 | 17 | 0
10:30 | 3166.5 | 1481.5 | 469 | 0 | 71 | 761.935 | 221 | 4647.2 | 720.205 | 439 | 2107.5 | 0 | 0 | 11.5 | 22
11:00 | 3127 | 1489.5 | 469 | 0 | 76 | 761.37 | 221 | 4751.8 | 767.74 | 472 | 2202 | 0 | 0 | 6 | 44
11:30 | 3153 | 1457.05 | 469 | 0 | 77 | 759.29 | 221 | 4776.8 | 742.495 | 508.21 | 2293.1 | 0 | 0 | 3 | 500.5
12:00 | 3179 | 1424.6 | 469 | 0 | 78 | 757.21 | 221 | 4801.8 | 717.25 | 544.42 | 2384.2 | 0 | 0 | 0 | 957
12:30 | 3158.5 | 1407.05 | 469 | 0 | 78 | 758.47 | 221 | 4829.3 | 703.39 | 503.17 | 2407.2 | 0 | 0 | 0 | 1054.5
13:00 | 3138 | 1389.5 | 469 | 0 | 78 | 759.73 | 221 | 4856.8 | 689.53 | 461.92 | 2430.2 | 0 | 0 | 0 | 1152
13:30 | 3143 | 1382.5 | 469 | 0 | 81 | 762.465 | 221 | 4854.8 | 638.72 | 465.92 | 2440.2 | 0 | 0 | 0 | 1241.5
14:00 | 3148 | 1375.5 | 469 | 0 | 84 | 765.2 | 221 | 4852.8 | 587.91 | 469.92 | 2450.2 | 0 | 0 | 0 | 1331
14:30 | 3132 | 1352.5 | 469 | 0 | 84 | 762.345 | 220.5 | 4894.8 | 521.425 | 479.92 | 2484.2 | 0 | 0 | 2.5 | 1683.5
15:00 | 3116 | 1329.5 | 469 | 0 | 84 | 759.49 | 220 | 4936.8 | 454.94 | 489.92 | 2518.2 | 0 | 0 | 5 | 2036
15:30 | 3070 | 1332 | 469.5 | 0 | 83 | 759.725 | 219.5 | 4936.8 | 346.35 | 496.92 | 2526.7 | 0 | 0 | 4 | 1954.5
16:00 | 3024 | 1334.5 | 470 | 0 | 82 | 759.96 | 219 | 4936.8 | 237.76 | 503.92 | 2535.2 | 0 | 0 | 3 | 1873
16:30 | 2994.5 | 1314 | 469.5 | 0 | 77 | 760.535 | 218.5 | 4936.8 | 141.635 | 505.42 | 2687.63 | 0 | 0 | 2.5 | 1879.5
17:00 | 2965 | 1293.5 | 469 | 0 | 72 | 761.11 | 218 | 4936.8 | 45.51 | 506.92 | 2840.06 | 0 | 0 | 2 | 1886
17:30 | 3021.5 | 1267.25 | 466.5 | 0 | 79 | 757.23 | 218.5 | 4936.8 | 22.755 | 578.92 | 3048.06 | 65 | 0 | 1 | 2130
18:00 | 3078 | 1241 | 464 | 0 | 86 | 753.35 | 219 | 4936.8 | 0 | 650.92 | 3256.06 | 130 | 0 | 0 | 2374
18:30 | 3069 | 1227 | 379 | 0 | 80 | 756.26 | 219.5 | 4974.3 | 0 | 719.67 | 3359.06 | 147.5 | 0 | 0 | 2463
19:00 | 3060 | 1213 | 294 | 0 | 74 | 759.17 | 220 | 5011.8 | 0 | 788.42 | 3462.06 | 165 | 0 | 0 | 2552
19:30 | 3041 | 1231 | 294 | 0 | 76 | 756.64 | 220 | 5021.8 | 0 | 806.42 | 3476.06 | 165 | 0 | 0 | 2580
20:00 | 3056 | 1221 | 294 | 0 | 74 | 761.54 | 221 | 5024.8 | 0 | 812.42 | 3481.06 | 165 | 0 | 0 | 2649
20:30 | 3067 | 1217 | 298 | 0 | 74 | 758.1 | 221 | 5023.3 | 0 | 816.42 | 3481.56 | 165 | 0 | 0 | 2848
21:00 | 3078 | 1213 | 302 | 0 | 74 | 754.66 | 221 | 5021.8 | 0 | 820.42 | 3482.06 | 165 | 0 | 0 | 3047
21:30 | 3058.5 | 1205.5 | 301.5 | 0 | 75 | 754.93 | 221 | 5024.3 | 0 | 811.42 | 3443.06 | 165 | 0 | 0 | 2721
22:00 | 3039 | 1198 | 301 | 0 | 76 | 755.2 | 221 | 5026.8 | 0 | 802.42 | 3404.06 | 165 | 0 | 0 | 2395
22:30 | 3026 | 1178.5 | 301 | 0 | 78 | 757.925 | 221.5 | 5026.8 | 0 | 810.92 | 3328.56 | 165 | 0 | 0 | 2553
23:00 | 3013 | 1159 | 301 | 0 | 80 | 760.65 | 222 | 5026.8 | 0 | 819.42 | 3253.06 | 165 | 0 | 0 | 2711
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 14-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | -19 | 27 | 50 | 132 | 866 | 420 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | -24 | 22 | 10 | 100 | 874 | 352
2:00 | -12 | 20 | 40 | 104 | 920 | 346 |  | Import | 0
3:00 | -3 | 21 | 60 | 120 | 732 | 400
4:00 | 1 | 17 | 98 | 126 | 754 | 384 | Ishurdi-Ghorashal Ckt-2 | Export | 710909.09
5:00 | 14 | 11 | 122 | 120 | 774 | 402
6:00 | 17 | 12 | 120 | 118 | 792 | 428 |  | Import | 71927.27
7:00 | -15 | 3 | 40 | 106 | 830 | 346
8:00 | 15 | 12 | 96 | 90 | 1050 | 380 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 71 | 19 | 234 | 108 | 1240 | 492
10:00 | 75 | 10 | 260 | 106 | 1324 | 502 |  | Import | 0
11:00 | 63 | 3 | 270 | 124 | 1312 | 480
12:00 | 59 | 14 | 226 | 106 | 1324 | 502 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 64 | 19 | 212 | 100 | 1356 | 492
14:00 | 64 | 25 | 176 | 100 | 1256 | 468 |  | Import | 0
15:00 | 74 | 29 | 214 | 116 | 1310 | 512
16:00 | 83 | 36 | 218 | 116 | 1360 | 560 | Gopalganj-Aminbazar Ckt-1 | Export | 12760000
17:00 | 51 | 23 | 168 | 104 | 1276 | 480
18:00 | 29 | 20 | 124 | 110 | 1000 | 428 |  | Import | 0
18:30 | -2 | 27 | 82 | 128 | 954 | 430
19:00 | 4 | 31 | 470 | 16 | 958 | 460 | Gopalganj-Aminbazar Ckt-2 | Export | 12780000
19:30 | -1 | 26 | 104 | 146 | 960 | 462
20:00 | 9 | 30 | 114 | 132 | 1020 | 470 |  | Import | 0
21:00 | 6 | 30 | 90 | 142 | 956 | 450
22:00 | -2 | 22 | 96 | 148 | 954 | 426 |  | Total Export | 26250909.09
23:00 | 14 | 28 | 118 | 124 | 1056 | 424 |  | Total Import | 71927.27
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 04:00 | 372 | 12:00 | Madunaghat | 409 | 09:00 | 402 | 00:00
Amtali | 414 | 06:00 | 408 | 12:00 | Meghnaghat | 395 | 03:00 | 383 | 10:00
Ashuganj | 402 | 3:00 | 391 | 12:00 | Mirsorai | 411 | 09:00 | 400 | 00:00
Bhulta | 395 | 03:00 | 382 | 12:00 | Payra | 415 | 05:00 | 410 | 11:00
Bibiana | 389 | 04:00 | 383 | 16:00 | Rahanpur | 409 | 03:00 | 398 | 07:00
BIPTC | 407 | 04:00 | 396 | 15:00 | Rampal | 399 | 03:00 | 390 | 12:00
Bogura | 403 | 04:00 | 389 | 07:00
Gopalganj | 397 | 04:00 | 388 | 10:00
Kaliakoir | 388 | 06:00 | 367 | 16:00
Korerhat | 409 | 09:00 | 398 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 04:00 | 224 | 12:00 | Hasnabad | 230 | 03:00 | 221 | 10:00
AKSML | 240 | 09:00 | 235 | 12:00 | Hathazari | 241 | 07:00 | 237 | 00:00
Aminbazar | 235 | 04:00 | 225 | 14:00 | Ishurdi | 235 | 01:00 | 223 | 07:00
Ashuganj | 230 | 01:00 | 223 | 10:00 | Jhenaidah | 226 | 04:00 | 213 | 07:00
Ashuganj-400 | 230 | 01:00 | 223 | 10:00 | Kachua | 235 | 08:00 | 229 | 00:00
Baghabari | 233 | 22:00 | 226 | 06:00 | Kaliakoir | 236 | 04:00 | 226 | 12:00
Barapukuria | 239 | 04:00 | 222 | 07:00 | Keranigonj | 232 | 04:00 | 221 | 12:00
Barapukuria-230 | 239 | 04:00 | 222 | 07:00 | Khulna(S) | 227 | 04:00 | 219 | 07:00
Barapukuria(N) | 239 | 04:00 | 225 | 07:00 | Korerhat | 238 | 18:00 | 228 | 00:00
Barishal | 226 | 06:00 | 220 | 01:00 | Madunaghat | 242 | 10:00 | 239 | 15:00
Bheramara | 235 | 03:00 | 222 | 07:00 | Madunaghat-400 | 245 | 09:00 | 242 | 00:00
Bhulta | 228 | 04:00 | 216 | 12:00 | Maniknagar | 226 | 06:00 | 215 | 12:00
Bibiana | 223 | 01:00 | 220 | 12:00 | Meghnaghat | 231 | 03:00 | 224 | 10:00
BIPTC | 235 | 01:00 | 221 | 07:00 | Meghnaghat-400 | 229 | 03:00 | 220 | 12:00
Birulia | 235 | 04:00 | 224 | 13:00 | Mirsorai | 240 | 09:00 | 226 | 18:30
Bogura | 240 | 04:00 | 230 | 07:00 | Naogaon | 228 | 04:00 | 212 | 07:00
Bogura-400 | 240 | 04:00 | 230 | 07:00 | Purbasadipur | 238 | 04:00 | 224 | 11:00
Borhanuddin | 228 | 00:00 | 222 | 11:00 | Rajshahi | 233 | 23:00 | 221 | 11:00
BSRM | 233 | 08:00 | 228 | 00:00 | Rampal | 228 | 06:00 | 220 | 07:00
Charfasson | 228 | 00:00 | 222 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 234 | 07:00 | 229 | 00:00 | Rampura | 227 | 03:00 | 214 | 13:00
Cumilla(N) | 225 | 01:00 | 220 | 11:00 | Shikalbaha | 243 | 18:00 | 239 | 16:00
Faridpur | 225 | 06:00 | 219 | 11:00 | Shyampur | 229 | 03:00 | 219 | 13:00
Fenchuganj | 225 | 06:00 | 221 | 16:00 | Siddhirganj | 228 | 05:00 | 218 | 12:00
Feni | 231 | 08:00 | 220 | 17:00 | Sirajgonj | 238 | 03:00 | 231 | 07:00
Ghorashal | 230 | 01:00 | 220 | 00:00 | Sreepur | 226 | 01:00 | 219 | 11:00
Ghorashal-230 | 225 | 04:00 | 212 | 16:00 | Tongi | 225 | 05:00 | 215 | 15:00
Gopalganj | 224 | 03:00 | 219 | 10:00
GPH | 240 | 08:00 | 232 | 00:00
Haripur | 227 | 03:00 | 217 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 126 | 12:00 | Madanganj | 138 | 05:00 | 131 | 14:00
Agargaon | 136 | 04:00 | 128 | 12:00 | Madaripur | 131 | 23:00 | 129 | 11:00
Agrabad | 138 | 06:00 | 135 | 10:00 | Madartek | 136 | 06:00 | 128 | 12:00
AKS | 136 | 07:00 | 133 | 12:00 | Madunaghat | 140 | 01:00 | 138 | 13:00
Aminbazar | 135 | 04:00 | 127 | 14:00 | Magura | 134 | 04:00 | 127 | 13:00
Amnura | 134 | 20:00 | 126 | 07:00 | Mahasthangarh | 138 | 04:00 | 130 | 07:00
Araihazar | 127 | 04:00 | 120 | 10:00 | Maijdee | 132 | 09:00 | 128 | 00:00
Ashuganj | 135 | 01:00 | 130 | 11:00 | Manikganj | 134 | 18:00 | 129 | 10:00
Ashuganj-230 | 138 | 01:00 | 135 | 00:00 | Maniknagar | 141 | 05:00 | 131 | 12:00
Bagerhat | 127 | 16:00 | 123 | 01:00 | Matarbari | 125 | 09:00 | 119 | 22:00
Bajitpur | 129 | 01:00 | 125 | 11:00 | Matuail | 138 | 04:00 | 131 | 11:00
Bakerganj | 133 | 00:00 | 130 | 12:00 | Metrorail_Motijheel | 141 | 05:00 | 131 | 12:00
Bakulia | 139 | 01:00 | 135 | 13:00 | Metrorail_Uttara | 138 | 05:00 | 127 | 13:00
Banani | 135 | 03:00 | 124 | 13:00 | Millgate | 137 | 03:00 | 127 | 13:00
Bangabhaban | 141 | 04:00 | 131 | 12:00 | Mirpur | 135 | 05:00 | 127 | 12:00
Barapukuria | 140 | 04:00 | 127 | 07:00 | Mirzapur | 136 | 18:30 | 129 | 07:00
Barguna | 133 | 05:00 | 130 | 11:00 | Mithapukur | 138 | 05:00 | 127 | 11:00
Barishal | 131 | 03:00 | 127 | 11:00 | MI_Cement | 136.1 | 04:00 | 126 | 13:00
Barishal-230 | 131 | 00:00 | 128 | 01:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 139 | 18:00 | 136 | 10:00 | Mogbazar | 136 | 01:00 | 128 | 11:00
Baroirhat | 135 | 09:00 | 132 | 06:00 | Mongla | 127 | 16:00 | 122 | 01:00
Bashundhara | 137 | 03:00 | 126 | 12:00 | Monirampur | 128 | 04:00 | 118 | 07:00
BashundharaCement | 138 | 05:00 | 131 | 14:00 | Motijheel | 141 | 04:00 | 131 | 12:00
Beanibazar | 124 | 08:00 | 118 | 13:00 | Muktagacha | 136 | 18:30 | 124 | 01:00
Benapole | 131 | 05:00 | 119 | 12:00 | Munshiganj | 137 | 03:00 | 130 | 12:00
Bhaluka | 132 | 17:00 | 125 | 07:00 | Muradnagar | 129 | 18:30 | 123 | 00:00
Bhandaria | 129 | 05:00 | 124 | 12:00 | Mymensingh | 137 | 18:30 | 121 | 11:00
Bhangura | 135 | 06:00 | 129 | 12:00 | Nabinagar | 133 | 04:00 | 127 | 08:00
Bheramara | 138 | 03:00 | 131 | 07:00 | Naogaon | 137 | 04:00 | 128 | 07:00
Bheramara(GK) | 137 | 20:00 | 131 | 07:00 | Narail | 133 | 04:00 | 126 | 07:00
Bhulta | 125 | 07:00 | 121 | 10:00 | Narinda | 141 | 05:00 | 131 | 12:00
Bhulta-400 | 128 | 03:00 | 121 | 10:00 | Narshingdi | 133 | 01:00 | 118 | 11:00
Birulia | 137 | 04:00 | 130 | 13:00 | Natore | 136 | 00:00 | 128 | 07:00
Bog-Sherpur | 137 | 03:00 | 131 | 07:00 | Nawabganj | 136 | 04:00 | 129 | 12:00
Bogura | 139 | 02:00 | 133 | 11:00 | Netrakona | 121 | 16:00 | 117 | 04:00
Bogura-230 | 140 | 04:00 | 133 | 07:00 | New | 137 | 01:00 | 128 | 15:00
Brahmanbaria | 133 | 01:00 | 126 | 11:00 | Niamatpur | 137 | 04:00 | 130 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 03:00 | 127 | 12:00 | Noapara | 130 | 06:00 | 124 | 07:00
Chandina | 131 | 06:00 | 128 | 00:00 | Pabna | 135 | 03:00 | 128 | 11:00
Chandpur | 137 | 08:00 | 134 | 00:00 | Palashbari | 135 | 18:00 | 126 | 07:00
Chandraghona | 141 | 08:00 | 138 | 12:00 | Panchagarh | 140 | 03:00 | 130 | 10:00
Chapai | 134 | 20:00 | 128 | 07:00 | Patiya | 137 | 01:00 | 132 | 16:00
Charsaidpur | 138 | 03:00 | 131 | 11:00 | Patnitala | 134 | 05:00 | 130 | 11:00
Chauddagram | 133 | 08:00 | 123 | 09:00 | Patuakhali | 134 | 18:00 | 130 | 12:00
Chhatak | 121 | 01:00 | 115 | 16:00 | Payra | 135 | 03:00 | 133 | 10:00
Chowmuhani | 132 | 07:00 | 128 | 00:00 | PHP | 135 | 08:00 | 132 | 00:00
Chuadanga | 133 | 06:00 | 125 | 11:00 | Postogola | 137 | 03:00 | 130 | 12:00
Coxsbazar | 122 | 09:00 | 118 | 00:00 | Pubail | 134 | 01:00 | 125 | 15:00
Cumilla(N) | 131 | 05:00 | 128 | 00:00 | Purbachal | 136 | 03:00 | 125 | 11:00
Cumilla(S) | 133 | 00:00 | 127 | 15:00 | Purbasadipur | 138 | 04:00 | 128 | 07:00
Daganbhuiyan | 133 | 08:00 | 130 | 00:00 | Rahanpur | 137 | 03:00 | 133 | 00:00
Daudkandi | 128 | 18:30 | 121 | 00:00 | Rahanpur-400 | 137 | 04:00 | 132 | 07:00
DhakaUniversity | 136 | 03:00 | 126 | 12:00 | Rahim | 138 | 06:00 | 131 | 13:00
Dhamrai | 135 | 04:00 | 128 | 14:00 | Rajbari | 128 | 05:00 | 124 | 11:00
Dhanmondi | 138.5 | 04:00 | 131.7 | 15:00 | Rajendrapur | 134 | 01:00 | 127 | 11:00
Dohazari | 134 | 09:00 | 130 | 13:00 | Rajshahi | 133 | 23:00 | 126 | 07:00
Faridpur | 130 | 05:00 | 126 | 15:00 | Rajshahi-230 | 134 | 23:00 | 127 | 11:00
Fatullah | 138 | 04:00 | 128 | 12:00 | Ramganj | 134 | 09:00 | 130 | 00:00
Fenchuganj | 132 | 06:00 | 129 | 12:00 | Rampur | 138 | 07:00 | 135 | 10:00
Feni | 133 | 07:00 | 130 | 00:00 | Rampura | 136 | 04:00 | 126 | 12:00
Feni-230 | 134 | 08:00 | 131 | 00:00 | Rangamati | 140 | 08:00 | 137 | 11:00
Ghatail | 134 | 18:30 | 122 | 07:00 | Rangpur | 134 | 05:00 | 124 | 07:00
Ghorashal | 136 | 01:00 | 129 | 16:00 | Ruppur | 137 | 01:00 | 130 | 07:00
Goalpara | 131 | 04:00 | 126 | 14:00 | Saidpur | 138 | 04:00 | 125 | 12:00
Gollamari | 131 | 04:00 | 128 | 01:00 | Santhia | 135 | 03:00 | 130 | 07:00
Gopalganj | 133 | 06:00 | 128 | 07:00 | Satkhira | 127 | 04:00 | 120 | 07:00
Gopalganj-400 | 135 | 23:00 | 130 | 10:00 | Satmasjid | 136 | 04:00 | 127 | 11:00
Gulshan | 135 | 05:00 | 126 | 12:00 | Savar | 134 | 02:00 | 127 | 12:00
Halishahar | 139 | 08:00 | 135 | 12:00 | SevenRings | 135 | 01:00 | 128 | 12:00
Haripur | 139 | 04:00 | 131 | 15:00 | ShahCement | 138 | 03:00 | 131 | 11:00
HaripurSBU | 139 | 04:00 | 131 | 16:00 | Shahjadpur | 134 | 00:00 | 129 | 11:00
Hasnabad | 138 | 04:00 | 130 | 10:00 | Shahjibazar | 132 | 01:00 | 123 | 13:00
Hathazari | 141 | 09:00 | 138 | 11:00 | Shahmirpur | 140 | 07:00 | 137 | 10:00
Hatirjheel | 136 | 04:00 | 125 | 13:00 | Shariatpur | 129 | 05:00 | 127 | 00:00
Ishurdi | 138 | 01:00 | 131 | 07:00 | Sherpur | 137 | 13:00 | 115 | 07:00
Jaldhaka | 134 | 04:00 | 123 | 12:00 | Shikalbaha | 128 | 00:00 | 125 | 11:00
Jamalpur | 140 | 18:30 | 119 | 07:00 | Shikalbaha-230 | 140 | 04:00 | 136 | 16:00
Jashore | 138 | 02:00 | 121 | 07:00 | Shitalakhya | 136.1 | 04:00 | 126 | 13:00
Jhenaidah | 135 | 03:00 | 129 | 11:00 | Sholosohor | 140 | 08:00 | 137 | 12:00
Jhenaidah-230 | 137 | 03:00 | 128 | 07:00 | Shomvuganj | 123 | 13:00 | 118 | 12:00
Joydebpur | 133 | 05:00 | 124 | 15:00 | Shyampur | 136 | 06:00 | 129 | 13:00
Joypurhat | 135 | 20:00 | 129 | 07:00 | Shyampur-230 | 138 | 03:00 | 131 | 12:00
Juldah | 139 | 07:00 | 136 | 11:00 | Siddhirganj | 139 | 04:00 | 132 | 11:00
Kabirpur | 138 | 18:00 | 124 | 09:00 | Sirajganj | 134 | 04:00 | 127 | 07:00
Kachua | 134 | 08:00 | 131 | 00:00 | Sitakunda | 140 | 08:00 | 137 | 00:00
Kaliakoir | 140 | 04:00 | 127 | 14:00 | Sonargaon | 137 | 04:00 | 129 | 10:00
Kaliganj | 135 | 06:00 | 127 | 11:00 | Sreemongol | 129 | 02:00 | 124 | 12:00
Kallyanpur | 135 | 01:00 | 127 | 12:00 | Sreepur | 134 | 01:00 | 129 | 11:00
Kalurghat | 141 | 09:00 | 138 | 11:00 | Srinagar | 136 | 03:00 | 129 | 13:00
Kamrangirchar | 137 | 05:00 | 124 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 118 | 02:00 | 114 | 16:00
Kasba | 129 | 18:30 | 122 | 00:00 | Sylhet | 124 | 01:00 | 121 | 11:00
Kazla | 141 | 05:00 | 131 | 13:00 | Sylhet_(South) | 125 | 01:00 | 121 | 16:00
Keranigonj | 137 | 04:00 | 130 | 11:00 | Tangail | 131 | 00:00 | 125 | 11:00
Khagrachori | 139 | 07:00 | 135 | 13:00 | Taraganj | 136 | 20:00 | 126 | 10:00
Khulna | 130 | 04:00 | 125 | 07:00 | Tasnim | 137 | 04:00 | 129 | 10:00
Khulna(S) | 132 | 06:00 | 126 | 07:00 | Thakurgaon | 142 | 04:00 | 131 | 10:00
Khulshi | 137 | 09:00 | 133 | 16:00 | TK | 139 | 00:00 | 137 | 07:00
Kishoreganj | 127 | 04:00 | 123 | 11:00 | Tongi | 140 | 05:00 | 131 | 15:00
Kodda | 138 | 18:30 | 125 | 16:00 | Ullahpara | 135 | 04:00 | 129 | 07:00
Korerhat | 138 | 08:00 | 134 | 00:00 | Ullon | 135 | 04:00 | 126 | 12:00
KSRM | 140 | 08:00 | 136 | 10:00 | Uttara | 136 | 04:00 | 125 | 15:00
Kulaura | 131 | 09:00 | 128 | 00:00 | UttaraNew | 138 | 05:00 | 127 | 13:00
Kurigram | 134 | 05:00 | 122 | 12:00 | Zigatola | 137 | 05:00 | 130 | 11:00
Kushtia | 136 | 03:00 | 130 | 11:00
Laksam | 132 | 06:00 | 130 | 00:00
Lakshmipur | 131 | 08:00 | 127 | 00:00
Lalbag | 136 | 05:00 | 129 | 12:00
Lalmonirhat | 133 | 06:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division