## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-10-2026 | during | 17-10-2026 | during | 17-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 366 | 355 | 412 | 412 | 400 | 400 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 297 | 285 | 335 | 335 | 317 | 317 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 90 | 127 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 11 | 24.75 | 24.75 | 5.5 | 5.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 18 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 25 | 52.19 | 52.19 | 16 | 47 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 295 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 133 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 95 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 455 | 380 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 380 | 430 | 583 | 583 | 450 | 450 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2347 | 2670.42 | 5558.55 | 5528.55 | 2693.92 | 2980.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 10 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 219 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 61 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 51 | 24 | 54 | 24 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 0 | 68 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 37 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 23 | 30 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 12 | 46 | 95.1 | 95.1 | 34 | 52 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.46 | 0 | 3.93 | 0 | 3.93 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 213 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 84 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 80 | 109 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 18 | 90 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 600 | 1224 | 1224 | 1224 | 600 | 1224
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1080 | 1080 | 1150 | 1150 | 1080 | 1080 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2558.46 | 3735.86 | 4106.89 | 4194.96 | 2861.93 | 3932.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 213 | 217 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 299 | 271 | 350.01 | 350.01 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 280 | 220 | 342.01 | 342.01 | 310 | 310 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 393 | 393
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 22 | 22 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 70 | 70 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 135 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 20 | 22 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 30 | 163 | 163 | 50 | 50 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 66 | 121 | 200 | 200 | 135 | 124 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 52 | 68 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 12 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 14 | 24.5 | 24.5 | 0 | 0 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 64 | 71 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 14 | 107 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1548 | 1701.2 | 2751.44 | 2680.44 | 1831.2 | 1808.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-10-2026 | during | 17-10-2026 | during | 17-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 0 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 0 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.73 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 0 | 22 | 22 | 22 | 22
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 271.73 | 35 | 673.6 | 601.5 | 290.1 | 304
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 146 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 135 | 137 | 137 | 137 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 86 | 86 | 13 | 13 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 76 | 76 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 297 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 398 | 398 | 400 | 400 | 400 | 400
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 392 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1546 | 1554 | 1596 | 1596 | 1584 | 1584
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 704 | 599 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 18 | 32 | 32 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 14 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1197 | 1204 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1979 | 1920 | 3296.2 | 3206.2 | 2729.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 850 | 850 | 850 | 850 | 850 | 850 | machine problem
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 48 | 110 | 110 | 48 | 64 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 105 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 100 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 293 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1602.65 | 1710 | 1838 | 1837 | 1675 | 1690
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.88 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 44 | 44 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 22 | 40 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 284 | 270 | 413.79 | 413.79 | 300 | 300 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 26 | 26 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 5.5 | 92 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 40 | 113 | 113 | 113 | 50 | 113
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.97 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1117.27 | 1101.43 | 1000 | 1400 | 1100 | 1400 | Machine Problem
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.52 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 69 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1790.14 | 1850.63 | 2813.11 | 2990.99 | 1900.32 | 2149.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 91 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 135 | 0 | 183.86 | 0 | 183.86 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 299.7 | 228 | 466.86 | 248 | 376.86 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 13942.68 | 15405.11 | 23100.65 | 22883.64 | 15942.53 | 17325.38
Forecast Scenario (17-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14460 |  | 130 |  | 14590
|  |  |  | 1:00 | 13910 |  | 400 |  | 14310
|  |  |  | 2:00 | 13690 |  | 150 |  | 13840
|  |  |  | 3:00 | 13510 |  | 0 |  | 13510
|  |  |  | 4:00 | 13550 |  | 0 |  | 13550
|  |  |  | 5:00 | 13450 |  | 0 |  | 13450
|  |  |  | 6:00 | 13460 |  | 0 |  | 13460
|  |  |  | 7:00 | 13550 |  | 0 |  | 13550
|  |  |  | 8:00 | 13680 |  | 0 |  | 13680
|  |  |  | 9:00 | 14120 |  | 0 |  | 14120
|  |  |  | 10:00 | 14330 |  | 0 |  | 14330
|  |  |  | 11:00 | 14350 |  | 0 |  | 14350
|  |  |  | 12:00 | 14520 |  | 170 |  | 14690
|  |  |  | 13:00 | 14420 |  | 540 |  | 14960
|  |  |  | 14:00 | 14320 |  | 780 |  | 15100
|  |  |  | 15:00 | 14380 |  | 920 |  | 15300
|  |  |  | 16:00 | 14490 |  | 710 |  | 15200
|  |  |  | 17:00 | 14710 |  | 460 |  | 15170
|  |  |  | 18:00 | 15400 |  | 300 |  | 15700
|  |  |  | 18:30 | 15540 |  | 900 |  | 16440
|  |  |  | 19:00 | 15800 |  | 1500 |  | 17300
|  |  |  | 19:30 | 15850 |  | 1600 |  | 17450
|  |  |  | 20:00 | 15860 |  | 1550 |  | 17410
|  |  |  | 21:00 | 15880 |  | 1870 |  | 17750
|  |  |  | 22:00 | 15600 |  | 1800 |  | 17400
|  |  |  | 23:00 | 15200 |  | 2150 |  | 17350
Probable Maximum Temperature: |  |  | 33.40°C
Probable Maximum Demand at Day Peak: |  |  | 14690.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 17750.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15880.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.38 MKWHr. |  | 330 | 150 | 250 | 320 | 120 | 290 | 100 | 170 | 140 | 1870
*** This report is generated digitally from Operation Information System (OIS) at 09:37 hrs on 17-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-10-2026 | [28 empty] | Date: | 16-10-2026 | [28 empty] | Date: | 16-10-2026 | [28 empty] | Date: | 16-10-2026 | [28 empty] | Date: | 16-10-2026 | [16 empty] | Date: | 16-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [16 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 35 | 54 | 135 | 128 | 295 | 55 | 55 | 108 | 0 | 0 | 430 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 7.2 | 21 | 0 | 505 | 107 | 85 | 66 | 0 | 0 | 67 | 50 | 35 | 24 | 25 | 0 | 221 | 93 | 4 | 1080 | 18 | 0 | 45 | 17 | 105 | 220 | 0 | 0 | 0 | 815 | 0 | 150 | 0 | 165 | 343 | 280 | 44 | 0 | 210 | 0 | 73 | 35 | 157 | 73 | 9 | 114 | 68 | 52.2 | 0 | 23 | 295 | 400 | 401 | 40 | 30 | 157 | 0 | 16 | 0 | 41 | 0 | 136 | 0 | 75 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 9407.82 | 717 | 0 | 28 | 35 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 749.41 | 0 | 47 | 0 | 113 | 113 | 0 | 100 | 38 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 280 | 110 | 0 | 0 | 1050 | 300 | 35 | 5765.81 | 15173.63 | 104.34
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 35 | 54 | 134 | 128 | 295 | 55 | 55 | 90 | 0 | 0 | 435 | 0 | 55 | 321 | 0 | 0 | 0 | 143.42 | 7.2 | 21 | 0 | 495 | 107 | 50 | 64 | 0 | 0 | 67 | 29 | 18 | 24 | 25 | 0 | 221 | 96 | 7 | 1080 | 16 | 0 | 45 | 18 | 102 | 220 | 0 | 0 | 0 | 630 | 0 | 150 | 0 | 215 | 347 | 280 | 44 | 0 | 191 | 0 | 72 | 36 | 154 | 69 | 9 | 114 | 62 | 52.2 | 0 | 23 | 290 | 400 | 403 | 40 | 30 | 158 | 0 | 16 | 0 | 41 | 0 | 136 | 0 | 77 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 22 | 9152.82 | 712 | 0 | 28 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 753.51 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 115 | 0 | 71 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 35 | 5208.91 | 14361.73 | 104.33
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 35 | 54 | 134 | 128 | 295 | 55 | 55 | 90 | 0 | 0 | 430 | 0 | 55 | 327 | 0 | 0 | 0 | 143.42 | 7.2 | 21 | 0 | 485 | 107 | 50 | 62 | 0 | 0 | 67 | 29 | 18 | 24 | 25 | 0 | 221 | 109 | 11 | 1080 | 16 | 0 | 45 | 17 | 105 | 219 | 0 | 0 | 0 | 600 | 0 | 150 | 0 | 215 | 324 | 280 | 44 | 0 | 184 | 0 | 88 | 34 | 140 | 76 | 9 | 114 | 64 | 52.2 | 0 | 23 | 281 | 400 | 404 | 40 | 30 | 158 | 0 | 16 | 0 | 70 | 0 | 136 | 0 | 0 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 23 | 9052.82 | 705 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 745.23 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 35 | 5167.63 | 14220.45 | 104.32
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 54 | 133 | 128 | 295 | 55 | 55 | 90 | 0 | 0 | 430 | 0 | 55 | 325 | 0 | 0 | 0 | 143.42 | 7.2 | 21 | 0 | 485 | 109 | 50 | 58 | 0 | 0 | 67 | 29 | 18 | 24 | 25 | 0 | 219 | 109 | 17 | 1080 | 16 | 0 | 45 | 17 | 105 | 220 | 0 | 0 | 0 | 600 | 0 | 140 | 0 | 215 | 338 | 280 | 44 | 0 | 195 | 0 | 88 | 36 | 139 | 25 | 9 | 114 | 62 | 52.2 | 0 | 23 | 280 | 400 | 400 | 40 | 30 | 157 | 0 | 16 | 0 | 81 | 0 | 136 | 0 | 0 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 9013.82 | 705 | 0 | 24 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 724.27 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 10 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4975.67 | 13989.49 | 104.31
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 54 | 133 | 128 | 295 | 55 | 55 | 90 | 0 | 0 | 430 | 0 | 35 | 327 | 0 | 0 | 0 | 143.42 | 7.5 | 21 | 0 | 480 | 107 | 50 | 58 | 0 | 0 | 67 | 29 | 18 | 24 | 25 | 0 | 218 | 110 | 25 | 1080 | 16 | 0 | 45 | 17 | 105 | 220 | 0 | 0 | 0 | 600 | 0 | 144 | 0 | 215 | 319 | 280 | 44 | 0 | 196 | 0 | 75 | 36 | 138 | 0 | 9 | 114 | 60 | 52.2 | 0 | 23 | 278 | 400 | 403 | 40 | 30 | 157 | 0 | 16 | 0 | 85 | 0 | 136 | 0 | 0 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 24 | 8948.12 | 705 | 0 | 24 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 722.93 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4977.33 | 13925.45 | 104.3
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 35 | 54 | 133 | 128 | 295 | 55 | 55 | 90 | 0 | 0 | 400 | 0 | 35 | 327 | 0 | 0 | 0 | 143.42 | 7.5 | 21 | 0 | 440 | 107 | 50 | 41 | 0 | 0 | 67 | 29 | 18 | 24 | 25 | 0 | 217 | 100 | 26 | 1080 | 16 | 0 | 45 | 17 | 105 | 219 | 0 | 0 | 0 | 600 | 0 | 144 | 0 | 215 | 326 | 280 | 44 | 0 | 204 | 0 | 53 | 35 | 139 | 0 | 9 | 114 | 60 | 52.2 | 0 | 23 | 275 | 400 | 403 | 40 | 30 | 155 | 0 | 16 | 0 | 82 | 0 | 136 | 0 | 0 | 35 | 58 | 0 | 68 | 0 | 0 | 0 | 24 | 8830.12 | 705 | 0 | 24 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 727.27 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4921.67 | 13751.79 | 104.29
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 54 | 133 | 95 | 95 | 55 | 35 | 90 | 0 | 0 | 390 | 0 | 35 | 300 | 0 | 0 | 0 | 105 | 7.5 | 21 | 0 | 445 | 109 | 50 | 46 | 0 | 0 | 67 | 29 | 35 | 0 | 25 | 0 | 217 | 92 | 14 | 1080 | 16 | 0 | 45 | 17 | 105 | 220 | 0 | 0 | 0 | 600 | 0 | 140 | 0 | 215 | 306 | 280 | 44 | 0 | 213 | 0 | 51 | 36 | 137 | 0 | 9 | 73 | 54 | 52.2 | 0 | 23 | 265 | 400 | 357 | 40 | 30 | 155 | 0 | 8 | 0 | 83 | 0 | 136 | 0 | 0 | 35 | 58 | 0.05 | 68 | 0 | 0 | 0.06 | 24 | 8352.81 | 704 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 733.22 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4890.62 | 13243.43 | 104.28
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 54 | 103 | 95 | 95 | 55 | 0 | 72 | 0 | 0 | 410 | 0 | 35 | 300 | 0 | 0 | 4 | 105 | 7.5 | 14 | 0 | 520 | 109 | 50 | 12 | 0 | 0 | 40 | 29 | 35 | 0 | 25 | 0.32 | 218 | 86 | 10 | 1080 | 16 | 0 | 45 | 17 | 104 | 221 | 0 | 0 | 0 | 605 | 4 | 142 | 0 | 215 | 344 | 280 | 44 | 0 | 188 | 0 | 51 | 36 | 138 | 0 | 9 | 50 | 52 | 52.2 | 14 | 23 | 276 | 400 | 397 | 40 | 30 | 158 | 2 | 8 | 0 | 81 | 0 | 135 | 0 | 0 | 35 | 59 | 3.66 | 68 | 0 | 0.3 | 8.73 | 24 | 8344.71 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1234.2 | 0 | 0 | 0 | 732.58 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 7 | 52.2 | 7.93 | 12 | 0 | 0 | 8.15 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0.77 | 0 | 0 | 50 | 4 | 34 | 0 | 0 | 0 | 0.8 | 26 | 0.14 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4797.77 | 13142.48 | 104.27
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17 | 54 | 98 | 95 | 95 | 55 | 0 | 72 | 0 | 0 | 410 | 0 | 35 | 300 | 0 | 0 | 12 | 105 | 8.5 | 21 | 0 | 420 | 107 | 50 | 12 | 0 | 0 | 34 | 29 | 35 | 0 | 25 | 1.63 | 219 | 73 | 14 | 1080 | 22 | 0 | 45 | 17 | 105 | 220 | 0 | 0 | 0 | 605 | 11 | 127 | 0 | 215 | 318 | 280 | 44 | 0 | 189 | 0 | 51 | 36 | 138 | 1 | 9 | 48 | 52 | 52.2 | 36 | 23 | 280 | 400 | 397 | 40 | 30 | 157 | 5 | 16 | 0 | 81 | 0 | 137 | 0 | 0 | 35 | 58 | 10 | 68 | 0 | 1 | 23.98 | 24 | 8265.31 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1234.2 | 0 | 0 | 0 | 725.35 | 0 | 47 | 0 | 55 | 50 | 0 | 0 | 24 | 52.2 | 23.32 | 38 | 0 | 0 | 25.73 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 2.32 | 0 | 0 | 50 | 13 | 34 | 0 | 0 | 0 | 2.8 | 74 | 0.16 | 64 | 280 | 110 | 0 | 0 | 850 | 300 | 17 | 4957.08 | 13222.39 | 104.26
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 54 | 94 | 60 | 45 | 30 | 17 | 54 | 0 | 0 | 345 | 0 | 35 | 307 | 0 | 0 | 21 | 86 | 8.5 | 21 | 0 | 500 | 35 | 50 | 12 | 0 | 0 | 19 | 29 | 35 | 0 | 25 | 2.52 | 219 | 34 | 7 | 1050 | 6 | 0 | 23 | 8 | 34 | 218 | 0 | 0 | 0 | 600 | 0 | 132 | 0 | 215 | 314 | 280 | 44 | 0 | 203 | 0 | 16 | 36 | 17 | 42 | 9 | 8 | 44 | 8 | 30 | 23 | 286 | 395 | 398 | 40 | 30 | 140 | 9 | 16 | 0 | 78 | 0 | 137 | 0 | 0 | 17 | 58 | 15 | 77 | 0 | 1.5 | 36.86 | 24 | 7679.38 | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1226 | 0 | 0 | 0 | 743.26 | 0 | 47 | 0 | 55 | 0 | 0 | 0 | 24 | 8 | 38.96 | 66 | 0 | 0 | 42.29 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 3.72 | 0 | 0 | 35 | 23 | 34 | 0 | 0 | 0 | 4.4 | 123 | 0.42 | 64 | 249 | 110 | 0 | 0 | 850 | 300 | 17 | 5111.05 | 12790.43 | 104.25
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 54 | 78 | 60 | 45 | 30 | 35 | 54 | 0 | 0 | 350 | 0 | 35 | 302 | 0 | 0 | 28 | 86 | 9.5 | 21 | 0 | 480 | 35 | 50 | 12 | 0 | 0 | 34 | 29 | 35 | 0 | 25 | 3.14 | 220 | 34 | 9 | 1020 | 0 | 0 | 20 | 8 | 34 | 217 | 0 | 0 | 0 | 600 | 14 | 130 | 0 | 215 | 305 | 280 | 44 | 0 | 212 | 0 | 0 | 36 | 16 | 56 | 9 | 0 | 46 | 8 | 29 | 22 | 292 | 395 | 398 | 40 | 29 | 152 | 10 | 16 | 0 | 80 | 0 | 137 | 0 | 0 | 17 | 49 | 18.6 | 65 | 0 | 1.9 | 45.03 | 24 | 7658.17 | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1189 | 0 | 0 | 0 | 843.38 | 0 | 44 | 0 | 35 | 0 | 0 | 0 | 24 | 8 | 49.59 | 86 | 0 | 0 | 54.26 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 4.75 | 0 | 0 | 35 | 29 | 34 | 0 | 0 | 0 | 5.8 | 158 | 0.62 | 32 | 294 | 110 | 0 | 0 | 850 | 300 | 17 | 5268.4 | 12926.57 | 104.24
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 54 | 78 | 60 | 95 | 30 | 35 | 54 | 0 | 0 | 375 | 0 | 35 | 307 | 0 | 0 | 30 | 86 | 9.5 | 14 | 0 | 545 | 55 | 50 | 10 | 0 | 0 | 0 | 28 | 35 | 0 | 25 | 3.43 | 220 | 50 | 7 | 1080 | 0 | 0 | 19 | 8 | 35 | 216 | 0 | 0 | 0 | 600 | 7 | 100 | 0 | 215 | 315 | 280 | 44 | 0 | 213 | 0 | 0 | 31 | 18 | 63 | 11 | 0 | 48 | 8 | 66 | 21 | 297 | 390 | 398 | 40 | 29 | 155 | 10 | 16 | 0 | 80 | 0 | 136 | 0 | 0 | 17 | 49 | 20.58 | 65 | 0 | 2 | 50.23 | 24 | 7881.74 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 1158 | 0 | 0 | 0 | 957.16 | 0 | 44 | 0 | 35 | 0 | 0 | 0 | 23 | 8 | 54.46 | 96 | 0 | 0 | 60.24 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 0 | 68 | 28 | 34 | 0 | 0 | 0 | 6.5 | 147 | 0.32 | 32 | 307 | 110 | 0 | 0 | 850 | 300 | 17 | 5414.68 | 13296.42 | 104.22
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 54 | 95 | 90 | 145 | 30 | 35 | 95 | 0 | 0 | 380 | 0 | 35 | 297 | 0 | 0 | 30 | 123 | 10 | 14 | 0 | 455 | 80 | 51 | 12 | 0 | 0 | 0 | 26 | 35 | 0 | 25 | 3.46 | 220 | 68 | 5 | 1080 | 18 | 0 | 32 | 10 | 61 | 214 | 0 | 0 | 0 | 600 | 18 | 108 | 0 | 215 | 299 | 280 | 44 | 0 | 213 | 0 | 14 | 30 | 66 | 64 | 11 | 52 | 52 | 12 | 68 | 20 | 297 | 392 | 398 | 40 | 29 | 154 | 4 | 16 | 0 | 81 | 0 | 135 | 0 | 0 | 17 | 58 | 21 | 114 | 0 | 2 | 35.73 | 24 | 8271.19 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1197 | 0 | 0 | 0 | 1117.27 | 0 | 44 | 0 | 55 | 40 | 0 | 5.5 | 22 | 34 | 51.88 | 69 | 0 | 0 | 62.52 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 4.97 | 0 | 0 | 91 | 33 | 34 | 0 | 0 | 0 | 6.7 | 135 | 0.65 | 32 | 293 | 110 | 0 | 0 | 850 | 300 | 17 | 5671.49 | 13942.68 | 104.2
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 54 | 132 | 60 | 95 | 30 | 35 | 108 | 0 | 0 | 440 | 0 | 35 | 310 | 0 | 0 | 29 | 105 | 10 | 14 | 0 | 540 | 90 | 51 | 0 | 0 | 0 | 0 | 26 | 35 | 0 | 25 | 3.24 | 220 | 79 | 13 | 1080 | 16 | 0 | 37 | 25.5 | 77 | 213 | 0 | 0 | 0 | 800 | 18 | 132 | 0 | 215 | 318 | 280 | 44 | 0 | 212 | 0 | 34 | 30 | 85 | 70 | 10 | 20 | 52 | 34 | 40 | 20 | 296 | 388 | 398 | 40 | 29 | 153 | 10 | 16 | 0 | 81 | 0 | 135 | 0 | 0 | 17 | 58 | 20 | 116 | 0 | 2 | 45.54 | 24 | 8693.28 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 1222 | 0 | 0 | 0 | 1123.58 | 0 | 44 | 0 | 55 | 70 | 0 | 8.3 | 24 | 34 | 51.34 | 97 | 0 | 0 | 55.29 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 4.9 | 0 | 0 | 95 | 31 | 34 | 0 | 0 | 0 | 6 | 170 | 0.52 | 32 | 277 | 110 | 0 | 0 | 850 | 300 | 35 | 5801.93 | 14495.21 | 104.18
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 35 | 110 | 30 | 45 | 30 | 35 | 35 | 0 | 0 | 420 | 0 | 35 | 309 | 0 | 0 | 25 | 105 | 11 | 14 | 0 | 535 | 72 | 51 | 0 | 0 | 0 | 0 | 26 | 35 | 0 | 25 | 2.71 | 220 | 51 | 10 | 1080 | 0 | 0 | 41 | 8 | 51 | 213 | 0 | 0 | 0 | 800 | 16 | 135 | 0 | 215 | 315 | 280 | 44 | 0 | 212 | 0 | 16 | 31 | 51 | 45 | 10 | 0 | 52 | 16 | 57 | 20 | 293 | 386 | 398 | 40 | 29 | 152 | 9 | 16 | 0 | 82 | 0 | 136 | 0 | 0 | 17 | 59 | 16.8 | 116 | 0 | 1.7 | 36.31 | 24 | 8244.52 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 1211 | 0 | 0 | 0 | 1115.02 | 0 | 44 | 0 | 55 | 35 | 0 | 8.3 | 23 | 34 | 9.79 | 79 | 0 | 0 | 46.57 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 4.31 | 0 | 0 | 70 | 25 | 34 | 0 | 0 | 0 | 5.4 | 141 | 0.48 | 32 | 277 | 110 | 0 | 0 | 850 | 300 | 35 | 5586.87 | 13831.39 | 104.16
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 35 | 97 | 60 | 145 | 30 | 35 | 72 | 0 | 0 | 430 | 0 | 17 | 312 | 0 | 0 | 17 | 105 | 11 | 14 | 0 | 550 | 97 | 51 | 0 | 0 | 0 | 0 | 26 | 35 | 0 | 25 | 1.8 | 220 | 83 | 8 | 1080 | 0 | 0 | 45 | 10 | 70 | 213 | 0 | 0 | 0 | 669 | 12 | 128 | 0 | 215 | 315 | 280 | 44 | 0 | 208 | 0 | 16 | 31 | 54 | 54 | 10 | 0 | 52 | 17 | 41 | 20 | 294 | 390 | 393 | 40 | 29 | 151 | 6 | 16 | 0 | 78 | 0 | 137 | 0 | 0 | 17 | 58 | 12.16 | 116 | 0 | 1.2 | 27.13 | 24 | 8275.29 | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1205 | 0 | 0 | 0 | 1120.98 | 0 | 44 | 0 | 100 | 58 | 0 | 8.3 | 23 | 44 | 30.72 | 57 | 0 | 0 | 33.57 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 2.94 | 0 | 0 | 105 | 18 | 70 | 0 | 0 | 0 | 3.9 | 94 | 0.06 | 32 | 307 | 105 | 0 | 0 | 850 | 300 | 35 | 5632.47 | 13907.76 | 104.14
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 35 | 104 | 60 | 145 | 30 | 35 | 108 | 0 | 0 | 395 | 0 | 17 | 307 | 0 | 0 | 9 | 105 | 11 | 14 | 0 | 470 | 107 | 51 | 5 | 0 | 0 | 0 | 26 | 35 | 0 | 25 | 0.84 | 219 | 93 | 15 | 1080 | 0 | 0 | 45 | 25.5 | 105 | 216 | 0 | 0 | 0 | 600 | 6 | 130 | 0 | 215 | 304 | 240 | 44 | 0 | 213 | 0 | 16 | 30 | 88 | 71 | 14 | 0 | 52 | 43 | 21 | 20 | 295 | 388 | 394 | 40 | 28 | 146 | 3 | 16 | 0 | 78 | 0 | 137 | 0 | 0 | 17 | 59 | 5.61 | 116 | 0 | 0.5 | 13.48 | 24 | 8152.93 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 22 | 1218 | 0 | 0 | 0 | 1118.6 | 0 | 44 | 0 | 113 | 35 | 0 | 8.3 | 23 | 52.2 | 16.53 | 30 | 0 | 0 | 16.02 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 1.42 | 0 | 0 | 50 | 10 | 87 | 0 | 0 | 0 | 1.8 | 42 | 0.01 | 32 | 291 | 105 | 0 | 0 | 850 | 300 | 35 | 5499.88 | 13652.81 | 104.12
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 35 | 114 | 60 | 145 | 30 | 35 | 162 | 0 | 0 | 325 | 0 | 17 | 250 | 0 | 0 | 2 | 105 | 11 | 14 | 0 | 420 | 107 | 202 | 30 | 0 | 0 | 0 | 40 | 54.36 | 0 | 25 | 0.09 | 218 | 93 | 19 | 1060 | 0 | 0 | 45 | 25.5 | 99 | 215 | 0 | 0 | 0 | 600 | 1 | 130 | 0 | 215 | 293 | 220 | 44 | 0 | 170 | 0 | 16 | 30 | 108 | 70 | 14 | 0 | 60 | 52.2 | 3 | 21 | 290 | 340 | 360 | 40 | 30 | 137 | 0 | 16 | 0 | 53 | 0 | 136 | 0 | 0 | 17 | 59 | 0.97 | 115 | 0 | 0.1 | 2.22 | 24 | 8029.44 | 649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 4 | 1209 | 0 | 0 | 0 | 1037.72 | 0 | 44 | 0 | 113 | 35 | 0 | 8.3 | 23 | 52.2 | 2.47 | 6 | 0 | 0 | 2.73 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0.2 | 0 | 0 | 35 | 2 | 49 | 0 | 0 | 0 | 0.4 | 9 | 0.02 | 48 | 241 | 105 | 0 | 0 | 790 | 300 | 100 | 5198.04 | 13227.48 | 104.1
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 133 | 77 | 278 | 40 | 55 | 162 | 0 | 0 | 355 | 0 | 35 | 303 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 535 | 107 | 206 | 50 | 0 | 0 | 0 | 51 | 54.36 | 24 | 38 | 0 | 218 | 96 | 21 | 1080 | 28 | 0 | 50 | 25.5 | 103 | 215 | 0 | 0 | 0 | 810 | 0 | 132 | 0 | 215 | 298 | 220 | 44 | 0 | 215 | 0 | 39 | 30 | 121 | 70 | 14 | 114 | 70 | 52.2 | 0 | 22 | 305 | 393 | 398 | 40 | 29 | 144 | 0 | 16 | 0 | 82 | 0 | 137 | 0 | 0 | 18 | 77 | 0 | 170 | 0 | 0 | 0 | 24 | 9323.48 | 592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1141 | 0 | 0 | 0 | 1109.88 | 0 | 44 | 0 | 113 | 40 | 0 | 89 | 35 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 261 | 105 | 0 | 0 | 850 | 300 | 100 | 5429.08 | 14752.56 | 104.08
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 133 | 127 | 295 | 55 | 55 | 162 | 0 | 0 | 430 | 0 | 55 | 285 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 380 | 109 | 213 | 46 | 0 | 0 | 67 | 51 | 54.36 | 37 | 38 | 0 | 220 | 84 | 23 | 1080 | 90 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 135 | 0 | 215 | 271 | 220 | 44 | 0 | 217 | 0 | 107 | 30 | 121 | 71 | 14 | 114 | 68 | 52.2 | 0 | 22 | 305 | 400 | 398 | 40 | 30 | 146 | 0 | 16 | 0 | 82 | 0 | 137 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9696.48 | 599 | 0 | 18 | 14 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1204 | 0 | 0 | 0 | 1101.43 | 0 | 44 | 0 | 113 | 113 | 0 | 92 | 40 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 105 | 0 | 0 | 850 | 300 | 100 | 5708.63 | 15405.11 | 104.06
19:30 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 35 | 133 | 127 | 225 | 30 | 55 | 108 | 0 | 0 | 420 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 560 | 107 | 213 | 18 | 0 | 0 | 67 | 14 | 54.36 | 12 | 38 | 0 | 219 | 68 | 23 | 1080 | 34 | 0 | 50 | 25.5 | 68 | 218 | 0 | 0 | 0 | 1224 | 0 | 135 | 0 | 215 | 321 | 220 | 44 | 0 | 207 | 0 | 68 | 31 | 121 | 74 | 14 | 17 | 70 | 52.2 | 0 | 22 | 300 | 393 | 398 | 40 | 30 | 147 | 0 | 16 | 0 | 82 | 0 | 137 | 0 | 0 | 35 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 9485.48 | 676 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1222 | 0 | 0 | 0 | 1114.87 | 0 | 0 | 0 | 113 | 50 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 115 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 105 | 0 | 0 | 850 | 300 | 100 | 5628.07 | 15113.55
20:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 54 | 35 | 133 | 127 | 225 | 30 | 55 | 108 | 0 | 0 | 395 | 0 | 55 | 307 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 535 | 107 | 213 | 19 | 0 | 0 | 67 | 14 | 54.36 | 12 | 38 | 0 | 220 | 68 | 27 | 1080 | 34 | 0 | 50 | 25.5 | 68 | 218 | 0 | 0 | 0 | 1224 | 0 | 133 | 0 | 215 | 306 | 220 | 44 | 0 | 202 | 0 | 68 | 31 | 122 | 73 | 10 | 17 | 68 | 52.2 | 0 | 22 | 305 | 397 | 398 | 40 | 30 | 141 | 0 | 16 | 0 | 82 | 0 | 138 | 0 | 0 | 35 | 5 | 0 | 128 | 0 | 0 | 0 | 8 | 9492.48 | 676 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1223 | 0 | 0 | 0 | 1190.29 | 0 | 0 | 0 | 113 | 50 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 105 | 0 | 0 | 850 | 300 | 100 | 5701.49 | 15193.97 | 104.04
21:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 35 | 133 | 108 | 225 | 30 | 55 | 108 | 0 | 0 | 400 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 410 | 107 | 213 | 18 | 0 | 0 | 67 | 14 | 54.36 | 12 | 38 | 0 | 220 | 68 | 27 | 1080 | 34 | 0 | 50 | 25.5 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 130 | 0 | 220 | 305 | 220 | 44 | 0 | 198 | 0 | 68 | 31 | 122 | 73 | 10 | 17 | 70 | 52.2 | 0 | 22 | 310 | 399 | 397 | 40 | 30 | 140 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 0 | 35 | 84 | 0 | 158 | 0 | 0 | 0 | 24 | 9477.48 | 724 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1225 | 0 | 0 | 0 | 1312.59 | 0 | 0 | 0 | 113 | 50 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 110 | 0 | 0 | 850 | 300 | 100 | 5879.79 | 15357.27 | 104.02
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 36 | 116 | 108 | 225 | 30 | 55 | 108 | 0 | 0 | 390 | 0 | 55 | 289 | 0 | 0 | 0 | 143.42 | 10 | 18 | 0 | 380 | 107 | 213 | 19 | 0 | 0 | 67 | 14 | 54.36 | 12 | 38 | 0 | 221 | 68 | 24 | 1080 | 34 | 0 | 50 | 25.5 | 68 | 219 | 0 | 0 | 0 | 1224 | 0 | 137 | 0 | 295 | 286 | 220 | 44 | 0 | 188 | 0 | 68 | 31 | 122 | 73 | 10 | 17 | 70 | 52.2 | 0 | 22 | 315 | 400 | 398 | 40 | 30 | 136 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 0 | 35 | 88 | 0 | 163 | 0 | 0 | 0 | 24 | 9411.48 | 723 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1227 | 0 | 0 | 0 | 1403.04 | 0 | 0 | 0 | 113 | 50 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 115 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 110 | 0 | 0 | 850 | 300 | 100 | 5970.24 | 15381.72 | 104.13
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 35 | 54 | 100 | 106 | 225 | 27 | 55 | 103 | 0 | 0 | 420 | 0 | 35 | 303 | 0 | 0 | 0 | 143.42 | 10 | 18 | 0 | 435 | 92 | 89 | 18 | 0 | 0 | 67 | 14 | 54.36 | 12 | 38 | 0 | 221 | 68 | 28 | 1080 | 16 | 0 | 50 | 25.5 | 68 | 221 | 0 | 0 | 0 | 1160 | 0 | 150 | 0 | 330 | 305 | 220 | 44 | 0 | 198 | 0 | 66 | 31 | 122 | 74 | 10 | 17 | 70 | 52.2 | 0 | 22 | 315 | 400 | 398 | 40 | 30 | 138 | 0 | 16 | 0 | 82 | 0 | 136 | 0 | 0 | 35 | 87 | 0 | 135 | 0 | 0 | 0 | 24 | 9301.48 | 724 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1208 | 0 | 0 | 0 | 1409.35 | 0 | 0 | 0 | 113 | 50 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 115 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 276 | 110 | 0 | 0 | 850 | 300 | 100 | 5926.55 | 15228.03 | 103.99
Total KWH | 0 | 623040 | 302400 | 0 | 0 | 0 | 0 | 0 | 8838000 | 0 | 0 | 784800 | 1155600 | 2802672 | 2299200 | 4378113 | 980311 | 935642 | 2255040 | 0 | 0 | 9754742 | 0 | 930432 | 7360421 | 0 | 0 | 206852 | 3038400 | 225000 | 430920 | 0 | 11575909.09 | 2320909 | 2205491 | 630720 | 0 | 0 | 904204 | 647500 | 918310 | 240000 | 659520 | 23156 | 5368596 | 2025673 | 364800 | 25760000 | 595491 | 0 | 1041600 | 431020.8 | 2075854 | 4914371 | 0 | 0 | 0 | 18370907 | 104085 | 3241745 | 0 | 5510000 | 7903700 | 6388000 | 1046316 | 0 | 4917000 | 0 | 1224000 | 784335 | 2547840 | 1237320 | 237700 | 1177620 | 1403520 | 1005355 | 428009 | 525088 | 7054000 | 9421200 | 9606000 | 953000 | 720000 | 3594272.73 | 76050 | 391632 | 0 | 1824000 | 0 | 3117000 | 0 | 123120 | 690480 | 1390800 | 142282 | 2301600 | 0 | 14050 | 333130 | 558480 | 210368346.62 | 17067636 | 0 | 146880 | 350720 | 0 | 0 | 0 | 0 | 0 | 635184 | 529200 | 29243640 | 0 | 0 | 0 | 23503636 | 0 | 872869 | 0 | 1884864 | 1330464 | 0 | 686672 | 293706 | 1073947 | 322064 | 654420 | 261480 | 0 | 408848 | 0 | 0 | 0 | 0 | 0 | 0 | 6528654 | 0 | 32820 | 0 | 0 | 2074905 | 214686 | 1189017 | 0 | 430133 | 0 | 42581.76 | 1120320 | 3444 | 1227456 | 6786000 | 2607000 | 0 | 0 | 20472727 | 7248000 | 1112400 | 130356373.76 | 340724720.38

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13942.68 | MW | 12:00 Hr. | Energy Generated |  |  | 340.7247 |  | MKWHr.
| Day Peak Demand |  |  | 13942.68 | MW | 12:00 Hr. | Energy Unserverd |  |  | 9.949 |  | MKWHr.
| Evening Peak Generation |  |  | 15405.11 | MW | 19:00 Hr. | Energy Demand |  |  | 350.6737 |  | MKWHr.
| Evening Peak Demand |  |  | 15696.11 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.9 |  | °C
| Minimum Generation of the Day |  |  | 12790.43 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 804.19 |  | MMCFD
| Maximum Generation of the Day |  |  | 15405.11 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 8.5735 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.185 | 0 | 20.4856 | 0 | 0 | 0.20685 | 0 | 0 | 58.8775 | Gas | 116.1911 | Gas | 396723684.0869
| Chattogram Zone |  |  | 5.2792 | 44.1309 | 14.6963 | 0 | 5.3686 | 0.12724 | 0 | 0 | 69.6022 | Coal | 107.8813 | Coal | 834925216.84
| Cumilla Zone |  |  | 26.7871 | 0 | 10.959 | 0 | 0 | 0.42801 | 1.4035 | 0 | 39.5775 | HFO | 64.2228 | HFO | 1323093944.678
| Mymensingh Zone |  |  | 0 | 0 | 4.9414 | 0 | 0 | 0.48946 | 0 | 0 | 5.4308 | HSD | 0.43013 | HSD | 15592321.25
| Sylhet Zone |  |  | 36.8042 | 0 | 0 | 0 | 0 | 0.07605 | 0 | 0 | 36.8803 | Hydro | 5.3686 | Hydro | 536859.6
| Khulna Zone |  |  | 0 | 29.2436 | 1.1328 | 0 | 0 | 0.5292 | 17.0676 | 0 | 47.9733 | Solar | 4.656 | Solar | 74680532.5256
| Barishal Zone |  |  | 2.607 | 34.5067 | 2.3399 | 0 | 0 | 0.003444 | 0 | 0 | 39.457 | Import | 41.9748 | Import | 275656628.12
| Rajshahi Zone |  |  | 6.5287 | 0 | 6.404 | 0 | 0 | 1.4182 | 23.5036 | 0 | 37.8544 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 0 | 3.2639 | 0.43013 | 0 | 1.3776 | 0 | 0 | 5.0716
| Total |  |  | 116.1911 | 107.8813 | 64.2228 | 0.43013 | 5.3686 | 4.656 | 41.9748 | 0 | 340.7247
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 396723684.0869 |  | Hydro | 536859.6
|  |  |  | Coal | 834925216.84 |  | Solar | 74680532.5256
|  |  |  | HFO | 1323093944.678 |  | Import | 275656628.12
|  |  |  | HSD | 15592321.25 |  | Wind | 0
[5 empty] | Total: | 292,12,09,187 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 10036.36 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.0676 | Peak Hr Flow | 599.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 25100272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.5036 | Peak Hr Flow | 1101.43 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 785 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4035 | Peak Hr Flow | 68.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1602 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.9748 | Peak Hr Flow | 1768.43 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 12 |  | 5379
|  |  |  | Chattogram |  | 0 |  | 1512
|  |  |  | Cumilla |  | 0 |  | 1516
|  |  |  | Mymensingh |  | 133 |  | 1125
|  |  |  | Sylhet |  | 133 |  | 733
|  |  |  | Khulna |  | 0 |  | 1789
|  |  |  | Barishal |  | 0 |  | 472
|  |  |  | Rajshahi |  | 0 |  | 1528
|  |  |  | Rangpur |  | 0 |  | 898
|  |  |  | Total |  | 278 |  | 14952
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 218.5
|  |  |  | Total Unavailable Capacity |  |  |  | 518.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:46 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to 400KV Shamvuganj Bay
Extension works.
|  | 09:52 | Kaliakoir-Tongi 230kV Ckt-2 is restored.
| 09:52 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Shomvuganj 400/132kV end Due to
132kV Shambhuganj-Kishoreganj Ckt-2 Re-Conductoring work. and from Kishoreganj 132/33kV
end Due to Line Re conductoring
| 10:13 |  | Manirampur-Satkhira 132kV Ckt-2 Project Work S/D from Monirampur 132/33kV end Due to For
project maintenance work and from Satkhira 132/33kVend.
| 10:13 |  | Manirampur-Satkhira 132kV Ckt-2 Project Work S/D from Monirampur 132/33kV end Due to For
project maintenance work and from Satkhira 132/33kVend.
| 10:27 | 18:00 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to
As per order of ALDC
| 10:30 | 18:00 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to
As per order of ALDC
| 10:41 | 18:01 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Project Work S/D from BIPTC end Due to For cattle
guard related work on Kushtia-Meherpur 132kV transmission line.
| 10:42 | 18:01 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Project Work S/D from BIPTC end Due to For cattle
guard related work on Kushtia-Meherpur 132kV transmission line.
| 12:00 |  | Day Peak Generation: 13943 MW.
|  | 12:20 | Patiya 132/33kV S/S TRAFO-02 HT is restored.
|  | 12:32 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT is restored.
|  | 12:34 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT is restored.
|  | 12:34 | Patiya 132/33kV S/S TRAFO-02 LT is restored.
| 12:38 | 13:20 | Dohazari-Sikalbaha 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Distance | [7 empty] | 64.0MW load
|  |  | Relay, Lockout relay. relays Due to None | [7 empty] | interrup. Dohazari
132/33kV end
| 12:38 | 12:47 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Lockout Relay. relays Due | [7 empty] | 64.0MW load
|  |  | to Due to Patiya-Dohazari ckt-01 trip. | [7 empty] | interrup.
| 14:45 | 20:10 | Bagerhat-Labanchura 132 kV Ckt-2 Tripped from Bagerhat 132/33kV end showing Distance Trip
A,B,C Zone1 relays Due to Unknown
| 15:07 | 17:24 | Patiya 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Substation end Maintenance | [7 empty] | 9.0MW load
interrup.
| 15:07 | 17:26 | Patiya 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Substation end Maintenance | [7 empty] | 9.0MW load
interrup.
| 15:45 | 17:04 | Goalpara-Labanchura 132kV Ckt-2 Tripped from Goalpara 132/33kV end showing distance
relay Z-1 relays Due to Trip
| 16:25 | 23:51 | Kabirpur 132/33kV S/S XFR, T-I HT Tripped showing Micom relays. | [7 empty] | 50.0MW load
interrup.
| 16:25 | 23:53 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micom relays. | [7 empty] | 50.0MW load
interrup.
| 16:38 |  | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 KV feeder Load side
Y-phase PT Blast
| 16:38 |  | Daganbhuiyan 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 KV feeder Load side
Y-phase PT Blast.
| 21:17 |  | At Bhola Notun Biddyut P/S , 230 KV Bus-bar S/D.
| 02:45 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
| 03:02 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 06:00 |  | Minimum Generation: 12681 MW.
| 06:41 |  | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| 07:14 | 07:49 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Ph Y, Z1, Dist. Send. relays
Due to Unknown.
| 07:19 |  | Satkhira 132/33kV S/S Transformer-3(T-3) LT Scheduled S/D Due to Due to PBS work.
| 07:19 |  | Satkhira 132/33kV S/S Transformer-3(T-3) HT Scheduled S/D Due to Due to PBS work.
| 07:19 |  | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D Due to Due to PBS work. | [7 empty] | 45.0MW load
interrup.
| 07:19 |  | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Due to PBS work.
| 07:24 |  | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T LT Scheduled S/D Due to Oil refill
| 07:27 |  | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T HT Scheduled S/D Due to Oil refill
| 07:35 |  | Ishurdi 230/132kV S/S 230 kV Bus 2 Project Work S/D Due to To connect the Baghabari-2
bus DS to 230KV bus-2
| 07:38 |  | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance work 2026
| 07:39 |  | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance work 2026
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8838000 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 980311 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 285 | 7360421 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Fuel Shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 784800 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 2299200 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935642 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 930432 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 225000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 430920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 302400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4378113 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2802672 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 623040 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Fuel Shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2255040 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 206852 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 1155600 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 380 | 11575909.09 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 430 | 9754742 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3038400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2670.42 | 58877494.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 431020.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104085 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1041600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5368596 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4914371 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2075854 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 51 | 647500 | plant availability zero
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 904204 | Fuel Shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 240000 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 364800 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 46 | 630720 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23156 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 213 | 2205491 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 918310 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 84 | 2025673 | Slow ramp rate
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 659520 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 2320909 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 90 | 595491 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 18370907 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 25760000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3735.86 | 69602207.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 217 | 4917000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 271 | 7903700 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 6388000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5510000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1046316 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 3241745 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 525088 | Plant availability less
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 784335 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 121 | 2547840 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 68 | 1403520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1005355 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 237700 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1177620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 71 | 1237320 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 107 | 1224000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 428009 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1701.2 | 39577548
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 142282 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 2301600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 1390800 | Grid trip
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 333130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 558480 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 690480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 35 | 5430822
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 76050 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 953000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720000 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3594272.73 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 137 | 3117000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1824000 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 123120 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 391632 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7054000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 398 | 9606000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9421200 | -
Sylhet Area Total |  |  |  |  | 2325 | 1554 | 36880274.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 599 | 17067636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 18 | 146880 | Machine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 14 | 350720 | Machine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel Shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 635184 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 529200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1204 | 29243640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1920 | 47973260
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 850 | 20472727 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 1227456 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 105 | 2607000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7248000 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1112400 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6786000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3444 | -
Barishal Area Total |  |  |  |  | 3326.69 | 1710 | 39457027
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 322064 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 44 | 872869 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 293706 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 270 | 6528654 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 261480 | Fuel Shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1073947 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 686672 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1330464 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1884864 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 32820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1101.43 | 23503636 | Plant availability less
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 408848 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 654420 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1850.63 | 37854444
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 430133 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1189017 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42581.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2074905 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 214686 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1120320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 5071642.76
Eastern Grid Total |  |  |  |  | 16961.086 | 9696.48 | 210368346.62
Western Grid Total |  |  |  |  | 11731.125 | 5708.63 | 130356373.76
National Grid Total |  |  |  |  | 28692.211 | 15405.11 | 340724720.38
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9987.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4687.2 | MW
i) Dhaka area |  |  | 5367.23 |  | MW | i) Khulna area |  |  |  | 1789 | MW
ii) Chattogram area |  |  | 1511.6 |  | MW | ii) Barishal area |  |  |  | 471.8 | MW
iii) Cumilla area |  |  | 1516.46 |  | MW | iii) Rajshahi area |  |  |  | 1528.4 | MW
iv) Mymensingh area |  |  | 992 |  | MW | iv) Rangpur area |  |  |  | 898 | MW
v) Sylhet area |  |  | 600 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14674.49 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 17:00 | 72 | Hatirjheel | 61 | 16:00 | 143 | PHP | 10 | 00:00
2 | AKSML | 128.5 | 10:00 | 73 | Ishurdi | 78 | 18:30 | 144 | Pabna | 95 | 00:00
3 | Aftabnagar | 46 | 00:00 | 74 | Jaldhaka | 70 | 18:30 | 145 | Palashbari | 130 | 18:30
4 | Agargaon | 123 | 00:00 | 75 | Jamalpur | 128 | 18:00 | 146 | Panchagarh | 57 | 18:00
5 | Agrabad | 62 | 12:00 | 76 | Jashore | 117 | 13:00 | 147 | Patiya | 34.6 | 18:00
6 | Amnura | 42 | 22:00 | 77 | Jhenaidah | 100 | 18:30 | 148 | Patnitala | 32 | 00:00
7 | Araihazar | 103 | 23:00 | 78 | Joydebpur | 140 | 18:00 | 149 | Patuakhali | 71 | 23:00
8 | Ashuganj | 0.59 | 23:00 | 79 | Joypurhat | 58 | 21:00 | 150 | Payra | 34 | 21:00
9 | Ashuganj-230 | 105 | 01:00 | 80 | Juldah | 18 | 07:00 | 151 | Postogola | 66 | 00:00
10 | BSRM | 186 | 19:30 | 81 | KSRM | 30 | 04:00 | 152 | Pubail | 42 | 07:00
11 | Bagerhat | 87 | 21:00 | 82 | Kabirpur | 232 | 12:00 | 153 | Purbachal | 32 | 00:00
12 | Bajitpur | 93 | 18:00 | 83 | Kachua | 102 | 21:00 | 154 | Purbasadipur | 115 | 12:00
13 | Bakerganj | 14.6 | 21:00 | 84 | Kaliganj | 43 | 18:30 | 155 | Rahanpur | 37 | 22:00
14 | Bakulia | 93 | 13:00 | 85 | Kallyanpur | 114 | 23:00 | 156 | Rahim | 44 | 00:00
15 | Banani | 46 | 13:00 | 86 | Kalurghat | 33 | 00:00 | 157 | Rajbari | 86 | 18:00
16 | Bangabhaban | 4 | 10:00 | 87 | Kamrangirchar | 92 | 01:00 | 158 | Rajendrapur | 114 | 20:00
17 | Barapukuria | 53 | 18:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 102 | 13:00
18 | Barguna | 22 | 21:00 | 89 | Kasba | 39 | 18:00 | 160 | Rajshahi-230 | 96 | 13:00
19 | Barishal | 100 | 13:00 | 90 | Kazla | 119 | 00:00 | 161 | Ramganj | 120 | 18:00
20 | Barishal-230 | 100 | 18:00 | 91 | Keranigonj | 78 | 02:00 | 162 | Rampur | 45 | 23:00
21 | Baroaulia | 42 | 07:00 | 92 | Khagrachori | 34 | 18:30 | 163 | Rangamati | 20 | 13:00
22 | Baroirhat | 66 | 18:00 | 93 | Khulna | 68 | 12:00 | 164 | Rangpur | 116 | 18:30
23 | Bashundhara | 201 | 13:00 | 94 | Khulshi | 182 | 19:00 | 165 | Ruppur | 4.2 | 10:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 142 | 18:00 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 72 | 20:00 | 96 | Kodda | 290 | 12:00 | 167 | Saidpur | 80 | 18:30
26 | Benapole | 64 | 18:30 | 97 | Kulaura | 49 | 13:00 | 168 | Santhia | 34 | 18:00
27 | Bhaluka | 149 | 18:30 | 98 | Kurigram | 64 | 18:00 | 169 | Satkhira | 133 | 22:00
28 | Bhandaria | 58 | 06:00 | 99 | Kushtia | 130 | 13:00 | 170 | Satmasjid | 107 | 00:00
29 | Bhangura | 38 | 18:00 | 100 | Laksam | 37 | 22:00 | 171 | Savar | 186 | 12:00
30 | Bheramara(GK) | 68 | 18:30 | 101 | Lakshmipur | 54 | 22:00 | 172 | SevenRings | 12.3 | 12:00
31 | Bhulta | 219 | 06:00 | 102 | Lalbag | 73 | 00:00 | 173 | ShahCement | 32 | 00:00
32 | Bog-Sherpur | 70 | 18:30 | 103 | Lalmonirhat | 58 | 18:00 | 174 | Shahjadpur | 73 | 18:00
33 | Bogura | 192 | 19:00 | 104 | MI_Cement | 18.6 | 17:00 | 175 | Shahjibazar | 125 | 05:00
34 | Borhanuddin | 78 | 22:00 | 105 | Madanganj | 42 | 12:00 | 176 | Shahmirpur | 54 | 18:00
35 | Brahmanbaria | 145 | 19:30 | 106 | Madaripur | 115 | 21:00 | 177 | Shariatpur | 107 | 22:00
36 | Cantonment | 126 | 12:00 | 107 | Madartek | 93 | 00:00 | 178 | Sherpur | 150 | 18:00
37 | Chandina | 26 | 12:00 | 108 | Madunaghat | 53 | 18:00 | 179 | Shikalbaha | 29.5 | 14:00
38 | Chandpur | 89 | 21:00 | 109 | Magura | 69 | 18:30 | 180 | Shitalakhya | 65.9 | 00:00
39 | Chandraghona | 33 | 18:30 | 110 | Mahasthangarh | 70 | 18:00 | 181 | Sholosohor | 46 | 12:00
40 | Chapai | 74 | 18:30 | 111 | Maijdee | 43 | 00:00 | 182 | Shomvuganj | 48 | 08:00
41 | Charfasson | 31 | 21:00 | 112 | Manikganj | 139 | 19:00 | 183 | Shyampur | 146 | 12:00
42 | Charsaidpur | 41 | 12:00 | 113 | Maniknagar | 86 | 00:00 | 184 | Siddhirganj | 116 | 01:00
43 | Chauddagram | 77 | 22:00 | 114 | Matarbari | 56 | 19:30 | 185 | Sirajganj | 106 | 18:30
44 | Chhatak | 34 | 13:00 | 115 | Matuail | 78 | 00:00 | 186 | Sitakunda | 34 | 18:00
45 | Chowmuhani | 162 | 22:00 | 116 | Metrorail_Motijheel | 18 | 17:00 | 187 | Sonargaon | 132 | 00:00
46 | Chuadanga | 116 | 18:00 | 117 | Metrorail_Uttara | 14 | 19:00 | 188 | Sreemongol | 77 | 22:00
47 | Coxsbazar | 141 | 20:00 | 118 | Millgate | 97 | 00:00 | 189 | Sreepur | 122 | 20:00
48 | Cumilla(N) | 155 | 19:00 | 119 | Mirpur | 151 | 00:00 | 190 | Srinagar | 51.77 | 21:00
49 | Cumilla(S) | 148 | 00:00 | 120 | Mirsorai | 32 | 10:00 | 191 | Sunamganj | 57 | 14:00
50 | Daganbhuiyan | 34 | 01:00 | 121 | Mirzapur | 52 | 07:00 | 192 | Sylhet | 110 | 19:00
51 | Daudkandi | 128 | 01:00 | 122 | Mithapukur | 70 | 18:30 | 193 | Sylhet_(South) | 75 | 00:00
52 | DhakaUniversity | 48 | 00:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 100 | 18:00 | 124 | Mogbazar | 69 | 13:00 | 195 | Tangail | 180 | 20:00
54 | Dhanmondi | 97.7 | 12:00 | 125 | Mongla | 37 | 00:00 | 196 | Taraganj | 29 | 18:00
55 | Dohazari | 118 | 19:00 | 126 | Monirampur | 24 | 22:00 | 197 | Tasnim | 45 | 17:00
56 | Faridpur | 173 | 21:00 | 127 | Motijheel | 45 | 00:00 | 198 | Thakurgaon | 94 | 18:30
57 | Fatullah | 110 | 00:00 | 128 | Muktagacha | 42 | 13:00 | 199 | Tongi | 142 | 10:00
58 | Fenchuganj | 40 | 23:00 | 129 | Munshiganj | 115 | 23:00 | 200 | Ullahpara | 38 | 18:30
59 | Feni | 115 | 19:00 | 130 | Muradnagar | 58 | 19:30 | 201 | Ullon | 38 | 00:00
60 | GPH | 2 | 11:00 | 131 | Mymensingh | 162 | 19:00 | 202 | Uttara | 92 | 12:00
61 | Ghatail | 98 | 18:00 | 132 | Nabinagar | 108 | 00:00 | 203 | UttaraNew | 59 | 00:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 113 | 00:00 | 204 | Zigatola | 76 | 00:00
63 | Ghorashal-230 | 98 | 05:00 | 134 | Narail | 61 | 18:30
64 | Goalpara | 42 | 13:00 | 135 | Narinda | 55.5 | 13:00
65 | Gollamari | 102 | 13:00 | 136 | Narshingdi | 189 | 21:00
66 | Gopalganj | 115 | 21:00 | 137 | Natore | 149 | 17:00
67 | Gulshan | 90 | 12:00 | 138 | Nawabganj | 51.6 | 22:00
68 | Halishahar | 75.5 | 18:30 | 139 | Netrakona | 142 | 20:00
69 | HaripurSBU | 125 | 05:00 | 140 | New | 76.5 | 00:00
70 | Hasnabad | 105 | 01:00 | 141 | Niamatpur | 83 | 18:30
71 | Hathazari | 95 | 19:00 | 142 | Noapara | 39 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15173.63 | 1733 |  | 16984.63
1:00 | 14361.73 | 1789 |  | 16231.73
2:00 | 14220.45 | 1714 |  | 16011.45
3:00 | 13989.49 | 1644 |  | 15707.49
4:00 | 13925.45 | 1547 |  | 15542.45
5:00 | 13751.79 | 331 |  | 14097.79
6:00 | 13243.43 | 0 |  | 13243.43
7:00 | 13142.48 | 0 |  | 13142.48
8:00 | 13222.39 | 0 |  | 13222.39
9:00 | 12790.43 | 0 |  | 12790.43
10:00 | 12926.57 | 0 |  | 12926.57
11:00 | 13296.42 | 0 |  | 13296.42
12:00 | 13942.68 | 0 |  | 13942.68
13:00 | 14495.21 | 84 |  | 14583.21
14:00 | 13831.39 | 57 |  | 13891.39
15:00 | 13907.76 | 54 |  | 13963.76
16:00 | 13652.81 | 53 |  | 13707.81
17:00 | 13227.48 | 51 |  | 13280.48
18:00 | 14752.56 | 169 |  | 14929.56
19:00 | 15405.11 | 278 |  | 15696.11
19:30 | 15113.55 | 215 |  | 15338.55
20:00 | 15193.97 | 136 |  | 15335.97
21:00 | 15357.27 | 104 |  | 15466.27
22:00 | 15381.72 | 108 |  | 15494.72
23:00 | 15228.03 | 97 |  | 15329.03
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9407.82 | 5765.81 | 15173.63 | DAILY GENERATION CURVE
00:30 | 9280.32 | 5487.36 | 14767.68
01:00 | 9152.82 | 5208.91 | 14361.73 | 16-10-2026
01:30 | 9102.82 | 5188.27 | 14291.09
02:00 | 9052.82 | 5167.63 | 14220.45
02:30 | 9033.32 | 5071.65 | 14104.97
03:00 | 9013.82 | 4975.67 | 13989.49
03:30 | 8980.97 | 4976.5 | 13957.47
04:00 | 8948.12 | 4977.33 | 13925.45
04:30 | 8889.12 | 4949.5 | 13838.62
05:00 | 8830.12 | 4921.67 | 13751.79
05:30 | 8591.465 | 4906.145 | 13497.61
06:00 | 8352.81 | 4890.62 | 13243.43
06:30 | 8348.76 | 4844.195 | 13192.955
07:00 | 8344.71 | 4797.77 | 13142.48
07:30 | 8305.01 | 4877.425 | 13182.435
08:00 | 8265.31 | 4957.08 | 13222.39
08:30 | 7972.345 | 5034.065 | 13006.41
09:00 | 7679.38 | 5111.05 | 12790.43
09:30 | 7668.775 | 5189.725 | 12858.5
10:00 | 7658.17 | 5268.4 | 12926.57
10:30 | 7769.955 | 5341.54 | 13111.495
11:00 | 7881.74 | 5414.68 | 13296.42
11:30 | 8076.465 | 5543.085 | 13619.55
12:00 | 8271.19 | 5671.49 | 13942.68
12:30 | 8482.235 | 5736.71 | 14218.945
13:00 | 8693.28 | 5801.93 | 14495.21
13:30 | 8468.9 | 5694.4 | 14163.3
14:00 | 8244.52 | 5586.87 | 13831.39
14:30 | 8259.905 | 5609.67 | 13869.575
15:00 | 8275.29 | 5632.47 | 13907.76
15:30 | 8214.11 | 5566.175 | 13780.285
16:00 | 8152.93 | 5499.88 | 13652.81
16:30 | 8091.185 | 5348.96 | 13440.145
17:00 | 8029.44 | 5198.04 | 13227.48
17:30 | 8676.46 | 5313.56 | 13990.02
18:00 | 9323.48 | 5429.08 | 14752.56
18:30 | 9509.98 | 5568.855 | 15078.835
19:00 | 9696.48 | 5708.63 | 15405.11
19:30 | 9485.48 | 5628.07 | 15113.55
20:00 | 9492.48 | 5701.49 | 15193.97
20:30 | 9484.98 | 5790.64 | 15275.62 |  | Executive Engineer
21:00 | 9477.48 | 5879.79 | 15357.27 |  | Network Operation Division
21:30 | 9444.48 | 5925.015 | 15369.495
22:00 | 9411.48 | 5970.24 | 15381.72
22:30 | 9356.48 | 5948.395 | 15304.875
23:00 | 9301.48 | 5926.55 | 15228.03

## En-Curve
QF-LDC-12
Date | 16-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3372 | 1529.2 | 717 | 0 | 68 | 749.41 | 221 | 4759.2 | 0 | 725.42 | 2867.4 | 165 | 0 | 0 | 1733 | DAILY ENERGY CURVE
00:30 | 3398.5 | 1526.2 | 714.5 | 0 | 65 | 751.46 | 221 | 4566.7 | 0 | 638.42 | 2720.9 | 165 | 0 | 0 | 1761 | 16-10-2026
01:00 | 3425 | 1523.2 | 712 | 0 | 62 | 753.51 | 221 | 4374.2 | 0 | 551.42 | 2574.4 | 165 | 0 | 0 | 1789
01:30 | 3378 | 1527.7 | 708.5 | 0 | 63 | 749.37 | 221 | 4359.2 | 0 | 551.92 | 2567.4 | 165 | 0 | 0 | 1751.5 | Energy Generated | 340.7247 |  | MKWHr
02:00 | 3331 | 1532.2 | 705 | 0 | 64 | 745.23 | 221 | 4344.2 | 0 | 552.42 | 2560.4 | 165 | 0 | 0 | 1714 | Energy not Served | 9.949 |  | MKWHr
02:30 | 3341.5 | 1539.7 | 705 | 0 | 63 | 734.75 | 220 | 4344.2 | 0 | 550.42 | 2518.9 | 87.5 | 0 | 0 | 1679 | Total Energy Requirement | 350.6737 |  | MKWHr
03:00 | 3352 | 1547.2 | 705 | 0 | 62 | 724.27 | 219 | 4344.2 | 0 | 548.42 | 2477.4 | 10 | 0 | 0 | 1644
03:30 | 3352 | 1549.85 | 705 | 0 | 61 | 723.6 | 218.5 | 4344.2 | 0 | 548.42 | 2449.9 | 5 | 0 | 0 | 1595.5
04:00 | 3352 | 1552.5 | 705 | 0 | 60 | 722.93 | 218 | 4344.2 | 0 | 548.42 | 2422.4 | 0 | 0 | 0 | 1547
04:30 | 3358.5 | 1514 | 705 | 0 | 60 | 725.1 | 217.5 | 4344.2 | 0 | 548.42 | 2365.9 | 0 | 0 | 0 | 939
05:00 | 3365 | 1475.5 | 705 | 0 | 60 | 727.27 | 217 | 4344.2 | 0 | 548.42 | 2309.4 | 0 | 0 | 0 | 331
05:30 | 3329 | 1458.5 | 704.5 | 0 | 57 | 730.245 | 217 | 4344.2 | 0.055 | 486.21 | 2170.9 | 0 | 0 | 0 | 165.5
06:00 | 3293 | 1441.5 | 704 | 0 | 54 | 733.22 | 217 | 4344.2 | 0.11 | 424 | 2032.4 | 0 | 0 | 0 | 0
06:30 | 3319.5 | 1489.5 | 633.5 | 0 | 53 | 732.9 | 217.5 | 4346.7 | 50.955 | 397.5 | 1951.9 | 0 | 0 | 0 | 0
07:00 | 3346 | 1537.5 | 563 | 0 | 52 | 732.58 | 218 | 4349.2 | 101.8 | 371 | 1871.4 | 0 | 0 | 0 | 0
07:30 | 3331.5 | 1499 | 562.5 | 0 | 52 | 728.965 | 218.5 | 4349.2 | 207.87 | 376.5 | 1856.4 | 0 | 0 | 0 | 0
08:00 | 3317 | 1460.5 | 562 | 0 | 52 | 725.35 | 219 | 4349.2 | 313.94 | 382 | 1841.4 | 0 | 0 | 0 | 0
08:30 | 3330.5 | 1457.5 | 632.5 | 0 | 48 | 734.305 | 219 | 4312.1 | 394.305 | 347.5 | 1530.7 | 0 | 0 | 0 | 0
09:00 | 3344 | 1454.5 | 703 | 0 | 44 | 743.26 | 219 | 4275 | 474.67 | 313 | 1220 | 0 | 0 | 0 | 0
09:30 | 3340.5 | 1458.5 | 703 | 0 | 45 | 793.32 | 219.5 | 4264 | 542.68 | 318.5 | 1173.5 | 0 | 0 | 0 | 0
10:00 | 3337 | 1462.5 | 703 | 0 | 46 | 843.38 | 220 | 4253 | 610.69 | 324 | 1127 | 0 | 0 | 0 | 0
10:30 | 3339 | 1508 | 703.5 | 0 | 47 | 900.27 | 220 | 4274 | 639.225 | 305.5 | 1175 | 0 | 0 | 0 | 0
11:00 | 3341 | 1553.5 | 704 | 0 | 48 | 957.16 | 220 | 4295 | 667.76 | 287 | 1223 | 0 | 0 | 0 | 0
11:30 | 3321.5 | 1510.25 | 704 | 0 | 50 | 1037.215 | 220 | 4307.5 | 645.835 | 346.75 | 1476.5 | 0 | 0 | 0 | 0
12:00 | 3302 | 1467 | 704 | 0 | 52 | 1117.27 | 220 | 4320 | 623.91 | 406.5 | 1730 | 0 | 0 | 0 | 0
12:30 | 3314 | 1542 | 707 | 0 | 52 | 1120.425 | 220 | 4424.5 | 645.87 | 384.9 | 1808.25 | 0 | 0 | 0 | 42
13:00 | 3326 | 1617 | 710 | 0 | 52 | 1123.58 | 220 | 4529 | 667.83 | 363.3 | 1886.5 | 0 | 0 | 0 | 84
13:30 | 3318 | 1602 | 710 | 0 | 52 | 1119.3 | 220 | 4523.5 | 602.45 | 347.8 | 1668.25 | 0 | 0 | 0 | 70.5
14:00 | 3310 | 1587 | 710 | 0 | 52 | 1115.02 | 220 | 4518 | 537.07 | 332.3 | 1450 | 0 | 0 | 0 | 57
14:30 | 3307.5 | 1596.5 | 710.5 | 0 | 52 | 1118 | 220 | 4464.5 | 457.775 | 321.8 | 1621 | 0 | 0 | 0 | 55.5
15:00 | 3305 | 1606 | 711 | 0 | 52 | 1120.98 | 220 | 4411 | 378.48 | 311.3 | 1792 | 0 | 0 | 0 | 54
15:30 | 3264 | 1552 | 710.5 | 0 | 52 | 1119.79 | 219.5 | 4375 | 288.845 | 327.3 | 1871.35 | 0 | 0 | 0 | 53.5
16:00 | 3223 | 1498 | 710 | 0 | 52 | 1118.6 | 219 | 4339 | 199.21 | 343.3 | 1950.7 | 0 | 0 | 0 | 53
16:30 | 3108.5 | 1420.5 | 679.5 | 0 | 56 | 1078.16 | 218.5 | 4269.5 | 117.705 | 368.3 | 2123.48 | 0 | 0 | 0 | 52
17:00 | 2994 | 1343 | 649 | 0 | 60 | 1037.72 | 218 | 4200 | 36.2 | 393.3 | 2296.26 | 0 | 0 | 0 | 51
17:30 | 3103 | 1442 | 620.5 | 0 | 65 | 1073.8 | 218 | 4321 | 18.1 | 518.36 | 2610.26 | 0 | 0 | 0 | 110
18:00 | 3212 | 1541 | 592 | 0 | 70 | 1109.88 | 218 | 4442 | 0 | 643.42 | 2924.26 | 0 | 0 | 0 | 169
18:30 | 3202 | 1505 | 595.5 | 0 | 69 | 1105.655 | 219 | 4703.5 | 0 | 724.42 | 2954.76 | 0 | 0 | 0 | 223.5
19:00 | 3192 | 1469 | 599 | 0 | 68 | 1101.43 | 220 | 4965 | 0 | 805.42 | 2985.26 | 0 | 0 | 0 | 278
19:30 | 3266 | 1635 | 676 | 0 | 70 | 1114.87 | 219 | 4983 | 0 | 672.42 | 2477.26 | 0 | 0 | 0 | 215
20:00 | 3228 | 1584 | 676 | 0 | 68 | 1190.29 | 220 | 4984 | 0 | 691.42 | 2552.26 | 0 | 0 | 0 | 136
20:30 | 3233.5 | 1526.5 | 700 | 0 | 69 | 1251.44 | 220 | 4985 | 0 | 677.42 | 2612.76 | 0 | 0 | 0 | 120
21:00 | 3239 | 1469 | 724 | 0 | 70 | 1312.59 | 220 | 4986 | 0 | 663.42 | 2673.26 | 0 | 0 | 0 | 104
21:30 | 3252.5 | 1447.5 | 723.5 | 0 | 70 | 1357.815 | 220.5 | 4987 | 0 | 637.42 | 2673.26 | 0 | 0 | 0 | 106
22:00 | 3266 | 1426 | 723 | 0 | 70 | 1403.04 | 221 | 4988 | 0 | 611.42 | 2673.26 | 0 | 0 | 0 | 108
22:30 | 3308.5 | 1471 | 723.5 | 0 | 70 | 1406.195 | 221 | 4931 | 0 | 610.42 | 2563.26 | 0 | 0 | 0 | 102.5
23:00 | 3351 | 1516 | 724 | 0 | 70 | 1409.35 | 221 | 4874 | 0 | 609.42 | 2453.26 | 0 | 0 | 0 | 97
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 16-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 60 | 18 | 158 | 120 | 904 | 430 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 48 | 11 | 110 | 94 | 800 | 370
2:00 | 45 | 7 | 134 | 92 | 802 | 334 |  | Import | 0
3:00 | 25 | 7 | 74 | 102 | 718 | 316
4:00 | 36 | 9 | 90 | 94 | 754 | 330 | Ishurdi-Ghorashal Ckt-2 | Export | 1639272.73
5:00 | 40 | 9 | 110 | 106 | 796 | 342
6:00 | 64 | 3 | 156 | 104 | 934 | 360 |  | Import | 10036.36
7:00 | 38 | 16 | 60 | 112 | 710 | 358
8:00 | 52 | 19 | 92 | 109 | 824 | 362 | Sirajganj-Sreepur Ckt-1 | Export | 1192000
9:00 | 107 | 25 | 200 | 98 | 1042 | 428
10:00 | 103 | 9 | 270 | 108 | 1220 | 444 |  | Import | 0
11:00 | 130 | 27 | 310 | 120 | 1162 | 448
12:00 | 121 | 14 | 340 | 116 | 1070 | 386 | Sirajganj-Sreepur Ckt-2 | Export | 1199000
13:00 | 108 | 6 | 308 | 140 | 944 | 374
14:00 | 110 | 8 | 316 | 116 | 992 | 396 |  | Import | 0
15:00 | 127 | 14 | 350 | 120 | 1084 | 382
16:00 | 118 | 11 | 322 | 96 | 1154 | 364 | Gopalganj-Aminbazar Ckt-1 | Export | 10520000
17:00 | 86 | -1 | 248 | 86 | 986 | 370
18:00 | 28 | -11 | 156 | 100 | 640 | 328 |  | Import | 0
18:30 | -16 | 5 | 86 | 140 | 486 | 356
19:00 | 7 | 3 | 150 | 146 | 628 | 380 | Gopalganj-Aminbazar Ckt-2 | Export | 10550000
19:30 | 14 | -6 | 144 | 140 | 628 | 378
20:00 | 20 | -9 | 150 | 112 | 672 | 372 |  | Import | 0
21:00 | 37 | -5 | 210 | 124 | 754 | 376
22:00 | 54 | -4 | 238 | 112 | 826 | 364 |  | Total Export | 25100272.73
23:00 | 60 | -2 | 250 | 108 | 826 | 376 |  | Total Import | 10036.36
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 03:00 | 378 | 12:00 | Madunaghat | 408 | 03:00 | 399 | 21:00
Amtali | 415 | 04:00 | 408 | 00:00 | Meghnaghat | 398 | 03:00 | 388 | 13:00
Ashuganj | 412 | 4:00 | 400 | 13:00 | Mirsorai | 409 | 03:00 | 397 | 19:30
Bhulta | 403 | 03:00 | 363 | 21:00 | Payra | 416 | 02:00 | 411 | 13:00
Bibiana | 390 | 02:00 | 384 | 14:00 | Rahanpur | 410 | 16:00 | 400 | 22:00
BIPTC | 405 | 08:00 | 394 | 13:00 | Rampal | 401 | 06:00 | 389 | 13:00
Bogura | 403 | 03:00 | 389 | 22:00
Gopalganj | 398 | 04:00 | 388 | 13:00
Kaliakoir | 384 | 03:00 | 370 | 11:00
Korerhat | 408 | 03:00 | 397 | 19:30
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 03:00 | 228 | 13:00 | Hasnabad | 233 | 03:00 | 226 | 11:00
AKSML | 241 | 08:00 | 232 | 19:30 | Hathazari | 240 | 17:00 | 233 | 23:00
Aminbazar | 238 | 06:00 | 229 | 12:00 | Ishurdi | 236 | 03:00 | 224 | 20:00
Ashuganj | 235 | 18:30 | 224 | 19:30 | Jhenaidah | 227 | 05:00 | 200 | 13:00
Ashuganj-400 | 235 | 18:30 | 224 | 19:30 | Kachua | 234 | 08:00 | 225 | 14:00
Baghabari | 234 | 02:00 | 225 | 20:00 | Kaliakoir | 239 | 03:00 | 230 | 11:00
Barapukuria | 237 | 00:00 | 223 | 13:00 | Keranigonj | 234 | 05:00 | 226 | 13:00
Barapukuria-230 | 237 | 00:00 | 223 | 13:00 | Khulna(S) | 229 | 10:00 | 213 | 18:00
Barapukuria(N) | 239 | 02:00 | 224 | 18:00 | Korerhat | 233 | 03:00 | 225 | 14:00
Barishal | 227 | 17:00 | 219 | 23:00 | Madunaghat | 243 | 03:00 | 237 | 20:00
Bheramara | 235 | 02:00 | 222 | 20:00 | Madunaghat-400 | 244 | 02:00 | 239 | 14:00
Bhulta | 230 | 03:00 | 222 | 00:00 | Maniknagar | 228 | 03:00 | 222 | 00:00
Bibiana | 224 | 01:00 | 220 | 12:00 | Meghnaghat | 236 | 05:00 | 228 | 14:00
BIPTC | 237 | 05:00 | 222 | 19:30 | Meghnaghat-400 | 231 | 04:00 | 225 | 13:00
Birulia | 237 | 04:00 | 228 | 13:00 | Mirsorai | 231 | 03:00 | 222 | 12:00
Bogura | 240 | 04:00 | 232 | 20:00 | Naogaon | 227 | 02:00 | 213 | 20:00
Bogura-400 | 239 | 02:00 | 231 | 18:00 | Purbasadipur | 237 | 01:00 | 221 | 18:00
Borhanuddin | 228 | 17:00 | 222 | 13:00 | Rajshahi | 233 | 01:00 | 221 | 18:00
BSRM | 233 | 02:00 | 225 | 19:30 | Rampal | 228 | 05:00 | 215 | 13:00
Charfasson | 227 | 17:00 | 220 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 233 | 02:00 | 225 | 22:00 | Rampura | 229 | 05:00 | 222 | 00:00
Cumilla(N) | 228 | 05:00 | 221 | 19:30 | Shikalbaha | 244 | 17:00 | 236 | 14:00
Faridpur | 225 | 17:00 | 218 | 21:00 | Shyampur | 231 | 02:00 | 225 | 00:00
Fenchuganj | 225 | 06:00 | 221 | 13:00 | Siddhirganj | 230 | 07:00 | 222 | 03:00
Feni | 231 | 02:00 | 222 | 21:00 | Sirajgonj | 238 | 02:00 | 232 | 13:00
Ghorashal | 235 | 04:00 | 222 | 00:00 | Sreepur | 228 | 04:00 | 219 | 13:00
Ghorashal-230 | 227 | 05:00 | 213 | 09:00 | Tongi | 260 | 18:00 | 216 | 07:00
Gopalganj | 225 | 04:00 | 219 | 13:00
GPH | 240 | 02:00 | 233 | 14:00
Haripur | 230 | 04:00 | 223 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 133 | 00:00 | Madanganj | 140 | 17:00 | 133 | 00:00
Agargaon | 137 | 03:00 | 132 | 11:00 | Madaripur | 132 | 17:00 | 128 | 13:00
Agrabad | 138 | 01:00 | 134 | 13:00 | Madartek | 137 | 06:00 | 131 | 15:00
AKS | 136 | 01:00 | 132 | 14:00 | Madunaghat | 140 | 02:00 | 137 | 14:00
Aminbazar | 139 | 04:00 | 131 | 13:00 | Magura | 134 | 02:00 | 119 | 13:00
Amnura | 134 | 00:00 | 128 | 20:00 | Mahasthangarh | 136 | 00:00 | 130 | 18:00
Araihazar | 129 | 17:00 | 124 | 19:30 | Maijdee | 131 | 01:00 | 125 | 21:00
Ashuganj | 136 | 04:00 | 130 | 19:30 | Manikganj | 134 | 02:00 | 129 | 11:00
Ashuganj-230 | 138 | 05:00 | 135 | 00:00 | Maniknagar | 143 | 08:00 | 134 | 20:00
Bagerhat | 128 | 10:00 | 119 | 20:00 | Matarbari | 129 | 03:00 | 109 | 18:00
Bajitpur | 130 | 06:00 | 123 | 00:00 | Matuail | 139.7 | 17:00 | 135 | 00:00
Bakerganj | 135 | 17:00 | 128 | 13:00 | Metrorail_Motijheel | 143 | 08:00 | 134 | 20:00
Bakulia | 138 | 05:00 | 133 | 14:00 | Metrorail_Uttara | 139 | 02:00 | 130 | 11:00
Banani | 137 | 04:00 | 131 | 13:00 | Millgate | 142 | 03:00 | 130 | 09:00
Bangabhaban | 142 | 04:00 | 134 | 20:00 | Mirpur | 136 | 03:00 | 130 | 11:00
Barapukuria | 139 | 00:00 | 128 | 13:00 | Mirzapur | 134 | 02:00 | 128 | 19:00
Barguna | 134 | 17:00 | 128 | 13:00 | Mithapukur | 136 | 00:00 | 126 | 18:00
Barishal | 133 | 17:00 | 126 | 13:00 | MI_Cement | 136 | 03:00 | 132 | 00:00
Barishal-230 | 132 | 07:00 | 127 | 14:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 138 | 07:00 | 134 | 14:00 | Mogbazar | 138 | 08:00 | 133 | 00:00
Baroirhat | 134 | 01:00 | 130 | 19:30 | Mongla | 126 | 08:00 | 119 | 18:00
Bashundhara | 140 | 03:00 | 130 | 09:00 | Monirampur | 127 | 10:00 | 113 | 13:00
BashundharaCement | 140 | 17:00 | 133 | 00:00 | Motijheel | 143 | 08:00 | 134 | 20:00
Beanibazar | 125 | 08:00 | 119 | 13:00 | Muktagacha | 131 | 13:00 | 116 | 19:00
Benapole | 133 | 04:00 | 113 | 18:00 | Munshiganj | 138 | 03:00 | 134 | 00:00
Bhaluka | 133 | 04:00 | 122 | 13:00 | Muradnagar | 128 | 08:00 | 120 | 21:00
Bhandaria | 130 | 17:00 | 120 | 05:00 | Mymensingh | 138 | 18:30 | 115 | 13:00
Bhangura | 135 | 02:00 | 130 | 18:00 | Nabinagar | 136 | 03:00 | 130 | 11:00
Bheramara | 138 | 02:00 | 130 | 13:00 | Naogaon | 136 | 00:00 | 128 | 20:00
Bheramara(GK) | 137 | 02:00 | 130 | 18:00 | Narail | 134 | 05:00 | 117 | 13:00
Bhulta | 128 | 07:00 | 120 | 00:00 | Narinda | 143 | 08:00 | 134 | 20:00
Bhulta-400 | 130 | 17:00 | 124 | 00:00 | Narshingdi | 132 | 18:00 | 123 | 00:00
Birulia | 138 | 17:00 | 132 | 01:00 | Natore | 136 | 04:00 | 129 | 13:00
Bog-Sherpur | 137 | 02:00 | 132 | 19:30 | Nawabganj | 137 | 03:00 | 132 | 13:00
Bogura | 139 | 00:00 | 132 | 21:00 | Netrakona | 124 | 03:00 | 112 | 19:00
Bogura-230 | 139 | 00:00 | 134 | 13:00 | New | 140 | 18:00 | 132 | 09:00
Brahmanbaria | 133 | 04:00 | 127 | 19:30 | Niamatpur | 134 | 03:00 | 130 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 137 | 03:00 | 132 | 11:00 | Noapara | 130 | 10:00 | 120 | 13:00
Chandina | 132 | 05:00 | 126 | 21:00 | Pabna | 136 | 05:00 | 129 | 19:30
Chandpur | 137 | 02:00 | 128 | 10:00 | Palashbari | 133 | 00:00 | 124 | 18:00
Chandraghona | 140 | 06:00 | 136 | 13:00 | Panchagarh | 142 | 02:00 | 131 | 10:00
Chapai | 133 | 00:00 | 130 | 13:00 | Patiya | 139 | 03:00 | 132 | 19:30
Charsaidpur | 139 | 03:00 | 135 | 00:00 | Patnitala | 133 | 04:00 | 128 | 21:00
Chauddagram | 132 | 01:00 | 127 | 14:00 | Patuakhali | 135 | 17:00 | 130 | 01:00
Chhatak | 121 | 01:00 | 113 | 14:00 | Payra | 135 | 08:00 | 134 | 00:00
Chowmuhani | 131 | 01:00 | 126 | 22:00 | PHP | 135 | 02:00 | 130 | 14:00
Chuadanga | 133 | 05:00 | 118 | 12:00 | Postogola | 138 | 08:00 | 134 | 00:00
Coxsbazar | 126 | 09:00 | 110 | 19:30 | Pubail | 134 | 05:00 | 127 | 09:00
Cumilla(N) | 138 | 01:00 | 126 | 22:00 | Purbachal | 138 | 08:00 | 132 | 00:00
Cumilla(S) | 133 | 02:00 | 127 | 14:00 | Purbasadipur | 138 | 01:00 | 128 | 18:00
Daganbhuiyan | 133 | 01:00 | 128 | 14:00 | Rahanpur | 137 | 08:00 | 132 | 21:00
Daudkandi | 126 | 17:00 | 118 | 18:30 | Rahanpur-400 | 137 | 15:00 | 134 | 07:00
DhakaUniversity | 137 | 02:00 | 133 | 00:00 | Rahim | 139 | 02:00 | 133 | 08:00
Dhamrai | 137 | 17:00 | 132 | 11:00 | Rajbari | 128 | 17:00 | 123 | 13:00
Dhanmondi | 140 | 03:00 | 137 | 00:00 | Rajendrapur | 134 | 03:00 | 128 | 00:00
Dohazari | 132 | 03:00 | 125 | 14:00 | Rajshahi | 133 | 03:00 | 127 | 19:30
Faridpur | 130 | 04:00 | 125 | 22:00 | Rajshahi-230 | 134 | 01:00 | 127 | 19:30
Fatullah | 139 | 04:00 | 133 | 00:00 | Ramganj | 132 | 01:00 | 124 | 11:00
Fenchuganj | 132 | 05:00 | 129 | 13:00 | Rampur | 139 | 03:00 | 133 | 14:00
Feni | 133 | 04:00 | 128 | 20:00 | Rampura | 137 | 05:00 | 132 | 00:00
Feni-230 | 134 | 01:00 | 128 | 21:00 | Rangamati | 139 | 03:00 | 135 | 14:00
Ghatail | 128 | 05:00 | 115 | 19:00 | Rangpur | 134 | 00:00 | 123 | 18:00
Ghorashal | 134 | 02:00 | 129 | 09:00 | Ruppur | 138 | 04:00 | 130 | 18:00
Goalpara | 133 | 10:00 | 123 | 13:00 | Saidpur | 137 | 00:00 | 126 | 18:00
Gollamari | 131 | 06:00 | 123 | 13:00 | Santhia | 136 | 03:00 | 129 | 20:00
Gopalganj | 131 | 17:00 | 123 | 13:00 | Satkhira | 127 | 10:00 | 115 | 13:00
Gopalganj-400 | 133 | 04:00 | 129 | 13:00 | Satmasjid | 137 | 03:00 | 131 | 13:00
Gulshan | 136 | 03:00 | 132 | 00:00 | Savar | 136 | 03:00 | 130 | 11:00
Halishahar | 140 | 03:00 | 133 | 14:00 | SevenRings | 135 | 02:00 | 130 | 09:00
Haripur | 140 | 03:00 | 136 | 00:00 | ShahCement | 139 | 03:00 | 135 | 00:00
HaripurSBU | 140 | 08:00 | 134 | 00:00 | Shahjadpur | 135 | 01:00 | 130 | 22:00
Hasnabad | 139 | 05:00 | 133 | 13:00 | Shahjibazar | 132 | 03:00 | 127 | 00:00
Hathazari | 140 | 08:00 | 136 | 04:00 | Shahmirpur | 139 | 07:00 | 134 | 14:00
Hatirjheel | 137 | 03:00 | 132 | 00:00 | Shariatpur | 129 | 03:00 | 124 | 13:00
Ishurdi | 139 | 05:00 | 131 | 20:00 | Sherpur | 131 | 21:00 | 117 | 11:00
Jaldhaka | 134 | 01:00 | 122 | 18:00 | Shikalbaha | 129 | 03:00 | 122 | 14:00
Jamalpur | 134 | 13:00 | 113 | 19:00 | Shikalbaha-230 | 140 | 02:00 | 135 | 14:00
Jashore | 139 | 01:00 | 115 | 13:00 | Shitalakhya | 136 | 03:00 | 132 | 00:00
Jhenaidah | 136 | 03:00 | 121 | 13:00 | Sholosohor | 140 | 03:00 | 133 | 14:00
Jhenaidah-230 | 138 | 05:00 | 121 | 13:00 | Shomvuganj | 126 | 17:00 | 115 | 00:00
Joydebpur | 131 | 17:00 | 119 | 00:00 | Shyampur | 138 | 17:00 | 132 | 12:00
Joypurhat | 134 | 05:00 | 128 | 21:00 | Shyampur-230 | 139 | 02:00 | 132 | 13:00
Juldah | 139 | 13:00 | 133 | 04:00 | Siddhirganj | 140 | 03:00 | 136 | 00:00
Kabirpur | 140 | 03:00 | 127 | 09:00 | Sirajganj | 134 | 04:00 | 127 | 20:00
Kachua | 134 | 08:00 | 127 | 22:00 | Sitakunda | 138 | 00:00 | 135 | 14:00
Kaliakoir | 141 | 03:00 | 135 | 11:00 | Sonargaon | 138 | 07:00 | 132 | 00:00
Kaliganj | 136 | 04:00 | 120 | 13:00 | Sreemongol | 130 | 03:00 | 125 | 19:30
Kallyanpur | 136 | 01:00 | 129 | 00:00 | Sreepur | 135 | 03:00 | 129 | 13:00
Kalurghat | 140 | 01:00 | 137 | 11:00 | Srinagar | 137 | 06:00 | 132 | 13:00
Kamrangirchar | 138 | 02:00 | 128 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 118 | 00:00 | 111 | 14:00
Kasba | 126 | 01:00 | 120 | 20:00 | Sylhet | 124 | 09:00 | 120 | 12:00
Kazla | 142 | 05:00 | 135 | 00:00 | Sylhet_(South) | 126 | 08:00 | 120 | 13:00
Keranigonj | 138 | 03:00 | 133 | 13:00 | Tangail | 129 | 03:00 | 123 | 19:00
Khagrachori | 138 | 03:00 | 134 | 13:00 | Taraganj | 134 | 03:00 | 126 | 13:00
Khulna | 130 | 04:00 | 120 | 13:00 | Tasnim | 139 | 17:00 | 134 | 00:00
Khulna(S) | 132 | 10:00 | 123 | 13:00 | Thakurgaon | 143 | 02:00 | 131 | 10:00
Khulshi | 137 | 01:00 | 131 | 14:00 | TK | 140 | 17:00 | 136 | 14:00
Kishoreganj | 129 | 04:00 | 122 | 13:00 | Tongi | 141 | 04:00 | 134 | 00:00
Kodda | 138 | 01:00 | 125 | 09:00 | Ullahpara | 136 | 05:00 | 129 | 19:30
Korerhat | 137 | 03:00 | 132 | 20:00 | Ullon | 137 | 03:00 | 132 | 00:00
KSRM | 139 | 07:00 | 134 | 15:00 | Uttara | 140 | 05:00 | 130 | 10:00
Kulaura | 131 | 06:00 | 127 | 13:00 | UttaraNew | 139 | 02:00 | 129 | 13:00
Kurigram | 133 | 04:00 | 119 | 18:00 | Zigatola | 138 | 03:00 | 133 | 00:00
Kushtia | 137 | 06:00 | 125 | 18:00
Laksam | 133 | 08:00 | 127 | 14:00
Lakshmipur | 130 | 01:00 | 124 | 19:30
Lalbag | 138 | 17:00 | 132 | 02:00
Lalmonirhat | 131 | 00:00 | 122 | 18:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division