## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-10-2026 | during | 18-10-2026 | during | 18-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 387 | 345 | 412 | 412 | 400 | 400 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 305 | 335 | 335 | 308 | 308 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 124 | 126 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 7 | 7 | 33 | 33 | 10 | 10 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 24 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 210 | 98 | 300 | 300 | 278 | 295 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 146 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 144 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 485 | 510 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 460 | 550 | 583 | 583 | 450 | 450 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2657.42 | 2741.42 | 5566.8 | 5536.8 | 2781.42 | 2985.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 182 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 213 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 88 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 29 | 49 | 24 | 54 | 24 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 37 | 100 | 100 | 24 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 78 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.16 | 0 | 3.46 | 0 | 3.46 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 214 | 300 | 300 | 158 | 230 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 54.36 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 46 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 44 | 100 | 100 | 25 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 158 | 160 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 600 | 1180 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1080 | 1080 | 1150 | 1150 | 1080 | 1080 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2672.52 | 3776.86 | 4106.42 | 4181.96 | 3473.46 | 3941.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 201 | 198 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 19 | 350.01 | 350.01 | 314 | 314 | FGMO
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 265 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 320 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 22 | 22 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 30 | 30 | 52.82 | 52.82 | 22 | 22 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 71 | 63 | 195 | 195 | 70 | 70 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 139 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 21 | 20 | 20 | 20 | 20 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 36 | 36 | 163 | 163 | 50 | 50 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 122 | 139 | 200 | 200 | 135 | 119 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 76 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 13 | 24.5 | 24.5 | 12 | 12 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 74 | 71 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 115 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1777 | 1726.2 | 2752.44 | 2680.44 | 2176.2 | 2152.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-10-2026 | during | 18-10-2026 | during | 18-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 17 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.8 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 165 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 88 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.04 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 268.84 | 306 | 673.6 | 601.5 | 290.1 | 322
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 136 | 129 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 80 | 81 | 81 | 81 | 81 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 259 | 245 | 341 | 341 | 341 | 341 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 399 | 397 | 400 | 400 | 400 | 400 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 390 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1514 | 1491 | 1592 | 1592 | 1576 | 1576
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 777 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 38 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 11 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86.1 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1230 | 1217 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2218.1 | 2131 | 3294.2 | 3204.2 | 2729.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 850 | 1080 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 48 | 110 | 110 | 48 | 64 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Station shutdown for GT-11& STG Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 100 | 150 | 150 | 54 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 275 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1524.59 | 1803 | 2158.6 | 2157.6 | 1995.6 | 2010.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 41.82 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 31 | 37 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 294 | 245 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 26 | 26 | 34 | 34 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8 | 102 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.98 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1006.8 | 1428.8 | 1200 | 1400 | 1200 | 1400 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.48 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1684.28 | 2150 | 3013.11 | 2990.99 | 2072.73 | 2221.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.1 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 120 | 0 | 180.56 | 0 | 180.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 340.1 | 228 | 443.56 | 228 | 353.56 | 217
System Total |  |  |  |  | 28843.2 | 28692.211 | 14656.85 | 16353.48 | 23600.73 | 23173.49 | 17448.27 | 18065.89
Forecast Scenario (18-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15030 |  | 1212.85 |  | 16300
|  |  |  | 1:00 | 14600 |  | 849.95 |  | 15490
|  |  |  | 2:00 | 14260 |  | 869.05 |  | 15170
|  |  |  | 3:00 | 13860 |  | 964.55 |  | 14870
|  |  |  | 4:00 | 13430 |  | 935.9 |  | 14410
|  |  |  | 5:00 | 12930 |  | 1069.6 |  | 14050
|  |  |  | 6:00 | 12680 |  | 687.6 |  | 13400
|  |  |  | 7:00 | 12950 |  | 410.65 |  | 13380
|  |  |  | 8:00 | 13150 |  | 38.2 |  | 13190
|  |  |  | 9:00 | 13250 |  | 38.2 |  | 13290
|  |  |  | 10:00 | 13450 |  | 28.65 |  | 13480
|  |  |  | 11:00 | 13740 |  | 9.55 |  | 13750
|  |  |  | 12:00 | 14520 |  | 28.65 |  | 14550
|  |  |  | 13:00 | 14550 |  | 38.2 |  | 14590
|  |  |  | 14:00 | 14290 |  | 372.45 |  | 14680
|  |  |  | 15:00 | 14360 |  | 783.1 |  | 15180
|  |  |  | 16:00 | 14430 |  | 286.5 |  | 14730
|  |  |  | 17:00 | 14550 |  | 28.65 |  | 14580
|  |  |  | 18:00 | 14700 |  | 28.65 |  | 14730
|  |  |  | 18:30 | 15450 |  | 38.2 |  | 15490
|  |  |  | 19:00 | 16130 |  | 114.6 |  | 16250
|  |  |  | 19:30 | 16350 |  | 0 |  | 16140
|  |  |  | 20:00 | 15190 |  | 935.9 |  | 16170
|  |  |  | 21:00 | 15360 |  | 830.85 |  | 16230
|  |  |  | 22:00 | 15380 |  | 534.8 |  | 15940
|  |  |  | 23:00 | 15230 |  | 764 |  | 16030
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.02 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:07 hrs on 18-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-10-2026 | [28 empty] | Date: | 17-10-2026 | [28 empty] | Date: | 17-10-2026 | [28 empty] | Date: | 17-10-2026 | [28 empty] | Date: | 17-10-2026 | [16 empty] | Date: | 17-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 54 | 114 | 128 | 244 | 36 | 55 | 108 | 0 | 0 | 450 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 10 | 18 | 0 | 440 | 94 | 87 | 18 | 0 | 0 | 57 | 14 | 35 | 12 | 25 | 0 | 221 | 80 | 28 | 1080 | 28 | 0 | 50 | 17 | 81 | 222 | 0 | 0 | 0 | 940 | 0 | 150 | 0 | 320 | 297 | 220 | 44 | 0 | 196 | 0 | 69 | 50 | 122 | 68 | 10 | 49 | 68 | 52.2 | 0 | 23 | 320 | 400 | 398 | 40 | 30 | 141 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 0 | 35 | 58 | 0 | 68 | 0 | 0 | 0 | 24 | 9140.62 | 724 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1224 | 0 | 0 | 0 | 1379.21 | 0 | 0 | 0 | 113 | 80 | 0 | 92 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 288 | 110 | 0 | 0 | 850 | 300 | 35 | 5892.41 | 15033.03 | 103.98
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 54 | 116 | 128 | 244 | 49 | 55 | 72 | 0 | 0 | 445 | 0 | 35 | 293 | 0 | 0 | 0 | 143.42 | 10 | 18 | 0 | 395 | 91 | 52 | 31 | 0 | 0 | 67 | 22 | 18 | 24 | 25 | 0 | 182 | 110 | 28 | 1080 | 98 | 0 | 50 | 17 | 101 | 222 | 0 | 0 | 0 | 760 | 0 | 150 | 0 | 330 | 300 | 220 | 44 | 0 | 193 | 0 | 88 | 51 | 122 | 68 | 10 | 104 | 64 | 52.2 | 0 | 23 | 315 | 400 | 398 | 40 | 30 | 154 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 0 | 35 | 58 | 0 | 68 | 0 | 0 | 0 | 24 | 9038.62 | 724 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1234.2 | 0 | 0 | 0 | 1192.95 | 0 | 0 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 268 | 110 | 0 | 0 | 850 | 300 | 35 | 5558.35 | 14596.97 | 103.97
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 54 | 116 | 130 | 212 | 47 | 55 | 72 | 0 | 0 | 440 | 0 | 35 | 288 | 0 | 0 | 0 | 143.42 | 10 | 18 | 0 | 385 | 86 | 52 | 56 | 0 | 0 | 67 | 22 | 18 | 24 | 25 | 0 | 172 | 110 | 28 | 1080 | 144 | 0 | 50 | 17 | 96 | 222 | 0 | 0 | 0 | 600 | 0 | 150 | 0 | 350 | 285 | 220 | 44 | 0 | 190 | 0 | 88 | 51 | 122 | 75 | 13 | 94 | 62 | 52.2 | 0 | 23 | 300 | 400 | 398 | 40 | 30 | 152 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 0 | 35 | 59 | 0 | 68 | 0 | 0 | 0 | 24 | 8851.62 | 724 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1016.98 | 0 | 0 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 269 | 110 | 0 | 0 | 850 | 300 | 35 | 5408.38 | 14260 | 103.96
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 54 | 116 | 130 | 147 | 46 | 55 | 72 | 0 | 0 | 435 | 0 | 35 | 303 | 0 | 0 | 0 | 143.42 | 10 | 19 | 0 | 425 | 89 | 52 | 0 | 0 | 0 | 67 | 22 | 18 | 0 | 25 | 0 | 180 | 104 | 28 | 1080 | 102 | 0 | 50 | 17 | 92 | 222 | 0 | 0 | 0 | 600 | 0 | 142 | 6 | 360 | 15 | 310 | 44 | 0 | 195 | 0 | 86 | 50 | 122 | 0 | 13 | 70 | 62 | 52.2 | 0 | 23 | 302 | 400 | 398 | 40 | 30 | 152 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 0 | 35 | 59 | 0 | 68 | 0 | 0 | 0 | 24 | 8443.62 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1022.58 | 0 | 0 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 270 | 110 | 0 | 0 | 850 | 300 | 17 | 5413.98 | 13857.6 | 103.95
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 54 | 116 | 130 | 147 | 47 | 55 | 72 | 0 | 0 | 440 | 0 | 35 | 290 | 0 | 0 | 0 | 68 | 10.5 | 19 | 0 | 395 | 89 | 52 | 0 | 0 | 0 | 67 | 0 | 18 | 0 | 25 | 0 | 180 | 105 | 28 | 1080 | 0 | 0 | 50 | 17 | 90 | 222 | 0 | 0 | 0 | 600 | 0 | 140 | 8 | 393 | 0 | 290 | 44 | 4 | 188 | 5 | 0 | 50 | 121 | 0 | 13 | 14 | 60 | 52.2 | 0 | 0 | 305 | 400 | 398 | 40 | 30 | 154 | 0 | 16 | 0 | 83 | 0 | 137 | 0 | 0 | 35 | 58 | 0 | 55 | 0 | 0 | 0 | 24 | 8040.7 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1013.1 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 272 | 110 | 0 | 0 | 850 | 300 | 17 | 5384.5 | 13425.2 | 103.94
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35 | 17 | 116 | 13 | 147 | 25 | 55 | 35 | 0 | 0 | 440 | 0 | 35 | 302 | 0 | 0 | 0 | 68 | 10 | 19 | 0 | 445 | 86 | 52 | 0 | 0 | 0 | 67 | 0 | 18 | 0 | 25 | 0 | 179 | 104 | 28 | 1080 | 0 | 0 | 50 | 17 | 88 | 222 | 0 | 0 | 0 | 600 | 0 | 137 | 8 | 393 | 0 | 305 | 44 | 5 | 196 | 5 | 0 | 50 | 17 | 0 | 10 | 0 | 60 | 16 | 0 | 0 | 306 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 0 | 35 | 59 | 0 | 16 | 0 | 0 | 0 | 24 | 7704 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1198 | 0 | 0 | 0 | 1021.09 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 278 | 110 | 0 | 0 | 820 | 300 | 17 | 5225.09 | 12929.09 | 103.93
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 17 | 129 | 14 | 30 | 13 | 35 | 31 | 0 | 0 | 445 | 0 | 35 | 305 | 0 | 0 | 0 | 68 | 10 | 19 | 0 | 500 | 45 | 52 | 0 | 0 | 0 | 67 | 0 | 54.36 | 0 | 25 | 0.01 | 179 | 68 | 28 | 1080 | 0 | 0 | 50 | 17 | 34 | 222 | 0 | 0 | 0 | 600 | 0 | 150 | 8 | 393 | 0 | 315 | 44 | 5 | 197 | 5 | 0 | 50 | 17 | 0 | 10 | 0 | 54 | 16 | 0 | 0 | 308 | 400 | 358 | 40 | 30 | 156 | 0 | 16 | 0 | 83 | 0 | 136 | 0 | 0 | 35 | 58 | 0.02 | 8 | 0 | 0 | 0 | 24 | 7513.39 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1197 | 0 | 0 | 0 | 1015.19 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 280 | 110 | 0 | 0 | 823 | 300 | 17 | 5168.19 | 12681.58 | 103.92
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 35 | 79 | 60 | 35 | 28 | 0 | 35 | 0 | 0 | 465 | 0 | 17 | 307 | 0 | 0 | 3 | 105 | 10 | 12 | 0 | 560 | 48 | 52 | 0 | 0 | 0 | 34 | 0 | 54.36 | 0 | 25 | 0.43 | 178 | 34 | 26 | 1080 | 6 | 0 | 50 | 17 | 33 | 220 | 0 | 0 | 0 | 600 | 1 | 150 | 16 | 393 | 0 | 310 | 44 | 8 | 199 | 5 | 8 | 50 | 57 | 0 | 10 | 17 | 54 | 8 | 13 | 0 | 320 | 400 | 340 | 40 | 30 | 159 | 2 | 0 | 0 | 83 | 0 | 137 | 0 | 0 | 0 | 69 | 2.6 | 48 | 0 | 0.3 | 7.21 | 24 | 7641.9 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1234.2 | 0 | 0 | 0 | 1028.77 | 0 | 0 | 0 | 55 | 46 | 0 | 0 | 0 | 34 | 6.31 | 11 | 0 | 0 | 6.76 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0.62 | 0 | 0 | 115 | 3 | 38 | 0 | 0 | 0 | 0.7 | 25 | 0.07 | 32 | 297 | 110 | 0 | 0 | 844 | 300 | 17 | 5307.43 | 12949.33 | 103.91
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 54 | 78 | 101 | 160 | 50 | 0 | 35 | 0 | 0 | 450 | 0 | 17 | 304 | 0 | 0 | 11 | 105 | 9.5 | 18 | 0 | 455 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 54.36 | 0 | 25 | 1.43 | 180 | 34 | 15 | 1080 | 16 | 0 | 50 | 17 | 17 | 222 | 0 | 0 | 0 | 600 | 0 | 144 | 16 | 393 | 0 | 310 | 44 | 15 | 196 | 22 | 41 | 50 | 121 | 4 | 10 | 17 | 58 | 8 | 33 | 0 | 310 | 400 | 340 | 40 | 30 | 157 | 5 | 0 | 0 | 80 | 0 | 137 | 0 | 0 | 10 | 59 | 7.76 | 65 | 0 | 0.6 | 20.48 | 18 | 7766.13 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1234.2 | 0 | 0 | 0 | 1024.74 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 44 | 20.03 | 32 | 0 | 0 | 22.08 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 1.93 | 0 | 0 | 115 | 9 | 90 | 0 | 0 | 0 | 2.5 | 56 | 0.22 | 32 | 278 | 110 | 0 | 0 | 830 | 300 | 17 | 5456.7 | 13222.83 | 103.9
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 54 | 85 | 100 | 164 | 48 | 17 | 35 | 0 | 0 | 445 | 0 | 17 | 296 | 0 | 0 | 18 | 105 | 8 | 18 | 0 | 400 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 54.36 | 0 | 25 | 2.46 | 181 | 17 | 4 | 1080 | 16 | 0 | 50 | 17 | 16 | 220 | 0 | 0 | 0 | 600 | 0 | 142 | 16 | 393 | 0 | 300 | 44 | 15 | 193 | 21 | 62 | 50 | 122 | 62 | 10 | 17 | 60 | 8 | 51 | 2 | 310 | 400 | 397 | 40 | 30 | 155 | 8 | 8 | 0 | 80 | 0 | 136 | 0 | 0 | 17 | 59 | 12.39 | 77 | 0 | 0.9 | 30.71 | 18 | 7876.82 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1234.2 | 0 | 0 | 0 | 1016.78 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 34.22 | 53 | 0 | 0 | 36.19 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 3.14 | 0 | 0 | 115 | 20 | 99 | 0 | 0 | 0 | 4.2 | 110 | 0.38 | 32 | 269 | 0 | 0 | 0 | 820 | 300 | 17 | 5602.31 | 13479.13 | 103.83
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 54 | 98 | 106 | 197 | 50 | 35 | 35 | 0 | 0 | 445 | 0 | 17 | 306 | 0 | 0 | 24 | 105 | 8 | 18 | 0 | 530 | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 54.36 | 0 | 25 | 3.11 | 181 | 17 | 0 | 1080 | 16 | 0 | 50 | 17 | 15 | 216 | 0 | 0 | 0 | 600 | 0 | 142 | 33 | 393 | 0 | 320 | 44 | 15 | 203 | 0 | 63 | 36 | 121 | 65 | 10 | 17 | 60 | 8 | 63 | 7 | 295 | 392 | 398 | 40 | 30 | 155 | 10 | 5 | 0 | 80 | 0 | 136 | 0 | 0 | 17 | 59 | 16 | 116 | 0 | 1.2 | 38.35 | 18 | 8212.02 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.19 | 1230 | 0 | 0 | 0 | 1021.07 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 52.2 | 44.02 | 73 | 0 | 0 | 47.02 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 4.08 | 0 | 0 | 115 | 28 | 106 | 0 | 0 | 0 | 5.1 | 147 | 0.52 | 32 | 278 | 0 | 0 | 0 | 850 | 300 | 17 | 5721.2 | 13933.22 | 103.88
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 54 | 128 | 124 | 197 | 40 | 35 | 35 | 0 | 0 | 460 | 0 | 35 | 306 | 0 | 0 | 26 | 123 | 7 | 18 | 0 | 545 | 16 | 49 | 0 | 0 | 0 | 0 | 23 | 54.36 | 10 | 25 | 3.11 | 181 | 17 | 0 | 1080 | 41 | 0 | 50 | 17 | 16 | 212 | 0 | 0 | 0 | 600 | 0 | 140 | 71 | 380 | 0 | 310 | 44 | 27 | 205 | 0 | 68 | 36 | 122 | 66 | 10 | 94 | 68 | 8 | 46 | 10 | 270 | 390 | 399 | 40 | 29 | 156 | 10 | 8 | 0 | 80 | 0 | 135 | 0 | 0 | 17 | 59 | 12 | 116 | 0 | 1.7 | 42.69 | 18 | 8494.86 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.52 | 1227 | 8 | 0 | 0 | 1011.31 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 8 | 52.2 | 46.33 | 83 | 0 | 0 | 50.39 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 4.38 | 0 | 0 | 115 | 28 | 113 | 0 | 0 | 0 | 6 | 164 | 0.57 | 32 | 307 | 0 | 0 | 0 | 850 | 300 | 17 | 5810.7 | 14305.56 | 103.87
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17 | 54 | 132 | 124 | 210 | 40 | 35 | 108 | 0 | 0 | 460 | 0 | 35 | 300 | 0 | 0 | 26 | 143.42 | 7 | 18 | 0 | 485 | 89 | 52 | 0 | 0 | 0 | 0 | 29 | 54.36 | 24 | 25 | 3.16 | 182 | 46 | 0 | 1080 | 158 | 0 | 50 | 17 | 51 | 212 | 0 | 0 | 0 | 600 | 0 | 139 | 71 | 393 | 0 | 310 | 44 | 30 | 201 | 0 | 69 | 36 | 122 | 74 | 12 | 114 | 70 | 8 | 70 | 14 | 259 | 390 | 399 | 39 | 30 | 156 | 10 | 16 | 0 | 79 | 0 | 136 | 0 | 0 | 17 | 58 | 17 | 116 | 0 | 1.8 | 41.04 | 18 | 8889.78 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1 | 1230 | 11 | 0 | 0 | 1006.8 | 0 | 0 | 0 | 55 | 50 | 0 | 8 | 31 | 52.2 | 41.82 | 88 | 0 | 0 | 52.48 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 4.98 | 0 | 0 | 115 | 32 | 70 | 0 | 0 | 0 | 3.1 | 120 | 0.59 | 32 | 307 | 0 | 0 | 0 | 850 | 300 | 35 | 5767.07 | 14656.85 | 103.86
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 54 | 132 | 121 | 213 | 40 | 35 | 108 | 0 | 0 | 445 | 0 | 35 | 300 | 0 | 0 | 25 | 143.42 | 7 | 18 | 0 | 490 | 109 | 52 | 41 | 0 | 0 | 0 | 29 | 54.36 | 24 | 25 | 3.22 | 182 | 96 | 0 | 1080 | 163 | 0 | 50 | 17 | 83 | 212 | 0 | 0 | 0 | 600 | 0 | 135 | 75 | 393 | 0 | 300 | 44 | 30 | 200 | 0 | 69 | 36 | 120 | 73 | 12 | 114 | 70 | 8 | 65 | 14 | 257 | 395 | 399 | 40 | 29 | 154 | 10 | 16 | 0 | 79 | 0 | 136 | 0 | 0 | 17 | 58 | 17.6 | 116 | 0 | 1.6 | 25.3 | 18 | 8924.5 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.59 | 1230 | 11 | 0 | 0 | 1011.55 | 0 | 0 | 0 | 55 | 50 | 0 | 8.5 | 30 | 52.2 | 47.29 | 80 | 0 | 0 | 50.22 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 4.43 | 0 | 0 | 115 | 26 | 35 | 0 | 0 | 0 | 6.3 | 137 | 0.54 | 32 | 307 | 0 | 0 | 0 | 850 | 300 | 35 | 5722.62 | 14647.12 | 103.85
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 54 | 132 | 121 | 97 | 40 | 35 | 108 | 0 | 0 | 435 | 0 | 35 | 308 | 0 | 0 | 22 | 143.42 | 7 | 18 | 0 | 465 | 107 | 52 | 55 | 0 | 0 | 0 | 27 | 54.36 | 24 | 25 | 2.79 | 182 | 108 | 0 | 1080 | 162 | 0 | 50 | 17 | 88 | 211 | 0 | 0 | 0 | 600 | 0 | 137 | 73 | 393 | 0 | 300 | 44 | 30 | 201 | 0 | 68 | 36 | 120 | 72 | 12 | 114 | 76 | 8 | 54 | 14 | 255 | 391 | 392 | 40 | 29 | 151 | 8 | 16 | 0 | 78 | 0 | 136 | 0 | 0 | 17 | 58 | 14.43 | 117 | 0 | 1.3 | 33.54 | 18 | 8780.84 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.15 | 1234.2 | 11 | 0 | 0 | 1010.34 | 0 | 0 | 0 | 55 | 50 | 0 | 8.5 | 30 | 52.2 | 37.09 | 45 | 0 | 0 | 32.77 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 3.35 | 0 | 0 | 115 | 24 | 35 | 0 | 0 | 0 | 4.8 | 80 | 0.42 | 32 | 288 | 0 | 0 | 0 | 850 | 300 | 35 | 5506.82 | 14287.66 | 103.84
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 54 | 132 | 121 | 97 | 40 | 35 | 144 | 0 | 0 | 410 | 0 | 35 | 308 | 0 | 0 | 15 | 143.42 | 7 | 18 | 0 | 490 | 107 | 52 | 57 | 0 | 0 | 0 | 27 | 54.36 | 24 | 25 | 1.96 | 182 | 110 | 0 | 1080 | 158 | 0 | 49 | 17 | 88 | 211 | 0 | 0 | 0 | 600 | 0 | 133 | 100 | 393 | 0 | 270 | 44 | 30 | 200 | 0 | 69 | 35 | 122 | 71 | 12 | 114 | 76 | 8 | 33 | 14 | 260 | 390 | 395 | 40 | 29 | 150 | 4 | 16 | 0 | 78 | 0 | 135 | 0 | 0 | 17 | 58 | 10.46 | 117 | 0 | 0.8 | 22.28 | 18 | 8754.28 | 891 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.52 | 1234.2 | 11 | 0 | 0 | 1016.25 | 0 | 0 | 0 | 100 | 70 | 0 | 8.5 | 30 | 52.2 | 25.68 | 43 | 0 | 0 | 24.64 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 2.25 | 0 | 0 | 115 | 17 | 35 | 0 | 0 | 0 | 3.7 | 99 | 0.29 | 32 | 307 | 0 | 0 | 0 | 850 | 300 | 35 | 5602.23 | 14356.51 | 103.8
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 54 | 132 | 121 | 97 | 40 | 35 | 144 | 0 | 0 | 425 | 0 | 55 | 312 | 0 | 0 | 8 | 143.42 | 7 | 18 | 0 | 540 | 109 | 67 | 57 | 0 | 0 | 0 | 28 | 54.36 | 24 | 25 | 1.04 | 182 | 110 | 0 | 1080 | 160 | 0 | 50 | 17 | 88 | 212 | 0 | 0 | 0 | 600 | 3 | 135 | 100 | 393 | 0 | 275 | 44 | 30 | 201 | 0 | 69 | 35 | 121 | 70 | 12 | 114 | 74 | 8 | 18 | 14 | 260 | 393 | 395 | 40 | 29 | 153 | 3 | 16 | 0 | 78 | 0 | 136 | 0 | 0 | 17 | 58 | 5.22 | 117 | 0 | 0.4 | 11.49 | 18 | 8851.93 | 890 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.82 | 1234.2 | 11 | 0 | 0 | 1013.91 | 0 | 0 | 0 | 113 | 113 | 0 | 8.5 | 31 | 52.2 | 13.81 | 23 | 0 | 0 | 11.64 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 1.05 | 0 | 0 | 115 | 8 | 70 | 0 | 0 | 0 | 1.4 | 40 | 0.16 | 48 | 307 | 0 | 0 | 0 | 850 | 300 | 35 | 5579.69 | 14431.62 | 103.81
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 35 | 54 | 145 | 121 | 97 | 40 | 35 | 162 | 0 | 0 | 400 | 0 | 55 | 296 | 0 | 0 | 1 | 143.42 | 7 | 18 | 0 | 385 | 107 | 203 | 63 | 0 | 0 | 0 | 56 | 54.36 | 24 | 25 | 0.08 | 180 | 110 | 0 | 1080 | 158 | 0 | 50 | 25.5 | 88 | 212 | 0 | 0 | 0 | 600 | 1 | 133 | 100 | 393 | 0 | 230 | 44 | 30 | 178 | 0 | 69 | 35 | 130 | 70 | 12 | 114 | 68 | 8 | 3 | 16 | 256 | 400 | 385 | 40 | 29 | 152 | 0 | 16 | 0 | 79 | 0 | 138 | 0 | 0 | 17 | 59 | 1.2 | 117 | 0 | 0.1 | 2.32 | 18 | 8735.98 | 864 | 0 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 50 | 4.21 | 1234.2 | 11 | 0 | 0 | 1189.94 | 0 | 32 | 0 | 113 | 113 | 0 | 8.5 | 36 | 52.2 | 2.3 | 4 | 0 | 0 | 2.39 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0.19 | 0 | 0 | 115 | 1 | 113 | 0 | 0 | 0 | 0.3 | 2 | 0.03 | 48 | 304 | 0 | 0 | 0 | 850 | 300 | 100 | 5814.26 | 14550.24 | 103.81
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 54 | 132 | 125 | 97 | 40 | 55 | 144 | 0 | 0 | 380 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 475 | 109 | 210 | 66 | 0 | 0 | 25 | 56 | 54.36 | 37 | 40 | 0 | 180 | 110 | 0 | 1080 | 160 | 0 | 46 | 25.5 | 88 | 213 | 0 | 0 | 0 | 862 | 0 | 140 | 66 | 330 | 100 | 260 | 44 | 30 | 193 | 0 | 96 | 35 | 139 | 71 | 12 | 114 | 80 | 43 | 0 | 21 | 263 | 400 | 395 | 40 | 29 | 150 | 0 | 16 | 0 | 80 | 0 | 137 | 0 | 0 | 20 | 88 | 0 | 161 | 0 | 0 | 0 | 18 | 9446.28 | 841 | 0 | 29 | 11 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 1228 | 0 | 0 | 0 | 1420.16 | 0 | 32 | 0 | 113 | 113 | 0 | 102 | 37 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 0 | 0 | 0 | 850 | 300 | 100 | 6144.36 | 15590.64 | 103.81
19:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 54 | 140 | 126 | 97 | 40 | 55 | 144 | 0 | 0 | 480 | 0 | 55 | 294 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 390 | 107 | 214 | 76 | 0 | 0 | 67 | 49 | 54.36 | 37 | 42 | 0 | 220 | 110 | 0 | 1080 | 160 | 0 | 49 | 25.5 | 88 | 213 | 0 | 0 | 0 | 1110 | 0 | 145 | 63 | 270 | 100 | 255 | 44 | 30 | 202 | 0 | 113 | 36 | 139 | 71 | 12 | 114 | 76 | 52.2 | 0 | 21 | 250 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 80 | 0 | 136 | 0 | 0 | 35 | 87 | 0 | 165 | 0 | 0 | 0 | 18 | 9763.48 | 771 | 0 | 36 | 30 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 1234.2 | 0 | 0 | 0 | 1408.07 | 0 | 32 | 0 | 113 | 113 | 0 | 102 | 37 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 120 | 0 | 0 | 0 | 0 | 48 | 307 | 0 | 0 | 0 | 1000 | 300 | 100 | 6369.47 | 16132.95 | 103.8
19:30 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 54 | 146 | 126 | 98 | 55 | 55 | 144 | 0 | 0 | 550 | 0 | 55 | 305 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 510 | 107 | 214 | 78 | 0 | 0 | 67 | 49 | 54.36 | 37 | 44 | 0 | 220 | 110 | 0 | 1080 | 160 | 0 | 50 | 25.5 | 88 | 213 | 0 | 0 | 0 | 1180 | 0 | 150 | 63 | 320 | 19 | 265 | 44 | 30 | 198 | 0 | 115 | 36 | 139 | 71 | 13 | 114 | 76 | 52.2 | 0 | 21 | 245 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 80 | 0 | 129 | 0 | 0 | 35 | 88 | 0 | 165 | 0 | 0 | 0 | 18 | 10041.48 | 777 | 0 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 1217 | 0 | 0 | 0 | 1428.8 | 0 | 32 | 0 | 113 | 113 | 0 | 102 | 37 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 275 | 0 | 0 | 0 | 1080 | 300 | 100 | 6312 | 16353.48
20:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 54 | 144 | 126 | 98 | 50 | 55 | 144 | 0 | 0 | 535 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 380 | 109 | 214 | 77 | 0 | 0 | 67 | 49 | 54.36 | 37 | 44 | 0 | 218 | 110 | 3 | 1080 | 158 | 0 | 50 | 25.5 | 88 | 213 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 385 | 20 | 230 | 44 | 30 | 180 | 0 | 115 | 36 | 139 | 72 | 13 | 90 | 74 | 52.2 | 0 | 21 | 245 | 400 | 397 | 40 | 30 | 153 | 0 | 16 | 0 | 80 | 0 | 136 | 0 | 0 | 35 | 87 | 0 | 165 | 0 | 0 | 0 | 18 | 9896.48 | 778 | 0 | 28 | 45 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1211 | 0 | 0 | 0 | 1420.59 | 0 | 31 | 0 | 113 | 113 | 0 | 102 | 40 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 265 | 0 | 0 | 0 | 1170.6 | 300 | 100 | 6398.39 | 16294.87 | 103.8
21:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 54 | 140 | 127 | 98 | 55 | 55 | 72 | 0 | 0 | 540 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 480 | 107 | 214 | 72 | 0 | 0 | 67 | 49 | 35 | 37 | 45 | 0 | 219 | 110 | 2 | 1080 | 34 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 100 | 393 | 18 | 305 | 44 | 30 | 200 | 0 | 34 | 37 | 100 | 73 | 13 | 34 | 72 | 52.2 | 0 | 21 | 245 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 80 | 0 | 136 | 0 | 0 | 35 | 88 | 0 | 165 | 0 | 0 | 0 | 15 | 9760.12 | 826 | 0 | 28 | 40 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1205 | 0 | 0 | 0 | 1416.91 | 0 | 31 | 0 | 113 | 35 | 0 | 102 | 38 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 50 | 0 | 0 | 1170.6 | 300 | 100 | 6328.51 | 16088.63 | 103.8
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 54 | 127 | 128 | 98 | 55 | 55 | 72 | 0 | 0 | 545 | 0 | 55 | 292 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 395 | 107 | 214 | 71 | 0 | 0 | 67 | 49 | 35 | 37 | 47 | 0 | 220 | 110 | 2 | 1080 | 34 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 13 | 295 | 44 | 30 | 191 | 0 | 34 | 37 | 100 | 74 | 13 | 34 | 70 | 52.2 | 0 | 21 | 245 | 400 | 397 | 40 | 30 | 155 | 0 | 0 | 0 | 80 | 0 | 137 | 0 | 0 | 35 | 88 | 0 | 165 | 0 | 0 | 0 | 18 | 9544.12 | 826 | 0 | 29 | 39 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1204 | 0 | 0 | 0 | 1420.16 | 0 | 31 | 0 | 113 | 35 | 0 | 102 | 38 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 115 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 274 | 116 | 0 | 0 | 1170.6 | 300 | 100 | 6393.76 | 15937.88 | 103.79
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 47 | 54 | 120 | 129 | 98 | 55 | 55 | 72 | 0 | 0 | 535 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 475 | 109 | 87 | 72 | 0 | 0 | 67 | 50 | 35 | 37 | 50 | 0 | 221 | 110 | 0 | 1080 | 34 | 0 | 50 | 25.5 | 103 | 218 | 0 | 0 | 0 | 1160 | 0 | 150 | 63 | 393 | 29 | 305 | 44 | 30 | 200 | 0 | 34 | 37 | 100 | 74 | 10 | 34 | 70 | 52.2 | 0 | 23 | 244 | 400 | 397 | 40 | 30 | 153 | 0 | 16 | 0 | 80 | 0 | 136 | 0 | 0 | 35 | 88 | 0 | 165 | 0 | 0 | 0 | 18 | 9477.12 | 825 | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1196 | 0 | 0 | 0 | 1416.88 | 0 | 31 | 0 | 113 | 40 | 0 | 100 | 30 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 115 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 299 | 0 | 0 | 0 | 1170.6 | 300 | 81 | 6258.48 | 15735.6 | 103.79
Total KWH | 0 | 627840 | 293760 | 0 | 0 | 0 | 0 | 0 | 8701200 | 0 | 0 | 779760 | 1227960 | 2936304 | 2636160 | 3158945 | 1055274 | 935828 | 2057760 | 0 | 0 | 11155455 | 0 | 928401 | 7307103 | 0 | 0 | 178508 | 3114000 | 225000 | 440280 | 0 | 11273181.82 | 2061218 | 2172873 | 873600 | 0 | 0 | 851954 | 580260 | 1090116 | 442560 | 708480 | 22922 | 4587624 | 2141091 | 257760 | 25861818.18 | 2109309 | 0 | 1207680 | 432514.8 | 1825781 | 5236970 | 0 | 0 | 0 | 18229089 | 3780 | 3424072 | 1170909 | 9086000 | 1185700 | 7046000 | 1048044 | 495840 | 4862000 | 52000 | 1456320 | 994823 | 2734560 | 1296960 | 253240 | 1594860 | 1079040 | 678586 | 470036 | 324016 | 6633000 | 9466300 | 9436000 | 948000 | 704280 | 3707181.82 | 69739 | 330240 | 0 | 1935360 | 0 | 3128000 | 0 | 0 | 634320 | 1587600 | 112910 | 2474400 | 0 | 11150 | 281880 | 479040 | 210922526.62 | 19797091 | 0 | 211680 | 280064 | 0 | 0 | 0 | 0 | 0 | 586512 | 515520 | 29440000 | 67200 | 0 | 0 | 27556364 | 0 | 242983 | 0 | 1909440 | 1792608 | 0 | 759344 | 399999 | 1054651 | 318544 | 552240 | 254900 | 0 | 338576 | 0 | 0 | 0 | 0 | 0 | 0 | 7003709 | 0 | 29700 | 0 | 0 | 2701699 | 194220 | 1733606 | 0 | 115447 | 0 | 38614.92 | 975600 | 3681 | 950688 | 6960000 | 1176000 | 0 | 0 | 22043636 | 7266909.09 | 1100400 | 138371626.01 | 349294152.63

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14656.85 | MW | 12:00 Hr. | Energy Generated |  |  | 349.2942 |  | MKWHr.
| Day Peak Demand |  |  | 15513.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 11.901 |  | MKWHr.
| Evening Peak Generation |  |  | 16353.48 | MW | 19:30 Hr. | Energy Demand |  |  | 361.1952 |  | MKWHr.
| Evening Peak Demand |  |  | 17321.64 | MW | 18:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12681.58 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 785.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 16353.48 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 8.6688 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.1022 | 0 | 19.752 | 0 | 0 | 0.17851 | 0 | 0 | 59.0327 | Gas | 115.2596 | Gas | 396682156.1338
| Chattogram Zone |  |  | 5.4947 | 44.0909 | 16.4974 | 0 | 4.5876 | 0.026702 | 0 | 0 | 70.6974 | Coal | 109.8015 | Coal | 849930046.2927
| Cumilla Zone |  |  | 26.1946 | 0 | 11.5094 | 0 | 0 | 0.47004 | 1.079 | 0 | 39.253 | HFO | 66.9799 | HFO | 1393847384.118
| Mymensingh Zone |  |  | 0 | 0 | 5.1754 | 0 | 0 | 0.40594 | 0 | 0 | 5.5813 | HSD | 0.11545 | HSD | 4184953.75
| Sylhet Zone |  |  | 36.2884 | 0 | 0 | 0 | 0 | 0.069739 | 0 | 0 | 36.3581 | Hydro | 4.5876 | Hydro | 458762.4
| Khulna Zone |  |  | 0 | 29.44 | 1.1455 | 0 | 0 | 0.51552 | 19.7971 | 0 | 50.8981 | Solar | 4.1176 | Solar | 65455270.6352
| Barishal Zone |  |  | 1.176 | 36.2705 | 2.0511 | 0 | 0 | 0.003681 | 0 | 0 | 39.5013 | Import | 48.4325 | Import | 317419835.84
| Rajshahi Zone |  |  | 7.0037 | 0 | 6.4139 | 0 | 0 | 1.2391 | 27.5564 | 0 | 42.2131 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 0 | 4.4353 | 0.11545 | 0 | 1.2084 | 0 | 0 | 5.7592
| Total |  |  | 115.2596 | 109.8015 | 66.9799 | 0.11545 | 4.5876 | 4.1176 | 48.4325 | 0 | 349.2942
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 396682156.1338 |  | Hydro | 458762.4
|  |  |  | Coal | 849930046.2927 |  | Solar | 65455270.6352
|  |  |  | HFO | 1393847384.118 |  | Import | 317419835.84
|  |  |  | HSD | 4184953.75 |  | Wind | 0
[5 empty] | Total: | 302,79,78,409 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.7971 | Peak Hr Flow | 777.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33054563.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5564 | Peak Hr Flow | 1428.80 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1319 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.079 | Peak Hr Flow | 76.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1884 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.4325 | Peak Hr Flow | 2281.80 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 51 |  | 6083
|  |  |  | Chattogram |  | 27 |  | 1579
|  |  |  | Cumilla |  | 73 |  | 1631
|  |  |  | Mymensingh |  | 232 |  | 1376
|  |  |  | Sylhet |  | 147 |  | 738
|  |  |  | Khulna |  | 201 |  | 1990
|  |  |  | Barishal |  | 15 |  | 531
|  |  |  | Rajshahi |  | 0 |  | 1594
|  |  |  | Rangpur |  | 0 |  | 896
|  |  |  | Total |  | 746 |  | 16418
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 438.5
|  |  |  | Total Unavailable Capacity |  |  |  | 738.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 17:00 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance Work
| 08:15 | 16:59 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance Work
| 08:15 | 15:26 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Annual Maintenance
| 08:16 | 15:23 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Annual Maintenance
| 08:22 | 18:02 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance
| 08:23 | 18:01 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Annual Maintenance
|  | 08:35 | Kodda(300MW)-Tongi 230kV Ckt-1 is restored.
| 08:46 | 14:49 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Annual maintenance
| 08:47 | 14:46 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Annual maintenance
| 09:00 |  | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to DEAD
LINE CHECKING
| 09:25 | 20:04 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to Protection testing
of Shombuganj Bay.
| 09:26 | 20:02 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to Protection test of
shombuganj bay.
| 09:39 | 12:47 | Nabinagar 132/33kV S/S T-2 LT Scheduled S/D Due to Shutdown is taken due to high
temperature maintenance work at 33 kV Bay CT.
| 09:40 | 12:46 | Nabinagar 132/33kV S/S T-2 HT Scheduled S/D Due to Shutdown is taken due to high
temperature maintenance work at 33 kV Bay CT.
| 09:47 | 17:12 | New Tongi-Tongi 132kV Ckt-1 Scheduled S/D from New Tongi end Due to Annual maintenance
in Tongi 230/132/33 KV Grid Substation. and from Tongi 230/132/33kV end Due to Annual
maintenance
|  | 10:24 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT is restored.
|  | 10:25 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT is restored.
|  | 11:10 | Ishurdi 230/132kV S/S 230 kV Bus 2 is restored.
| 11:42 | 14:52 | Ishurdi 230/132kV S/S 230 kV Bus 1 Scheduled S/D Due to Bay upgradation work
|  | 11:49 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T HT is restored.
| 11:55 | 13:55 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Forced S/D Due to Maintenance work at 33
kv BUS of T1 transformer by NESCO.
| 11:55 | 13:54 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Forced S/D Due to Maintenance work at 33
kv BUS of T1 transformer by NESCO.
|  | 11:56 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T LT is restored.
| 12:00 |  | Day Peak Generation: 14657MW.
| 12:00 |  | .
| 12:03 | 14:32 | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to CT PT test by SPMD
| 12:04 | 14:32 | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D Due to CT PT shutdown by SPMD
| 13:38 | 14:01 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing O/c, E/F relays Due to Gor pbs | [7 empty] | 41.0MW load
|  |  | chorbaria 33kv feeder fault. | [7 empty] | interrup.
|  | 15:07 | Daganbhuiyan 132/33kV S/S Transformer-1 HT is restored.
|  | 15:12 | Daganbhuiyan 132/33kV S/S Transformer-1 LT is restored.
|  | 15:28 | Rajbari 132/33kV S/S Transformer-1 HT is restored.
| 15:29 | 16:23 | Daganbhuiyan 132/33kV S/S Transformer-2 HT Forced S/D Due to Oil leakage check by
manufacture TAIKAI
|  | 15:29 | Rajbari 132/33kV S/S Transformer-1 LT is restored.
| 15:30 | 16:24 | Daganbhuiyan 132/33kV S/S Transformer-2 LT Forced S/D Due to Oil leakage check by
manufacture TAIKAI
| 16:30 | 18:24 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Forced S/D | [7 empty] | 20.0MW load
interrup.
| 16:36 | 18:13 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Forced S/D Due to ckt-2 | [7 empty] | 20.0MW load
|  |  | shutdown, ckt-1 overload | [7 empty] | interrup.
| 16:36 | 18:10 | Kabirpur - Manikganj 132kV Ckt-2 Forced S/D from Manikganj 132/33kV end. | [7 empty] | 20.0MW load
interrup. Manikganj
132/33kV end
| 17:13 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
|  | 18:24 | Manirampur-Satkhira 132kV Ckt-2 is restored.
|  | 18:24 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
| 19:30 |  | Evening Peak Generation: 16353 MW.
| 20:24 | 21:44 | Barishal 230/132kV S/S ATR-1 HT Forced S/D Due to OLTC problem
| 20:24 | 21:43 | Barishal 230/132kV S/S ATR-1 LT Forced S/D Due to OLTC problem
| 00:11 |  | Sylhet 225 MW CCPP Synchronized with remarks:- GT
| 01:47 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Tripped showing Differential Protection
relays Due to None
| 07:01 |  | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance Work
| 07:02 |  | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance Work
| 07:16 |  | Pabna 132/33kV S/S T-3 LT Scheduled S/D Due to Atghoriya 33 kv Incoming DS ( Y Phase) | [7 empty] | 10.0MW load
|  |  | Redhot Maintenance under bus-section 3. | [7 empty] | interrup.
| 07:17 |  | Pabna 132/33kV S/S T-3 HT Scheduled S/D Due to Atghoriya 33 kv Incoming DS ( Y Phase) | [7 empty] | 10.0MW load
|  |  | Redhot Maintenance under bus-section 3. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8701200 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1055274 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 305 | 7307103 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 779760 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 2636160 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935828 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 928401 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7 | 225000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 440280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 293760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 98 | 3158945 | Fuel Shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 146 | 2936304 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 627840 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2057760 | Fuel Shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 178508 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1227960 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 510 | 11273181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 11155455 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3114000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2741.42 | 59032719.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 432514.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 3780 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1207680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 4587624 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 5236970 | ps availability is less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 1825781 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 580260 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 851954 | Fuel Shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 442560 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 257760 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 78 | 873600 | Machine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22922 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 2172873 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 1090116 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2141091 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 44 | 708480 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2061218 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 160 | 2109309 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1180 | 18229089 | Coal Shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 25861818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3776.86 | 70697399.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 198 | 4862000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 19 | 1185700 | ST synch process going on
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 265 | 7046000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 9086000 | Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 52000 | Bay shifting
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 30 | 495840 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1170909 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1048044 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 3424072 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 324016 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 36 | 994823 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 139 | 2734560 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 76 | 1079040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 678586 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 253240 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1594860 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 71 | 1296960 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1456320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 470036 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1726.2 | 39253006
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 112910 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 165 | 2474400 | Fuel Shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1587600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 281880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 479040 | Machine Problem
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 634320 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 674.21 | 306 | 5581300
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 69739 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 948000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 704280 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3707181.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 129 | 3128000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1935360 | machine problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 330240 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 245 | 6633000 | Gas Shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 397 | 9436000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9466300 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1491 | 36358100.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 777 | 19797091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 211680 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 38 | 280064 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 67200 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 586512 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 515520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1217 | 29440000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2131 | 50898067
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1080 | 22043636 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 950688 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 1176000 | Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7266909.09 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1100400 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 6960000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3681 | -
Barishal Area Total |  |  |  |  | 3326.69 | 1803 | 39501314.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 318544 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 242983 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 399999 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 245 | 7003709 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 254900 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1054651 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 759344 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1792608 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1909440 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 29700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1428.8 | 27556364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 338576 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 552240 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2150 | 42213058
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 115447 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1733606 | Fuel Shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38614.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2701699 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194220 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 975600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 5759186.92
Eastern Grid Total |  |  |  |  | 16961.086 | 10041.48 | 210922526.62
Western Grid Total |  |  |  |  | 11731.125 | 6312 | 138371626.01
National Grid Total |  |  |  |  | 28692.211 | 16353.48 | 349294152.63
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-10-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10876.43 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4795 | MW
i) Dhaka area |  |  | 6032.33 |  | MW | i) Khulna area |  |  |  | 1789 | MW
ii) Chattogram area |  |  | 1551.6 |  | MW | ii) Barishal area |  |  |  | 515.8 | MW
iii) Cumilla area |  |  | 1557.5 |  | MW | iii) Rajshahi area |  |  |  | 1594.2 | MW
iv) Mymensingh area |  |  | 1144 |  | MW | iv) Rangpur area |  |  |  | 896 | MW
v) Sylhet area |  |  | 591 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15671.43 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 19:30 | 72 | Hatirjheel | 83 | 12:00 | 143 | PHP | 12 | 09:00
2 | AKSML | 150.6 | 16:00 | 73 | Ishurdi | 85 | 19:00 | 144 | Pabna | 102 | 19:00
3 | Aftabnagar | 46 | 13:00 | 74 | Jaldhaka | 71 | 18:30 | 145 | Palashbari | 126 | 19:00
4 | Agargaon | 139 | 13:00 | 75 | Jamalpur | 122 | 21:00 | 146 | Panchagarh | 60 | 18:30
5 | Agrabad | 76 | 11:00 | 76 | Jashore | 130 | 18:30 | 147 | Patiya | 32.3 | 19:30
6 | Amnura | 41 | 00:00 | 77 | Jhenaidah | 99 | 19:30 | 148 | Patnitala | 30 | 19:30
7 | Araihazar | 109 | 02:00 | 78 | Joydebpur | 175 | 18:30 | 149 | Patuakhali | 75.7 | 22:00
8 | Ashuganj | 0.58 | 00:00 | 79 | Joypurhat | 58 | 19:00 | 150 | Payra | 36 | 23:00
9 | Ashuganj-230 | 104 | 00:00 | 80 | Juldah | 20 | 18:00 | 151 | Postogola | 65 | 13:00
10 | BSRM | 194 | 18:00 | 81 | KSRM | 25 | 08:00 | 152 | Pubail | 96 | 06:00
11 | Bagerhat | 97 | 21:00 | 82 | Kabirpur | 280 | 19:00 | 153 | Purbachal | 32 | 18:00
12 | Bajitpur | 94 | 19:00 | 83 | Kachua | 104 | 19:30 | 154 | Purbasadipur | 115 | 19:00
13 | Bakerganj | 15 | 19:00 | 84 | Kaliganj | 43 | 21:00 | 155 | Rahanpur | 37 | 20:00
14 | Bakulia | 104 | 19:00 | 85 | Kallyanpur | 123 | 12:00 | 156 | Rahim | 52 | 16:00
15 | Banani | 68 | 14:00 | 86 | Kalurghat | 41 | 12:00 | 157 | Rajbari | 89 | 20:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 98 | 13:00 | 158 | Rajendrapur | 144 | 18:00
17 | Barapukuria | 62 | 19:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 113 | 20:00
18 | Barguna | 24 | 20:00 | 89 | Kasba | 38 | 19:30 | 160 | Rajshahi-230 | 97 | 20:00
19 | Barishal | 103 | 20:00 | 90 | Kazla | 126 | 13:00 | 161 | Ramganj | 114 | 20:00
20 | Barishal-230 | 112 | 19:00 | 91 | Keranigonj | 94 | 18:30 | 162 | Rampur | 46 | 00:00
21 | Baroaulia | 43 | 13:00 | 92 | Khagrachori | 32 | 14:00 | 163 | Rangamati | 16 | 18:30
22 | Baroirhat | 65 | 13:00 | 93 | Khulna | 68 | 18:00 | 164 | Rangpur | 120 | 18:30
23 | Bashundhara | 210 | 13:00 | 94 | Khulshi | 169 | 00:00 | 165 | Ruppur | 3 | 14:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 132 | 00:00 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 70 | 01:00 | 96 | Kodda | 285 | 11:00 | 167 | Saidpur | 106 | 19:00
26 | Benapole | 66 | 18:30 | 97 | Kulaura | 50 | 18:30 | 168 | Santhia | 36 | 19:00
27 | Bhaluka | 135 | 23:00 | 98 | Kurigram | 64 | 19:00 | 169 | Satkhira | 134 | 22:00
28 | Bhandaria | 60 | 22:00 | 99 | Kushtia | 157 | 19:30 | 170 | Satmasjid | 113 | 13:00
29 | Bhangura | 40 | 19:00 | 100 | Laksam | 37 | 00:00 | 171 | Savar | 230 | 15:00
30 | Bheramara(GK) | 66 | 21:00 | 101 | Lakshmipur | 52 | 19:30 | 172 | SevenRings | 17.56 | 11:00
31 | Bhulta | 200 | 14:00 | 102 | Lalbag | 87 | 13:00 | 173 | ShahCement | 28 | 08:00
32 | Bog-Sherpur | 70 | 19:00 | 103 | Lalmonirhat | 56 | 18:30 | 174 | Shahjadpur | 80 | 19:00
33 | Bogura | 183 | 19:30 | 104 | MI_Cement | 17.6 | 00:00 | 175 | Shahjibazar | 126 | 18:30
34 | Borhanuddin | 82 | 22:00 | 105 | Madanganj | 44 | 22:00 | 176 | Shahmirpur | 64 | 18:00
35 | Brahmanbaria | 142 | 00:00 | 106 | Madaripur | 120 | 21:00 | 177 | Shariatpur | 106 | 21:00
36 | Cantonment | 138 | 13:00 | 107 | Madartek | 88 | 00:00 | 178 | Sherpur | 144 | 18:30
37 | Chandina | 34 | 12:00 | 108 | Madunaghat | 59 | 18:30 | 179 | Shikalbaha | 24 | 00:00
38 | Chandpur | 86 | 20:00 | 109 | Magura | 66 | 21:00 | 180 | Shitalakhya | 82.6 | 15:00
39 | Chandraghona | 32 | 19:30 | 110 | Mahasthangarh | 74 | 19:00 | 181 | Sholosohor | 51 | 18:30
40 | Chapai | 76 | 20:00 | 111 | Maijdee | 41 | 00:00 | 182 | Shomvuganj | 37 | 00:00
41 | Charfasson | 33 | 22:00 | 112 | Manikganj | 145 | 19:30 | 183 | Shyampur | 162 | 14:00
42 | Charsaidpur | 38 | 18:30 | 113 | Maniknagar | 94 | 13:00 | 184 | Siddhirganj | 131 | 13:00
43 | Chauddagram | 77 | 19:30 | 114 | Matarbari | 56 | 02:00 | 185 | Sirajganj | 114 | 18:30
44 | Chhatak | 39 | 03:00 | 115 | Matuail | 80 | 10:00 | 186 | Sitakunda | 36 | 19:00
45 | Chowmuhani | 168 | 19:30 | 116 | Metrorail_Motijheel | 21 | 09:00 | 187 | Sonargaon | 139 | 18:30
46 | Chuadanga | 121 | 19:30 | 117 | Metrorail_Uttara | 9 | 12:00 | 188 | Sreemongol | 81 | 03:00
47 | Coxsbazar | 153 | 20:00 | 118 | Millgate | 101 | 15:00 | 189 | Sreepur | 142 | 19:30
48 | Cumilla(N) | 148 | 22:00 | 119 | Mirpur | 149 | 15:00 | 190 | Srinagar | 49.6 | 00:00
49 | Cumilla(S) | 157 | 14:00 | 120 | Mirsorai | 38 | 12:00 | 191 | Sunamganj | 54 | 04:00
50 | Daganbhuiyan | 37 | 19:30 | 121 | Mirzapur | 51 | 21:00 | 192 | Sylhet | 120 | 19:30
51 | Daudkandi | 128 | 00:00 | 122 | Mithapukur | 68 | 19:00 | 193 | Sylhet_(South) | 69 | 18:00
52 | DhakaUniversity | 102 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 110 | 23:00 | 124 | Mogbazar | 73.6 | 13:00 | 195 | Tangail | 182 | 20:00
54 | Dhanmondi | 123 | 13:00 | 125 | Mongla | 45 | 18:00 | 196 | Taraganj | 36 | 21:00
55 | Dohazari | 119 | 20:00 | 126 | Monirampur | 25 | 21:00 | 197 | Tasnim | 46 | 02:00
56 | Faridpur | 181 | 21:00 | 127 | Motijheel | 58 | 13:00 | 198 | Thakurgaon | 99 | 18:30
57 | Fatullah | 125 | 12:00 | 128 | Muktagacha | 35 | 17:00 | 199 | Tongi | 170 | 18:30
58 | Fenchuganj | 41 | 18:30 | 129 | Munshiganj | 117 | 00:00 | 200 | Ullahpara | 39 | 19:00
59 | Feni | 114 | 00:00 | 130 | Muradnagar | 60 | 20:00 | 201 | Ullon | 37 | 00:00
60 | GPH | 7 | 17:00 | 131 | Mymensingh | 161 | 18:00 | 202 | Uttara | 100 | 13:00
61 | Ghatail | 89 | 22:00 | 132 | Nabinagar | 110 | 14:00 | 203 | UttaraNew | 59 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 120 | 19:00 | 204 | Zigatola | 76 | 13:00
63 | Ghorashal-230 | 105 | 15:00 | 134 | Narail | 61 | 21:00
64 | Goalpara | 42 | 23:00 | 135 | Narinda | 76 | 13:00
65 | Gollamari | 106 | 23:00 | 136 | Narshingdi | 188 | 00:00
66 | Gopalganj | 123 | 22:00 | 137 | Natore | 159 | 19:00
67 | Gulshan | 126 | 12:00 | 138 | Nawabganj | 48.9 | 22:00
68 | Halishahar | 146 | 16:00 | 139 | Netrakona | 127 | 01:00
69 | HaripurSBU | 126 | 07:00 | 140 | New | 88 | 12:00
70 | Hasnabad | 107 | 20:00 | 141 | Niamatpur | 78 | 19:00
71 | Hathazari | 102 | 18:30 | 142 | Noapara | 42 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15033.03 | 186 |  | 15227.03
1:00 | 14596.97 | 418 |  | 15033.97
2:00 | 14260 | 154 |  | 14421
3:00 | 13857.6 | 0 |  | 13857.6
4:00 | 13425.2 | 0 |  | 13425.2
5:00 | 12929.09 | 0 |  | 12929.09
6:00 | 12681.58 | 0 |  | 12681.58
7:00 | 12949.33 | 0 |  | 12949.33
8:00 | 13222.83 | 0 |  | 13222.83
9:00 | 13479.13 | 0 |  | 13479.13
10:00 | 13933.22 | 0 |  | 13933.22
11:00 | 14305.56 | 0 |  | 14305.56
12:00 | 14656.85 | 820 |  | 15513.85
13:00 | 14647.12 | 1148 |  | 15847.12
14:00 | 14287.66 | 1412 |  | 15763.66
15:00 | 14356.51 | 1705 |  | 16138.51
16:00 | 14431.62 | 1479 |  | 15977.62
17:00 | 14550.24 | 975 |  | 15569.24
18:00 | 15590.64 | 1656 |  | 17321.64
19:00 | 16132.95 | 820 |  | 16989.95
19:30 | 16353.48 | 746 |  | 17133.48
20:00 | 16294.87 | 492 |  | 16808.87
21:00 | 16088.63 | 255 |  | 16354.63
22:00 | 15937.88 | 224 |  | 16171.88
23:00 | 15735.6 | 157 |  | 15899.6
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9140.62 | 5892.41 | 15033.03 | DAILY GENERATION CURVE
00:30 | 9089.62 | 5725.38 | 14815
01:00 | 9038.62 | 5558.35 | 14596.97 | 17-10-2026
01:30 | 8945.12 | 5483.365 | 14428.485
02:00 | 8851.62 | 5408.38 | 14260
02:30 | 8647.62 | 5411.18 | 14058.8
03:00 | 8443.62 | 5413.98 | 13857.6
03:30 | 8242.16 | 5399.24 | 13641.4
04:00 | 8040.7 | 5384.5 | 13425.2
04:30 | 7872.35 | 5304.795 | 13177.145
05:00 | 7704 | 5225.09 | 12929.09
05:30 | 7608.695 | 5196.64 | 12805.335
06:00 | 7513.39 | 5168.19 | 12681.58
06:30 | 7577.645 | 5237.81 | 12815.455
07:00 | 7641.9 | 5307.43 | 12949.33
07:30 | 7704.015 | 5382.065 | 13086.08
08:00 | 7766.13 | 5456.7 | 13222.83
08:30 | 7821.475 | 5529.505 | 13350.98
09:00 | 7876.82 | 5602.31 | 13479.13
09:30 | 8044.42 | 5661.755 | 13706.175
10:00 | 8212.02 | 5721.2 | 13933.22
10:30 | 8353.44 | 5765.95 | 14119.39
11:00 | 8494.86 | 5810.7 | 14305.56
11:30 | 8692.32 | 5788.885 | 14481.205
12:00 | 8889.78 | 5767.07 | 14656.85
12:30 | 8907.14 | 5744.845 | 14651.985
13:00 | 8924.5 | 5722.62 | 14647.12
13:30 | 8852.67 | 5614.72 | 14467.39
14:00 | 8780.84 | 5506.82 | 14287.66
14:30 | 8767.56 | 5554.525 | 14322.085
15:00 | 8754.28 | 5602.23 | 14356.51
15:30 | 8803.105 | 5590.96 | 14394.065
16:00 | 8851.93 | 5579.69 | 14431.62
16:30 | 8793.955 | 5696.975 | 14490.93
17:00 | 8735.98 | 5814.26 | 14550.24
17:30 | 9091.13 | 5979.31 | 15070.44
18:00 | 9446.28 | 6144.36 | 15590.64
18:30 | 9604.88 | 6256.915 | 15861.795
19:00 | 9763.48 | 6369.47 | 16132.95
19:30 | 10041.48 | 6312 | 16353.48
20:00 | 9896.48 | 6398.39 | 16294.87
20:30 | 9828.3 | 6363.45 | 16191.75 |  | Executive Engineer
21:00 | 9760.12 | 6328.51 | 16088.63 |  | Network Operation Division
21:30 | 9652.12 | 6361.135 | 16013.255
22:00 | 9544.12 | 6393.76 | 15937.88
22:30 | 9510.62 | 6326.12 | 15836.74
23:00 | 9477.12 | 6258.48 | 15735.6

## En-Curve
QF-LDC-12
Date | 17-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3379 | 1560 | 724 | 0 | 68 | 1379.21 | 221 | 4682 | 0 | 569.42 | 2450.4 | 0 | 0 | 0 | 186 | DAILY ENERGY CURVE
00:30 | 3380 | 1539 | 724 | 0 | 66 | 1286.08 | 201.5 | 4587.1 | 0 | 531.92 | 2499.4 | 0 | 0 | 0 | 302 | 17-10-2026
01:00 | 3381 | 1518 | 724 | 0 | 64 | 1192.95 | 182 | 4492.2 | 0 | 494.42 | 2548.4 | 0 | 0 | 0 | 418
01:30 | 3389.5 | 1503.5 | 724 | 0 | 63 | 1104.965 | 177 | 4412.7 | 0 | 486.92 | 2566.9 | 0 | 0 | 0 | 286 | Energy Generated | 349.2942 |  | MKWHr
02:00 | 3398 | 1489 | 724 | 0 | 62 | 1016.98 | 172 | 4333.2 | 0 | 479.42 | 2585.4 | 0 | 0 | 0 | 154 | Energy not Served | 11.901 |  | MKWHr
02:30 | 3323 | 1511 | 746 | 0 | 62 | 1019.78 | 176 | 4333.7 | 0 | 464.92 | 2422.4 | 0 | 0 | 0 | 77 | Total Energy Requirement | 361.1952 |  | MKWHr
03:00 | 3248 | 1533 | 768 | 0 | 62 | 1022.58 | 180 | 4334.2 | 0 | 450.42 | 2259.4 | 0 | 0 | 0 | 0
03:30 | 3248.5 | 1526.25 | 829.5 | 0 | 61 | 1017.84 | 180 | 4335.2 | 0 | 382.71 | 2060.4 | 0 | 0 | 0 | 0
04:00 | 3249 | 1519.5 | 891 | 0 | 60 | 1013.1 | 180 | 4336.2 | 0 | 315 | 1861.4 | 0 | 0 | 0 | 0
04:30 | 3266 | 1543.75 | 890.5 | 0 | 60 | 1017.095 | 179.5 | 4306.1 | 0 | 244 | 1670.2 | 0 | 0 | 0 | 0
05:00 | 3283 | 1568 | 890 | 0 | 60 | 1021.09 | 179 | 4276 | 0 | 173 | 1479 | 0 | 0 | 0 | 0
05:30 | 3278.5 | 1600 | 890 | 0 | 57 | 1018.14 | 179 | 4278 | 0.015 | 173.5 | 1331.18 | 0 | 0 | 0 | 0
06:00 | 3274 | 1632 | 890 | 0 | 54 | 1015.19 | 179 | 4280 | 0.03 | 174 | 1183.36 | 0 | 0 | 0 | 0
06:30 | 3275 | 1672.5 | 819.5 | 0 | 54 | 1021.98 | 178.5 | 4317.6 | 44.015 | 199 | 1233.36 | 0 | 0 | 0 | 0
07:00 | 3276 | 1713 | 749 | 0 | 54 | 1028.77 | 178 | 4355.2 | 88 | 224 | 1283.36 | 0 | 0 | 0 | 0
07:30 | 3276 | 1646.25 | 749 | 0 | 56 | 1026.755 | 179 | 4338.7 | 173.015 | 227.5 | 1413.86 | 0 | 0 | 0 | 0
08:00 | 3276 | 1579.5 | 749 | 0 | 58 | 1024.74 | 180 | 4322.2 | 258.03 | 231 | 1544.36 | 0 | 0 | 0 | 0
08:30 | 3225.5 | 1546.25 | 819.5 | 0 | 59 | 1020.76 | 180.5 | 4312.7 | 349.81 | 231.5 | 1605.46 | 0 | 0 | 0 | 0
09:00 | 3175 | 1513 | 890 | 0 | 60 | 1016.78 | 181 | 4303.2 | 441.59 | 232 | 1666.56 | 0 | 0 | 0 | 0
09:30 | 3166 | 1575.5 | 890 | 0 | 60 | 1018.925 | 181 | 4320.6 | 500.09 | 270.5 | 1723.56 | 0 | 0 | 0 | 0
10:00 | 3157 | 1638 | 890 | 0 | 60 | 1021.07 | 181 | 4338 | 558.59 | 309 | 1780.56 | 0 | 0 | 0 | 0
10:30 | 3148.5 | 1667 | 890.5 | 0 | 64 | 1016.19 | 181 | 4351 | 581.14 | 336.5 | 1883.56 | 0 | 0 | 0 | 0
11:00 | 3140 | 1696 | 891 | 0 | 68 | 1011.31 | 181 | 4364 | 603.69 | 364 | 1986.56 | 0 | 0 | 0 | 0
11:30 | 3133.5 | 1666.5 | 891 | 0 | 69 | 1009.055 | 181.5 | 4365.5 | 600.88 | 394.71 | 2169.56 | 0 | 0 | 0 | 410
12:00 | 3127 | 1637 | 891 | 0 | 70 | 1006.8 | 182 | 4367 | 598.07 | 425.42 | 2352.56 | 0 | 0 | 0 | 820
12:30 | 3109.5 | 1632 | 890.5 | 0 | 70 | 1009.175 | 182 | 4367 | 586.58 | 398.17 | 2407.06 | 0 | 0 | 0 | 984
13:00 | 3092 | 1627 | 890 | 0 | 70 | 1011.55 | 182 | 4367 | 575.09 | 370.92 | 2461.56 | 0 | 0 | 0 | 1148
13:30 | 3080 | 1605.5 | 875 | 0 | 73 | 1010.945 | 182 | 4359.6 | 493.365 | 369.92 | 2418.06 | 0 | 0 | 0 | 1280
14:00 | 3068 | 1584 | 860 | 0 | 76 | 1010.34 | 182 | 4352.2 | 411.64 | 368.92 | 2374.56 | 0 | 0 | 0 | 1412
14:30 | 3042 | 1599.5 | 875.5 | 0 | 76 | 1013.295 | 182 | 4361.7 | 376.61 | 371.92 | 2423.56 | 0 | 0 | 0 | 1558.5
15:00 | 3016 | 1615 | 891 | 0 | 76 | 1016.25 | 182 | 4371.2 | 341.58 | 374.92 | 2472.56 | 0 | 0 | 0 | 1705
15:30 | 3019 | 1649 | 890.5 | 0 | 75 | 1015.08 | 182 | 4371.2 | 256.805 | 380.42 | 2555.06 | 0 | 0 | 0 | 1592
16:00 | 3022 | 1683 | 890 | 0 | 74 | 1013.91 | 182 | 4371.2 | 172.03 | 385.92 | 2637.56 | 0 | 0 | 0 | 1479
16:30 | 2968.5 | 1591 | 877 | 0 | 71 | 1101.925 | 181 | 4369.7 | 98.575 | 447.92 | 2784.31 | 0 | 0 | 0 | 1227
17:00 | 2915 | 1499 | 864 | 0 | 68 | 1189.94 | 180 | 4368.2 | 25.12 | 509.92 | 2931.06 | 0 | 0 | 0 | 975
17:30 | 2972 | 1520 | 852.5 | 0 | 74 | 1305.05 | 180 | 4497.6 | 12.56 | 630.67 | 3026.06 | 0 | 0 | 0 | 1315.5
18:00 | 3029 | 1541 | 841 | 0 | 80 | 1420.16 | 180 | 4627 | 0 | 751.42 | 3121.06 | 0 | 0 | 0 | 1656
18:30 | 2991.5 | 1542.5 | 806 | 0 | 78 | 1414.115 | 200 | 4829.1 | 0 | 782.42 | 3158.16 | 60 | 0 | 0 | 1238
19:00 | 2954 | 1544 | 771 | 0 | 76 | 1408.07 | 220 | 5031.2 | 0 | 813.42 | 3195.26 | 120 | 0 | 0 | 820
19:30 | 2942 | 1730 | 777 | 0 | 76 | 1428.8 | 220 | 5132 | 0 | 817.42 | 3230.26 | 0 | 0 | 0 | 746
20:00 | 2931 | 1587 | 778 | 0 | 74 | 1420.59 | 218 | 5250.6 | 0 | 840.42 | 3195.26 | 0 | 0 | 0 | 492
20:30 | 3015.5 | 1658 | 802 | 0 | 73 | 1418.75 | 218.5 | 5255.1 | 0 | 837.42 | 2913.48 | 0 | 0 | 0 | 373.5
21:00 | 3100 | 1729 | 826 | 0 | 72 | 1416.91 | 219 | 5259.6 | 0 | 834.42 | 2631.7 | 0 | 0 | 0 | 255
21:30 | 3123 | 1663 | 826 | 0 | 71 | 1418.535 | 219.5 | 5256.1 | 0 | 809.42 | 2626.7 | 0 | 0 | 0 | 239.5
22:00 | 3146 | 1597 | 826 | 0 | 70 | 1420.16 | 220 | 5252.6 | 0 | 784.42 | 2621.7 | 0 | 0 | 0 | 224
22:30 | 3105.5 | 1636 | 825.5 | 0 | 70 | 1418.52 | 220.5 | 5229.1 | 0 | 776.42 | 2555.2 | 0 | 0 | 0 | 190.5
23:00 | 3065 | 1675 | 825 | 0 | 70 | 1416.88 | 221 | 5205.6 | 0 | 768.42 | 2488.7 | 0 | 0 | 0 | 157
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 17-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 69 | 0 | 280 | 104 | 886 | 342 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 63 | 9 | 240 | 110 | 914 | 372
2:00 | 56 | 8 | 208 | 110 | 866 | 332 |  | Import | 0
3:00 | 83 | 10 | 272 | 108 | 970 | 344
4:00 | 98 | 0 | 316 | 106 | 1054 | 334 | Ishurdi-Ghorashal Ckt-2 | Export | 2823563.64
5:00 | 98 | 0 | 298 | 92 | 1048 | 368
6:00 | 113 | 9 | 302 | 88 | 1140 | 424 |  | Import | 0
7:00 | 99 | 32 | 226 | 104 | 998 | 416
8:00 | 117 | 38 | 270 | 110 | 1128 | 432 | Sirajganj-Sreepur Ckt-1 | Export | 1772000
9:00 | 152 | 30 | 366 | 108 | 1284 | 492
10:00 | 164 | 36 | 404 | 120 | 1316 | 528 |  | Import | 0
11:00 | 172 | 38 | 424 | 140 | 1252 | 534
12:00 | 148 | 35 | 350 | 124 | 1260 | 564 | Sirajganj-Sreepur Ckt-2 | Export | 1779000
13:00 | 152 | 36 | 320 | 126 | 1240 | 540
14:00 | 131 | 31 | 300 | 114 | 1172 | 532 |  | Import | 0
15:00 | 151 | 37 | 300 | 112 | 1186 | 570
16:00 | 156 | 51 | 300 | 118 | 1222 | 596 | Gopalganj-Aminbazar Ckt-1 | Export | 13320000
17:00 | 158 | 51 | 340 | 116 | 1354 | 624
18:00 | 122 | 36 | 310 | 146 | 978 | 528 |  | Import | 0
18:30 | 128 | 58 | 340 | 174 | 1078 | 562
19:00 | 108 | 47 | 260 | 142 | 982 | 556 | Gopalganj-Aminbazar Ckt-2 | Export | 13360000
19:30 | 93 | 44 | 250 | 164 | 976 | 524
20:00 | 96 | 45 | 260 | 160 | 998 | 538 |  | Import | 0
21:00 | 90 | 30 | 220 | 130 | 980 | 482
22:00 | 97 | 32 | 240 | 130 | 1018 | 466 |  | Total Export | 33054563.64
23:00 | 101 | 34 | 260 | 130 | 1008 | 454 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 368 | 21:00 | Madunaghat | 407 | 02:00 | 395 | 21:00
Amtali | 414 | 03:00 | 407 | 21:00 | Meghnaghat | 398 | 02:00 | 378 | 19:30
Ashuganj | 413 | 2:00 | 383 | 19:30 | Mirsorai | 410 | 02:00 | 390 | 21:00
Bhulta | 404 | 02:00 | 377 | 19:30 | Payra | 415 | 02:00 | 408 | 22:00
Bibiana | 390 | 02:00 | 381 | 18:30 | Rahanpur | 413 | 03:00 | 394 | 21:00
BIPTC | 403 | 02:00 | 393 | 12:00 | Rampal | 400 | 08:00 | 386 | 22:00
Bogura | 406 | 03:00 | 381 | 21:00
Gopalganj | 398 | 02:00 | 382 | 21:00
Kaliakoir | 382 | 02:00 | 363 | 21:00
Korerhat | 408 | 02:00 | 388 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 02:00 | 221 | 22:00 | Hasnabad | 230 | 06:00 | 219 | 11:00
AKSML | 241 | 01:00 | 232 | 21:00 | Hathazari | 238 | 14:00 | 232 | 21:00
Aminbazar | 235 | 02:00 | 223 | 18:00 | Ishurdi | 236 | 02:00 | 222 | 21:00
Ashuganj | 231 | 04:00 | 220 | 19:30 | Jhenaidah | 227 | 03:00 | 210 | 21:00
Ashuganj-400 | 231 | 4:00 | 220 | 20:00 | Kachua | 232 | 02:00 | 221 | 21:00
Baghabari | 234 | 01:00 | 222 | 21:00 | Kaliakoir | 238 | 04:00 | 221 | 18:30
Barapukuria | 238 | 02:00 | 219 | 21:00 | Keranigonj | 234 | 02:00 | 218 | 19:30
Barapukuria-230 | 238 | 2:00 | 218 | 21:00 | Khulna(S) | 229 | 05:00 | 216 | 21:00
Barapukuria(N) | 240 | 03:00 | 220 | 21:00 | Korerhat | 232 | 02:00 | 221 | 21:00
Barishal | 226 | 04:00 | 216 | 12:00 | Madunaghat | 241 | 01:00 | 235 | 23:00
Bheramara | 234 | 01:00 | 221 | 21:00 | Madunaghat-400 | 243 | 02:00 | 237 | 11:00
Bhulta | 230 | 02:00 | 215 | 19:30 | Maniknagar | 228 | 04:00 | 214 | 19:30
Bibiana | 224 | 08:00 | 217 | 19:30 | Meghnaghat | 236 | 03:00 | 223 | 12:00
BIPTC | 236 | 01:00 | 221 | 21:00 | Meghnaghat-400 | 231 | 02:00 | 218 | 19:30
Birulia | 237 | 02:00 | 221 | 19:30 | Mirsorai | 232 | 01:00 | 221 | 21:00
Bogura | 241 | 02:00 | 227 | 21:00 | Naogaon | 229 | 03:00 | 204 | 22:00
Bogura-400 | 241 | 03:00 | 226 | 21:00 | Purbasadipur | 238 | 03:00 | 218 | 21:00
Borhanuddin | 227 | 20:00 | 216 | 11:00 | Rajshahi | 233 | 02:00 | 219 | 22:00
BSRM | 233 | 02:00 | 222 | 21:00 | Rampal | 229 | 08:00 | 217 | 21:00
Charfasson | 226 | 08:00 | 215 | 18:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 232 | 02:00 | 221 | 21:00 | Rampura | 230 | 02:00 | 214 | 13:00
Cumilla(N) | 226 | 05:00 | 217 | 19:30 | Shikalbaha | 241 | 01:00 | 235 | 10:00
Faridpur | 225 | 19:30 | 216 | 18:30 | Shyampur | 232 | 02:00 | 217 | 19:30
Fenchuganj | 226 | 06:00 | 217 | 22:00 | Siddhirganj | 230 | 05:00 | 226 | 21:00
Feni | 230 | 02:00 | 218 | 21:00 | Sirajgonj | 239 | 03:00 | 228 | 21:00
Ghorashal | 230 | 00:00 | 220 | 22:00 | Sreepur | 228 | 01:00 | 216 | 19:30
Ghorashal-230 | 226 | 02:00 | 204 | 18:30 | Tongi | 225 | 00:00 | 206 | 18:30
Gopalganj | 230 | 20:00 | 217 | 18:30
GPH | 239 | 01:00 | 229 | 18:30
Haripur | 230 | 02:00 | 216 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 02:00 | 126 | 12:00 | Madanganj | 137 | 00:00 | 132 | 11:00
Agargaon | 139 | 07:00 | 127 | 12:00 | Madaripur | 131 | 01:00 | 126 | 22:00
Agrabad | 138 | 01:00 | 133 | 10:00 | Madartek | 137 | 04:00 | 125 | 12:00
AKS | 135 | 03:00 | 132 | 10:00 | Madunaghat | 140 | 16:00 | 136 | 21:00
Aminbazar | 135 | 02:00 | 127 | 10:00 | Magura | 134 | 01:00 | 122 | 21:00
Amnura | 133 | 02:00 | 127 | 23:00 | Mahasthangarh | 137 | 01:00 | 127 | 21:00
Araihazar | 127 | 06:00 | 119 | 18:30 | Maijdee | 130 | 02:00 | 123 | 22:00
Ashuganj | 136 | 06:00 | 128 | 19:30 | Manikganj | 132 | 00:00 | 123 | 17:00
Ashuganj-230 | 138 | 03:00 | 132 | 18:30 | Maniknagar | 138 | 06:00 | 126 | 13:00
Bagerhat | 127 | 07:00 | 118 | 21:00 | Matarbari | 120 | 01:00 | 108 | 21:00
Bajitpur | 131 | 14:00 | 123 | 19:30 | Matuail | 139 | 03:00 | 132 | 11:00
Bakerganj | 133 | 17:00 | 129 | 11:00 | Metrorail_Motijheel | 138 | 06:00 | 126 | 13:00
Bakulia | 139 | 18:00 | 134 | 00:00 | Metrorail_Uttara | 136 | 03:00 | 122 | 16:00
Banani | 137 | 02:00 | 124 | 13:00 | Millgate | 139 | 01:00 | 123 | 16:00
Bangabhaban | 138 | 02:00 | 127 | 12:00 | Mirpur | 135 | 01:00 | 126 | 11:00
Barapukuria | 141 | 02:00 | 126 | 21:00 | Mirzapur | 134 | 01:00 | 126 | 19:30
Barguna | 133 | 17:00 | 129 | 12:00 | Mithapukur | 137 | 02:00 | 124 | 21:00
Barishal | 132 | 20:00 | 126 | 13:00 | MI_Cement | 137 | 04:00 | 125 | 12:00
Barishal-230 | 133 | 20:00 | 126 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 14:00 | 134 | 10:00 | Mogbazar | 140 | 03:00 | 126 | 13:00
Baroirhat | 133 | 07:00 | 130 | 19:30 | Mongla | 127 | 06:00 | 117 | 21:00
Bashundhara | 139 | 01:00 | 122 | 16:00 | Monirampur | 130 | 08:00 | 114 | 21:00
BashundharaCement | 137 | 00:00 | 132 | 12:00 | Motijheel | 138 | 02:00 | 127 | 12:00
Beanibazar | 125 | 06:00 | 117 | 19:30 | Muktagacha | 131 | 09:00 | 119 | 06:00
Benapole | 131 | 03:00 | 115 | 21:00 | Munshiganj | 138 | 02:00 | 130 | 11:00
Bhaluka | 131 | 03:00 | 122 | 19:30 | Muradnagar | 126 | 02:00 | 117 | 19:30
Bhandaria | 129 | 08:00 | 122 | 18:30 | Mymensingh | 129 | 18:00 | 116 | 06:00
Bhangura | 135 | 03:00 | 127 | 21:00 | Nabinagar | 136 | 03:00 | 123 | 16:00
Bheramara | 138 | 01:00 | 129 | 21:00 | Naogaon | 138 | 03:00 | 124 | 21:00
Bheramara(GK) | 137 | 01:00 | 128 | 21:00 | Narail | 134 | 05:00 | 119 | 21:00
Bhulta | 127 | 03:00 | 120 | 19:30 | Narinda | 138 | 6:00 | 126 | 13:00
Bhulta-400 | 129 | 02:00 | 120 | 18:30 | Narshingdi | 133 | 04:00 | 118 | 19:30
Birulia | 138 | 01:00 | 130 | 19:30 | Natore | 135 | 01:00 | 126 | 21:00
Bog-Sherpur | 137 | 01:00 | 128 | 21:00 | Nawabganj | 138 | 05:00 | 128 | 13:00
Bogura | 139 | 08:00 | 130 | 21:00 | Netrakona | 122 | 06:00 | 112 | 19:30
Bogura-230 | 140 | 02:00 | 131 | 21:00 | New | 140 | 01:00 | 124 | 15:00
Brahmanbaria | 134 | 07:00 | 126 | 19:30 | Niamatpur | 134 | 01:00 | 126 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 137 | 02:00 | 126 | 13:00 | Noapara | 130 | 05:00 | 121 | 21:00
Chandina | 131 | 02:00 | 124 | 19:30 | Pabna | 135 | 01:00 | 126 | 21:00
Chandpur | 134 | 08:00 | 127 | 21:00 | Palashbari | 133 | 01:00 | 122 | 21:00
Chandraghona | 139 | 18:00 | 136 | 11:00 | Panchagarh | 142 | 02:00 | 132 | 18:00
Chapai | 133 | 08:00 | 129 | 00:00 | Patiya | 136 | 01:00 | 131 | 23:00
Charsaidpur | 139 | 03:00 | 131 | 12:00 | Patnitala | 134 | 05:00 | 125 | 21:00
Chauddagram | 132 | 02:00 | 124 | 21:00 | Patuakhali | 134 | 20:00 | 129 | 15:00
Chhatak | 121 | 06:00 | 112 | 22:00 | Payra | 135 | 20:00 | 134 | 00:00
Chowmuhani | 130 | 02:00 | 124 | 21:00 | PHP | 134 | 01:00 | 127 | 21:00
Chuadanga | 133 | 01:00 | 121 | 21:00 | Postogola | 137 | 02:00 | 128 | 11:00
Coxsbazar | 121 | 07:00 | 106 | 21:00 | Pubail | 133 | 03:00 | 121 | 16:00
Cumilla(N) | 130 | 05:00 | 124 | 19:30 | Purbachal | 137 | 01:00 | 125 | 13:00
Cumilla(S) | 133 | 05:00 | 124 | 21:00 | Purbasadipur | 138 | 02:00 | 127 | 21:00
Daganbhuiyan | 133 | 02:00 | 125 | 21:00 | Rahanpur | 137 | 06:00 | 131 | 21:00
Daudkandi | 124 | 06:00 | 113 | 19:30 | Rahanpur-400 | 138 | 03:00 | 131 | 21:00
DhakaUniversity | 137 | 01:00 | 126 | 13:00 | Rahim | 140 | 04:00 | 132 | 12:00
Dhamrai | 135 | 00:00 | 124 | 16:00 | Rajbari | 128 | 06:00 | 123 | 11:00
Dhanmondi | 139 | 04:00 | 131 | 13:00 | Rajendrapur | 134 | 02:00 | 124 | 19:30
Dohazari | 132 | 01:00 | 125 | 20:00 | Rajshahi | 133 | 08:00 | 125 | 21:00
Faridpur | 130 | 08:00 | 125 | 18:30 | Rajshahi-230 | 134 | 02:00 | 126 | 21:00
Fatullah | 139 | 02:00 | 127 | 11:00 | Ramganj | 130 | 17:00 | 122 | 21:00
Fenchuganj | 133 | 06:00 | 127 | 18:30 | Rampur | 138 | 01:00 | 133 | 12:00
Feni | 131 | 07:00 | 125 | 21:00 | Rampura | 137 | 02:00 | 126 | 12:00
Feni-230 | 134 | 02:00 | 126 | 21:00 | Rangamati | 138 | 01:00 | 135 | 10:00
Ghatail | 129 | 09:00 | 121 | 17:00 | Rangpur | 135 | 01:00 | 122 | 21:00
Ghorashal | 133 | 00:00 | 123 | 22:00 | Ruppur | 137 | 01:00 | 129 | 21:00
Goalpara | 133 | 08:00 | 123 | 21:00 | Saidpur | 135 | 03:00 | 126 | 21:00
Gollamari | 132 | 01:00 | 123 | 22:00 | Santhia | 135 | 01:00 | 128 | 21:00
Gopalganj | 131 | 01:00 | 125 | 11:00 | Satkhira | 131 | 08:00 | 115 | 21:00
Gopalganj-400 | 133 | 01:00 | 129 | 11:00 | Satmasjid | 137 | 03:00 | 126 | 13:00
Gulshan | 137 | 05:00 | 125 | 13:00 | Savar | 134 | 00:00 | 121 | 23:00
Halishahar | 139 | 01:00 | 134 | 10:00 | SevenRings | 135 | 01:00 | 122 | 22:00
Haripur | 140 | 02:00 | 132 | 13:00 | ShahCement | 139 | 01:00 | 131 | 12:00
HaripurSBU | 140 | 02:00 | 132 | 11:00 | Shahjadpur | 134 | 01:00 | 130 | 21:00
Hasnabad | 137 | 07:00 | 128 | 12:00 | Shahjibazar | 133 | 07:00 | 125 | 18:30
Hathazari | 139 | 17:00 | 135 | 21:00 | Shahmirpur | 137 | 16:00 | 134 | 10:00
Hatirjheel | 138 | 04:00 | 125 | 13:00 | Shariatpur | 129 | 02:00 | 125 | 00:00
Ishurdi | 138 | 01:00 | 130 | 21:00 | Sherpur | 132 | 10:00 | 112 | 06:00
Jaldhaka | 132 | 05:00 | 123 | 01:00 | Shikalbaha | 128 | 01:00 | 125 | 16:00
Jamalpur | 134 | 09:00 | 118 | 07:00 | Shikalbaha-230 | 140 | 01:00 | 135 | 00:00
Jashore | 133 | 03:00 | 117 | 21:00 | Shitalakhya | 137 | 04:00 | 125 | 12:00
Jhenaidah | 136 | 01:00 | 125 | 21:00 | Sholosohor | 139 | 01:00 | 134 | 10:00
Jhenaidah-230 | 137 | 01:00 | 125 | 21:00 | Shomvuganj | 127 | 04:00 | 116 | 20:00
Joydebpur | 131 | 02:00 | 119 | 16:00 | Shyampur | 137 | 01:00 | 128 | 12:00
Joypurhat | 134 | 09:00 | 125 | 21:00 | Shyampur-230 | 140 | 02:00 | 131 | 11:00
Juldah | 139 | 18:00 | 133 | 10:00 | Siddhirganj | 140 | 02:00 | 132 | 12:00
Kabirpur | 139 | 01:00 | 119 | 16:00 | Sirajganj | 134 | 02:00 | 124 | 21:00
Kachua | 132 | 02:00 | 125 | 23:00 | Sitakunda | 138 | 01:00 | 134 | 21:00
Kaliakoir | 140 | 01:00 | 132 | 20:00 | Sonargaon | 136 | 02:00 | 131 | 12:00
Kaliganj | 137 | 04:00 | 125 | 21:00 | Sreemongol | 132 | 07:00 | 123 | 21:00
Kallyanpur | 135 | 01:00 | 127 | 12:00 | Sreepur | 135 | 03:00 | 126 | 19:30
Kalurghat | 140 | 02:00 | 136 | 10:00 | Srinagar | 137 | 04:00 | 128 | 19:30
Kamrangirchar | 137 | 07:00 | 124 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaptai | 140 | 1:00 | 136 | 9:00 | Sunamganj | 119 | 09:00 | 110 | 22:00
Kasba | 125 | 02:00 | 118 | 19:30 | Sylhet | 125 | 06:00 | 117 | 23:00
Kazla | 138 | 04:00 | 127 | 12:00 | Sylhet_(South) | 126 | 07:00 | 118 | 22:00
Keranigonj | 139 | 02:00 | 129 | 13:00 | Tangail | 130 | 09:00 | 122 | 19:30
Khagrachori | 138 | 02:00 | 134 | 10:00 | Taraganj | 135 | 01:00 | 125 | 21:00
Khulna | 132 | 04:00 | 121 | 21:00 | Tasnim | 138 | 02:00 | 130 | 13:00
Khulna(S) | 133 | 08:00 | 124 | 21:00 | Thakurgaon | 142 | 02:00 | 132 | 18:00
Khulshi | 136 | 03:00 | 132 | 10:00 | TK | 140 | 16:00 | 136 | 10:00
Kishoreganj | 131 | 14:00 | 121 | 18:30 | Tongi | 138 | 00:00 | 125 | 18:30
Kodda | 138 | 02:00 | 121 | 22:00 | Ullahpara | 134 | 01:00 | 126 | 21:00
Korerhat | 136 | 01:00 | 130 | 20:00 | Ullon | 137 | 04:00 | 126 | 12:00
KSRM | 138 | 17:00 | 134 | 10:00 | Uttara | 140 | 02:00 | 118 | 19:00
Kulaura | 132 | 08:00 | 126 | 18:30 | UttaraNew | 136 | 03:00 | 122 | 16:00
Kurigram | 130 | 01:00 | 118 | 21:00 | Zigatola | 138 | 01:00 | 124 | 08:00
Kushtia | 136 | 05:00 | 126 | 21:00
Laksam | 132 | 02:00 | 124 | 22:00
Lakshmipur | 128 | 01:00 | 122 | 21:00
Lalbag | 139 | 07:00 | 128 | 16:00
Lalmonirhat | 130 | 01:00 | 120 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division