## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-10-2026 | during | 19-10-2026 | during | 19-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 355 | 412 | 412 | 400 | 400 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 22 | 40 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 320 | 335 | 335 | 318 | 318 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 75 | 126 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5.5 | 5.5 | 24.75 | 24.75 | 10 | 10 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 24 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 97 | 145 | 300 | 300 | 98 | 98 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 117 | 127 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 108 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 38 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 550 | 435 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 520 | 530 | 583 | 583 | 450 | 450 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2577.92 | 2646.92 | 5558.55 | 5528.55 | 2609.42 | 2796.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 17 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 218 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 88 | 51 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 40 | 24 | 54 | 24 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 12 | 58 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.36 | 0 | 3.15 | 0 | 3.15 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 209 | 300 | 300 | 52 | 214 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 69 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 111 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 10 | 16 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 600 | 1029 | 1224 | 1224 | 600 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1080 | 1080 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2551.36 | 3382.86 | 4105.11 | 4181.96 | 2821.15 | 3844.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 215 | 216 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 347 | 310 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 290 | 220 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 330 | 393 | 393 | 393 | 280 | 280 | ST Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 10 | 10 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 20 | 44 | 51 | 51 | 20 | 20 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 125 | 128 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 22 | 20 | 20 | 20 | 20 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 36 | 35 | 163 | 163 | 50 | 50 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 118 | 100 | 200 | 200 | 135 | 119 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 74 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 10 | 24.5 | 24.5 | 11 | 11 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 19 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 71 | 70 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 11 | 55 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1753 | 1721 | 2752.44 | 2680.44 | 1978.21 | 1954.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-10-2026 | during | 19-10-2026 | during | 19-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 162 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 88 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.69 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 296.89 | 309 | 673.6 | 601.5 | 290.1 | 322
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 136 | 136 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 51 | 83 | 83 | 11 | 11 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Gas shortage
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 254 | 247 | 341 | 341 | 341 | 341 | Low gas pressure
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 397 | 398 | 400 | 400 | 400 | 400 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 391 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1542 | 1574 | 1694 | 1694 | 1606 | 1606
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 919 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 25 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 13 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 80 | 0 | 87 | 0 | 87 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1193 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2192 | 2303.2 | 3291.2 | 3204.2 | 2726.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 65 | 110 | 110 | 32 | 48 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 112 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Station shutdown for GT-11& STG Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 100 | 150 | 150 | 35 | 100 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 281 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.56 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1898.16 | 2054.6 | 2158.6 | 2157.6 | 1960.6 | 2040.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 56.39 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 256 | 206 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 44 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 43 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.6 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1210.03 | 1416.32 | 1200 | 1400 | 1000 | 1400 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.26 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1812.28 | 2097.52 | 3006.11 | 2983.99 | 1857.73 | 2256.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 44 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 185 | 0 | 179.97 | 0 | 179.97 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 356 | 228 | 476.97 | 262 | 386.97 | 251
System Total |  |  |  |  | 28843.2 | 28692.211 | 14979.61 | 16317.1 | 23716.58 | 23294.24 | 16236.38 | 17710.9
Forecast Scenario (19-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15540 |  | 219.65 |  | 15770
|  |  |  | 1:00 | 14834 |  | 152.8 |  | 14834
|  |  |  | 2:00 | 14209 |  | 9.55 |  | 14209
|  |  |  | 3:00 | 13805 |  | 0 |  | 13805
|  |  |  | 4:00 | 13198 |  | 0 |  | 13198
|  |  |  | 5:00 | 12875 |  | 0 |  | 12875
|  |  |  | 6:00 | 12651 |  | 0 |  | 12651
|  |  |  | 7:00 | 13420 |  | 0 |  | 13420
|  |  |  | 8:00 | 13440 |  | 0 |  | 13440
|  |  |  | 9:00 | 13590 |  | 0 |  | 13590
|  |  |  | 10:00 | 13920 |  | 0 |  | 13920
|  |  |  | 11:00 | 14260 |  | 0 |  | 14260
|  |  |  | 12:00 | 14980 |  | 0 |  | 14980
|  |  |  | 13:00 | 15190 |  | 0 |  | 15190
|  |  |  | 14:00 | 15150 |  | 47.75 |  | 15200
|  |  |  | 15:00 | 15380 |  | 19.1 |  | 15400
|  |  |  | 16:00 | 15150 |  | 19.1 |  | 15170
|  |  |  | 17:00 | 14840 |  | 9.55 |  | 14850
|  |  |  | 18:00 | 16190 |  | 143.25 |  | 16340
|  |  |  | 18:30 | 16200 |  | 238.75 |  | 16450
|  |  |  | 19:00 | 16250 |  | 248.3 |  | 16510
|  |  |  | 19:30 | 16270 |  | 267.4 |  | 16550
|  |  |  | 20:00 | 15840 |  | 0 |  | 15840
|  |  |  | 21:00 | 15620 |  | 0 |  | 15620
|  |  |  | 22:00 | 15400 |  | 0 |  | 15400
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 33.6°C
Probable Maximum Demand at Day Peak: |  |  | 14980.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 267.4
Probable Maximum Demand at Evening Peak: |  |  | 16550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16270.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 354.00 MKWHr. |  | 80 | 0 | 22 | 115 | 20 | 0 | 10 | 0 | 20 | 267
*** This report is generated digitally from Operation Information System (OIS) at 08:53 hrs on 19-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-10-2026 | [28 empty] | Date: | 18-10-2026 | [28 empty] | Date: | 18-10-2026 | [28 empty] | Date: | 18-10-2026 | [28 empty] | Date: | 18-10-2026 | [16 empty] | Date: | 18-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 35 | 54 | 122 | 129 | 98 | 55 | 55 | 72 | 0 | 0 | 520 | 0 | 35 | 303 | 0 | 0 | 0 | 143.42 | 7 | 18 | 0 | 465 | 107 | 87 | 72 | 0 | 0 | 67 | 22 | 35 | 24 | 25 | 0 | 221 | 110 | 4 | 1080 | 65 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1053 | 0 | 150 | 63 | 393 | 38 | 310 | 44 | 30 | 200 | 0 | 50 | 50 | 110 | 68 | 10 | 71 | 68 | 52.2 | 0 | 23 | 244 | 400 | 397 | 40 | 30 | 157 | 0 | 16 | 0 | 81 | 0 | 138 | 0 | 0 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 18 | 9266.12 | 854 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1228 | 0 | 0 | 0 | 1378.55 | 0 | 31 | 0 | 113 | 70 | 0 | 100 | 30 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 0 | 0 | 0 | 1170.6 | 300 | 35 | 6271.35 | 15537.47 | 103.78
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 54 | 114 | 129 | 98 | 55 | 55 | 72 | 0 | 0 | 515 | 0 | 55 | 301 | 0 | 0 | 0 | 143.42 | 7.5 | 18 | 0 | 475 | 109 | 51 | 68 | 0 | 0 | 67 | 27 | 17 | 24 | 25 | 0 | 221 | 110 | 9 | 1080 | 130 | 0 | 50 | 17 | 105 | 219 | 0 | 0 | 0 | 870 | 0 | 150 | 63 | 393 | 43 | 310 | 44 | 30 | 202 | 0 | 69 | 50 | 134 | 68 | 10 | 114 | 64 | 52.2 | 0 | 23 | 245 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 100 | 35 | 59 | 0 | 68 | 0 | 0 | 0 | 18 | 9216.12 | 918 | 0 | 24 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1223.49 | 0 | 31 | 0 | 55 | 100 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 0 | 0 | 0 | 1100 | 300 | 35 | 5929.89 | 15146.01 | 103.78
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 54 | 122 | 129 | 98 | 55 | 55 | 72 | 0 | 0 | 510 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 7.5 | 18 | 0 | 440 | 107 | 51 | 65 | 0 | 0 | 50 | 27 | 17 | 24 | 25 | 0 | 221 | 110 | 9 | 1080 | 158 | 0 | 50 | 17 | 105 | 221 | 0 | 0 | 0 | 660 | 0 | 144 | 35 | 393 | 92 | 305 | 20 | 17 | 199 | 0 | 85 | 50 | 138 | 74 | 10 | 114 | 64 | 52.2 | 0 | 23 | 246 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 11 | 0 | 134 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 18 | 8973.12 | 919 | 0 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1214.69 | 0 | 31 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 0 | 0 | 0 | 1020 | 300 | 35 | 5842.09 | 14815.21 | 103.77
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 54 | 127 | 92 | 98 | 55 | 55 | 72 | 0 | 0 | 510 | 0 | 55 | 298 | 0 | 0 | 0 | 123 | 7.5 | 18 | 0 | 430 | 109 | 51 | 65 | 0 | 0 | 50 | 27 | 17 | 24 | 25 | 0 | 221 | 110 | 22 | 1080 | 16 | 0 | 50 | 17 | 96 | 221 | 0 | 0 | 0 | 602 | 0 | 135 | 35 | 393 | 127 | 305 | 20 | 10 | 196 | 0 | 34 | 50 | 144 | 0 | 10 | 45 | 62 | 52.2 | 0 | 23 | 247 | 400 | 397 | 40 | 30 | 153 | 0 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 18 | 8538.7 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1216.91 | 0 | 0 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 0 | 0 | 0 | 1020 | 300 | 17 | 5715.31 | 14254.01 | 103.76
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 54 | 127 | 45 | 98 | 0 | 55 | 72 | 0 | 0 | 505 | 0 | 35 | 290 | 0 | 0 | 0 | 86 | 7.5 | 19 | 0 | 420 | 107 | 51 | 66 | 0 | 0 | 50 | 0 | 17 | 24 | 25 | 0 | 221 | 110 | 28 | 1080 | 0 | 0 | 50 | 0 | 105 | 221 | 0 | 0 | 0 | 600 | 0 | 142 | 35 | 393 | 151 | 295 | 20 | 10 | 192 | 0 | 15 | 50 | 152 | 0 | 10 | 0 | 62 | 52.2 | 0 | 23 | 244 | 400 | 397 | 40 | 30 | 152 | 0 | 16 | 0 | 11 | 0 | 137 | 0 | 100 | 35 | 58 | 0 | 68 | 0 | 0 | 0 | 18 | 8262.7 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1214.25 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 0 | 0 | 115 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 0 | 0 | 0 | 1020 | 300 | 17 | 5553.45 | 13816.15 | 103.75
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 35 | 54 | 127 | 45 | 98 | 0 | 55 | 72 | 0 | 0 | 495 | 0 | 35 | 298 | 0 | 0 | 0 | 68 | 7.5 | 19 | 0 | 460 | 72 | 51 | 66 | 0 | 0 | 50 | 0 | 17 | 24 | 25 | 0 | 220 | 68 | 23 | 1080 | 0 | 0 | 50 | 0 | 68 | 221 | 0 | 0 | 0 | 600 | 2 | 150 | 35 | 393 | 251 | 305 | 20 | 10 | 200 | 0 | 0 | 50 | 100 | 0 | 10 | 0 | 60 | 0 | 0 | 23 | 245 | 400 | 397 | 40 | 30 | 154 | 0 | 16 | 0 | 11 | 0 | 135 | 0 | 101 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 18 | 8178.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 0 | 0 | 1220.12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 267 | 20 | 0 | 0 | 1020 | 300 | 17 | 5361.12 | 13539.62 | 103.74
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 54 | 100 | 45 | 60 | 0 | 35 | 54 | 0 | 0 | 485 | 0 | 17 | 293 | 0 | 0 | 0 | 68 | 7.5 | 19 | 0 | 415 | 72 | 51 | 56 | 0 | 0 | 50 | 0 | 35 | 12 | 25 | 0 | 219 | 68 | 28 | 1080 | 0 | 0 | 50 | 0 | 34 | 221 | 0 | 0 | 0 | 600 | 0 | 150 | 35 | 350 | 337 | 250 | 20 | 0 | 191 | 0 | 0 | 50 | 34 | 0 | 10 | 0 | 54 | 0 | 0 | 23 | 244 | 400 | 397 | 40 | 30 | 152 | 0 | 8 | 0 | 11 | 0 | 136 | 0 | 101 | 35 | 59 | 0.02 | 67 | 0 | 0 | 0 | 18 | 7841.52 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 0 | 0 | 0 | 1208.95 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 228 | 80 | 0 | 0 | 1020 | 300 | 17 | 5354.95 | 13196.47 | 103.73
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 35 | 100 | 45 | 60 | 0 | 17 | 54 | 0 | 0 | 490 | 0 | 17 | 292 | 0 | 0 | 3 | 86 | 7.5 | 19 | 0 | 430 | 72 | 51 | 32 | 0 | 0 | 34 | 0 | 35 | 12 | 25 | 0.74 | 219 | 51 | 27 | 1080 | 0 | 0 | 48 | 0 | 34 | 222 | 0 | 0 | 0 | 600 | 2 | 150 | 35 | 330 | 350 | 250 | 20 | 0 | 194 | 0 | 0 | 36 | 34 | 0 | 10 | 0 | 52 | 0 | 12 | 23 | 247 | 400 | 397 | 40 | 30 | 153 | 2 | 16 | 0 | 11 | 0 | 136 | 0 | 102 | 35 | 59 | 2.9 | 67 | 0 | 0.3 | 7.7 | 14 | 7790.14 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1154 | 0 | 0 | 0 | 1217.24 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 7.14 | 13 | 0 | 0 | 7.76 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0.71 | 0 | 0 | 35 | 3 | 0 | 0 | 0 | 0 | 0.8 | 24 | 0.07 | 16 | 270 | 115 | 0 | 0 | 1170.6 | 300 | 17 | 5634.32 | 13424.46 | 103.72
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 35 | 100 | 45 | 60 | 0 | 17 | 54 | 0 | 0 | 490 | 0 | 17 | 301 | 0 | 0 | 14 | 86 | 7.5 | 19 | 0 | 430 | 35 | 51 | 30 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 1.7 | 219 | 34 | 3 | 1080 | 0 | 0 | 45 | 0 | 17 | 222 | 0 | 0 | 0 | 600 | 5 | 130 | 35 | 330 | 345 | 265 | 20 | 0 | 197 | 0 | 0 | 36 | 17 | 1 | 10 | 0 | 58 | 0 | 31 | 23 | 247 | 400 | 397 | 40 | 30 | 152 | 5 | 16 | 0 | 11 | 0 | 137 | 0 | 101 | 35 | 59 | 9.1 | 67 | 0 | 0.9 | 22.54 | 18 | 7697.74 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1187 | 0 | 0 | 0 | 1218.04 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 17.34 | 43 | 0 | 0 | 24.87 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.27 | 0 | 0 | 35 | 11 | 0 | 0 | 0 | 0 | 0 | 70 | 0.02 | 16 | 249 | 115 | 0 | 0 | 1157 | 300 | 17 | 5745.54 | 13443.28 | 103.71
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 17 | 35 | 100 | 45 | 60 | 0 | 17 | 54 | 0 | 0 | 490 | 0 | 17 | 301 | 0 | 0 | 22 | 86 | 5.5 | 19 | 0 | 445 | 34 | 51 | 12 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 2.45 | 219 | 34 | 0 | 1080 | 0 | 0 | 45 | 0 | 0 | 218 | 0 | 0 | 0 | 600 | 9 | 100 | 35 | 330 | 345 | 260 | 20 | 0 | 197 | 0 | 0 | 37 | 17 | 52 | 7 | 0 | 60 | 0 | 48 | 23 | 244 | 400 | 397 | 40 | 30 | 138 | 8 | 16 | 0 | 11 | 0 | 136 | 0 | 102 | 35 | 59 | 14.98 | 65 | 0 | 1.5 | 35.84 | 18 | 7723.27 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1195 | 0 | 0 | 0 | 1215.43 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 41.21 | 68 | 0 | 0 | 42.86 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 3.81 | 0 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 0 | 119 | 0.36 | 16 | 247 | 115 | 0 | 0 | 1134 | 300 | 17 | 5869.67 | 13592.94 | 103.68
10:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 35 | 100 | 45 | 60 | 0 | 35 | 54 | 0 | 0 | 495 | 0 | 17 | 303 | 0 | 0 | 18 | 86 | 5.5 | 16 | 0 | 510 | 34 | 51 | 12 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.07 | 220 | 34 | 0 | 1080 | 0 | 0 | 44 | 0 | 0 | 216 | 0 | 0 | 0 | 600 | 12 | 100 | 35 | 330 | 347 | 260 | 20 | 0 | 207 | 0 | 0 | 37 | 17 | 71 | 7 | 0 | 62 | 0 | 60 | 23 | 250 | 395 | 398 | 40 | 30 | 141 | 10 | 16 | 0 | 11 | 0 | 135 | 0 | 100 | 35 | 97 | 19 | 65 | 0 | 2 | 44.72 | 18 | 7949.29 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1190 | 0 | 0 | 0 | 1226.86 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 47.38 | 93 | 0 | 0 | 55.05 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 4.22 | 0 | 0 | 35 | 26 | 0 | 0 | 0 | 0 | 5.1 | 155 | 0.47 | 16 | 249 | 115 | 0 | 0 | 1140 | 300 | 17 | 5971.08 | 13920.37 | 103.68
11:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 35 | 101 | 45 | 97 | 4 | 35 | 54 | 0 | 0 | 505 | 0 | 18 | 318 | 0 | 0 | 23 | 86 | 5.5 | 14 | 0 | 520 | 51 | 51 | 12 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.37 | 220 | 40 | 0 | 1080 | 0 | 0 | 45 | 1 | 0 | 215 | 0 | 0 | 0 | 600 | 18 | 108 | 8 | 330 | 345 | 280 | 20 | 0 | 216 | 0 | 0 | 36 | 23 | 72 | 11 | 0 | 66 | 0 | 67 | 22 | 252 | 395 | 398 | 40 | 30 | 152 | 6 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 115 | 21 | 65 | 0 | 2.2 | 49.78 | 18 | 8132.85 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1195 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 8 | 58.15 | 96 | 0 | 0 | 61.39 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 5.3 | 0 | 0 | 72 | 29 | 6 | 0 | 0 | 0 | 5.9 | 176 | 0.53 | 16 | 281 | 113 | 0 | 0 | 1153 | 300 | 17 | 6130.27 | 14263.12 | 103.67
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 38 | 117 | 75 | 97 | 22 | 35 | 108 | 0 | 0 | 520 | 0 | 35 | 313 | 0 | 0 | 33 | 143.42 | 5.5 | 18 | 0 | 550 | 96 | 51 | 12 | 0 | 0 | 0 | 15 | 35 | 12 | 25 | 3.36 | 220 | 69 | 0 | 1080 | 10 | 0 | 0 | 8 | 88 | 211 | 0 | 0 | 0 | 600 | 16 | 125 | 0 | 330 | 347 | 290 | 20 | 0 | 215 | 0 | 11 | 36 | 118 | 71 | 11 | 17 | 70 | 2 | 68 | 22 | 254 | 391 | 397 | 40 | 30 | 155 | 12 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 115 | 20 | 57 | 0 | 2.2 | 49.69 | 18 | 8721.17 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1193 | 0 | 0 | 0 | 1210.03 | 0 | 0 | 0 | 55 | 43 | 0 | 0 | 0 | 44 | 56.39 | 104 | 0 | 0 | 38.26 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 5.6 | 0 | 0 | 115 | 9 | 44 | 0 | 0 | 0 | 3 | 185 | 0.56 | 16 | 281 | 113 | 0 | 0 | 1170.6 | 300 | 17 | 6258.44 | 14979.61 | 103.65
13:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 54 | 101 | 122 | 97 | 0 | 35 | 108 | 0 | 0 | 490 | 0 | 35 | 291 | 0 | 0 | 30 | 143.42 | 5.5 | 14 | 0 | 400 | 106 | 51 | 31 | 0 | 0 | 0 | 20 | 35 | 24 | 25 | 3.38 | 221 | 97 | 0 | 1080 | 133 | 0 | 0 | 8 | 105 | 212 | 0 | 0 | 0 | 600 | 17 | 127 | 0 | 330 | 345 | 235 | 20 | 0 | 218 | 0 | 57 | 36 | 156 | 69 | 11 | 98 | 70 | 34 | 57 | 21 | 259 | 392 | 399 | 40 | 29 | 153 | 10 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 115 | 20 | 57 | 0 | 1.9 | 37.39 | 18 | 8817.59 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1195 | 11 | 0 | 0 | 1204.89 | 0 | 0 | 0 | 55 | 91 | 0 | 8.5 | 4 | 52.2 | 56.69 | 100 | 0 | 0 | 49.2 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 3.72 | 0 | 0 | 115 | 30 | 77 | 0 | 0 | 0 | 6.1 | 169 | 0.41 | 32 | 307 | 113 | 0 | 0 | 1170.6 | 300 | 35 | 6379.31 | 15196.9 | 103.63
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 54 | 101 | 122 | 97 | 4 | 35 | 126 | 0 | 0 | 430 | 0 | 35 | 300 | 0 | 0 | 26 | 143.42 | 0 | 18 | 0 | 450 | 107 | 51 | 48 | 0 | 0 | 0 | 20 | 35 | 24 | 25 | 2.76 | 221 | 110 | 0 | 1080 | 145 | 0 | 3 | 17 | 105 | 141 | 0 | 0 | 0 | 600 | 16 | 128 | 0 | 330 | 322 | 245 | 20 | 0 | 184 | 0 | 92 | 35 | 158 | 68 | 10 | 105 | 72 | 43 | 38 | 21 | 255 | 392 | 375 | 40 | 29 | 152 | 9 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 115 | 16.17 | 57 | 0 | 1.8 | 43.56 | 18 | 8746.71 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1234.2 | 11 | 0 | 0 | 1210.97 | 0 | 0 | 0 | 70 | 95 | 0 | 8.5 | 16 | 52.2 | 42.31 | 84 | 0 | 0 | 36.54 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 4.48 | 0 | 0 | 115 | 28 | 98 | 0 | 0 | 0 | 5.2 | 127 | 0.47 | 32 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 35 | 6406.47 | 15153.18 | 103.61
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 54 | 101 | 123 | 97 | 38 | 35 | 126 | 0 | 0 | 425 | 0 | 35 | 314 | 0 | 0 | 17 | 143.42 | 5.5 | 18 | 0 | 520 | 101 | 51 | 44 | 0 | 0 | 0 | 20 | 35 | 24 | 25 | 1.91 | 221 | 110 | 0 | 1080 | 156 | 0 | 22 | 17 | 105 | 80 | 0 | 0 | 0 | 600 | 11 | 125 | 0 | 350 | 350 | 300 | 27 | 0 | 209 | 0 | 96 | 35 | 161 | 68 | 10 | 106 | 72 | 43 | 43 | 21 | 270 | 390 | 397 | 40 | 29 | 148 | 7 | 16 | 0 | 11 | 0 | 137 | 0 | 100 | 35 | 87 | 12.48 | 85 | 0 | 1 | 28.06 | 19 | 8990.37 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1234.2 | 11 | 0 | 0 | 1229.89 | 0 | 0 | 0 | 113 | 113 | 0 | 8.5 | 16 | 52.2 | 35.71 | 57 | 0 | 0 | 34.03 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 2.8 | 0 | 0 | 115 | 18 | 98 | 0 | 0 | 0 | 3.2 | 106 | 0.21 | 32 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 35 | 6394.34 | 15384.71 | 103.6
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 54 | 112 | 123 | 97 | 43 | 35 | 144 | 0 | 0 | 450 | 0 | 35 | 304 | 0 | 0 | 10 | 143.42 | 5.5 | 18 | 0 | 450 | 94 | 51 | 40 | 0 | 0 | 0 | 20 | 35 | 24 | 25 | 0.98 | 221 | 107 | 0 | 1080 | 149 | 0 | 43 | 17 | 99 | 80 | 0 | 0 | 0 | 600 | 5 | 127 | 0 | 350 | 352 | 310 | 44 | 0 | 200 | 0 | 106 | 35 | 163 | 68 | 10 | 105 | 70 | 52.2 | 12 | 21 | 258 | 394 | 398 | 40 | 29 | 152 | 3 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 78 | 6.08 | 95 | 0 | 0.6 | 14.56 | 20 | 8940.34 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 1234.2 | 11 | 0 | 0 | 1215.27 | 0 | 0 | 0 | 113 | 113 | 0 | 8.5 | 22 | 52.2 | 15.71 | 32 | 0 | 0 | 15.32 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 1.06 | 0 | 0 | 115 | 8 | 98 | 0 | 0 | 0 | 1.1 | 43 | 0.15 | 32 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 35 | 6211.11 | 15151.45 | 103.59
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 54 | 127 | 123 | 97 | 55 | 17 | 162 | 0 | 0 | 365 | 0 | 35 | 294 | 0 | 0 | 1 | 143.42 | 5.5 | 18 | 0 | 420 | 85 | 115 | 40 | 0 | 0 | 17 | 34 | 35 | 24 | 25 | 0.07 | 221 | 103 | 0 | 1030 | 151 | 0 | 44 | 25.5 | 92 | 80 | 0 | 0 | 0 | 600 | 1 | 128 | 0 | 340 | 297 | 285 | 44 | 0 | 193 | 0 | 115 | 35 | 170 | 68 | 10 | 105 | 68 | 52.2 | 3 | 21 | 257 | 397 | 399 | 40 | 29 | 152 | 0 | 16 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 79 | 0.92 | 96 | 0 | 0.1 | 1.9 | 24 | 8781.61 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1216 | 11 | 0 | 0 | 1246.35 | 0 | 0 | 0 | 113 | 113 | 0 | 17 | 22 | 52.2 | 2.73 | 7 | 0 | 0 | 2.34 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0.17 | 0 | 0 | 115 | 1 | 110 | 0 | 0 | 0 | 0.5 | 9 | 0.03 | 32 | 250 | 112 | 0 | 0 | 1150 | 300 | 35 | 6055.32 | 14836.93 | 103.58
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 54 | 127 | 125 | 196 | 55 | 55 | 162 | 0 | 0 | 360 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 440 | 95 | 200 | 46 | 0 | 0 | 53 | 35 | 54.36 | 37 | 38 | 0 | 221 | 107 | 0 | 1080 | 155 | 0 | 44 | 25.5 | 101 | 81 | 0 | 0 | 0 | 850 | 0 | 132 | 0 | 310 | 314 | 300 | 44 | 0 | 198 | 0 | 115 | 35 | 172 | 69 | 10 | 114 | 78 | 52.2 | 0 | 22 | 258 | 400 | 398 | 40 | 29 | 146 | 0 | 16 | 0 | 51 | 0 | 138 | 0 | 100 | 35 | 88 | 0 | 162 | 0 | 0 | 0 | 24 | 9668.98 | 919 | 0 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 1190 | 11 | 0 | 0 | 1392.04 | 0 | 32 | 0 | 113 | 113 | 0 | 100 | 30 | 52.2 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 277 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6516.84 | 16185.82 | 103.57
19:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 54 | 127 | 126 | 145 | 40 | 55 | 108 | 0 | 0 | 530 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 435 | 111 | 209 | 58 | 0 | 0 | 67 | 40 | 54.36 | 12 | 38 | 0 | 220 | 110 | 0 | 1080 | 16 | 0 | 44 | 25.5 | 51 | 218 | 0 | 0 | 0 | 1029 | 0 | 128 | 0 | 393 | 310 | 220 | 44 | 0 | 216 | 0 | 55 | 35 | 100 | 70 | 10 | 19 | 74 | 25 | 0 | 22 | 247 | 400 | 398 | 40 | 30 | 156 | 0 | 16 | 0 | 51 | 0 | 136 | 0 | 100 | 35 | 88 | 0 | 162 | 0 | 0 | 0 | 24 | 9633.78 | 919 | 0 | 27 | 25 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 13 | 0 | 0 | 1416.32 | 0 | 34 | 0 | 113 | 113 | 0 | 100 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6683.32 | 16317.1 | 103.56
19:30 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 17 | 127 | 125 | 95 | 30 | 55 | 54 | 0 | 0 | 540 | 0 | 17 | 323 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 114 | 211 | 16 | 0 | 0 | 67 | 40 | 54.36 | 12 | 38 | 0 | 220 | 51 | 2 | 1080 | 16 | 0 | 44 | 17 | 51 | 216 | 0 | 0 | 0 | 1100 | 0 | 135 | 0 | 393 | 310 | 220 | 44 | 0 | 197 | 0 | 16 | 35 | 100 | 70 | 10 | 17 | 74 | 8 | 0 | 22 | 255 | 400 | 398 | 40 | 30 | 155 | 0 | 8 | 0 | 51 | 0 | 136 | 0 | 100 | 35 | 88 | 0 | 130 | 0 | 0 | 0 | 24 | 9351.28 | 919 | 0 | 23 | 34 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 32 | 0 | 0 | 1420.37 | 0 | 34 | 0 | 113 | 113 | 0 | 100 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6595.37 | 15946.65
20:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 127 | 95 | 80 | 30 | 55 | 35 | 0 | 0 | 540 | 0 | 17 | 325 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 300 | 90 | 213 | 15 | 0 | 0 | 67 | 40 | 54.36 | 12 | 38 | 0 | 219 | 51 | 5 | 1080 | 16 | 0 | 44 | 17 | 17 | 217 | 0 | 0 | 0 | 1180 | 0 | 135 | 0 | 393 | 318 | 240 | 44 | 0 | 204 | 0 | 16 | 35 | 100 | 71 | 10 | 17 | 72 | 8 | 0 | 22 | 251 | 400 | 395 | 40 | 30 | 153 | 0 | 6 | 0 | 52 | 0 | 138 | 0 | 100 | 35 | 88 | 0 | 115 | 0 | 0 | 0 | 24 | 9167.28 | 919 | 0 | 30 | 46 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 32 | 0 | 0 | 1415.18 | 0 | 32 | 0 | 113 | 70 | 0 | 100 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6547.18 | 15714.46 | 103.55
21:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 17 | 127 | 95 | 80 | 30 | 55 | 35 | 0 | 0 | 545 | 0 | 17 | 305 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 330 | 90 | 213 | 12 | 0 | 0 | 67 | 40 | 54.36 | 12 | 38 | 0 | 220 | 51 | 2 | 1080 | 16 | 0 | 50 | 25.5 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 147 | 0 | 393 | 325 | 220 | 44 | 0 | 201 | 0 | 16 | 35 | 85 | 72 | 10 | 17 | 68 | 8 | 0 | 23 | 251 | 400 | 399 | 40 | 30 | 155 | 0 | 13 | 0 | 52 | 0 | 137 | 0 | 100 | 35 | 88 | 0 | 115 | 0 | 0 | 0 | 12 | 9215.78 | 919 | 0 | 27 | 39 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 16 | 0 | 0 | 1424.42 | 0 | 32 | 0 | 113 | 70 | 0 | 100 | 31 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 72 | 6409.22 | 15625 | 103.54
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 54 | 17 | 127 | 95 | 45 | 30 | 55 | 35 | 0 | 0 | 545 | 0 | 17 | 290 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 330 | 90 | 135 | 12 | 0 | 0 | 67 | 33 | 54.36 | 12 | 38 | 0 | 220 | 51 | 2 | 1080 | 16 | 0 | 50 | 25.5 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 26 | 360 | 281 | 220 | 44 | 0 | 221 | 0 | 16 | 35 | 85 | 73 | 10 | 17 | 70 | 8 | 0 | 23 | 250 | 400 | 398 | 40 | 30 | 155 | 0 | 13 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 88 | 0 | 115 | 0 | 0 | 0 | 24 | 8977.78 | 919 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1413.89 | 0 | 32 | 0 | 113 | 70 | 0 | 100 | 31 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 72 | 6384.69 | 15362.47 | 103.53
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 17 | 128 | 95 | 45 | 30 | 55 | 17 | 0 | 0 | 545 | 0 | 17 | 315 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 330 | 90 | 135 | 12 | 0 | 0 | 67 | 33 | 54.36 | 12 | 38 | 0 | 220 | 51 | 3 | 1080 | 16 | 0 | 50 | 25.5 | 17 | 221 | 0 | 0 | 0 | 1130 | 0 | 150 | 26 | 220 | 331 | 240 | 44 | 0 | 220 | 0 | 16 | 35 | 85 | 72 | 10 | 17 | 66 | 8 | 0 | 23 | 255 | 400 | 398 | 40 | 30 | 155 | 0 | 13 | 0 | 11 | 0 | 136 | 0 | 100 | 35 | 88 | 0 | 95 | 0 | 0 | 0 | 24 | 8802.78 | 919 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1421.95 | 0 | 40 | 0 | 113 | 35 | 0 | 100 | 24 | 25 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 72 | 6340.75 | 15143.53 | 103.52
Total KWH | 0 | 635520 | 300000 | 0 | 0 | 0 | 0 | 0 | 8510400 | 0 | 0 | 783720 | 1067400 | 2806992 | 2210880 | 2267716 | 656053 | 935089 | 1971360 | 0 | 0 | 11878636 | 0 | 806332 | 7308776 | 0 | 0 | 197442 | 2965200 | 144600 | 437040 | 0 | 10558636.36 | 2127709 | 2165345 | 876480 | 0 | 0 | 759665 | 443374 | 919017 | 403200 | 651840 | 22679 | 5351404 | 1983018 | 170880 | 25869090.91 | 1508800 | 0 | 995040 | 289987.2 | 1562327 | 4517396 | 0 | 0 | 0 | 18250907 | 106920 | 3260145 | 518545 | 8379500 | 7080500 | 6602000 | 817596 | 88320 | 4950000 | 0 | 1088640 | 928424 | 2616480 | 1260840 | 230800 | 1138860 | 1574400 | 584966 | 444318 | 534720 | 5997000 | 9585600 | 9583000 | 952000 | 706320 | 3648845.46 | 65228 | 376008 | 0 | 429120 | 0 | 3146000 | 0 | 2331360 | 868320 | 1929600 | 142117 | 2008800 | 0 | 14500 | 316130 | 477600 | 210093473.93 | 22085091 | 0 | 203520 | 245888 | 0 | 0 | 0 | 0 | 0 | 251424 | 493200 | 29076360 | 115680 | 0 | 0 | 30592724 | 0 | 299863 | 0 | 1896864 | 1643616 | 0 | 727504 | 248238 | 759187 | 364992 | 713040 | 237798 | 0 | 393364 | 0 | 0 | 0 | 0 | 0 | 0 | 5933163 | 0 | 34200 | 0 | 0 | 2162642 | 198820 | 1494576 | 0 | 0 | 0 | 32305.68 | 1164240 | 3501 | 589824 | 6916000 | 2062000 | 0 | 0 | 27367273 | 7307636.36 | 1017600 | 146632134.04 | 356725607.97

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14979.61 | MW | 12:00 Hr. | Energy Generated |  |  | 356.7256 |  | MKWHr.
| Day Peak Demand |  |  | 14979.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.196 |  | MKWHr.
| Evening Peak Generation |  |  | 16317.1 | MW | 19:00 Hr. | Energy Demand |  |  | 357.9216 |  | MKWHr.
| Evening Peak Demand |  |  | 16539.1 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.6 |  | °C
| Minimum Generation of the Day |  |  | 13196.47 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 838.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 16317.1 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 8.2859 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.8381 | 0 | 17.4063 | 0 | 0 | 0.19744 | 0 | 0 | 56.4418 | Gas | 117.8725 | Gas | 399256343.3944
| Chattogram Zone |  |  | 4.6883 | 44.12 | 14.6858 | 0 | 5.3514 | 0.1296 | 0 | 0 | 68.9751 | Coal | 114.7873 | Coal | 889724051.2315
| Cumilla Zone |  |  | 29.5957 | 0 | 10.4847 | 0 | 0 | 0.44432 | 1.5744 | 0 | 42.0991 | HFO | 59.7553 | HFO | 1234973899.392
| Mymensingh Zone |  |  | 0 | 0 | 5.2843 | 0 | 0 | 0.47275 | 0 | 0 | 5.7571 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.7553 | 0 | 0 | 0 | 0 | 0.065228 | 0 | 0 | 36.8205 | Hydro | 5.3514 | Hydro | 535140.4
| Khulna Zone |  |  | 0 | 29.0764 | 0.81651 | 0 | 0 | 0.4932 | 22.0851 | 0 | 52.4712 | Solar | 4.707 | Solar | 75217596.7208
| Barishal Zone |  |  | 2.062 | 41.5909 | 1.6074 | 0 | 0 | 0.003501 | 0 | 0 | 45.2638 | Import | 54.2522 | Import | 356091875.44
| Rajshahi Zone |  |  | 5.9332 | 0 | 5.8131 | 0 | 0 | 1.5056 | 30.5927 | 0 | 43.8446 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 0 | 3.6572 | 0 | 0 | 1.3954 | 0 | 0 | 5.0526
| Total |  |  | 117.8725 | 114.7873 | 59.7553 | 0 | 5.3514 | 4.707 | 54.2522 | 0 | 356.7256
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 399256343.3944 |  | Hydro | 535140.4
|  |  |  | Coal | 889724051.2315 |  | Solar | 75217596.7208
|  |  |  | HFO | 1234973899.392 |  | Import | 356091875.44
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 295,57,98,906 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0851 | Peak Hr Flow | 919.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34193563.63 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.5927 | Peak Hr Flow | 1416.32 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1720 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5744 | Peak Hr Flow | 74.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2140 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2522 | Peak Hr Flow | 2409.32 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 70 |  | 6096
|  |  |  | Chattogram |  | 0 |  | 1616
|  |  |  | Cumilla |  | 0 |  | 1468
|  |  |  | Mymensingh |  | 114 |  | 1270
|  |  |  | Sylhet |  | 23 |  | 692
|  |  |  | Khulna |  | 0 |  | 1795
|  |  |  | Barishal |  | 3 |  | 481
|  |  |  | Rajshahi |  | 0 |  | 1549
|  |  |  | Rangpur |  | 2 |  | 899
|  |  |  | Total |  | 212 |  | 15866
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Fenchugonj CCPP Phase-2 ST |  |  | 35
[7 empty] | 4 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 5 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 473.5
|  |  |  | Total Unavailable Capacity |  |  |  | 773.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 16:31 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end.
| 08:20 | 16:31 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/230/132kV end Due
to গাছপালা কর্তন
| 08:20 | 16:32 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/230/132kV end Due
to গাছপালা কর্তন
|  | 08:27 | Saidpur 132/33kV S/S TR-01 HT is restored.
|  | 08:28 | Saidpur 132/33kV S/S TR-01 LT is restored.
| 08:30 | 14:04 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D
| 08:30 | 14:07 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D
| 09:01 | 13:09 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Annual Maintenance
| 09:01 | 12:32 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T LT Forced S/D Due to 132KV B phase LA
replacement work.
| 09:02 | 13:08 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Annual Maintenance
| 09:02 | 12:30 | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T HT Forced S/D Due to 132KV B phase LA
replacement work.
|  | 09:13 | Bajitpur 132/33kV S/S Tr-2(414T) HT is restored.
| 09:20 | 14:39 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to QF- GMD-39 and as the
instruction of ALDC Bogura (499264)
| 09:21 | 14:38 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to QF- GMD-39 and as the
instruction of ALDC Bogura (499264)
|  | 09:59 | Pabna 132/33kV S/S T-3 HT is restored.
|  | 10:00 | Pabna 132/33kV S/S T-3 LT is restored.
| 10:16 | 11:15 | Maijdee 132/33kV S/S Tr-02 HT Forced S/D Due to BREB & PDB maintenance work
|  | 11:06 | Satkhira 132/33kV S/S Transformer-3(T-3) HT is restored.
|  | 11:17 | Satkhira 132/33kV S/S Transformer-3(T-3) LT is restored.
| 12:20 | 13:16 | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing ABB REL 670 | [7 empty] | 44.0MW load
|  |  | relays Due to For Munshignaj ckt-1 fault | [7 empty] | interrup.
| 12:20 | 12:42 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing ABB REL 670 relays | [7 empty] | 70.0MW load
|  |  | Due to For Munshignaj ckt-1 fault | [7 empty] | interrup.
| 12:20 | 13:11 | Madanganj-Munsiganj 132 kV Ckt-2 Tripped from Munshiganj 132/33kV end showing Dir O/C & | [7 empty] | 38.0MW load
|  |  | E/F proten.optd relays. and from Madanganj 132/33kV end showing ABB REL670 relays Due to | [7 empty] | interrup.
|  |  | For Munshignaj ckt-1 fault | [7 empty] | Munshiganj 132/33kV
end and 40.0MW load
interrup. Madanganj
132/33kV end
| 12:20 | 16:00 | Madanganj-Munsiganj 132 kV Ckt-1 Tripped from Munshiganj 132/33kV end showing Dir O/C & | [7 empty] | 38.0MW load
|  |  | E/F proten.optd relays. and from Madanganj 132/33kV end showing ABB REL 670 relays Due to | [7 empty] | interrup.
|  |  | Line Fult by crane | [7 empty] | Munshiganj 132/33kV
end and 40.0MW load
interrup. Madanganj
132/33kV end
| 12:20 | 12:56 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing OC/EF:
EF(t). Optimho: Z3, CN, DEF Start. relays.
| 12:20 | 16:01 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing ABB REL 670 relays. | [7 empty] | 24.0MW load
interrup.
| 12:21 | 15:04 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Initiation. relays Due to
Unknown
| 12:24 | 12:58 | Sirajganj 132/33kV S/S T4-(445) LT Tripped showing O/C, E/F relays Due to Economic Zone | [7 empty] | 30.0MW load
|  |  | Feeder fault | [7 empty] | interrup.
| 12:24 | 12:58 | Sirajganj 132/33kV S/S T3-(435) LT Tripped showing O/C ,E/F relays Due to Economic feeder | [7 empty] | 30.0MW load
|  |  | fault | [7 empty] | interrup.
| 13:29 |  | Maijdee 132/33kV S/S Tr-02 HT Forced S/D Due to Maintenance work
| 15:54 | 16:51 | Chapai 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to T-01 33 kv bus pt maintenance work
| 15:55 | 16:49 | Chapai 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to T-01 33 kv pt maintenance work
| 16:10 | 16:28 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Tripped showing Over current relay relays | [7 empty] | 35.0MW load
|  |  | Due to PBS Rampal 33 KV CB fault. | [7 empty] | interrup.
| 16:10 | 16:27 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Tripped showing Over current relay relays | [7 empty] | 20.0MW load
|  |  | Due to PBS Rampal 33 KV CB fault. | [7 empty] | interrup.
| 16:10 | 16:28 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Tripped showing Over current relay relays | [7 empty] | 20.0MW load
|  |  | Due to PBS Rampal 33 KV CB fault. | [7 empty] | interrup.
| 16:50 | 18:38 | Jhenaidah 132/33kV S/S Transformer T-2 HT Forced S/D Due to 33kV, T2A CT secondary
terminal Redhot maintenance.
| 16:50 | 18:38 | Jhenaidah 132/33kV S/S Transformer T-2 LT Forced S/D Due to 33kV, T2A CT secondary
terminal Redhot maintenance.
|  | 16:51 | Chapai 132/33kV S/S T-1 (405T) LT is restored.
|  | 16:52 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 16:56 | Barguna 132/33kV S/S Transformer-2 HT is restored.
|  | 16:57 | Barguna 132/33kV S/S Transformer-2 LT is restored.
| 19:49 | 20:07 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Tripped showing over current relays. | [7 empty] | 21.0MW load
interrup.
| 19:49 | 20:06 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Tripped showing over current relays. | [7 empty] | 21.0MW load
interrup.
| 19:49 | 20:20 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Tripped showing over current relay | [7 empty] | 36.0MW load
|  |  | relays. | [7 empty] | interrup.
| 06:00 |  | Minimum Generation: 12650 MW.
| 07:01 |  | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance Work
| 07:01 |  | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance Work
| 07:05 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Maintenance work at DS-324 and
DS-321(main bus) of ATR-3 132kV side due to temperature rise.
| 07:05 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Maintenance work at DS-324 and
DS-321(main bus) of ATR-3 132kV side due to temperature rise.
| 07:13 |  | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to High
temperature reduce maintenance work and from Ashuganj 132/33kVend.
| 07:20 |  | Rampur 230/132/33 S/S TR-1 LT Scheduled S/D Due to High temparature maintenance
| 07:22 |  | Rampur 230/132/33 S/S TR-1 HT Scheduled S/D Due to High temparature maintenance
| 07:31 |  | Hasnabad 132/33kV S/S 132kV Main Bus Scheduled S/D Due to 230/132 kV AutoTR-3 LT side
Main bus DS maintenance.
| 07:34 |  | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing General | [7 empty] | 67.0MW load
|  |  | trip, Distance relay, Blue phase, Zone-1 relays Due to Line fault. | [7 empty] | interrup.
Siddhirganj
132/33kV end
| 07:48 |  | Bogura West-Rooppur ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Rooppur ckt- 01
has been S/D due to (QB5) DS box change at Bogura 400kV substation as per instruction of
ALDC Bogura.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8510400 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 656053 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7308776 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 783720 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 2210880 | Machine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 935089 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 806332 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5.5 | 144600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 437040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 300000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 2267716 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 127 | 2806992 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 635520 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1971360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 197442 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1067400 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 435 | 10558636.36 | Gas Shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 530 | 11878636 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2965200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2646.92 | 56441792.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 289987.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 106920 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 995040 | Machine Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5351404 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 4517396 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1562327 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 443374 | Fuel Shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 759665 | Fuel Shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 403200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 170880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 58 | 876480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22679 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 209 | 2165345 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 919017 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1983018 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 651840 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 111 | 2127709 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 1508800 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1029 | 18250907 | Coal Shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 25869090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3382.86 | 68975079.11
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 4950000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 310 | 7080500 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 6602000 | Line Overload
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8379500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 88320 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 518545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 817596 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 128 | 3260145 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 534720 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 928424 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 2616480 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 74 | 1574400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 584966 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 10 | 230800 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 19 | 1138860 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 1260840 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 55 | 1088640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 444318 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1721 | 42099054
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 142117 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2008800 | Fuel Shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1929600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 316130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 477600 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 868320 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 674.21 | 309 | 5757067
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65228 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 952000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 706320 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3648845.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 136 | 3146000 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 51 | 429120 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2331360 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 376008 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 247 | 5997000 | Gas Shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 398 | 9583000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9585600 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1574 | 36820481.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 919 | 22085091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 203520 | Fuel Shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 245888 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 13 | 115680 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 251424 | Machine Problem
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 493200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29076360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2303.2 | 52471163
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 27367273 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 65 | 589824 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 112 | 2062000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7307636.36 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1017600 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6916000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3501 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2054.6 | 45263834.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 364992 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 299863 | Machine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 248238 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 206 | 5933163 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 237798 | Machine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 759187 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 727504 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1643616 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1896864 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 34200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1416.32 | 30592724 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 393364 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 713040 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2097.52 | 43844553
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1494576 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32305.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2162642 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 198820 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1164240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 5052583.68
Eastern Grid Total |  |  |  |  | 16961.086 | 9633.78 | 210093473.93
Western Grid Total |  |  |  |  | 11731.125 | 6683.32 | 146632134.04
National Grid Total |  |  |  |  | 28692.211 | 16317.1 | 356725607.97
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10935.94 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4718.9 | MW
i) Dhaka area |  |  | 6026.48 |  | MW | i) Khulna area |  |  |  | 1795 | MW
ii) Chattogram area |  |  | 1616 |  | MW | ii) Barishal area |  |  |  | 478.3 | MW
iii) Cumilla area |  |  | 1468.46 |  | MW | iii) Rajshahi area |  |  |  | 1548.6 | MW
iv) Mymensingh area |  |  | 1156 |  | MW | iv) Rangpur area |  |  |  | 897 | MW
v) Sylhet area |  |  | 669 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15654.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 17:00 | 72 | Hatirjheel | 85 | 15:00 | 143 | PHP | 12 | 23:00
2 | AKSML | 165.8 | 12:00 | 73 | Ishurdi | 80 | 18:30 | 144 | Pabna | 101 | 18:00
3 | Aftabnagar | 44 | 18:00 | 74 | Jaldhaka | 70 | 18:00 | 145 | Palashbari | 125 | 18:00
4 | Agargaon | 131 | 13:00 | 75 | Jamalpur | 126 | 18:30 | 146 | Panchagarh | 59 | 18:30
5 | Agrabad | 76 | 14:00 | 76 | Jashore | 125 | 18:00 | 147 | Patiya | 31 | 19:00
6 | Amnura | 40 | 22:00 | 77 | Jhenaidah | 97 | 18:00 | 148 | Patnitala | 31 | 21:00
7 | Araihazar | 105 | 18:00 | 78 | Joydebpur | 158 | 12:00 | 149 | Patuakhali | 70.5 | 00:00
8 | Ashuganj | 0.56 | 00:00 | 79 | Joypurhat | 58 | 01:00 | 150 | Payra | 34 | 00:00
9 | Ashuganj-230 | 103 | 00:00 | 80 | Juldah | 19.5 | 13:00 | 151 | Postogola | 65 | 13:00
10 | BSRM | 204 | 05:00 | 81 | KSRM | 28 | 12:00 | 152 | Pubail | 47 | 18:00
11 | Bagerhat | 94 | 18:30 | 82 | Kabirpur | 272 | 09:00 | 153 | Purbachal | 29 | 00:00
12 | Bajitpur | 87 | 19:30 | 83 | Kachua | 94 | 00:00 | 154 | Purbasadipur | 111 | 13:00
13 | Bakerganj | 14.6 | 18:00 | 84 | Kaliganj | 42 | 18:30 | 155 | Rahanpur | 36 | 21:00
14 | Bakulia | 100 | 18:00 | 85 | Kallyanpur | 132 | 11:00 | 156 | Rahim | 46 | 00:00
15 | Banani | 68 | 12:00 | 86 | Kalurghat | 42 | 17:00 | 157 | Rajbari | 85 | 18:00
16 | Bangabhaban | 16 | 10:00 | 87 | Kamrangirchar | 98 | 13:00 | 158 | Rajendrapur | 143 | 18:00
17 | Barapukuria | 60 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 110 | 00:00
18 | Barguna | 22 | 00:00 | 89 | Kasba | 37 | 19:30 | 160 | Rajshahi-230 | 99 | 13:00
19 | Barishal | 102 | 12:00 | 90 | Kazla | 116 | 00:00 | 161 | Ramganj | 106 | 00:00
20 | Barishal-230 | 104 | 21:00 | 91 | Keranigonj | 90 | 18:30 | 162 | Rampur | 46 | 00:00
21 | Baroaulia | 38 | 07:00 | 92 | Khagrachori | 34 | 18:00 | 163 | Rangamati | 20 | 18:00
22 | Baroirhat | 63 | 18:00 | 93 | Khulna | 68 | 13:00 | 164 | Rangpur | 122 | 18:00
23 | Bashundhara | 204 | 13:00 | 94 | Khulshi | 196 | 18:30 | 165 | Ruppur | 4.4 | 10:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 130 | 22:00 | 166 | SSM | 3 | 02:00
25 | Beanibazar | 76 | 18:30 | 96 | Kodda | 303 | 11:00 | 167 | Saidpur | 104 | 18:00
26 | Benapole | 65 | 00:00 | 97 | Kulaura | 51 | 19:00 | 168 | Santhia | 36 | 18:30
27 | Bhaluka | 148 | 17:00 | 98 | Kurigram | 66 | 18:00 | 169 | Satkhira | 130 | 22:00
28 | Bhandaria | 58 | 00:00 | 99 | Kushtia | 150 | 18:00 | 170 | Satmasjid | 111 | 14:00
29 | Bhangura | 37 | 18:30 | 100 | Laksam | 38 | 02:00 | 171 | Savar | 224 | 15:00
30 | Bheramara(GK) | 68 | 18:00 | 101 | Lakshmipur | 53 | 18:00 | 172 | SevenRings | 20.3 | 03:00
31 | Bhulta | 214 | 15:00 | 102 | Lalbag | 86 | 13:00 | 173 | ShahCement | 22 | 02:00
32 | Bog-Sherpur | 72 | 18:30 | 103 | Lalmonirhat | 58 | 18:00 | 174 | Shahjadpur | 80 | 18:00
33 | Bogura | 185 | 19:30 | 104 | MI_Cement | 11.5 | 13:00 | 175 | Shahjibazar | 145 | 18:30
34 | Borhanuddin | 76 | 22:00 | 105 | Madanganj | 46 | 20:00 | 176 | Shahmirpur | 60 | 18:00
35 | Brahmanbaria | 141 | 18:30 | 106 | Madaripur | 110 | 00:00 | 177 | Shariatpur | 97 | 00:00
36 | Cantonment | 130 | 13:00 | 107 | Madartek | 86 | 00:00 | 178 | Sherpur | 140 | 18:00
37 | Chandina | 22 | 20:00 | 108 | Madunaghat | 58 | 19:00 | 179 | Shikalbaha | 20 | 18:00
38 | Chandpur | 83 | 00:00 | 109 | Magura | 67 | 18:30 | 180 | Shitalakhya | 83.1 | 12:00
39 | Chandraghona | 33 | 18:30 | 110 | Mahasthangarh | 72 | 00:00 | 181 | Sholosohor | 51 | 15:00
40 | Chapai | 74 | 00:00 | 111 | Maijdee | 40 | 00:00 | 182 | Shomvuganj | 40 | 22:00
41 | Charfasson | 35 | 18:30 | 112 | Manikganj | 142 | 18:00 | 183 | Shyampur | 168 | 11:00
42 | Charsaidpur | 42 | 15:00 | 113 | Maniknagar | 96 | 13:00 | 184 | Siddhirganj | 134 | 18:30
43 | Chauddagram | 74 | 18:30 | 114 | Matarbari | 57 | 19:00 | 185 | Sirajganj | 118 | 19:30
44 | Chhatak | 38 | 02:00 | 115 | Matuail | 80 | 12:00 | 186 | Sitakunda | 36 | 18:30
45 | Chowmuhani | 161 | 18:30 | 116 | Metrorail_Motijheel | 19 | 14:00 | 187 | Sonargaon | 143 | 16:00
46 | Chuadanga | 116 | 18:30 | 117 | Metrorail_Uttara | 8 | 11:00 | 188 | Sreemongol | 81 | 19:00
47 | Coxsbazar | 151 | 00:00 | 118 | Millgate | 99 | 12:00 | 189 | Sreepur | 136 | 21:00
48 | Cumilla(N) | 142 | 15:00 | 119 | Mirpur | 144 | 14:00 | 190 | Srinagar | 47.6 | 00:00
49 | Cumilla(S) | 156 | 18:00 | 120 | Mirsorai | 33 | 02:00 | 191 | Sunamganj | 61 | 19:00
50 | Daganbhuiyan | 36 | 00:00 | 121 | Mirzapur | 49 | 18:00 | 192 | Sylhet | 125 | 18:00
51 | Daudkandi | 128 | 23:00 | 122 | Mithapukur | 70 | 18:00 | 193 | Sylhet_(South) | 64 | 18:00
52 | DhakaUniversity | 100 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 106 | 00:00 | 124 | Mogbazar | 68.6 | 14:00 | 195 | Tangail | 184 | 18:30
54 | Dhanmondi | 115.6 | 13:00 | 125 | Mongla | 40 | 00:00 | 196 | Taraganj | 31 | 18:00
55 | Dohazari | 117 | 18:00 | 126 | Monirampur | 24 | 00:00 | 197 | Tasnim | 33 | 21:00
56 | Faridpur | 170 | 00:00 | 127 | Motijheel | 57 | 13:00 | 198 | Thakurgaon | 96 | 18:30
57 | Fatullah | 124 | 16:00 | 128 | Muktagacha | 42 | 18:00 | 199 | Tongi | 165 | 11:00
58 | Fenchuganj | 41 | 18:30 | 129 | Munshiganj | 109 | 16:00 | 200 | Ullahpara | 38 | 18:30
59 | Feni | 110 | 18:00 | 130 | Muradnagar | 58 | 19:30 | 201 | Ullon | 56 | 18:00
60 | GPH | 80 | 15:00 | 131 | Mymensingh | 166 | 18:00 | 202 | Uttara | 97 | 13:00
61 | Ghatail | 91 | 19:00 | 132 | Nabinagar | 110 | 16:00 | 203 | UttaraNew | 58 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 119 | 00:00 | 204 | Zigatola | 96 | 18:00
63 | Ghorashal-230 | 104 | 17:00 | 134 | Narail | 58 | 00:00
64 | Goalpara | 39 | 00:00 | 135 | Narinda | 76 | 13:00
65 | Gollamari | 108 | 00:00 | 136 | Narshingdi | 189 | 19:00
66 | Gopalganj | 110 | 00:00 | 137 | Natore | 155 | 18:30
67 | Gulshan | 122 | 12:00 | 138 | Nawabganj | 46.4 | 02:00
68 | Halishahar | 134 | 16:00 | 139 | Netrakona | 131 | 17:00
69 | HaripurSBU | 135 | 01:00 | 140 | New | 86 | 12:00
70 | Hasnabad | 104 | 21:00 | 141 | Niamatpur | 74 | 18:30
71 | Hathazari | 95 | 18:30 | 142 | Noapara | 43 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15537.47 | 231 |  | 15778.47
1:00 | 15146.01 | 161 |  | 15314.01
2:00 | 14815.21 | 14 |  | 14830.21
3:00 | 14254.01 | 0 |  | 14254.01
4:00 | 13816.15 | 0 |  | 13816.15
5:00 | 13539.62 | 0 |  | 13539.62
6:00 | 13196.47 | 0 |  | 13196.47
7:00 | 13424.46 | 0 |  | 13424.46
8:00 | 13443.28 | 0 |  | 13443.28
9:00 | 13592.94 | 20 |  | 13613.94
10:00 | 13920.37 | 0 |  | 13920.37
11:00 | 14263.12 | 0 |  | 14263.12
12:00 | 14979.61 | 0 |  | 14979.61
13:00 | 15196.9 | 0 |  | 15196.9
14:00 | 15153.18 | 45 |  | 15200.18
15:00 | 15384.71 | 20 |  | 15405.71
16:00 | 15151.45 | 20 |  | 15172.45
17:00 | 14836.93 | 20 |  | 14857.93
18:00 | 16185.82 | 152.99 |  | 16345.82
19:00 | 16317.1 | 212 |  | 16539.1
19:30 | 15946.65 | 130 |  | 16082.65
20:00 | 15714.46 | 125 |  | 15845.46
21:00 | 15625 | 85 |  | 15714
22:00 | 15362.47 | 55 |  | 15419.47
23:00 | 15143.53 | 35 |  | 15180.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 18-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 112 | 36 | 270 | 132 | 1014 | 442 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 103 | 31 | 250 | 132 | 942 | 408
2:00 | 112 | 34 | 280 | 126 | 948 | 382 |  | Import | 0
3:00 | 122 | 33 | 310 | 124 | 1026 | 378
4:00 | 117 | 25 | 300 | 114 | 1046 | 376 | Ishurdi-Ghorashal Ckt-2 | Export | 3283563.63
5:00 | 112 | 20 | 280 | 102 | 1028 | 386
6:00 | 128 | 28 | 310 | 104 | 1114 | 434 |  | Import | 0
7:00 | 108 | 18 | 260 | 94 | 1260 | 424
8:00 | 124 | 17 | 280 | 82 | 1400 | 496 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 163 | 43 | 350 | 86 | 1542 | 556
10:00 | 172 | 44 | 390 | 104 | 1570 | 598 |  | Import | 0
11:00 | 168 | 46 | 410 | 138 | 1562 | 624
12:00 | 160 | 48 | 380 | 146 | 1474 | 596 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 154 | 44 | 360 | 140 | 1434 | 586
14:00 | 161 | 50 | 400 | 174 | 1500 | 590 |  | Import | 0
15:00 | 165 | 55 | 410 | 178 | 1498 | 606
16:00 | 163 | 55 | 380 | 152 | 1500 | 574 | Gopalganj-Aminbazar Ckt-1 | Export | 15470000
17:00 | 158 | 52 | 370 | 166 | 1404 | 558
18:00 | 123 | 30 | 300 | 152 | 1170 | 484 |  | Import | 0
18:30 | 109 | 24 | 280 | 144 | 1192 | 498
19:00 | 122 | 30 | 310 | 150 | 1288 | 534 | Gopalganj-Aminbazar Ckt-2 | Export | 15440000
19:30 | 125 | 36 | 310 | 146 | 1248 | 550
20:00 | 135 | 39 | 330 | 140 | 1400 | 576 |  | Import | 0
21:00 | 127 | 34 | 300 | 134 | 1230 | 544
22:00 | 135 | 41 | 330 | 146 | 1252 | 550 |  | Total Export | 34193563.63
23:00 | 140 | 41 | 340 | 144 | 1306 | 566 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9266.12 | 6271.35 | 15537.47 | DAILY GENERATION CURVE
00:30 | 9241.12 | 6100.62 | 15341.74
01:00 | 9216.12 | 5929.89 | 15146.01 | 18-10-2026
01:30 | 9094.62 | 5885.99 | 14980.61
02:00 | 8973.12 | 5842.09 | 14815.21
02:30 | 8755.91 | 5778.7 | 14534.61
03:00 | 8538.7 | 5715.31 | 14254.01
03:30 | 8400.7 | 5634.38 | 14035.08
04:00 | 8262.7 | 5553.45 | 13816.15
04:30 | 8220.6 | 5457.285 | 13677.885
05:00 | 8178.5 | 5361.12 | 13539.62
05:30 | 8010.01 | 5358.035 | 13368.045
06:00 | 7841.52 | 5354.95 | 13196.47
06:30 | 7815.83 | 5494.635 | 13310.465
07:00 | 7790.14 | 5634.32 | 13424.46
07:30 | 7743.94 | 5689.93 | 13433.87
08:00 | 7697.74 | 5745.54 | 13443.28
08:30 | 7710.505 | 5807.605 | 13518.11
09:00 | 7723.27 | 5869.67 | 13592.94
09:30 | 7836.28 | 5920.375 | 13756.655
10:00 | 7949.29 | 5971.08 | 13920.37
10:30 | 8041.07 | 6050.675 | 14091.745
11:00 | 8132.85 | 6130.27 | 14263.12
11:30 | 8427.01 | 6194.355 | 14621.365
12:00 | 8721.17 | 6258.44 | 14979.61
12:30 | 8769.38 | 6318.875 | 15088.255
13:00 | 8817.59 | 6379.31 | 15196.9
13:30 | 8782.15 | 6392.89 | 15175.04
14:00 | 8746.71 | 6406.47 | 15153.18
14:30 | 8868.54 | 6400.405 | 15268.945
15:00 | 8990.37 | 6394.34 | 15384.71
15:30 | 8965.355 | 6302.725 | 15268.08
16:00 | 8940.34 | 6211.11 | 15151.45
16:30 | 8860.975 | 6133.215 | 14994.19
17:00 | 8781.61 | 6055.32 | 14836.93
17:30 | 9225.295 | 6286.08 | 15511.375
18:00 | 9668.98 | 6516.84 | 16185.82
18:30 | 9651.38 | 6600.08 | 16251.46
19:00 | 9633.78 | 6683.32 | 16317.1
19:30 | 9351.28 | 6595.37 | 15946.65
20:00 | 9167.28 | 6547.18 | 15714.46
20:30 | 9191.53 | 6478.2 | 15669.73 |  | Executive Engineer
21:00 | 9215.78 | 6409.22 | 15625 |  | Network Operation Division
21:30 | 9096.78 | 6396.955 | 15493.735
22:00 | 8977.78 | 6384.69 | 15362.47
22:30 | 8890.28 | 6362.72 | 15253
23:00 | 8802.78 | 6340.75 | 15143.53

## En-Curve
QF-LDC-12
Date | 18-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3114 | 1659 | 854 | 0 | 68 | 1378.55 | 221 | 5138.6 | 0 | 669.42 | 2434.9 | 0 | 0 | 0 | 231 | DAILY ENERGY CURVE
00:30 | 3160.5 | 1628.25 | 886 | 0 | 66 | 1301.02 | 221 | 5014.9 | 0 | 597.92 | 2466.15 | 0 | 0 | 0 | 196 | 18-10-2026
01:00 | 3207 | 1597.5 | 918 | 0 | 64 | 1223.49 | 221 | 4891.2 | 0 | 526.42 | 2497.4 | 0 | 0 | 0 | 161
01:30 | 3227 | 1545.5 | 918.5 | 0 | 64 | 1219.09 | 221 | 4746.2 | 0 | 510.42 | 2528.9 | 0 | 0 | 0 | 87.5 | Energy Generated | 356.7256 |  | MKWHr
02:00 | 3247 | 1493.5 | 919 | 0 | 64 | 1214.69 | 221 | 4601.2 | 0 | 494.42 | 2560.4 | 0 | 0 | 0 | 14 | Energy not Served | 1.196 |  | MKWHr
02:30 | 3265.5 | 1491.5 | 919 | 0 | 63 | 1215.8 | 221 | 4572.2 | 0 | 417.21 | 2369.4 | 0 | 0 | 0 | 7 | Total Energy Requirement | 357.9216 |  | MKWHr
03:00 | 3284 | 1489.5 | 919 | 0 | 62 | 1216.91 | 221 | 4543.2 | 0 | 340 | 2178.4 | 0 | 0 | 0 | 0
03:30 | 3287 | 1483.5 | 918.5 | 0 | 62 | 1215.58 | 221 | 4542.2 | 0 | 284.5 | 2020.8 | 0 | 0 | 0 | 0
04:00 | 3290 | 1477.5 | 918 | 0 | 62 | 1214.25 | 221 | 4541.2 | 0 | 229 | 1863.2 | 0 | 0 | 0 | 0
04:30 | 3367 | 1491.5 | 918 | 0 | 61 | 1217.185 | 220.5 | 4498.1 | 1 | 220 | 1683.6 | 0 | 0 | 0 | 0
05:00 | 3444 | 1505.5 | 918 | 0 | 60 | 1220.12 | 220 | 4455 | 2 | 211 | 1504 | 0 | 0 | 0 | 0
05:30 | 3464.5 | 1470 | 918.5 | 0 | 57 | 1214.535 | 219.5 | 4420.5 | 1.01 | 211 | 1391.5 | 0 | 0 | 0 | 0
06:00 | 3485 | 1434.5 | 919 | 0 | 54 | 1208.95 | 219 | 4386 | 0.02 | 211 | 1279 | 0 | 0 | 0 | 0
06:30 | 3505 | 1450 | 919 | 0 | 53 | 1213.095 | 219 | 4480.3 | 48.57 | 212 | 1210.5 | 0 | 0 | 0 | 0
07:00 | 3525 | 1465.5 | 919 | 0 | 52 | 1217.24 | 219 | 4574.6 | 97.12 | 213 | 1142 | 0 | 0 | 0 | 0
07:30 | 3536.5 | 1453 | 918.5 | 0 | 55 | 1217.64 | 219 | 4573.8 | 192.43 | 196 | 1072 | 0 | 0 | 0 | 0
08:00 | 3548 | 1440.5 | 918 | 0 | 58 | 1218.04 | 219 | 4573 | 287.74 | 179 | 1002 | 0 | 0 | 0 | 0
08:30 | 3543.5 | 1435.5 | 918.5 | 0 | 59 | 1216.735 | 219 | 4564.5 | 388.875 | 179 | 993.5 | 0 | 0 | 0 | 10
09:00 | 3539 | 1430.5 | 919 | 0 | 60 | 1215.43 | 219 | 4556 | 490.01 | 179 | 985 | 0 | 0 | 0 | 20
09:30 | 3536 | 1468.5 | 918.5 | 0 | 61 | 1221.145 | 219.5 | 4557.5 | 556.51 | 196 | 1022 | 0 | 0 | 0 | 10
10:00 | 3533 | 1506.5 | 918 | 0 | 62 | 1226.86 | 220 | 4559 | 623.01 | 213 | 1059 | 0 | 0 | 0 | 0
10:30 | 3555 | 1510.5 | 918.5 | 0 | 64 | 1222.43 | 220 | 4584 | 659.815 | 212.5 | 1145 | 0 | 0 | 0 | 0
11:00 | 3577 | 1514.5 | 919 | 0 | 66 | 1218 | 220 | 4609 | 696.62 | 212 | 1231 | 0 | 0 | 0 | 0
11:30 | 3578.5 | 1537.5 | 919 | 0 | 68 | 1214.015 | 220 | 4616.8 | 691.34 | 271.71 | 1504.5 | 0 | 0 | 0 | 0
12:00 | 3580 | 1560.5 | 919 | 0 | 70 | 1210.03 | 220 | 4624.6 | 686.06 | 331.42 | 1778 | 0 | 0 | 0 | 0
12:30 | 3518.5 | 1470 | 919 | 0 | 70 | 1207.46 | 220.5 | 4638.6 | 660.425 | 355.17 | 2028.6 | 0 | 0 | 0 | 0
13:00 | 3457 | 1379.5 | 919 | 0 | 70 | 1204.89 | 221 | 4652.6 | 634.79 | 378.92 | 2279.2 | 0 | 0 | 0 | 0
13:30 | 3382.5 | 1370.75 | 918.5 | 0 | 71 | 1207.93 | 221 | 4672.2 | 591.04 | 367.42 | 2372.7 | 0 | 0 | 0 | 22.5
14:00 | 3308 | 1362 | 918 | 0 | 72 | 1210.97 | 221 | 4691.8 | 547.29 | 355.92 | 2466.2 | 0 | 0 | 0 | 45
14:30 | 3371 | 1406.25 | 918.5 | 0 | 72 | 1220.43 | 221 | 4691.8 | 484.845 | 356.42 | 2526.7 | 0 | 0 | 0 | 32.5
15:00 | 3434 | 1450.5 | 919 | 0 | 72 | 1229.89 | 221 | 4691.8 | 422.4 | 356.92 | 2587.2 | 0 | 0 | 0 | 20
15:30 | 3430 | 1432.5 | 919 | 0 | 71 | 1222.58 | 221 | 4691.8 | 306.98 | 359.92 | 2613.3 | 0 | 0 | 0 | 20
16:00 | 3426 | 1414.5 | 919 | 0 | 70 | 1215.27 | 221 | 4691.8 | 191.56 | 362.92 | 2639.4 | 0 | 0 | 0 | 20
16:30 | 3362 | 1356.5 | 919 | 0 | 69 | 1230.81 | 221 | 4618.9 | 117.66 | 382.67 | 2716.65 | 0 | 0 | 0 | 20
17:00 | 3298 | 1298.5 | 919 | 0 | 68 | 1246.35 | 221 | 4546 | 43.76 | 402.42 | 2793.9 | 0 | 0 | 0 | 20
17:30 | 3312.5 | 1323.5 | 919 | 0 | 73 | 1319.195 | 221 | 4706.8 | 21.88 | 572.92 | 3041.58 | 0 | 0 | 0 | 86.495
18:00 | 3327 | 1348.5 | 919 | 0 | 78 | 1392.04 | 221 | 4867.6 | 0 | 743.42 | 3289.26 | 0 | 0 | 0 | 152.99
18:30 | 3408 | 1430.5 | 919 | 0 | 76 | 1404.18 | 220.5 | 4994.2 | 0 | 775.92 | 3023.16 | 0 | 0 | 0 | 182.495
19:00 | 3489 | 1512.5 | 919 | 0 | 74 | 1416.32 | 220 | 5120.8 | 0 | 808.42 | 2757.06 | 0 | 0 | 0 | 212
19:30 | 3477 | 1548.5 | 919 | 0 | 74 | 1420.37 | 220 | 5191.8 | 0 | 742.42 | 2353.56 | 0 | 0 | 0 | 130
20:00 | 3514 | 1384.5 | 919 | 0 | 72 | 1415.18 | 219 | 5271.8 | 0 | 729.42 | 2189.56 | 0 | 0 | 0 | 125
20:30 | 3505 | 1405 | 919 | 0 | 70 | 1419.8 | 219.5 | 5293.8 | 0 | 722.42 | 2115.21 | 0 | 0 | 0 | 105
21:00 | 3496 | 1425.5 | 919 | 0 | 68 | 1424.42 | 220 | 5315.8 | 0 | 715.42 | 2040.86 | 0 | 0 | 0 | 85
21:30 | 3463.5 | 1417.5 | 919 | 0 | 69 | 1419.155 | 220 | 5315.8 | 0 | 685.42 | 1984.36 | 0 | 0 | 0 | 70
22:00 | 3431 | 1409.5 | 919 | 0 | 70 | 1413.89 | 220 | 5315.8 | 0 | 655.42 | 1927.86 | 0 | 0 | 0 | 55
22:30 | 3410 | 1412.5 | 919 | 0 | 68 | 1417.92 | 220 | 5268.8 | 0 | 655.92 | 1880.86 | 0 | 0 | 0 | 45
23:00 | 3389 | 1415.5 | 919 | 0 | 66 | 1421.95 | 220 | 5221.8 | 0 | 656.42 | 1833.86 | 0 | 0 | 0 | 35
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 04:00 | 364 | 11:00 | Madunaghat | 404 | 03:00 | 392 | 21:00
Amtali | 412 | 05:00 | 406 | 12:00 | Meghnaghat | 392 | 05:00 | 375 | 12:00
Ashuganj | 402 | 03:00 | 379 | 18:30 | Mirsorai | 405 | 02:00 | 384 | 00:00
Bhulta | 400 | 05:00 | 375 | 11:00 | Payra | 413 | 05:00 | 408 | 00:00
Bibiana | 387 | 02:00 | 380 | 11:00 | Rahanpur | 410 | 03:00 | 393 | 18:30
BIPTC | 399 | 05:00 | 393 | 15:00 | Rampal | 396 | 05:00 | 387 | 11:00
Bogura | 402 | 03:00 | 379 | 18:30
Gopalganj | 395 | 06:00 | 381 | 12:00
Kaliakoir | 377 | 03:00 | 358 | 12:00
Korerhat | 403 | 02:00 | 387 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 06:00 | 218 | 11:00 | Hasnabad | 228 | 06:00 | 216 | 12:00
AKSML | 238 | 02:00 | 229 | 11:00 | Hathazari | 236 | 02:00 | 230 | 11:00
Aminbazar | 234 | 04:00 | 219 | 11:00 | Ishurdi | 236 | 03:00 | 220 | 18:30
Ashuganj | 229 | 04:00 | 217 | 18:30 | Jhenaidah | 227 | 06:00 | 210 | 18:30
Ashuganj-400 | 229 | 04:00 | 217 | 18:30 | Kachua | 230 | 17:00 | 220 | 19:30
Baghabari | 233 | 05:00 | 219 | 18:00 | Kaliakoir | 233 | 05:00 | 217 | 12:00
Barapukuria | 233 | 05:00 | 215 | 18:30 | Keranigonj | 231 | 05:00 | 215 | 12:00
Barapukuria-230 | 233 | 05:00 | 215 | 18:30 | Khulna(S) | 228 | 06:00 | 217 | 18:30
Barapukuria(N) | 239 | 03:00 | 217 | 18:30 | Korerhat | 229 | 02:00 | 219 | 21:00
Barishal | 234 | 05:00 | 224 | 00:00 | Madunaghat | 240 | 01:00 | 233 | 22:00
Bheramara | 234 | 03:00 | 218 | 18:30 | Madunaghat-400 | 242 | 03:00 | 234 | 12:00
Bhulta | 228 | 05:00 | 212 | 11:00 | Maniknagar | 226 | 04:00 | 210 | 12:00
Bibiana | 223 | 04:00 | 216 | 19:30 | Meghnaghat | 233 | 05:00 | 220 | 12:00
BIPTC | 236 | 03:00 | 218 | 18:30 | Meghnaghat-400 | 228 | 04:00 | 215 | 12:00
Birulia | 234 | 05:00 | 218 | 11:00 | Mirsorai | 230 | 02:00 | 220 | 19:30
Bogura | 240 | 03:00 | 225 | 18:30 | Naogaon | 226 | 02:00 | 207 | 18:30
Bogura-400 | 239 | 03:00 | 224 | 18:30 | Purbasadipur | 237 | 03:00 | 216 | 10:00
Borhanuddin | 233 | 08:00 | 224 | 00:00 | Rajshahi | 233 | 03:00 | 217 | 18:30
BSRM | 230 | 02:00 | 221 | 21:00 | Rampal | 226 | 05:00 | 217 | 18:30
Charfasson | 232 | 06:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 17:00 | 220 | 19:30 | Rampura | 228 | 05:00 | 210 | 12:00
Cumilla(N) | 225 | 06:00 | 214 | 23:00 | Shikalbaha | 239 | 02:00 | 233 | 09:00
Faridpur | 235 | 06:00 | 226 | 00:00 | Shyampur | 228 | 04:00 | 215 | 12:00
Fenchuganj | 224 | 06:00 | 218 | 18:30 | Siddhirganj | 227 | 00:00 | 213 | 12:00
Feni | 227 | 02:00 | 218 | 19:00 | Sirajgonj | 236 | 06:00 | 226 | 18:30
Ghorashal | 230 | 04:00 | 110 | 13:00 | Sreepur | 226 | 05:00 | 211 | 18:30
Ghorashal-230 | 220 | 05:00 | 201 | 12:00 | Tongi | 222 | 04:00 | 202 | 11:00
Gopalganj | 237 | 06:00 | 229 | 00:00
GPH | 236 | 02:00 | 230 | 11:00
Haripur | 227 | 04:00 | 213 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 124 | 12:00 | Madanganj | 136 | 02:00 | 129 | 11:00
Agargaon | 135 | 04:00 | 124 | 12:00 | Madaripur | 133 | 05:00 | 128 | 00:00
Agrabad | 136 | 01:00 | 130 | 11:00 | Madartek | 136 | 05:00 | 124 | 12:00
AKS | 135 | 02:00 | 130 | 12:00 | Madunaghat | 139 | 03:00 | 135 | 10:00
Aminbazar | 134 | 03:00 | 124 | 11:00 | Magura | 134 | 06:00 | 121 | 18:30
Amnura | 131 | 01:00 | 126 | 10:00 | Mahasthangarh | 137 | 02:00 | 127 | 10:00
Araihazar | 125 | 05:00 | 117 | 11:00 | Maijdee | 129 | 02:00 | 123 | 19:30
Ashuganj | 133 | 05:00 | 125 | 18:30 | Manikganj | 130 | 03:00 | 124 | 11:00
Ashuganj-230 | 136 | 04:00 | 131 | 11:00 | Maniknagar | 135 | 05:00 | 124 | 12:00
Bagerhat | 126 | 05:00 | 120 | 00:00 | Matarbari | 118 | 09:00 | 106 | 22:00
Bajitpur | 130 | 06:00 | 121 | 19:00 | Matuail | 138 | 05:00 | 128 | 12:00
Bakerganj | 134 | 20:00 | 129 | 00:00 | Metrorail_Motijheel | 135 | 05:00 | 120 | 12:00
Bakulia | 137 | 03:00 | 131 | 11:00 | Metrorail_Uttara | 134 | 04:00 | 120 | 12:00
Banani | 135 | 04:00 | 122 | 12:00 | Millgate | 134 | 03:00 | 121 | 12:00
Bangabhaban | 137 | 05:00 | 124 | 12:00 | Mirpur | 134 | 04:00 | 123 | 11:00
Barapukuria | 137 | 06:00 | 124 | 18:30 | Mirzapur | 133 | 04:00 | 126 | 07:00
Barguna | 133 | 17:00 | 129 | 00:00 | Mithapukur | 137 | 03:00 | 123 | 10:00
Barishal | 134 | 06:00 | 129 | 00:00 | MI_Cement | 134 | 04:00 | 122 | 12:00
Barishal-230 | 134 | 05:00 | 129 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 136 | 02:00 | 131 | 11:00 | Mogbazar | 138 | 07:00 | 125 | 11:00
Baroirhat | 133 | 04:00 | 128 | 12:00 | Mongla | 130 | 20:00 | 121 | 00:00
Bashundhara | 136 | 03:00 | 120 | 11:00 | Monirampur | 126 | 06:00 | 116 | 00:00
BashundharaCement | 136 | 02:00 | 129 | 12:00 | Motijheel | 137 | 05:00 | 124 | 12:00
Beanibazar | 124 | 07:00 | 117 | 19:30 | Muktagacha | 129 | 18:30 | 116 | 07:00
Benapole | 132 | 03:00 | 116 | 00:00 | Munshiganj | 137 | 03:00 | 127 | 11:00
Bhaluka | 130 | 03:00 | 119 | 18:30 | Muradnagar | 124 | 03:00 | 118 | 19:00
Bhandaria | 131 | 06:00 | 124 | 00:00 | Mymensingh | 147 | 21:00 | 113 | 18:30
Bhangura | 134 | 03:00 | 126 | 18:30 | Nabinagar | 134 | 04:00 | 120 | 15:00
Bheramara | 138 | 03:00 | 127 | 18:30 | Naogaon | 136 | 02:00 | 125 | 18:30
Bheramara(GK) | 137 | 05:00 | 127 | 18:30 | Narail | 134 | 06:00 | 119 | 18:30
Bhulta | 124 | 08:00 | 120 | 00:00 | Narinda | 135 | 05:00 | 124 | 12:00
Bhulta-400 | 128 | 04:00 | 118 | 11:00 | Narshingdi | 126 | 07:00 | 116 | 12:00
Birulia | 137 | 04:00 | 127 | 11:00 | Natore | 133 | 04:00 | 126 | 18:30
Bog-Sherpur | 137 | 03:00 | 127 | 18:30 | Nawabganj | 136 | 05:00 | 125 | 12:00
Bogura | 138 | 17:00 | 130 | 11:00 | Netrakona | 122 | 05:00 | 108 | 18:00
Bogura-230 | 140 | 03:00 | 130 | 18:30 | New | 132 | 05:00 | 122 | 11:00
Brahmanbaria | 131 | 08:00 | 122 | 18:30 | Niamatpur | 134 | 06:00 | 126 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 134 | 03:00 | 124 | 12:00 | Noapara | 130 | 06:00 | 122 | 00:00
Chandina | 129 | 02:00 | 123 | 19:30 | Pabna | 135 | 03:00 | 124 | 18:30
Chandpur | 135 | 17:00 | 125 | 19:30 | Palashbari | 131 | 06:00 | 121 | 18:00
Chandraghona | 139 | 02:00 | 134 | 12:00 | Panchagarh | 143 | 03:00 | 126 | 10:00
Chapai | 132 | 06:00 | 127 | 18:30 | Patiya | 135 | 06:00 | 128 | 12:00
Charsaidpur | 138 | 03:00 | 128 | 12:00 | Patnitala | 133 | 03:00 | 126 | 18:00
Chauddagram | 130 | 01:00 | 124 | 19:30 | Patuakhali | 134 | 06:00 | 130 | 00:00
Chhatak | 120 | 05:00 | 113 | 19:00 | Payra | 135 | 07:00 | 133 | 00:00
Chowmuhani | 129 | 02:00 | 123 | 19:30 | PHP | 133 | 02:00 | 127 | 11:00
Chuadanga | 134 | 06:00 | 120 | 18:30 | Postogola | 136 | 04:00 | 125 | 12:00
Coxsbazar | 118 | 14:00 | 105 | 21:00 | Pubail | 130 | 03:00 | 119 | 11:00
Cumilla(N) | 129 | 06:00 | 123 | 19:00 | Purbachal | 136 | 03:00 | 123 | 12:00
Cumilla(S) | 133 | 03:00 | 123 | 19:00 | Purbasadipur | 138 | 03:00 | 124 | 10:00
Daganbhuiyan | 131 | 02:00 | 125 | 19:30 | Rahanpur | 136 | 05:00 | 130 | 18:30
Daudkandi | 123 | 05:00 | 117 | 00:00 | Rahanpur-400 | 137 | 03:00 | 131 | 18:30
DhakaUniversity | 136 | 03:00 | 124 | 12:00 | Rahim | 138 | 04:00 | 129 | 12:00
Dhamrai | 134 | 05:00 | 122 | 15:00 | Rajbari | 132 | 06:00 | 126 | 00:00
Dhanmondi | 139 | 06:00 | 129 | 12:00 | Rajendrapur | 131 | 03:00 | 122 | 18:00
Dohazari | 130 | 05:00 | 122 | 20:00 | Rajshahi | 132 | 05:00 | 125 | 11:00
Faridpur | 132 | 04:00 | 128 | 00:00 | Rajshahi-230 | 133 | 04:00 | 125 | 18:30
Fatullah | 137 | 03:00 | 124 | 11:00 | Ramganj | 130 | 14:00 | 121 | 21:00
Fenchuganj | 131 | 06:00 | 127 | 00:00 | Rampur | 137 | 06:00 | 131 | 12:00
Feni | 132 | 17:00 | 125 | 11:00 | Rampura | 136 | 04:00 | 124 | 12:00
Feni-230 | 132 | 02:00 | 126 | 19:30 | Rangamati | 137 | 01:00 | 134 | 10:00
Ghatail | 128 | 04:00 | 116 | 07:00 | Rangpur | 131 | 15:00 | 122 | 18:30
Ghorashal | 132 | 04:00 | 123 | 10:00 | Ruppur | 137 | 04:00 | 128 | 18:30
Goalpara | 132 | 05:00 | 124 | 18:30 | Saidpur | 135 | 06:00 | 124 | 10:00
Gollamari | 131 | 06:00 | 125 | 00:00 | Santhia | 135 | 05:00 | 126 | 18:30
Gopalganj | 130 | 06:00 | 125 | 00:00 | Satkhira | 127 | 06:00 | 117 | 00:00
Gopalganj-400 | 134 | 06:00 | 129 | 00:00 | Satmasjid | 135 | 04:00 | 123 | 12:00
Gulshan | 136 | 05:00 | 123 | 12:00 | Savar | 133 | 04:00 | 123 | 10:00
Halishahar | 138 | 03:00 | 130 | 12:00 | SevenRings | 134 | 19:30 | 122 | 11:00
Haripur | 139 | 05:00 | 129 | 12:00 | ShahCement | 138 | 03:00 | 128 | 12:00
HaripurSBU | 138 | 04:00 | 130 | 15:00 | Shahjadpur | 134 | 05:00 | 130 | 00:00
Hasnabad | 136 | 03:00 | 125 | 12:00 | Shahjibazar | 128 | 06:00 | 120 | 22:00
Hathazari | 138 | 02:00 | 133 | 11:00 | Shahmirpur | 136 | 03:00 | 131 | 12:00
Hatirjheel | 136 | 04:00 | 123 | 12:00 | Shariatpur | 132 | 06:00 | 125 | 00:00
Ishurdi | 138 | 03:00 | 128 | 18:30 | Sherpur | 130 | 19:00 | 119 | 00:00
Jaldhaka | 134 | 02:00 | 121 | 18:30 | Shikalbaha | 126 | 02:00 | 121 | 23:00
Jamalpur | 135 | 19:00 | 117 | 07:00 | Shikalbaha-230 | 138 | 02:00 | 132 | 12:00
Jashore | 134 | 06:00 | 118 | 00:00 | Shitalakhya | 134 | 04:00 | 122 | 12:00
Jhenaidah | 136 | 05:00 | 123 | 18:30 | Sholosohor | 138 | 02:00 | 133 | 10:00
Jhenaidah-230 | 138 | 06:00 | 125 | 18:30 | Shomvuganj | 122 | 08:00 | 116 | 15:00
Joydebpur | 128 | 03:00 | 116 | 14:00 | Shyampur | 135 | 06:00 | 126 | 12:00
Joypurhat | 133 | 06:00 | 126 | 11:00 | Shyampur-230 | 137 | 04:00 | 126 | 12:00
Juldah | 137 | 04:00 | 131 | 12:00 | Siddhirganj | 138 | 04:00 | 129 | 12:00
Kabirpur | 135 | 04:00 | 117 | 15:00 | Sirajganj | 132 | 06:00 | 123 | 18:30
Kachua | 131 | 03:00 | 125 | 19:30 | Sitakunda | 137 | 03:00 | 132 | 11:00
Kaliakoir | 137 | 02:00 | 131 | 10:00 | Sonargaon | 135 | 02:00 | 129 | 11:00
Kaliganj | 136 | 06:00 | 124 | 18:30 | Sreemongol | 129 | 08:00 | 122 | 12:00
Kallyanpur | 130 | 01:00 | 123 | 12:00 | Sreepur | 133 | 05:00 | 124 | 18:30
Kalurghat | 139 | 03:00 | 134 | 11:00 | Srinagar | 136 | 05:00 | 126 | 12:00
Kamrangirchar | 136 | 05:00 | 120 | 12:00 | SSM | 140 | 00:00 | 135 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 118 | 06:00 | 110 | 19:30
Kasba | 125 | 03:00 | 118 | 19:00 | Sylhet | 123 | 05:00 | 118 | 00:00
Kazla | 137 | 06:00 | 125 | 12:00 | Sylhet_(South) | 126 | 08:00 | 120 | 18:30
Keranigonj | 137 | 05:00 | 126 | 12:00 | Tangail | 128 | 04:00 | 121 | 18:30
Khagrachori | 137 | 03:00 | 132 | 12:00 | Taraganj | 134 | 03:00 | 122 | 18:00
Khulna | 131 | 06:00 | 123 | 00:00 | Tasnim | 137 | 05:00 | 127 | 12:00
Khulna(S) | 132 | 06:00 | 124 | 18:30 | Thakurgaon | 143 | 03:00 | 126 | 10:00
Khulshi | 136 | 02:00 | 129 | 12:00 | TK | 138 | 03:00 | 135 | 10:00
Kishoreganj | 127 | 05:00 | 119 | 18:30 | Tongi | 136 | 04:00 | 123 | 11:00
Kodda | 134 | 02:00 | 117 | 15:00 | Ullahpara | 134 | 01:00 | 125 | 18:30
Korerhat | 134 | 17:00 | 126 | 19:30 | Ullon | 136 | 05:00 | 124 | 12:00
KSRM | 137 | 00:00 | 132 | 11:00 | Uttara | 133 | 04:00 | 119 | 12:00
Kulaura | 131 | 08:00 | 125 | 19:00 | UttaraNew | 134 | 04:00 | 120 | 11:00
Kurigram | 134 | 03:00 | 118 | 18:30 | Zigatola | 137 | 06:00 | 125 | 15:00
Kushtia | 135 | 05:00 | 124 | 18:00
Laksam | 130 | 02:00 | 123 | 23:00
Lakshmipur | 127 | 02:00 | 122 | 19:30
Lalbag | 136 | 04:00 | 125 | 12:00
Lalmonirhat | 129 | 06:00 | 118 | 18:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division