## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-10-2026 | during | 20-10-2026 | during | 20-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 384 | 373 | 412 | 412 | 400 | 400 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 290 | 335 | 335 | 318 | 318 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 90 | 94 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5.5 | 5.5 | 24.75 | 24.75 | 5.5 | 5.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 18 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 48 | 52.19 | 52.19 | 24 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 98 | 196 | 300 | 300 | 98 | 98 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 97 | 133 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 0 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 144 | 157 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP | 1*448+1*208 | 584 | 584 | 440 | 460 | 584 | 584 | 526 | 526 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 490 | 450 | 583 | 583 | 525 | 525 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2521.92 | 2640.92 | 5558.55 | 5528.55 | 2621.92 | 2808.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 2 | 25.5 | 25.5 | 25.5 | 17 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 215 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 92 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 21 | 14 | 24 | 14 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 57 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 37 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 25 | 51 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.19 | 0 | 3.35 | 0 | 3.35 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 194 | 300 | 300 | 51 | 212 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 35 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 76 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 150 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 600 | 1050 | 1224 | 1224 | 600 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 4 | 0 | 4 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 880 | 1080 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2410.19 | 3533.5 | 4096.31 | 4151.96 | 2799.35 | 3800.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 207 | 180 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 323 | 284 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 280 | 275 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 200 | 0 | 280 | 280 | 200 | 200 | FGMO operation requires an NG pressure of 31 bar.
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 20 | 52.82 | 52.82 | 45 | 45 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 35 | 195 | 195 | 55 | 55 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 133 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 7 | 23 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 15 | 65 | 163 | 163 | 50 | 50 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 111 | 151 | 200 | 200 | 135 | 119 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 72 | 84 | 82 | 84 | 82 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 30 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 12 | 24.5 | 24.5 | 11 | 11 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 100 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 70 | 69 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 30 | 108 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1665 | 1623.2 | 2643.44 | 2571.44 | 2008.21 | 1984.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-10-2026 | during | 20-10-2026 | during | 20-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 161 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 88 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.07 | 0 | 49.5 | 0 | 49.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 283.37 | 308 | 673.1 | 601.5 | 307.6 | 322
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 0 | 0 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 95 | 100 | 138 | 138 | 138 | 138 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 22 | 83 | 83 | 11 | 11 | machine problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 102 | 100 | 100 | 100 | 100 | Gas shortage
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 16 | 16 | 13 | 13 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 256 | 262 | 341 | 341 | 260 | 260 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 398 | 400 | 400 | 400 | 400 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 395 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1466 | 1509 | 1674 | 1674 | 1522 | 1522
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 843 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2304.2 | 2246.2 | 3294.2 | 3204.2 | 2729.2 | 2639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1156 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 112 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Station shutdown for GT-11& STG Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 100 | 150 | 150 | 35 | 100 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1925.59 | 2053.6 | 2158.6 | 2157.6 | 1944.6 | 2008.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 61.65 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 233 | 191 | 413.79 | 413.79 | 372.41 | 372.41 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 34 | 34 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 55 | 50 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.59 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1234.8 | 1415.66 | 1200 | 1400 | 1200 | 1400 | Coal Shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.71 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1872.95 | 2014.86 | 3021.11 | 2998.99 | 2718.73 | 2867.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 90 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 188 | 0 | 177.37 | 0 | 177.37 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 370 | 228 | 474.37 | 262 | 384.37 | 251
System Total |  |  |  |  | 28843.2 | 28692.211 | 14819.22 | 16157.28 | 23593.68 | 23150.24 | 17035.98 | 18204.4
Forecast Scenario (20-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15050 |  | 0 |  | 15050
|  |  |  | 1:00 | 14790 |  | 0 |  | 14790
|  |  |  | 2:00 | 14470 |  | 0 |  | 14470
|  |  |  | 3:00 | 13690 |  | 0 |  | 13690
|  |  |  | 4:00 | 13120 |  | 0 |  | 13120
|  |  |  | 5:00 | 12710 |  | 0 |  | 12710
|  |  |  | 6:00 | 12490 |  | 0 |  | 12490
|  |  |  | 7:00 | 12570 |  | 0 |  | 12570
|  |  |  | 8:00 | 12550 |  | 0 |  | 12550
|  |  |  | 9:00 | 12920 |  | 0 |  | 12920
|  |  |  | 10:00 | 13370 |  | 0 |  | 13370
|  |  |  | 11:00 | 13980 |  | 0 |  | 13980
|  |  |  | 12:00 | 14490 |  | 0 |  | 14490
|  |  |  | 13:00 | 14730 |  | 0 |  | 14730
|  |  |  | 14:00 | 14710 |  | 0 |  | 14710
|  |  |  | 15:00 | 14400 |  | 0 |  | 14400
|  |  |  | 16:00 | 12800 |  | 0 |  | 12800
|  |  |  | 17:00 | 13890 |  | 0 |  | 13890
|  |  |  | 18:00 | 14630 |  | 0 |  | 14630
|  |  |  | 18:30 | 14865 |  | 0 |  | 14865
|  |  |  | 19:00 | 15100 |  | 0 |  | 15100
|  |  |  | 19:30 | 15040 |  | 0 |  | 15040
|  |  |  | 20:00 | 14980 |  | 0 |  | 14980
|  |  |  | 21:00 | 14610 |  | 0 |  | 14610
|  |  |  | 22:00 | 14710 |  | 0 |  | 14710
|  |  |  | 23:00 | 14460 |  | 0 |  | 14460
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 14490.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 335.22 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:12 hrs on 20-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-10-2026 | [28 empty] | Date: | 19-10-2026 | [28 empty] | Date: | 19-10-2026 | [28 empty] | Date: | 19-10-2026 | [28 empty] | Date: | 19-10-2026 | [16 empty] | Date: | 19-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 54 | 40 | 134 | 128 | 279 | 34 | 55 | 162 | 0 | 0 | 505 | 0 | 55 | 276 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 365 | 104 | 89 | 12 | 0 | 0 | 0 | 33 | 35 | 12 | 25 | 0 | 221 | 66 | 3 | 1080 | 16 | 0 | 50 | 25.5 | 60 | 220 | 0 | 0 | 0 | 1100 | 0 | 150 | 26 | 135 | 292 | 250 | 44 | 0 | 192 | 0 | 27 | 50 | 99 | 64 | 10 | 17 | 66 | 34 | 0 | 23 | 253 | 360 | 397 | 40 | 30 | 148 | 0 | 13 | 0 | 11 | 0 | 99 | 0 | 100 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8901.42 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 1392.88 | 0 | 40 | 0 | 113 | 76 | 0 | 50 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 115 | 0 | 0 | 1170.6 | 300 | 119 | 6438.88 | 15340.3 | 103.51
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 54 | 134 | 128 | 295 | 55 | 55 | 162 | 0 | 0 | 360 | 0 | 55 | 271 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 455 | 109 | 52 | 12 | 0 | 0 | 0 | 33 | 17 | 12 | 25 | 0 | 221 | 92 | 9 | 1080 | 16 | 0 | 50 | 25.5 | 105 | 220 | 0 | 0 | 0 | 880 | 0 | 150 | 26 | 130 | 290 | 250 | 44 | 0 | 194 | 0 | 68 | 50 | 139 | 67 | 10 | 17 | 64 | 50 | 0 | 23 | 250 | 400 | 397 | 40 | 30 | 141 | 0 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 23 | 8789.42 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1195 | 0 | 0 | 0 | 1199.52 | 0 | 40 | 0 | 55 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 6043.32 | 14832.74 | 103.5
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 54 | 133 | 90 | 98 | 45 | 55 | 162 | 0 | 0 | 405 | 0 | 55 | 320 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 485 | 109 | 52 | 12 | 0 | 0 | 0 | 33 | 17 | 12 | 25 | 0 | 221 | 93 | 13 | 1080 | 0 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 610 | 0 | 140 | 26 | 130 | 337 | 310 | 44 | 0 | 215 | 0 | 0 | 50 | 155 | 71 | 10 | 0 | 62 | 52 | 0 | 0 | 244 | 400 | 397 | 40 | 30 | 143 | 0 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 59 | 0 | 67 | 0 | 0 | 0 | 22 | 8428.42 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1188 | 0 | 0 | 0 | 1219.53 | 0 | 0 | 0 | 55 | 95 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 115 | 0 | 0 | 970 | 300 | 35 | 5780.73 | 14209.15 | 103.49
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 54 | 133 | 45 | 98 | 0 | 55 | 162 | 0 | 0 | 445 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 5.5 | 19 | 0 | 490 | 110 | 52 | 12 | 0 | 0 | 0 | 0 | 17 | 12 | 25 | 0 | 221 | 110 | 22 | 1080 | 0 | 0 | 50 | 0 | 105 | 219 | 0 | 0 | 0 | 600 | 0 | 150 | 26 | 130 | 306 | 305 | 44 | 0 | 198 | 0 | 0 | 50 | 120 | 0 | 10 | 0 | 60 | 26 | 0 | 0 | 242 | 400 | 397 | 40 | 30 | 155 | 0 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 59 | 0 | 24 | 0 | 0 | 0 | 24 | 8121.92 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 1234.2 | 0 | 0 | 0 | 1202.84 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 970 | 300 | 17 | 5682.24 | 13804.16 | 103.48
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 17 | 134 | 0 | 98 | 0 | 35 | 54 | 0 | 0 | 445 | 0 | 35 | 303 | 0 | 0 | 0 | 68 | 5.5 | 19 | 0 | 485 | 114 | 52 | 10 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 0 | 221 | 110 | 28 | 1080 | 0 | 0 | 50 | 0 | 51 | 222 | 0 | 0 | 0 | 600 | 0 | 150 | 53 | 130 | 301 | 300 | 44 | 0 | 194 | 0 | 0 | 50 | 68 | 0 | 10 | 0 | 60 | 0 | 0 | 0 | 240 | 400 | 398 | 40 | 30 | 156 | 0 | 13 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 59 | 0 | 8 | 0 | 0 | 0 | 24 | 7666.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1221.68 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 970 | 300 | 17 | 5530.88 | 13197.38 | 103.47
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 17 | 133 | 0 | 81 | 0 | 35 | 35 | 0 | 0 | 450 | 0 | 17 | 307 | 0 | 0 | 0 | 68 | 5.5 | 19 | 0 | 490 | 114 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 0 | 221 | 110 | 28 | 870 | 0 | 0 | 50 | 0 | 17 | 221 | 0 | 0 | 0 | 600 | 0 | 150 | 53 | 130 | 313 | 310 | 44 | 0 | 201 | 0 | 0 | 51 | 34 | 0 | 10 | 0 | 56 | 0 | 0 | 0 | 243 | 400 | 398 | 40 | 0 | 157 | 0 | 13 | 0 | 11 | 0 | 97 | 0 | 100 | 35 | 59 | 0 | 8 | 0 | 0 | 0 | 24 | 7341.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1215.97 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 970 | 300 | 17 | 5533.17 | 12874.67 | 103.46
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35 | 17 | 133 | 0 | 98 | 0 | 35 | 35 | 0 | 0 | 495 | 0 | 17 | 315 | 0 | 0 | 0 | 68 | 5.5 | 19 | 0 | 490 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 0.02 | 220 | 34 | 28 | 730 | 0 | 0 | 50 | 0 | 17 | 221 | 0 | 0 | 0 | 600 | 0 | 150 | 53 | 160 | 321 | 325 | 44 | 0 | 205 | 0 | 0 | 50 | 34 | 0 | 10 | 0 | 52 | 0 | 0 | 0 | 240 | 400 | 390 | 40 | 0 | 159 | 0 | 13 | 0 | 11 | 0 | 94 | 0 | 100 | 35 | 59 | 0 | 8 | 0 | 0 | 0 | 24 | 7187.52 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1212.53 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 970 | 300 | 17 | 5462.73 | 12650.25 | 103.45
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 19 | 105 | 60 | 98 | 0 | 0 | 55 | 0 | 0 | 510 | 0 | 17 | 320 | 0 | 0 | 5 | 86 | 5.5 | 19 | 0 | 500 | 32 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 0.47 | 220 | 34 | 26 | 730 | 0 | 0 | 46 | 0 | 17 | 221 | 0 | 0 | 0 | 600 | 2 | 150 | 55 | 160 | 335 | 335 | 44 | 3 | 212 | 0 | 0 | 30 | 34 | 0 | 10 | 0 | 54 | 0 | 17 | 0 | 247 | 400 | 390 | 40 | 0 | 159 | 1 | 13 | 0 | 11 | 0 | 94 | 0 | 100 | 35 | 59 | 3.4 | 38 | 0 | 0.3 | 8.93 | 24 | 7329.6 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 1234.2 | 0 | 0 | 0 | 1212.41 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 8.81 | 16 | 0 | 0 | 8.96 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0.55 | 0 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 0.7 | 23 | 0.11 | 16 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 17 | 5739.34 | 13068.94 | 103.4
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 54 | 115 | 60 | 98 | 15 | 0 | 72 | 0 | 0 | 460 | 0 | 17 | 296 | 0 | 0 | 14 | 143.42 | 5.5 | 19 | 0 | 490 | 30 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 0.9 | 219 | 34 | 4 | 730 | 0 | 0 | 45 | 0 | 17 | 222 | 0 | 0 | 0 | 600 | 5 | 147 | 55 | 140 | 292 | 265 | 44 | 24 | 190 | 0 | 0 | 30 | 60 | 6 | 10 | 0 | 58 | 19 | 46 | 0 | 245 | 400 | 395 | 40 | 0 | 155 | 5 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 59 | 10 | 65 | 0 | 0.9 | 24.93 | 24 | 7348.65 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 37.73 | 1234.2 | 0 | 0 | 0 | 1222.01 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 25.97 | 44 | 0 | 0 | 25.85 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 1.51 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 0 | 2.4 | 71 | 0.26 | 16 | 304 | 115 | 0 | 0 | 1170.6 | 300 | 17 | 5915.53 | 13264.18 | 103.43
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 54 | 115 | 60 | 98 | 15 | 17 | 72 | 0 | 0 | 420 | 0 | 30 | 308 | 0 | 0 | 23 | 143.42 | 5.5 | 19 | 0 | 460 | 30 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 2.48 | 219 | 34 | 2 | 730 | 0 | 0 | 45 | 0 | 17 | 221 | 0 | 0 | 0 | 600 | 14 | 100 | 55 | 140 | 311 | 265 | 44 | 45 | 191 | 0 | 0 | 30 | 34 | 63 | 10 | 0 | 60 | 25 | 28 | 0 | 243 | 400 | 397 | 40 | 0 | 140 | 8 | 13 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 59 | 15 | 75 | 0 | 1.6 | 38.17 | 24 | 7342.17 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 1203 | 0 | 0 | 0 | 1214.54 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 41.33 | 75 | 0 | 0 | 44.72 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 3.93 | 0 | 0 | 35 | 21 | 0 | 0 | 0 | 0 | 4.1 | 121 | 0.4 | 16 | 276 | 115 | 0 | 0 | 1156 | 300 | 17 | 5949.02 | 13291.19 | 103.42
10:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17 | 54 | 115 | 60 | 98 | 15 | 35 | 72 | 0 | 0 | 465 | 0 | 35 | 318 | 0 | 0 | 29 | 143.42 | 5.5 | 19 | 0 | 450 | 32 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.08 | 220 | 35 | 0 | 730 | 0 | 0 | 50 | 0 | 17 | 217 | 0 | 0 | 0 | 600 | 15 | 100 | 16 | 140 | 320 | 275 | 44 | 36 | 200 | 0 | 0 | 31 | 36 | 71 | 10 | 0 | 62 | 25 | 44 | 8 | 240 | 395 | 399 | 40 | 0 | 147 | 10 | 13 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 78 | 19.4 | 75 | 0 | 2 | 46.72 | 24 | 7553.12 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 77 | 1204 | 0 | 0 | 0 | 1217.92 | 0 | 0 | 0 | 55 | 2 | 0 | 0 | 0 | 8 | 53.89 | 96 | 0 | 0 | 56.59 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 5.02 | 0 | 0 | 35 | 28 | 0 | 0 | 0 | 0 | 5.3 | 156 | 0.53 | 16 | 300 | 115 | 0 | 0 | 1151 | 300 | 17 | 6071.25 | 13624.37 | 103.41
11:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17 | 54 | 97 | 63 | 98 | 15 | 35 | 108 | 0 | 0 | 485 | 0 | 35 | 320 | 0 | 0 | 32 | 143.42 | 5.5 | 19 | 0 | 440 | 72 | 51 | 2 | 0 | 0 | 0 | 1 | 35 | 0 | 25 | 3.45 | 220 | 45 | 0 | 730 | 6 | 0 | 50 | 0 | 40 | 215 | 0 | 0 | 0 | 600 | 9 | 100 | 16 | 220 | 335 | 290 | 44 | 20 | 202 | 0 | 0 | 15 | 66 | 70 | 10 | 7 | 68 | 25 | 57 | 7 | 244 | 391 | 395 | 40 | 0 | 155 | 12 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 78 | 21.7 | 75 | 0 | 2.2 | 48.79 | 24 | 7848.06 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 89 | 1234.2 | 0 | 0 | 0 | 1234.02 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 16 | 59.65 | 109 | 0 | 0 | 63.22 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 5.66 | 0 | 0 | 70 | 30 | 35 | 0 | 0 | 0 | 6 | 170 | 0.61 | 32 | 307 | 115 | 0 | 0 | 1153 | 300 | 17 | 6334.36 | 14182.42 | 103.4
12:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 54 | 97 | 90 | 98 | 15 | 35 | 144 | 0 | 0 | 490 | 0 | 35 | 318 | 0 | 0 | 33 | 143.42 | 5.5 | 19 | 0 | 440 | 91 | 51 | 25 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.19 | 221 | 76 | 0 | 880 | 35 | 0 | 45 | 2 | 92 | 213 | 0 | 0 | 0 | 600 | 16 | 108 | 16 | 200 | 323 | 280 | 44 | 20 | 207 | 0 | 30 | 15 | 111 | 70 | 10 | 52 | 70 | 30 | 72 | 7 | 256 | 395 | 390 | 40 | 0 | 154 | 12 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 78 | 22 | 75 | 0 | 2.3 | 47.07 | 24 | 8346.48 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 82 | 1234.2 | 0 | 0 | 0 | 1234.8 | 0 | 0 | 0 | 55 | 55 | 0 | 0 | 0 | 52.2 | 61.65 | 110 | 0 | 0 | 65.71 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 5.59 | 0 | 0 | 90 | 16 | 70 | 0 | 0 | 0 | 6 | 188 | 0.59 | 32 | 307 | 113 | 0 | 0 | 1156 | 300 | 17 | 6472.74 | 14819.22 | 103.39
13:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 17 | 54 | 97 | 123 | 97 | 15 | 35 | 162 | 0 | 0 | 505 | 0 | 35 | 300 | 0 | 0 | 31 | 123 | 5.5 | 18 | 0 | 440 | 102 | 51 | 30 | 0 | 0 | 0 | 7 | 35 | 24 | 25 | 3.17 | 221 | 103 | 0 | 1080 | 95 | 0 | 43 | 17 | 105 | 213 | 0 | 0 | 0 | 600 | 12 | 127 | 16 | 180 | 309 | 265 | 44 | 20 | 209 | 0 | 77 | 15 | 124 | 68 | 10 | 79 | 70 | 43 | 64 | 7 | 260 | 393 | 397 | 39 | 0 | 154 | 10 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 78 | 20.5 | 95 | 0 | 1.9 | 46.71 | 24 | 8849.78 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 79 | 1234.2 | 0 | 0 | 0 | 1192.54 | 0 | 0 | 0 | 55 | 70 | 0 | 8.5 | 0 | 52.2 | 58.18 | 105 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 2.04 | 0 | 0 | 115 | 28 | 98 | 0 | 0 | 0 | 5 | 136 | 0.42 | 32 | 292 | 113 | 0 | 0 | 1153 | 300 | 35 | 6416.19 | 15265.97 | 103.37
14:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 54 | 97 | 123 | 97 | 15 | 35 | 162 | 0 | 0 | 460 | 0 | 55 | 313 | 0 | 0 | 26 | 123 | 5.5 | 18 | 0 | 430 | 115 | 51 | 50 | 0 | 0 | 0 | 7 | 35 | 24 | 25 | 2.76 | 221 | 110 | 0 | 1080 | 70 | 0 | 43 | 25.5 | 105 | 214 | 0 | 0 | 0 | 600 | 16 | 133 | 16 | 200 | 328 | 290 | 44 | 20 | 206 | 0 | 100 | 17 | 136 | 68 | 10 | 68 | 74 | 52.2 | 54 | 10 | 260 | 388 | 390 | 39 | 0 | 150 | 9 | 13 | 0 | 11 | 0 | 95 | 0 | 100 | 35 | 78 | 16.47 | 96 | 0 | 1.8 | 41.48 | 24 | 8911.71 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 67 | 1232 | 0 | 0 | 0 | 1230.73 | 0 | 0 | 0 | 55 | 70 | 0 | 8.5 | 0 | 52.2 | 50.75 | 89 | 0 | 0 | 54.73 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 4.22 | 0 | 0 | 115 | 22 | 105 | 0 | 0 | 0 | 4.6 | 121 | 0.56 | 32 | 270 | 113 | 0 | 0 | 1130 | 300 | 35 | 6362.29 | 15274 | 103.35
15:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 17 | 54 | 97 | 124 | 97 | 28 | 35 | 144 | 0 | 0 | 455 | 0 | 55 | 309 | 0 | 0 | 19 | 143.42 | 5.5 | 18 | 0 | 425 | 111 | 51 | 50 | 0 | 0 | 0 | 7 | 35 | 24 | 25 | 1.83 | 221 | 110 | 0 | 1080 | 69 | 0 | 43 | 25.5 | 105 | 211 | 0 | 0 | 0 | 600 | 5 | 133 | 0 | 165 | 310 | 270 | 44 | 20 | 210 | 0 | 68 | 58 | 138 | 68 | 10 | 52 | 72 | 52.2 | 34 | 14 | 267 | 393 | 390 | 39 | 0 | 150 | 6 | 13 | 0 | 41 | 0 | 95 | 0 | 100 | 35 | 78 | 12.33 | 96 | 0 | 1.1 | 27.91 | 24 | 8826.79 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 28 | 1218 | 3 | 0 | 0 | 1219.91 | 0 | 0 | 0 | 113 | 81 | 0 | 8.5 | 0 | 52.2 | 37.93 | 68 | 0 | 0 | 39.36 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 3.33 | 0 | 0 | 115 | 18 | 106 | 0 | 0 | 0 | 3.6 | 107 | 0.33 | 32 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 35 | 6380.76 | 15207.55 | 103.33
16:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 47 | 97 | 123 | 97 | 55 | 35 | 162 | 0 | 0 | 455 | 0 | 55 | 314 | 0 | 0 | 10 | 143.42 | 5.5 | 18 | 0 | 440 | 107 | 52 | 50 | 0 | 0 | 0 | 7 | 35 | 24 | 25 | 0.67 | 221 | 99 | 0 | 1080 | 67 | 0 | 43 | 25.5 | 105 | 212 | 0 | 0 | 0 | 600 | 6 | 133 | 0 | 0 | 305 | 280 | 44 | 20 | 205 | 0 | 68 | 65 | 138 | 68 | 12 | 52 | 72 | 52.2 | 15 | 14 | 266 | 391 | 390 | 39 | 0 | 151 | 3 | 0 | 0 | 41 | 0 | 95 | 0 | 100 | 35 | 78 | 6.68 | 96 | 0 | 0.5 | 14.78 | 24 | 8637.25 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 1234.2 | 17 | 0 | 0 | 1213.95 | 0 | 10 | 0 | 113 | 113 | 0 | 8.5 | 0 | 52.2 | 20.38 | 33 | 0 | 0 | 14.79 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1.5 | 0 | 0 | 115 | 9 | 103 | 0 | 0 | 0 | 1.5 | 48 | 0.16 | 32 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 35 | 6269.78 | 14907.03 | 103.31
17:00 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 54 | 39 | 109 | 123 | 97 | 55 | 35 | 162 | 0 | 0 | 450 | 0 | 55 | 298 | 0 | 0 | 2 | 143.42 | 5 | 18 | 0 | 440 | 108 | 52 | 50 | 0 | 0 | 0 | 21 | 35 | 24 | 25 | 0.15 | 222 | 110 | 0 | 1080 | 67 | 0 | 50 | 25.5 | 105 | 212 | 0 | 0 | 0 | 600 | 0 | 133 | 28 | 0 | 288 | 285 | 44 | 20 | 191 | 0 | 73 | 65 | 139 | 69 | 12 | 100 | 66 | 52.2 | 1 | 20 | 262 | 400 | 398 | 40 | 0 | 152 | 0 | 13 | 0 | 41 | 0 | 105 | 0 | 100 | 35 | 78 | 1.23 | 96 | 0 | 0.1 | 2.2 | 24 | 8626.8 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 1227 | 34 | 0 | 0 | 1206.69 | 0 | 37 | 0 | 113 | 113 | 0 | 8.5 | 0 | 52.2 | 2.87 | 5 | 0 | 0 | 2.76 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0.18 | 0 | 0 | 115 | 2 | 103 | 0 | 0 | 0 | 0.3 | 8 | 0.02 | 32 | 307 | 107 | 0 | 0 | 1115 | 300 | 35 | 6116.52 | 14743.32 | 103.29
18:00 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 54 | 54 | 133 | 126 | 196 | 55 | 55 | 158 | 0 | 0 | 370 | 0 | 55 | 303 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 107 | 132 | 45 | 0 | 0 | 10 | 21 | 35 | 37 | 25 | 0 | 222 | 110 | 0 | 1080 | 126 | 0 | 50 | 25.5 | 105 | 212 | 0 | 0 | 0 | 840 | 0 | 130 | 38 | 0 | 314 | 310 | 44 | 20 | 201 | 0 | 115 | 65 | 144 | 69 | 12 | 114 | 78 | 52.2 | 0 | 21 | 265 | 400 | 398 | 40 | 20 | 142 | 0 | 13 | 0 | 41 | 0 | 100 | 0 | 102 | 35 | 88 | 0 | 141 | 0 | 0 | 0 | 24 | 9294.62 | 903 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1177 | 17 | 0 | 0 | 1417.68 | 0 | 30 | 0 | 113 | 113 | 0 | 100 | 12 | 52.2 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6549.48 | 15844.1 | 103.27
19:00 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 54 | 54 | 133 | 94 | 196 | 55 | 55 | 157 | 0 | 0 | 450 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 107 | 194 | 51 | 0 | 0 | 57 | 21 | 35 | 37 | 25 | 0 | 221 | 110 | 0 | 1080 | 150 | 0 | 50 | 25.5 | 105 | 215 | 0 | 0 | 0 | 1050 | 0 | 133 | 35 | 0 | 284 | 275 | 44 | 20 | 180 | 0 | 108 | 65 | 151 | 69 | 12 | 100 | 72 | 52.2 | 0 | 23 | 262 | 400 | 398 | 40 | 20 | 152 | 0 | 13 | 0 | 22 | 0 | 100 | 0 | 102 | 35 | 88 | 0 | 161 | 0 | 0 | 0 | 24 | 9614.62 | 843 | 0 | 32 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 17 | 0 | 0 | 1415.66 | 0 | 30 | 0 | 113 | 50 | 0 | 100 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6542.66 | 16157.28 | 103.25
19:30 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 54 | 133 | 60 | 196 | 55 | 55 | 100 | 0 | 0 | 430 | 0 | 55 | 295 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 108 | 206 | 51 | 0 | 0 | 67 | 21 | 35 | 24 | 25 | 0 | 221 | 110 | 0 | 1080 | 34 | 0 | 50 | 17 | 105 | 215 | 0 | 0 | 0 | 1130 | 0 | 150 | 35 | 0 | 300 | 300 | 44 | 20 | 193 | 0 | 34 | 65 | 120 | 69 | 13 | 14 | 74 | 25 | 0 | 23 | 258 | 400 | 398 | 40 | 30 | 150 | 0 | 13 | 0 | 22 | 0 | 100 | 0 | 102 | 35 | 88 | 0 | 162 | 0 | 0 | 0 | 24 | 9316.92 | 812 | 0 | 39 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1234.2 | 17 | 0 | 0 | 1418.21 | 0 | 30 | 0 | 113 | 50 | 0 | 100 | 31 | 24 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6364.01 | 15680.93
20:00 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 54 | 133 | 60 | 145 | 55 | 55 | 108 | 0 | 0 | 395 | 0 | 55 | 296 | 0 | 0 | 0 | 143.42 | 5.5 | 18 | 0 | 460 | 109 | 210 | 51 | 0 | 0 | 50 | 21 | 35 | 24 | 25 | 0 | 220 | 110 | 0 | 1080 | 0 | 0 | 48 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1207 | 0 | 150 | 35 | 0 | 300 | 300 | 44 | 20 | 191 | 0 | 34 | 65 | 85 | 70 | 13 | 0 | 68 | 25 | 0 | 0 | 256 | 400 | 398 | 40 | 30 | 152 | 0 | 13 | 0 | 22 | 0 | 101 | 0 | 102 | 35 | 88 | 0 | 163 | 0 | 0 | 0 | 24 | 9197.42 | 811 | 0 | 30 | 45 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1234.2 | 37 | 0 | 0 | 1420.96 | 0 | 32 | 0 | 113 | 50 | 0 | 65 | 32 | 24 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 100 | 6339.76 | 15537.18 | 103.23
21:00 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 49 | 120 | 30 | 30 | 15 | 35 | 17 | 0 | 0 | 480 | 0 | 35 | 298 | 0 | 0 | 0 | 143.42 | 5.5 | 19 | 0 | 460 | 107 | 213 | 52 | 0 | 0 | 50 | 21 | 35 | 24 | 25 | 0 | 220 | 110 | 2 | 1080 | 0 | 0 | 50 | 25.5 | 105 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 35 | 120 | 305 | 300 | 44 | 20 | 194 | 0 | 0 | 66 | 17 | 71 | 13 | 0 | 70 | 8 | 0 | 0 | 254 | 400 | 398 | 42 | 30 | 152 | 0 | 13 | 0 | 22 | 0 | 100 | 0 | 102 | 35 | 88 | 0 | 105 | 0 | 0 | 0 | 24 | 8916.42 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1234.2 | 34 | 0 | 0 | 1429.23 | 0 | 0 | 0 | 70 | 35 | 0 | 33 | 0 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 112 | 0 | 0 | 1170.6 | 300 | 35 | 6059.03 | 14975.45 | 103.21
22:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 17 | 97 | 15 | 15 | 0 | 35 | 15 | 0 | 0 | 530 | 0 | 17 | 290 | 0 | 0 | 0 | 143.42 | 5 | 19 | 0 | 460 | 107 | 213 | 52 | 0 | 0 | 50 | 0 | 35 | 24 | 25 | 0 | 220 | 110 | 3 | 1080 | 0 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 35 | 265 | 280 | 275 | 44 | 20 | 180 | 0 | 0 | 66 | 17 | 72 | 13 | 0 | 68 | 8 | 0 | 0 | 247 | 400 | 398 | 41 | 30 | 151 | 0 | 13 | 0 | 22 | 0 | 101 | 0 | 102 | 35 | 88 | 0 | 100 | 0 | 0 | 0 | 24 | 8836.42 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1414.11 | 0 | 0 | 0 | 35 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 5851.91 | 14688.33 | 103.19
23:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 17 | 97 | 15 | 15 | 0 | 17 | 14 | 0 | 0 | 495 | 0 | 17 | 303 | 0 | 0 | 0 | 143.42 | 5 | 19 | 0 | 470 | 99 | 213 | 51 | 0 | 0 | 50 | 0 | 35 | 24 | 25 | 0 | 220 | 110 | 5 | 1080 | 0 | 0 | 50 | 8 | 104 | 219 | 0 | 0 | 0 | 1167 | 0 | 150 | 35 | 170 | 312 | 305 | 44 | 20 | 186 | 0 | 0 | 65 | 17 | 26 | 13 | 0 | 68 | 8 | 0 | 0 | 249 | 400 | 398 | 41 | 30 | 154 | 0 | 13 | 0 | 22 | 0 | 100 | 0 | 100 | 35 | 88 | 0 | 100 | 0 | 0 | 0 | 24 | 8673.42 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1226 | 0 | 0 | 0 | 1429.4 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 281 | 115 | 0 | 0 | 1149 | 300 | 17 | 5773.4 | 14446.82 | 103.17
Total KWH | 0 | 848640 | 607680 | 0 | 0 | 0 | 0 | 0 | 8888400 | 0 | 0 | 750240 | 1077480 | 2781360 | 1743840 | 2649349 | 571252 | 864134 | 2424960 | 0 | 0 | 11160455 | 0 | 940243 | 7365230 | 0 | 0 | 222755 | 3145200 | 126600 | 442440 | 0 | 10923181.82 | 2186673 | 2197964 | 668160 | 0 | 0 | 305439 | 180554 | 800554 | 351360 | 596160 | 22078 | 5354038 | 2184580 | 173760 | 23294545.46 | 839709 | 0 | 1162080 | 284254.2 | 1923636 | 5082214 | 0 | 0 | 0 | 18239998 | 100710 | 3348800 | 786182 | 3236500 | 7877100 | 7098000 | 1034088 | 385920 | 4885000 | 0 | 827520 | 1100401 | 2123520 | 1230600 | 278920 | 613320 | 1574400 | 690024 | 466273 | 163776 | 6037000 | 9378300 | 9535000 | 948000 | 325440 | 3646963.64 | 75111 | 372408 | 0 | 453120 | 0 | 2231000 | 0 | 2404660 | 868320 | 1741200 | 147909 | 1903200 | 0 | 14550 | 339500 | 586320 | 202210252.12 | 21848727 | 0 | 69120 | 63104 | 0 | 0 | 0 | 0 | 0 | 1383120 | 542160 | 29243640 | 158400 | 0 | 0 | 30617898 | 0 | 223311 | 0 | 1738944 | 1268352 | 0 | 403728 | 80435 | 675485 | 421736 | 772346 | 158805 | 0 | 424304 | 0 | 0 | 0 | 0 | 0 | 0 | 5503272 | 0 | 36120 | 0 | 0 | 2026950 | 186890 | 1336684 | 0 | 0 | 0 | 39231.6 | 1148400 | 3922 | 699456 | 7157000 | 2705000 | 0 | 0 | 27040000 | 7341090.91 | 913200 | 146230831.51 | 348441083.63

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14819.22 | MW | 12:00 Hr. | Energy Generated |  |  | 348.4411 |  | MKWHr.
| Day Peak Demand |  |  | 14836.22 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.822 |  | MKWHr.
| Evening Peak Generation |  |  | 16157.28 | MW | 19:00 Hr. | Energy Demand |  |  | 349.2631 |  | MKWHr.
| Evening Peak Demand |  |  | 16346.28 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.7 |  | °C
| Minimum Generation of the Day |  |  | 12650.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 828.45 |  | MMCFD
| Maximum Generation of the Day |  |  | 16157.28 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 8.226 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.9063 | 0 | 18.4044 | 0 | 0 | 0.22276 | 0 | 0 | 57.5334 | Gas | 114.3846 | Gas | 387588182.4782
| Chattogram Zone |  |  | 5.256 | 41.5345 | 13.6811 | 0 | 5.354 | 0.12279 | 0 | 0 | 65.9485 | Coal | 112.3163 | Coal | 873424395.2965
| Cumilla Zone |  |  | 26.6821 | 0 | 8.9976 | 0 | 0 | 0.46627 | 1.5744 | 0 | 37.7203 | HFO | 57.3812 | HFO | 1170423727.472
| Mymensingh Zone |  |  | 0 | 0 | 5.099 | 0 | 0 | 0.50196 | 0 | 0 | 5.601 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.3319 | 0 | 0 | 0 | 0 | 0.075111 | 0 | 0 | 35.407 | Hydro | 5.354 | Hydro | 535403.8
| Khulna Zone |  |  | 0 | 29.2436 | 1.6737 | 0 | 0 | 0.54216 | 21.8487 | 0 | 53.3083 | Solar | 4.964 | Solar | 78930518.156
| Barishal Zone |  |  | 2.705 | 41.5381 | 1.6127 | 0 | 0 | 0.003922 | 0 | 0 | 45.8597 | Import | 54.041 | Import | 355385992.98
| Rajshahi Zone |  |  | 5.5033 | 0 | 4.5491 | 0 | 0 | 1.6545 | 30.6179 | 0 | 42.3247 | Wind | 0 | Wind | 0
| Rangpur Zone |  |  | 0 | 0 | 3.3636 | 0 | 0 | 1.3745 | 0 | 0 | 4.7382
| Total |  |  | 114.3846 | 112.3163 | 57.3812 | 0 | 5.354 | 4.964 | 54.041 | 0 | 348.4411
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 387588182.4782 |  | Hydro | 535403.8
|  |  |  | Coal | 873424395.2965 |  | Solar | 78930518.156
|  |  |  | HFO | 1170423727.472 |  | Import | 355385992.98
|  |  |  | HSD | 0 |  | Wind | 0
[5 empty] | Total: | 286,62,88,220 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8487 | Peak Hr Flow | 843.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42760672.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.6179 | Peak Hr Flow | 1415.66 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1773 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5744 | Peak Hr Flow | 72.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2488 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.041 | Peak Hr Flow | 2330.66 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 65 |  | 6006
|  |  |  | Chattogram |  | 0 |  | 1554
|  |  |  | Cumilla |  | 0 |  | 1464
|  |  |  | Mymensingh |  | 115 |  | 1292
|  |  |  | Sylhet |  | 1 |  | 656
|  |  |  | Khulna |  | 0 |  | 1720
|  |  |  | Barishal |  | 0 |  | 454
|  |  |  | Rajshahi |  | 0 |  | 1497
|  |  |  | Rangpur |  | 0 |  | 879
|  |  |  | Total |  | 181 |  | 15522
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Fenchugonj CCPP Phase-2 ST |  |  | 35
[7 empty] | 4 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 5 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 554.5
|  |  |  | Total Unavailable Capacity |  |  |  | 854.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:24 | 11:02 | Madunaghat 132/33kV S/S T-1 33kV BUS Scheduled S/D Due to Due to Mohora ckt-01
Maintenance by BPDB.
| 08:35 | 10:53 | Keranigonj 230/132/33kV S/S TR-2 LT Scheduled S/D Due to Oil leakage and Temperature
Management
| 08:36 | 10:52 | Keranigonj 230/132/33kV S/S TR-2 HT Scheduled S/D Due to Oil leakage and Temperature
Management
| 08:38 | 16:46 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/230/132kV end.
| 08:39 | 16:47 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/230/132kV end.
| 08:50 | 15:58 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual
maintenance
|  | 09:30 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
| 09:34 | 15:25 | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to Annual maintenance work.
| 09:34 | 15:26 | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to Annual maintenance work.
| 09:53 | 13:53 | Baghabari-Ishwardi 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to For
carrying out project work at the Ishwardi end.
|  | 10:17 | Rampur 230/132/33 S/S TR-1 HT is restored.
|  | 10:18 | Rampur 230/132/33 S/S TR-1 LT is restored.
|  | 10:21 | Bogura(New) South-Naogaon 132 kV Ckt-2 is restored.
|  | 10:24 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 10:24 | Hasnabad 230/132kV S/S AUTO TR-3 LT is restored.
| 10:34 | 11:50 | Khulshi 132/33kV S/S 405T (T1) LT Scheduled S/D Due to Red hot maintenance work at LT
Bushing(Y-Phase)
| 10:35 | 11:50 | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to Red hot maintenance work at LT
Bushing(Y-Phase)
| 10:37 | 12:46 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Forced S/D Due to LA grounding connection
| 10:37 | 12:47 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Forced S/D Due to LA Grounding connection
|  | 10:54 | Matuail-Siddhirganj 132kV Ckt-1 is restored.
| 11:28 | 11:42 | Rahanpur 132/33kV S/S TR-2 (414T) HT Scheduled S/D Due to MFM change
| 11:28 | 11:42 | Rahanpur 132/33kV S/S TR-2 (414T) LT Scheduled S/D Due to MFM change
| 11:56 | 12:08 | Chowdhala-Rahanpur(400kV) 132kV Ckt-2 Scheduled S/D from Rahanpur 132/33kV end Due to MFM
change
| 12:00 |  | Day Peak Generation: 14819 MW.
| 12:40 |  | Khulshi 132/33kV S/S 415T (T2) LT Scheduled S/D Due to Red Hot Maintenance Work
| 12:41 |  | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to Red Hot Maintenance Work
|  | 13:08 | Bogura West-Rooppur ckt-1 is restored.
|  | 13:22 | Bhulta 400/230/132kV S/S 132kV Araihazar-02 is restored.
|  | 13:23 | Bhulta (New)–Araihazar 132 kV Circuit-2 was switched on under load for the first time
|  | 13:58 | Baghabari-Ishwardi 230 kV Ckt-2 is restored.
| 15:10 | 15:58 | Daganbhuiyan 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 KV load side DS red hot
maintenance
| 15:10 | 15:58 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 KV load side DS red hot
maintenance
|  | 16:20 | Barguna 132/33kV S/S Transformer-2 HT is restored.
|  | 16:21 | Barguna 132/33kV S/S Transformer-2 LT is restored.
| 19:00 |  | Evening Peak Generation: 16157 MW.
| 20:46 | 22:00 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Scheduled S/D Due to 33kV maintenance by PDB. | [7 empty] | 20.0MW load
interrup.
| 20:47 | 21:59 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Scheduled S/D Due to 33kV maintenance by PDB. | [7 empty] | 20.0MW load
interrup.
| 00:35 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 02:18 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 06:00 |  | Minimum generation is 11933 MW.
| 06:25 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to 33 kv rampal feder | [7 empty] | 22.0MW load
|  |  | redhot maintenance work. | [7 empty] | interrup.
| 06:27 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to 33 kv rampal feder | [7 empty] | 22.0MW load
|  |  | redhot maintenance work. | [7 empty] | interrup.
| 07:10 |  | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 25.0MW load
interrup.
| 07:10 |  | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 25.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 373 | 8888400 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 571252 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7365230 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 750240 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 94 | 1743840 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 864134 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 940243 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5.5 | 126600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 442440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 607680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 196 | 2649349 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2781360 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 848640 | Tripped
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 157 | 2424960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 222755 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1077480 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 1*448+1*208 | 584 | 460 | 10923181.82 | Machine Problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 450 | 11160455 | Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 3145200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2640.92 | 57533439.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 284254.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 100710 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1162080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5354038 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5082214 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1923636 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 21 | 180554 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 57 | 305439 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 351360 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 173760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 51 | 668160 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22078 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 194 | 2197964 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 800554 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2184580 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 596160 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2186673 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 150 | 839709 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1050 | 18239998 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 23294545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3533.5 | 65948466.66
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 180 | 4885000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 284 | 7877100 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 275 | 7098000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 3236500 | Tripped
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 385920 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 35 | 786182 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1034088 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 133 | 3348800 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 163776 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 65 | 1100401 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 151 | 2123520 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 72 | 1574400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 690024 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 12 | 278920 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 613320 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 69 | 1230600 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 108 | 827520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 466273 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1623.2 | 37720344
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 147909 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 161 | 1903200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1741200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 339500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 586320 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 868320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 308 | 5600999
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 75111 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 948000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 325440 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3646963.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2231000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 22 | 453120 | Gas Shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2404660 | Gas shortage
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 372408 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 262 | 6037000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 398 | 9535000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9378300 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1509 | 35407002.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 843 | 21848727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 69120 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 63104 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 158400 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1383120 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 542160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 29243640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2246.2 | 53308271
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 27040000 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 699456 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 112 | 2705000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7341090.91 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 913200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7157000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3922 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2053.6 | 45859668.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 421736 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 223311 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 80435 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 191 | 5503272 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 158805 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 675485 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 403728 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1268352 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1738944 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 36120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1415.66 | 30617898 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 424304 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 772346 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2014.86 | 42324736
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1336684 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39231.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2026950 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186890 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1148400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 4738155.6
Eastern Grid Total |  |  |  |  | 16961.086 | 9614.62 | 202210252.12
Western Grid Total |  |  |  |  | 11731.125 | 6542.66 | 146230831.51
National Grid Total |  |  |  |  | 28692.211 | 16157.28 | 348441083.63
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10792.13 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4549.9 | MW
i) Dhaka area |  |  | 5941.18 |  | MW | i) Khulna area |  |  |  | 1720 | MW
ii) Chattogram area |  |  | 1554.5 |  | MW | ii) Barishal area |  |  |  | 453.5 | MW
iii) Cumilla area |  |  | 1464.45 |  | MW | iii) Rajshahi area |  |  |  | 1497.4 | MW
iv) Mymensingh area |  |  | 1177 |  | MW | iv) Rangpur area |  |  |  | 879 | MW
v) Sylhet area |  |  | 655 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15342.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 06:00 | 72 | Hatirjheel | 82 | 12:00 | 143 | PHP | 12 | 01:00
2 | AKSML | 144.9 | 07:00 | 73 | Ishurdi | 78 | 18:30 | 144 | Pabna | 97 | 18:30
3 | Aftabnagar | 40 | 00:00 | 74 | Jaldhaka | 66 | 18:00 | 145 | Palashbari | 120 | 18:00
4 | Agargaon | 130 | 13:00 | 75 | Jamalpur | 143 | 18:30 | 146 | Panchagarh | 59 | 18:00
5 | Agrabad | 76 | 11:00 | 76 | Jashore | 119 | 13:00 | 147 | Patiya | 31.5 | 18:00
6 | Amnura | 39 | 00:00 | 77 | Jhenaidah | 95 | 18:00 | 148 | Patnitala | 31 | 00:00
7 | Araihazar | 112 | 20:00 | 78 | Joydebpur | 166 | 18:00 | 149 | Patuakhali | 67.5 | 18:00
8 | Ashuganj | 0.51 | 00:00 | 79 | Joypurhat | 58 | 00:00 | 150 | Payra | 30 | 00:00
9 | Ashuganj-230 | 97 | 00:00 | 80 | Juldah | 19 | 14:00 | 151 | Postogola | 64 | 13:00
10 | BSRM | 202 | 16:00 | 81 | KSRM | 25 | 03:00 | 152 | Pubail | 44 | 20:00
11 | Bagerhat | 91 | 18:30 | 82 | Kabirpur | 281 | 18:30 | 153 | Purbachal | 30 | 18:00
12 | Bajitpur | 82 | 18:00 | 83 | Kachua | 94 | 18:00 | 154 | Purbasadipur | 103 | 12:00
13 | Bakerganj | 14.2 | 18:00 | 84 | Kaliganj | 41 | 18:00 | 155 | Rahanpur | 36 | 00:00
14 | Bakulia | 96 | 18:30 | 85 | Kallyanpur | 114 | 13:00 | 156 | Rahim | 44 | 14:00
15 | Banani | 68 | 12:00 | 86 | Kalurghat | 40 | 10:00 | 157 | Rajbari | 81 | 18:00
16 | Bangabhaban | 15 | 10:00 | 87 | Kamrangirchar | 89 | 11:00 | 158 | Rajendrapur | 136 | 18:00
17 | Barapukuria | 57 | 18:00 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 105 | 18:00
18 | Barguna | 20 | 00:00 | 89 | Kasba | 38 | 18:00 | 160 | Rajshahi-230 | 90 | 12:00
19 | Barishal | 104 | 13:00 | 90 | Kazla | 124 | 12:00 | 161 | Ramganj | 110 | 18:00
20 | Barishal-230 | 96 | 00:00 | 91 | Keranigonj | 87 | 12:00 | 162 | Rampur | 60 | 13:00
21 | Baroaulia | 58 | 13:00 | 92 | Khagrachori | 36 | 18:00 | 163 | Rangamati | 16 | 18:00
22 | Baroirhat | 66 | 18:00 | 93 | Khulna | 64 | 13:00 | 164 | Rangpur | 120 | 18:30
23 | Bashundhara | 203 | 13:00 | 94 | Khulshi | 187 | 18:30 | 165 | Ruppur | 4.2 | 15:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 127 | 19:30 | 166 | SSM | 10 | 23:00
25 | Beanibazar | 78 | 18:00 | 96 | Kodda | 332 | 18:30 | 167 | Saidpur | 94 | 18:00
26 | Benapole | 62 | 18:30 | 97 | Kulaura | 51 | 18:00 | 168 | Santhia | 32 | 18:00
27 | Bhaluka | 149 | 17:00 | 98 | Kurigram | 66 | 18:00 | 169 | Satkhira | 128 | 00:00
28 | Bhandaria | 54 | 00:00 | 99 | Kushtia | 138 | 18:30 | 170 | Satmasjid | 105 | 13:00
29 | Bhangura | 35 | 18:00 | 100 | Laksam | 35 | 18:00 | 171 | Savar | 222 | 15:00
30 | Bheramara(GK) | 66 | 18:00 | 101 | Lakshmipur | 50 | 18:00 | 172 | SevenRings | 20.07 | 00:00
31 | Bhulta | 211 | 16:00 | 102 | Lalbag | 85 | 13:00 | 173 | ShahCement | 22 | 19:30
32 | Bog-Sherpur | 68 | 18:00 | 103 | Lalmonirhat | 60 | 18:00 | 174 | Shahjadpur | 78 | 18:30
33 | Bogura | 192 | 19:00 | 104 | MI_Cement | 10.3 | 10:00 | 175 | Shahjibazar | 139 | 18:00
34 | Borhanuddin | 75 | 00:00 | 105 | Madanganj | 52 | 13:00 | 176 | Shahmirpur | 60 | 15:00
35 | Brahmanbaria | 142 | 18:30 | 106 | Madaripur | 98 | 19:30 | 177 | Shariatpur | 89 | 00:00
36 | Cantonment | 131 | 13:00 | 107 | Madartek | 82 | 00:00 | 178 | Sherpur | 150 | 18:30
37 | Chandina | 23 | 18:00 | 108 | Madunaghat | 60 | 18:00 | 179 | Shikalbaha | 20 | 00:00
38 | Chandpur | 80 | 18:30 | 109 | Magura | 64 | 18:30 | 180 | Shitalakhya | 80.8 | 13:00
39 | Chandraghona | 34 | 18:00 | 110 | Mahasthangarh | 72 | 00:00 | 181 | Sholosohor | 51 | 18:00
40 | Chapai | 70 | 13:00 | 111 | Maijdee | 37 | 00:00 | 182 | Shomvuganj | 40 | 23:00
41 | Charfasson | 31 | 21:00 | 112 | Manikganj | 138 | 18:00 | 183 | Shyampur | 148 | 00:00
42 | Charsaidpur | 31 | 01:00 | 113 | Maniknagar | 92 | 13:00 | 184 | Siddhirganj | 135 | 12:00
43 | Chauddagram | 74 | 18:00 | 114 | Matarbari | 58 | 18:30 | 185 | Sirajganj | 114 | 19:00
44 | Chhatak | 41 | 18:30 | 115 | Matuail | 80 | 12:00 | 186 | Sitakunda | 35 | 18:30
45 | Chowmuhani | 163 | 18:00 | 116 | Metrorail_Motijheel | 19 | 18:30 | 187 | Sonargaon | 135 | 16:00
46 | Chuadanga | 112 | 18:30 | 117 | Metrorail_Uttara | 7 | 10:00 | 188 | Sreemongol | 79 | 18:30
47 | Coxsbazar | 152 | 18:30 | 118 | Millgate | 98 | 11:00 | 189 | Sreepur | 135 | 17:00
48 | Cumilla(N) | 150 | 18:30 | 119 | Mirpur | 144 | 12:00 | 190 | Srinagar | 44.6 | 00:00
49 | Cumilla(S) | 155 | 14:00 | 120 | Mirsorai | 20 | 02:00 | 191 | Sunamganj | 62 | 18:30
50 | Daganbhuiyan | 36 | 23:00 | 121 | Mirzapur | 48 | 18:30 | 192 | Sylhet | 125 | 16:00
51 | Daudkandi | 130 | 00:00 | 122 | Mithapukur | 68 | 18:00 | 193 | Sylhet_(South) | 63 | 18:00
52 | DhakaUniversity | 96 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 96 | 23:00 | 124 | Mogbazar | 48.5 | 14:00 | 195 | Tangail | 176 | 18:30
54 | Dhanmondi | 112 | 13:00 | 125 | Mongla | 43 | 18:30 | 196 | Taraganj | 30 | 18:00
55 | Dohazari | 115 | 18:30 | 126 | Monirampur | 23 | 18:00 | 197 | Tasnim | 45 | 17:00
56 | Faridpur | 165 | 18:30 | 127 | Motijheel | 55 | 13:00 | 198 | Thakurgaon | 91 | 18:30
57 | Fatullah | 126 | 15:00 | 128 | Muktagacha | 38 | 18:00 | 199 | Tongi | 164 | 15:00
58 | Fenchuganj | 40 | 18:00 | 129 | Munshiganj | 104 | 00:00 | 200 | Ullahpara | 37 | 18:30
59 | Feni | 103 | 11:00 | 130 | Muradnagar | 55 | 18:00 | 201 | Ullon | 49 | 00:00
60 | GPH | 77 | 14:00 | 131 | Mymensingh | 164 | 18:00 | 202 | Uttara | 98 | 13:00
61 | Ghatail | 97 | 18:00 | 132 | Nabinagar | 110 | 08:00 | 203 | UttaraNew | 58 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 116 | 00:00 | 204 | Zigatola | 92 | 00:00
63 | Ghorashal-230 | 102 | 19:00 | 134 | Narail | 56 | 18:00
64 | Goalpara | 39 | 00:00 | 135 | Narinda | 76 | 13:00
65 | Gollamari | 102 | 00:00 | 136 | Narshingdi | 185 | 18:30
66 | Gopalganj | 104 | 18:30 | 137 | Natore | 147 | 18:00
67 | Gulshan | 126 | 13:00 | 138 | Nawabganj | 43 | 00:00
68 | Halishahar | 140 | 14:00 | 139 | Netrakona | 132 | 17:00
69 | HaripurSBU | 138 | 12:00 | 140 | New | 86 | 12:00
70 | Hasnabad | 107 | 18:30 | 141 | Niamatpur | 74 | 18:00
71 | Hathazari | 90 | 18:30 | 142 | Noapara | 42.5 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15340.3 | 10 |  | 15350.3
1:00 | 14832.74 | 0 |  | 14832.74
2:00 | 14209.15 | 0 |  | 14209.15
3:00 | 13804.16 | 0 |  | 13804.16
4:00 | 13197.38 | 0 |  | 13197.38
5:00 | 12874.67 | 0 |  | 12874.67
6:00 | 12650.25 | 0 |  | 12650.25
7:00 | 13068.94 | 0 |  | 13068.94
8:00 | 13264.18 | 0 |  | 13264.18
9:00 | 13291.19 | 17 |  | 13309.19
10:00 | 13624.37 | 21 |  | 13646.37
11:00 | 14182.42 | 21 |  | 14204.42
12:00 | 14819.22 | 16 |  | 14836.22
13:00 | 15265.97 | 21 |  | 15287.97
14:00 | 15274 | 21 |  | 15295.95
15:00 | 15207.55 | 31 |  | 15239.55
16:00 | 14907.03 | 30 |  | 14938.03
17:00 | 14743.32 | 30 |  | 14774.67
18:00 | 15844.1 | 187 |  | 16039.1
19:00 | 16157.28 | 181 |  | 16346.28
19:30 | 15680.93 | 130 |  | 15816.93
20:00 | 15537.18 | 98 |  | 15639.18
21:00 | 14975.45 | 74 |  | 15052.45
22:00 | 14688.33 | 64 |  | 14755.33
23:00 | 14446.82 | 0 |  | 14446.82
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8901.42 | 6438.88 | 15340.3 | DAILY GENERATION CURVE
00:30 | 8845.42 | 6241.1 | 15086.52
01:00 | 8789.42 | 6043.32 | 14832.74 | 19-10-2026
01:30 | 8608.92 | 5912.025 | 14520.945
02:00 | 8428.42 | 5780.73 | 14209.15
02:30 | 8275.17 | 5731.485 | 14006.655
03:00 | 8121.92 | 5682.24 | 13804.16
03:30 | 7894.21 | 5606.56 | 13500.77
04:00 | 7666.5 | 5530.88 | 13197.38
04:30 | 7504 | 5532.025 | 13036.025
05:00 | 7341.5 | 5533.17 | 12874.67
05:30 | 7264.51 | 5497.95 | 12762.46
06:00 | 7187.52 | 5462.73 | 12650.25
06:30 | 7258.56 | 5601.035 | 12859.595
07:00 | 7329.6 | 5739.34 | 13068.94
07:30 | 7339.125 | 5827.435 | 13166.56
08:00 | 7348.65 | 5915.53 | 13264.18
08:30 | 7345.41 | 5932.275 | 13277.685
09:00 | 7342.17 | 5949.02 | 13291.19
09:30 | 7447.645 | 6010.135 | 13457.78
10:00 | 7553.12 | 6071.25 | 13624.37
10:30 | 7700.59 | 6202.805 | 13903.395
11:00 | 7848.06 | 6334.36 | 14182.42
11:30 | 8097.27 | 6403.55 | 14500.82
12:00 | 8346.48 | 6472.74 | 14819.22
12:30 | 8598.13 | 6444.465 | 15042.595
13:00 | 8849.78 | 6416.19 | 15265.97
13:30 | 8880.745 | 6389.24 | 15269.985
14:00 | 8911.71 | 6362.29 | 15274
14:30 | 8869.25 | 6371.525 | 15240.775
15:00 | 8826.79 | 6380.76 | 15207.55
15:30 | 8732.02 | 6325.27 | 15057.29
16:00 | 8637.25 | 6269.78 | 14907.03
16:30 | 8632.025 | 6193.15 | 14825.175
17:00 | 8626.8 | 6116.52 | 14743.32
17:30 | 8960.71 | 6333 | 15293.71
18:00 | 9294.62 | 6549.48 | 15844.1
18:30 | 9454.62 | 6546.07 | 16000.69
19:00 | 9614.62 | 6542.66 | 16157.28
19:30 | 9316.92 | 6364.01 | 15680.93
20:00 | 9197.42 | 6339.76 | 15537.18
20:30 | 9056.92 | 6199.395 | 15256.315 |  | Executive Engineer
21:00 | 8916.42 | 6059.03 | 14975.45 |  | Network Operation Division
21:30 | 8876.42 | 5955.47 | 14831.89
22:00 | 8836.42 | 5851.91 | 14688.33
22:30 | 8754.92 | 5812.655 | 14567.575
23:00 | 8673.42 | 5773.4 | 14446.82

## En-Curve
QF-LDC-12
Date | 19-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3137 | 1401.5 | 919 | 0 | 66 | 1392.88 | 221 | 5161.8 | 0 | 554.42 | 2486.7 | 0 | 0 | 0 | 10 | DAILY ENERGY CURVE
00:30 | 3148 | 1372 | 918.5 | 0 | 65 | 1296.2 | 221 | 5025.7 | 0 | 529.42 | 2510.7 | 0 | 0 | 0 | 5 | 19-10-2026
01:00 | 3159 | 1342.5 | 918 | 0 | 64 | 1199.52 | 221 | 4889.6 | 0 | 504.42 | 2534.7 | 0 | 0 | 0 | 0
01:30 | 3256 | 1380 | 917 | 0 | 63 | 1209.525 | 221 | 4656.8 | 0 | 440.42 | 2377.2 | 0 | 0 | 0 | 0 | Energy Generated | 348.4411 |  | MKWHr
02:00 | 3353 | 1417.5 | 916 | 0 | 62 | 1219.53 | 221 | 4424 | 0 | 376.42 | 2219.7 | 0 | 0 | 0 | 0 | Energy not Served | 0.822 |  | MKWHr
02:30 | 3327 | 1450 | 916 | 0 | 61 | 1211.185 | 221 | 4457.6 | 0 | 321.92 | 2040.95 | 0 | 0 | 0 | 0 | Total Energy Requirement | 349.2631 |  | MKWHr
03:00 | 3301 | 1482.5 | 916 | 0 | 60 | 1202.84 | 221 | 4491.2 | 0 | 267.42 | 1862.2 | 0 | 0 | 0 | 0
03:30 | 3297.5 | 1496 | 916 | 0 | 60 | 1212.26 | 221 | 4491.2 | 0 | 183.71 | 1623.1 | 0 | 0 | 0 | 0
04:00 | 3294 | 1509.5 | 916 | 0 | 60 | 1221.68 | 221 | 4491.2 | 0 | 100 | 1384 | 0 | 0 | 0 | 0
04:30 | 3302 | 1516.5 | 916 | 0 | 58 | 1218.825 | 221 | 4386.2 | 0 | 100 | 1317.5 | 0 | 0 | 0 | 0
05:00 | 3310 | 1523.5 | 916 | 0 | 56 | 1215.97 | 221 | 4281.2 | 0 | 100 | 1251 | 0 | 0 | 0 | 0
05:30 | 3351 | 1545.5 | 915.5 | 0 | 54 | 1214.25 | 220.5 | 4211.2 | 0.01 | 100 | 1150.5 | 0 | 0 | 0 | 0
06:00 | 3392 | 1567.5 | 915 | 0 | 52 | 1212.53 | 220 | 4141.2 | 0.02 | 100 | 1050 | 0 | 0 | 0 | 0
06:30 | 3400 | 1585 | 915 | 0 | 53 | 1212.47 | 220 | 4241.5 | 53.625 | 146.5 | 1032.5 | 0 | 0 | 0 | 0
07:00 | 3408 | 1602.5 | 915 | 0 | 54 | 1212.41 | 220 | 4341.8 | 107.23 | 193 | 1015 | 0 | 0 | 0 | 0
07:30 | 3312 | 1569 | 909.5 | 0 | 56 | 1217.21 | 219.5 | 4340.3 | 217.84 | 235.71 | 1089.5 | 0 | 0 | 0 | 0
08:00 | 3216 | 1535.5 | 904 | 0 | 58 | 1222.01 | 219 | 4338.8 | 328.45 | 278.42 | 1164 | 0 | 0 | 0 | 0
08:30 | 3219 | 1501.5 | 904 | 0 | 59 | 1218.275 | 219 | 4301.9 | 415.09 | 260.92 | 1179 | 0 | 0 | 0 | 8.5
09:00 | 3222 | 1467.5 | 904 | 0 | 60 | 1214.54 | 219 | 4265 | 501.73 | 243.42 | 1194 | 0 | 0 | 0 | 17
09:30 | 3239 | 1462 | 903.5 | 0 | 61 | 1216.23 | 219.5 | 4275 | 574.63 | 277.92 | 1229 | 0 | 0 | 0 | 19
10:00 | 3256 | 1456.5 | 903 | 0 | 62 | 1217.92 | 220 | 4285 | 647.53 | 312.42 | 1264 | 0 | 0 | 0 | 21
10:30 | 3306.5 | 1459.5 | 903.5 | 0 | 65 | 1225.97 | 220 | 4304.6 | 683.405 | 340.42 | 1394.5 | 0 | 0 | 0 | 21
11:00 | 3357 | 1462.5 | 904 | 0 | 68 | 1234.02 | 220 | 4324.2 | 719.28 | 368.42 | 1525 | 0 | 0 | 0 | 21
11:30 | 3331.5 | 1470.5 | 903.5 | 0 | 69 | 1234.41 | 220.5 | 4400.7 | 731.19 | 398.92 | 1740.6 | 0 | 0 | 0 | 18.5
12:00 | 3306 | 1478.5 | 903 | 0 | 70 | 1234.8 | 221 | 4477.2 | 743.1 | 429.42 | 1956.2 | 0 | 0 | 0 | 16
12:30 | 3264.5 | 1487.5 | 903 | 0 | 70 | 1213.67 | 221 | 4568.2 | 698.065 | 463.96 | 2152.7 | 0 | 0 | 0 | 18.5
13:00 | 3223 | 1496.5 | 903 | 0 | 70 | 1192.54 | 221 | 4659.2 | 653.03 | 498.5 | 2349.2 | 0 | 0 | 0 | 21
13:30 | 3243.5 | 1467 | 903.5 | 0 | 72 | 1211.635 | 221 | 4635.6 | 617.2 | 504 | 2394.55 | 0 | 0 | 0 | 21
14:00 | 3264 | 1437.5 | 904 | 0 | 74 | 1230.73 | 221 | 4612 | 581.37 | 509.5 | 2439.9 | 0 | 0 | 0 | 21
14:30 | 3263 | 1443 | 904 | 0 | 73 | 1225.32 | 221 | 4643.8 | 497.045 | 522.21 | 2448.4 | 0 | 0 | 0 | 26
15:00 | 3262 | 1448.5 | 904 | 0 | 72 | 1219.91 | 221 | 4675.6 | 412.72 | 534.92 | 2456.9 | 0 | 0 | 0 | 31
15:30 | 3171 | 1450.5 | 904 | 0 | 72 | 1216.93 | 221 | 4683.7 | 309.34 | 539.42 | 2489.4 | 0 | 0 | 0 | 30.5
16:00 | 3080 | 1452.5 | 904 | 0 | 72 | 1213.95 | 221 | 4691.8 | 205.96 | 543.92 | 2521.9 | 0 | 0 | 0 | 30
16:30 | 3069.5 | 1468.75 | 904 | 0 | 69 | 1210.32 | 221.5 | 4660.4 | 118.885 | 514.92 | 2587.9 | 0 | 0 | 0 | 30
17:00 | 3059 | 1485 | 904 | 0 | 66 | 1206.69 | 222 | 4629 | 31.81 | 485.92 | 2653.9 | 0 | 0 | 0 | 30
17:30 | 3084 | 1456.75 | 903.5 | 0 | 72 | 1312.185 | 222 | 4751.8 | 15.905 | 570.17 | 2905.4 | 0 | 0 | 0 | 108.5
18:00 | 3109 | 1428.5 | 903 | 0 | 78 | 1417.68 | 222 | 4874.6 | 0 | 654.42 | 3156.9 | 0 | 0 | 0 | 187
18:30 | 3077 | 1461 | 873 | 0 | 75 | 1416.67 | 221.5 | 5008.2 | 0 | 692.92 | 3175.4 | 0 | 0 | 0 | 184
19:00 | 3045 | 1493.5 | 843 | 0 | 72 | 1415.66 | 221 | 5141.8 | 0 | 731.42 | 3193.9 | 0 | 0 | 0 | 181
19:30 | 3096 | 1468.5 | 812 | 0 | 74 | 1418.21 | 221 | 5221.8 | 0 | 694.42 | 2675 | 0 | 0 | 0 | 130
20:00 | 3094 | 1433.5 | 811 | 0 | 68 | 1420.96 | 220 | 5298.8 | 0 | 608.42 | 2582.5 | 0 | 0 | 0 | 98
20:30 | 3167.5 | 1476.5 | 858.5 | 0 | 69 | 1425.095 | 220 | 5307.3 | 0 | 499.92 | 2232.5 | 0 | 0 | 0 | 86
21:00 | 3241 | 1519.5 | 906 | 0 | 70 | 1429.23 | 220 | 5315.8 | 0 | 391.42 | 1882.5 | 0 | 0 | 0 | 74
21:30 | 3276.5 | 1540.75 | 906 | 0 | 69 | 1421.67 | 220 | 5315.8 | 0 | 336.42 | 1745.75 | 0 | 0 | 0 | 69
22:00 | 3312 | 1562 | 906 | 0 | 68 | 1414.11 | 220 | 5315.8 | 0 | 281.42 | 1609 | 0 | 0 | 0 | 64
22:30 | 3312 | 1553 | 906.5 | 0 | 68 | 1421.755 | 220 | 5259.4 | 0 | 273.42 | 1553.5 | 0 | 0 | 0 | 32
23:00 | 3312 | 1544 | 907 | 0 | 68 | 1429.4 | 220 | 5203 | 0 | 265.42 | 1498 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 19-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 132 | 36 | 390 | 154 | 1328 | 514 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 110 | 31 | 330 | 148 | 1178 | 466
2:00 | 128 | 31 | 320 | 120 | 1172 | 532 |  | Import | 0
3:00 | 135 | 31 | 340 | 104 | 1266 | 450
4:00 | 134 | 28 | 350 | 106 | 1294 | 460 | Ishurdi-Ghorashal Ckt-2 | Export | 3497672.73
5:00 | 145 | 19 | 380 | 96 | 1420 | 456
6:00 | 148 | 19 | 370 | 90 | 1450 | 472 |  | Import | 0
7:00 | 121 | 6 | 290 | 68 | 1470 | 406
8:00 | 139 | 7 | 320 | 48 | 1600 | 446 | Sirajganj-Sreepur Ckt-1 | Export | 2207000
9:00 | 172 | 22 | 410 | 66 | 1730 | 530
10:00 | 184 | 27 | 450 | 80 | 1786 | 540 |  | Import | 0
11:00 | 196 | 40 | 480 | 100 | 1812 | 560
12:00 | 186 | 43 | 470 | 130 | 1096 | 578 | Sirajganj-Sreepur Ckt-2 | Export | 2216000
13:00 | 155 | 35 | 400 | 152 | 1416 | 550
14:00 | 149 | 33 | 400 | 156 | 1506 | 550 |  | Import | 0
15:00 | 167 | 49 | 434 | 162 | 1632 | 592
16:00 | 166 | 45 | 456 | 164 | 1684 | 604 | Gopalganj-Aminbazar Ckt-1 | Export | 17400000
17:00 | 163 | 56 | 412 | 166 | 1518 | 612
18:00 | 132 | 38 | 320 | 150 | 1400 | 560 |  | Import | 0
18:30 | 121 | 45 | 312 | 156 | 1270 | 558
19:00 | 125 | 56 | 340 | 180 | 1308 | 586 | Gopalganj-Aminbazar Ckt-2 | Export | 17440000
19:30 | 123 | 57 | 330 | 176 | 1312 | 572
20:00 | 120 | 55 | 290 | 152 | 1298 | 586 |  | Import | 0
21:00 | 129 | 55 | 290 | 152 | 1240 | 620
22:00 | 126 | 50 | 260 | 132 | 1198 | 598 |  | Total Export | 42760672.73
23:00 | 126 | 45 | 280 | 136 | 1172 | 584 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 02:00 | 365 | 21:00 | Madunaghat | 401 | 03:00 | 391 | 22:00
Amtali | 412 | 03:00 | 406 | 22:00 | Meghnaghat | 391 | 02:00 | 375 | 21:00
Ashuganj | 405 | 6:00 | 382 | 16:00 | Mirsorai | 401 | 02:00 | 386 | 21:00
Bhulta | 396 | 05:00 | 374 | 16:00 | Payra | 414 | 02:00 | 408 | 20:00
Bibiana | 388 | 03:00 | 379 | 22:00 | Rahanpur | 411 | 03:00 | 396 | 18:00
BIPTC | 401 | 20:00 | 394 | 01:00 | Rampal | 400 | 02:00 | 388 | 23:00
Bogura | 402 | 02:00 | 384 | 08:00
Gopalganj | 395 | 03:00 | 383 | 21:00
Kaliakoir | 377 | 02:00 | 357 | 21:00
Korerhat | 401 | 07:00 | 385 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 02:00 | 220 | 12:00 | Hasnabad | 228 | 02:00 | 216 | 13:00
AKSML | 237 | 02:00 | 228 | 21:00 | Hathazari | 235 | 07:00 | 230 | 21:00
Aminbazar | 233 | 01:00 | 221 | 12:00 | Ishurdi | 236 | 03:00 | 223 | 18:00
Ashuganj | 230 | 06:00 | 218 | 21:00 | Jhenaidah | 227 | 03:00 | 214 | 12:00
Ashuganj-400 | 230 | 06:00 | 218 | 21:00 | Kachua | 230 | 16:00 | 216 | 21:00
Baghabari | 234 | 02:00 | 223 | 13:00 | Kaliakoir | 233 | 01:00 | 218 | 21:00
Barapukuria | 233 | 05:00 | 219 | 08:00 | Keranigonj | 230 | 04:00 | 217 | 12:00
Barapukuria-230 | 233 | 05:00 | 219 | 08:00 | Khulna(S) | 230 | 04:00 | 220 | 13:00
Barapukuria(N) | 238 | 02:00 | 221 | 08:00 | Korerhat | 228 | 05:00 | 218 | 21:00
Barishal | 235 | 05:00 | 228 | 12:00 | Madunaghat | 238 | 02:00 | 234 | 00:00
Bheramara | 234 | 02:00 | 221 | 10:00 | Madunaghat-400 | 240 | 03:00 | 235 | 00:00
Bhulta | 226 | 05:00 | 213 | 12:00 | Maniknagar | 223 | 03:00 | 212 | 12:00
Bibiana | 223 | 06:00 | 216 | 21:00 | Meghnaghat | 231 | 05:00 | 220 | 13:00
BIPTC | 237 | 03:00 | 221 | 12:00 | Meghnaghat-400 | 227 | 03:00 | 217 | 12:00
Birulia | 232 | 02:00 | 219 | 21:00 | Mirsorai | 227 | 06:00 | 218 | 21:00
Bogura | 239 | 01:00 | 227 | 22:00 | Naogaon | 230 | 15:00 | 210 | 18:00
Bogura-400 | 239 | 02:00 | 227 | 08:00 | Purbasadipur | 236 | 02:00 | 218 | 08:00
Borhanuddin | 234 | 08:00 | 229 | 12:00 | Rajshahi | 236 | 02:00 | 220 | 11:00
BSRM | 230 | 08:00 | 219 | 21:00 | Rampal | 228 | 02:00 | 219 | 13:00
Charfasson | 232 | 10:00 | 228 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 02:00 | 217 | 21:00 | Rampura | 226 | 05:00 | 212 | 12:00
Cumilla(N) | 223 | 06:00 | 215 | 21:00 | Shikalbaha | 238 | 11:00 | 234 | 02:00
Faridpur | 235 | 06:00 | 228 | 00:00 | Shyampur | 227 | 03:00 | 216 | 12:00
Fenchuganj | 225 | 06:00 | 218 | 18:30 | Siddhirganj | 226 | 07:00 | 216 | 15:00
Feni | 226 | 08:00 | 215 | 21:00 | Sirajgonj | 236 | 03:00 | 229 | 08:00
Ghorashal | 230 | 01:00 | 220 | 10:00 | Sreepur | 224 | 03:00 | 214 | 12:00
Ghorashal-230 | 219 | 04:00 | 201 | 21:00 | Tongi | 224 | 04:00 | 205 | 11:00
Gopalganj | 237 | 03:00 | 222 | 15:00
GPH | 234 | 01:00 | 230 | 12:00
Haripur | 226 | 05:00 | 215 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 125 | 12:00 | Madanganj | 135 | 07:00 | 129 | 13:00
Agargaon | 135 | 03:00 | 126 | 12:00 | Madaripur | 133 | 01:00 | 130 | 12:00
Agrabad | 135 | 06:00 | 132 | 00:00 | Madartek | 135 | 05:00 | 124 | 13:00
AKS | 133 | 17:00 | 130 | 00:00 | Madunaghat | 138 | 18:00 | 135 | 01:00
Aminbazar | 134 | 01:00 | 126 | 12:00 | Magura | 134 | 05:00 | 124 | 18:00
Amnura | 133 | 03:00 | 127 | 08:00 | Mahasthangarh | 137 | 01:00 | 128 | 08:00
Araihazar | 126 | 03:00 | 118 | 12:00 | Maijdee | 128 | 08:00 | 121 | 21:00
Ashuganj | 134 | 05:00 | 126 | 18:00 | Manikganj | 130 | 08:00 | 122 | 21:00
Ashuganj-230 | 136 | 06:00 | 131 | 18:30 | Maniknagar | 136 | 05:00 | 125 | 13:00
Bagerhat | 130 | 17:00 | 122 | 22:00 | Matarbari | 123 | 18:00 | 107 | 00:00
Bajitpur | 129 | 06:00 | 122 | 13:00 | Matuail | 135 | 01:00 | 125 | 10:00
Bakerganj | 135 | 20:00 | 131 | 12:00 | Metrorail_Motijheel | 136 | 06:00 | 125 | 13:00
Bakulia | 136 | 18:00 | 131 | 00:00 | Metrorail_Uttara | 134 | 01:00 | 121 | 12:00
Banani | 135 | 05:00 | 124 | 13:00 | Millgate | 137 | 04:00 | 122 | 12:00
Bangabhaban | 136 | 05:00 | 126 | 12:00 | Mirpur | 133 | 04:00 | 125 | 12:00
Barapukuria | 138 | 03:00 | 127 | 08:00 | Mirzapur | 133 | 01:00 | 126 | 18:30
Barguna | 134 | 05:00 | 129 | 23:00 | Mithapukur | 136 | 01:00 | 124 | 08:00
Barishal | 134 | 05:00 | 130 | 12:00 | MI_Cement | 134 | 02:00 | 124 | 12:00
Barishal-230 | 135 | 17:00 | 131 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 135 | 06:00 | 132 | 00:00 | Mogbazar | 135 | 03:00 | 125 | 11:00
Baroirhat | 132 | 02:00 | 126 | 21:00 | Mongla | 129 | 17:00 | 121 | 22:00
Bashundhara | 135 | 03:00 | 122 | 12:00 | Monirampur | 129 | 04:00 | 118 | 18:30
BashundharaCement | 135 | 07:00 | 129 | 13:00 | Motijheel | 136 | 05:00 | 126 | 12:00
Beanibazar | 125 | 08:00 | 118 | 18:00 | Muktagacha | 130 | 10:00 | 117 | 07:00
Benapole | 134 | 04:00 | 119 | 13:00 | Munshiganj | 135 | 01:00 | 128 | 12:00
Bhaluka | 132 | 05:00 | 120 | 13:00 | Muradnagar | 129 | 08:00 | 120 | 22:00
Bhandaria | 136 | 08:00 | 125 | 00:00 | Mymensingh | 131 | 09:00 | 115 | 13:00
Bhangura | 134 | 01:00 | 128 | 10:00 | Nabinagar | 132 | 03:00 | 121 | 12:00
Bheramara | 138 | 02:00 | 130 | 12:00 | Naogaon | 136 | 01:00 | 127 | 08:00
Bheramara(GK) | 137 | 01:00 | 130 | 18:00 | Narail | 134 | 04:00 | 123 | 18:30
Bhulta | 125 | 07:00 | 119 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhulta-400 | 126 | 02:00 | 118 | 12:00 | Narshingdi | 129 | 03:00 | 116 | 12:00
Birulia | 136 | 02:00 | 128 | 21:00 | Natore | 135 | 01:00 | 128 | 08:00
Bog-Sherpur | 137 | 01:00 | 130 | 08:00 | Nawabganj | 135 | 03:00 | 126 | 12:00
Bogura | 138 | 01:00 | 131 | 08:00 | Netrakona | 121 | 04:00 | 109 | 13:00
Bogura-230 | 139 | 01:00 | 132 | 08:00 | New | 134 | 07:00 | 124 | 12:00
Brahmanbaria | 131 | 08:00 | 122 | 18:30 | Niamatpur | 135 | 05:00 | 129 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 135 | 02:00 | 126 | 12:00 | Noapara | 131 | 04:00 | 124 | 13:00
Chandina | 131 | 08:00 | 124 | 21:00 | Pabna | 135 | 01:00 | 128 | 12:00
Chandpur | 134 | 17:00 | 121 | 22:00 | Palashbari | 135 | 02:00 | 125 | 07:00
Chandraghona | 137 | 04:00 | 135 | 00:00 | Panchagarh | 142 | 03:00 | 130 | 08:00
Chapai | 134 | 05:00 | 127 | 22:00 | Patiya | 134 | 02:00 | 129 | 00:00
Charsaidpur | 135 | 03:00 | 129 | 12:00 | Patnitala | 134 | 06:00 | 127 | 22:00
Chauddagram | 130 | 08:00 | 123 | 21:00 | Patuakhali | 134 | 00:00 | 130 | 12:00
Chhatak | 121 | 07:00 | 113 | 18:00 | Payra | 135 | 01:00 | 133 | 23:00
Chowmuhani | 128 | 07:00 | 122 | 21:00 | PHP | 132 | 08:00 | 125 | 21:00
Chuadanga | 134 | 03:00 | 124 | 13:00 | Postogola | 135 | 02:00 | 126 | 12:00
Coxsbazar | 118 | 10:00 | 106 | 00:00 | Pubail | 131 | 01:00 | 118 | 21:00
Cumilla(N) | 130 | 06:00 | 123 | 23:00 | Purbachal | 135 | 01:00 | 124 | 12:00
Cumilla(S) | 133 | 00:00 | 123 | 21:00 | Purbasadipur | 139 | 03:00 | 126 | 08:00
Daganbhuiyan | 130 | 08:00 | 123 | 22:00 | Rahanpur | 137 | 01:00 | 132 | 21:00
Daudkandi | 127 | 02:00 | 120 | 21:00 | Rahanpur-400 | 138 | 03:00 | 132 | 18:00
DhakaUniversity | 135 | 03:00 | 125 | 12:00 | Rahim | 136 | 05:00 | 129 | 13:00
Dhamrai | 133 | 06:00 | 122 | 12:00 | Rajbari | 133 | 06:00 | 127 | 00:00
Dhanmondi | 138 | 00:00 | 129 | 12:00 | Rajendrapur | 133 | 04:00 | 124 | 13:00
Dohazari | 130 | 11:00 | 122 | 00:00 | Rajshahi | 132 | 01:00 | 126 | 13:00
Faridpur | 134 | 06:00 | 130 | 00:00 | Rajshahi-230 | 134 | 03:00 | 126 | 12:00
Fatullah | 135 | 01:00 | 124 | 12:00 | Ramganj | 130 | 17:00 | 118 | 21:00
Fenchuganj | 132 | 07:00 | 127 | 00:00 | Rampur | 136 | 08:00 | 132 | 00:00
Feni | 130 | 07:00 | 124 | 21:00 | Rampura | 135 | 03:00 | 125 | 12:00
Feni-230 | 131 | 08:00 | 124 | 21:00 | Rangamati | 136 | 02:00 | 134 | 00:00
Ghatail | 128 | 09:00 | 119 | 07:00 | Rangpur | 133 | 03:00 | 124 | 18:00
Ghorashal | 132 | 01:00 | 122 | 17:00 | Ruppur | 137 | 01:00 | 131 | 10:00
Goalpara | 132 | 03:00 | 126 | 18:30 | Saidpur | 135 | 05:00 | 125 | 08:00
Gollamari | 133 | 17:00 | 126 | 18:30 | Santhia | 134 | 03:00 | 129 | 18:00
Gopalganj | 133 | 17:00 | 126 | 22:00 | Satkhira | 128 | 05:00 | 119 | 18:30
Gopalganj-400 | 134 | 02:00 | 130 | 12:00 | Satmasjid | 135 | 04:00 | 125 | 13:00
Gulshan | 134 | 05:00 | 124 | 12:00 | Savar | 133 | 02:00 | 124 | 21:00
Halishahar | 137 | 02:00 | 132 | 16:00 | SevenRings | 133 | 04:00 | 121 | 18:00
Haripur | 136 | 03:00 | 129 | 13:00 | ShahCement | 135 | 03:00 | 129 | 12:00
HaripurSBU | 136 | 03:00 | 129 | 13:00 | Shahjadpur | 136 | 04:00 | 127 | 11:00
Hasnabad | 135 | 06:00 | 126 | 12:00 | Shahjibazar | 129 | 09:00 | 121 | 18:30
Hathazari | 137 | 07:00 | 134 | 21:00 | Shahmirpur | 137 | 04:00 | 133 | 10:00
Hatirjheel | 135 | 03:00 | 124 | 13:00 | Shariatpur | 133 | 06:00 | 127 | 13:00
Ishurdi | 138 | 01:00 | 131 | 13:00 | Sherpur | 130 | 09:00 | 113 | 07:00
Jaldhaka | 133 | 16:00 | 122 | 07:00 | Shikalbaha | 125 | 03:00 | 121 | 00:00
Jamalpur | 132 | 10:00 | 118 | 07:00 | Shikalbaha-230 | 136 | 00:00 | 133 | 02:00
Jashore | 134 | 03:00 | 120 | 18:30 | Shitalakhya | 134 | 02:00 | 124 | 12:00
Jhenaidah | 134 | 04:00 | 128 | 13:00 | Sholosohor | 137 | 08:00 | 133 | 12:00
Jhenaidah-230 | 138 | 03:00 | 128 | 12:00 | Shomvuganj | 126 | 07:00 | 116 | 00:00
Joydebpur | 127 | 06:00 | 114 | 18:00 | Shyampur | 135 | 07:00 | 128 | 12:00
Joypurhat | 133 | 04:00 | 127 | 08:00 | Shyampur-230 | 136 | 02:00 | 129 | 12:00
Juldah | 136 | 08:00 | 132 | 00:00 | Siddhirganj | 136 | 02:00 | 129 | 12:00
Kabirpur | 134 | 08:00 | 118 | 12:00 | Sirajganj | 133 | 01:00 | 126 | 10:00
Kachua | 131 | 17:00 | 122 | 21:00 | Sitakunda | 136 | 05:00 | 133 | 00:00
Kaliakoir | 139 | 02:00 | 130 | 21:00 | Sonargaon | 133 | 07:00 | 127 | 12:00
Kaliganj | 136 | 03:00 | 127 | 13:00 | Sreemongol | 128 | 07:00 | 121 | 18:30
Kallyanpur | 132 | 06:00 | 125 | 12:00 | Sreepur | 133 | 02:00 | 125 | 13:00
Kalurghat | 137 | 02:00 | 135 | 00:00 | Srinagar | 135 | 05:00 | 126 | 12:00
Kamrangirchar | 135 | 05:00 | 122 | 12:00 | SSM | 140 | 02:00 | 138 | 00:00
Kaptai | 139 | 3:00 | 137 | 1:00 | Sunamganj | 118 | 06:00 | 110 | 18:00
Kasba | 128 | 02:00 | 120 | 21:00 | Sylhet | 124 | 06:00 | 119 | 19:30
Kazla | 136 | 06:00 | 125 | 12:00 | Sylhet_(South) | 126 | 07:00 | 120 | 18:00
Keranigonj | 136 | 05:00 | 127 | 13:00 | Tangail | 129 | 08:00 | 122 | 18:00
Khagrachori | 136 | 03:00 | 133 | 00:00 | Taraganj | 135 | 01:00 | 125 | 08:00
Khulna | 132 | 06:00 | 124 | 00:00 | Tasnim | 134 | 06:00 | 127 | 12:00
Khulna(S) | 133 | 04:00 | 127 | 13:00 | Thakurgaon | 142 | 02:00 | 129 | 08:00
Khulshi | 135 | 03:00 | 131 | 07:00 | TK | 135 | 00:00 | 135 | 00:00
Kishoreganj | 129 | 07:00 | 120 | 13:00 | Tongi | 139 | 04:00 | 124 | 11:00
Kodda | 136 | 01:00 | 114 | 21:00 | Ullahpara | 134 | 01:00 | 127 | 11:00
Korerhat | 134 | 03:00 | 128 | 21:00 | Ullon | 135 | 04:00 | 125 | 12:00
KSRM | 136 | 03:00 | 133 | 14:00 | Uttara | 134 | 01:00 | 121 | 18:00
Kulaura | 131 | 08:00 | 126 | 00:00 | UttaraNew | 134 | 01:00 | 121 | 12:00
Kurigram | 130 | 00:00 | 120 | 07:00 | Zigatola | 135 | 03:00 | 127 | 12:00
Kushtia | 137 | 02:00 | 128 | 18:00
Laksam | 130 | 17:00 | 122 | 21:00
Lakshmipur | 128 | 17:00 | 120 | 21:00
Lalbag | 135 | 04:00 | 126 | 12:00
Lalmonirhat | 130 | 02:00 | 119 | 18:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division