## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-10-2026 | during | 22-10-2026 | during | 22-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 388 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 309 | 318 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 69 | 94 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8.5 | 8.5 | 24.75 | 24.75 | 5.5 | 5.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 42 | 52.19 | 52.19 | 24 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 135 | 245 | 300 | 300 | 98 | 98 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 133 | 149 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 68 | 126 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 19 | 48 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP | 1*448+1*208 | 584 | 584 | 455 | 465 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 510 | 525 | 583 | 583 | 525 | 525 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2471.5 | 2840.92 | 5368.55 | 5338.55 | 2610.92 | 2797.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 25.5 | 25.5 | 25.5 | 17 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 139 | 141 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 68 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 7 | 14 | 24 | 14 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 30 | 28 | 30 | 30 | 30 | 30 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 5 | 95.1 | 95.1 | 34 | 57 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.5 | 0 | 3.81 | 0 | 3.81 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 87 | 210 | 300 | 300 | 51 | 212 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 49 | 73 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 52 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 600 | 950 | 1224 | 1224 | 740 | 950 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 730 | 1080 | 1150 | 1150 | 790 | 1080 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2164.5 | 3161.86 | 3873.77 | 3929.96 | 2356.81 | 3234.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 184 | 210 | 221.25 | 221.25 | 205 | 205 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 315 | 285 | 350.01 | 350.01 | 350.01 | 350.01 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 250 | 342.01 | 342.01 | 306 | 306 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 160 | 165 | 280 | 280 | 200 | 200 | STG Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 45 | 45 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 55 | 55 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 95 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 20 | 20 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 65 | 65 | 163 | 163 | 65 | 65 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 2 | 126 | 200 | 200 | 135 | 119 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 66 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 3 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 24.5 | 24.5 | 11 | 11 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 49 | 43 | 113 | 113 | 73 | 73 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 68 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1362 | 1579.2 | 2555.44 | 2485.44 | 1939.21 | 1917.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-10-2026 | during | 22-10-2026 | during | 22-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 160 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 87 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.19 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 33 | 35 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 287.49 | 306 | 673.6 | 601.5 | 308.1 | 322
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 30 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 96 | 95 | 95 | 95 | 100 | 100 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 28 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 83 | 83 | 11 | 11 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 13 | 13 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 294 | 293 | 341 | 341 | 260 | 260 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 397 | 397 | 400 | 400 | 400 | 400 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 15 | 57 | 350 | 350 | 260 | 260 | STG Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1256 | 1291 | 1668 | 1668 | 1361 | 1361
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 904 | 915 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 25 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 54 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2282.2 | 2259.2 | 2249.2 | 2164.2 | 1724.2 | 1639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1159 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 48 | 80 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 115 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 137 | 150 | 150 | 35 | 100 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 298 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.59 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1965.19 | 2098 | 2158.6 | 2157.6 | 1944.6 | 2008.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 57.97 | 0 | 55.42 | 0 | 55.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 32 | 32 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 305 | 297 | 413.79 | 413.79 | 300 | 300 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 34 | 34 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 60 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 18 | 70 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.62 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1030.13 | 1101.16 | 800 | 800 | 1200 | 1400 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.59 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1697.31 | 1788.36 | 2606.11 | 2383.99 | 1992.32 | 2141.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 37 | 113 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 197 | 0 | 188.25 | 0 | 188.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 391.3 | 228 | 471.25 | 248 | 381.25 | 237
System Total |  |  |  |  | 28843.2 | 28692.211 | 13877.49 | 15552.54 | 21624.52 | 20977.24 | 14618.41 | 15658.99
Forecast Scenario (22-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15226.1 |  | 0 |  | 15226.1
|  |  |  | 1:00 | 14980 |  | 0 |  | 14980
|  |  |  | 2:00 | 14231 |  | 0 |  | 14231
|  |  |  | 3:00 | 13888.6 |  | 0 |  | 13888.6
|  |  |  | 4:00 | 13375 |  | 0 |  | 13375
|  |  |  | 5:00 | 12968.4 |  | 0 |  | 12968.4
|  |  |  | 6:00 | 12262.2 |  | 0 |  | 12262.2
|  |  |  | 7:00 | 12347.8 |  | 0 |  | 12347.8
|  |  |  | 8:00 | 12561.8 |  | 0 |  | 12561.8
|  |  |  | 9:00 | 12872.1 |  | 0 |  | 12872.1
|  |  |  | 10:00 | 12947 |  | 0 |  | 12947
|  |  |  | 11:00 | 14231 |  | 0 |  | 14231
|  |  |  | 12:00 | 14723.2 |  | 0 |  | 14723.2
|  |  |  | 13:00 | 14701.8 |  | 0 |  | 14701.8
|  |  |  | 14:00 | 14691.1 |  | 0 |  | 14691.1
|  |  |  | 15:00 | 14552 |  | 0 |  | 14552
|  |  |  | 16:00 | 14070.5 |  | 0 |  | 14070.5
|  |  |  | 17:00 | 13963.5 |  | 0 |  | 13963.5
|  |  |  | 18:00 | 15099.84 |  | 0 |  | 15099.84
|  |  |  | 18:30 | 15361.99 |  | 0 |  | 15361.99
|  |  |  | 19:00 | 16212.14 |  | 0 |  | 16212.14
|  |  |  | 19:30 | 16047.99 |  | 0 |  | 16047.99
|  |  |  | 20:00 | 15892.072 |  | 0 |  | 15892.072
|  |  |  | 21:00 | 15489.782 |  | 0 |  | 15489.782
|  |  |  | 22:00 | 14012.726 |  | 0 |  | 14012.726
|  |  |  | 23:00 | 14764.288 |  | 0 |  | 14764.288
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14723.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16212.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16212.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 318.74 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:40 hrs on 22-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-10-2026 | [28 empty] | Date: | 21-10-2026 | [28 empty] | Date: | 21-10-2026 | [28 empty] | Date: | 21-10-2026 | [28 empty] | Date: | 21-10-2026 | [16 empty] | Date: | 21-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 35 | 17 | 115 | 15 | 30 | 15 | 55 | 17 | 0 | 0 | 490 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 7.5 | 20 | 0 | 475 | 53 | 50 | 14 | 0 | 0 | 67 | 22 | 35 | 12 | 25 | 0 | 141 | 51 | 29 | 1080 | 0 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 1224 | 0 | 150 | 26 | 160 | 305 | 255 | 44 | 0 | 186 | 0 | 0 | 65 | 17 | 72 | 13 | 0 | 64 | 8 | 0 | 0 | 242 | 260 | 397 | 40 | 30 | 155 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8137.5 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1316.5 | 0 | 32 | 0 | 50 | 35 | 0 | 50 | 0 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 270 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 5922.3 | 14059.8 | 102.97
01:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 17 | 114 | 15 | 30 | 15 | 55 | 17 | 0 | 0 | 495 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 7.5 | 20 | 0 | 475 | 53 | 50 | 12 | 0 | 0 | 67 | 15 | 0 | 12 | 25 | 0 | 142 | 51 | 29 | 1080 | 0 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 992 | 0 | 150 | 26 | 200 | 298 | 285 | 44 | 0 | 220 | 0 | 0 | 65 | 17 | 72 | 13 | 0 | 60 | 8 | 0 | 0 | 242 | 260 | 397 | 40 | 30 | 152 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 23 | 7962.5 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 0 | 0 | 0 | 1250.28 | 0 | 32 | 0 | 50 | 35 | 0 | 50 | 0 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 5872.08 | 13834.58 | 102.96
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 0 | 114 | 0 | 30 | 0 | 55 | 0 | 0 | 0 | 490 | 0 | 0 | 295 | 0 | 0 | 0 | 68 | 7.5 | 20 | 0 | 485 | 53 | 50 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 25 | 0 | 142 | 51 | 29 | 1080 | 0 | 0 | 50 | 0 | 34 | 224 | 0 | 0 | 0 | 796 | 0 | 150 | 26 | 220 | 300 | 265 | 44 | 0 | 222 | 0 | 0 | 65 | 2 | 72 | 13 | 0 | 58 | 0 | 0 | 0 | 244 | 260 | 397 | 40 | 30 | 140 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 59 | 0 | 45 | 0 | 0 | 0 | 22 | 7494.5 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1223.28 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 296 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 5675.08 | 13169.58 | 102.96
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35 | 0 | 114 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 495 | 0 | 0 | 305 | 0 | 0 | 0 | 68 | 7.5 | 20 | 0 | 490 | 17 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 142 | 34 | 29 | 1080 | 0 | 0 | 50 | 0 | 0 | 223 | 0 | 0 | 0 | 682 | 0 | 150 | 26 | 220 | 312 | 310 | 44 | 0 | 223 | 0 | 0 | 65 | 0 | 0 | 13 | 0 | 58 | 0 | 0 | 0 | 246 | 260 | 397 | 40 | 30 | 141 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 35 | 59 | 0 | 35 | 0 | 0 | 0 | 24 | 7239.5 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1223.67 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5565.47 | 12804.97 | 102.95
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 307 | 0 | 0 | 0 | 68 | 7.5 | 20 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 142 | 0 | 29 | 1080 | 0 | 0 | 30 | 0 | 0 | 223 | 0 | 0 | 0 | 603 | 0 | 150 | 26 | 220 | 301 | 300 | 44 | 0 | 223 | 0 | 0 | 65 | 0 | 0 | 13 | 0 | 56 | 0 | 0 | 0 | 241 | 260 | 397 | 40 | 30 | 152 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 17 | 59 | 0 | 24 | 0 | 0 | 0 | 16 | 6900.5 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1228.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5552.36 | 12452.86 | 102.95
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 300 | 0 | 0 | 0 | 68 | 7.5 | 20 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 29 | 870 | 0 | 0 | 18 | 0 | 0 | 221 | 0 | 0 | 0 | 600 | 0 | 100 | 26 | 220 | 304 | 305 | 44 | 0 | 223 | 0 | 0 | 65 | 0 | 0 | 13 | 0 | 56 | 0 | 0 | 0 | 244 | 260 | 397 | 40 | 30 | 157 | 0 | 16 | 0 | 11 | 0 | 96 | 0 | 100 | 17 | 59 | 0 | 24 | 0 | 0 | 0 | 12 | 6520.5 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1248.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5590.04 | 12110.54 | 102.94
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 314 | 0 | 0 | 0 | 51 | 7.5 | 20 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 29 | 735 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 600 | 0 | 50 | 0 | 200 | 323 | 325 | 44 | 0 | 223 | 0 | 0 | 65 | 0 | 0 | 13 | 0 | 52 | 0 | 0 | 0 | 243 | 260 | 382 | 40 | 30 | 160 | 0 | 16 | 0 | 11 | 20 | 95 | 0 | 0 | 17 | 59 | 0.05 | 24 | 0 | 0 | 0 | 0 | 6196.55 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1169 | 0 | 0 | 0 | 1237.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5528.15 | 11724.7 | 102.94
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 57 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 316 | 0 | 0 | 5 | 51 | 7.5 | 20 | 0 | 490 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0.44 | 142 | 0 | 29 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 600 | 4 | 50 | 0 | 200 | 337 | 340 | 44 | 0 | 206 | 0 | 0 | 65 | 0 | 0 | 13 | 0 | 48 | 0 | 13 | 0 | 242 | 208 | 376 | 40 | 30 | 160 | 2 | 16 | 0 | 83 | 30 | 95 | 0 | 0 | 17 | 59 | 3.11 | 65 | 0 | 0.2 | 5.86 | 0 | 6347.11 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1212 | 0 | 0 | 0 | 1243.3 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8.31 | 14 | 0 | 0 | 9.38 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0.83 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.3 | 28 | 0.07 | 0 | 297 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5690.79 | 12037.9 | 102.93
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 0 | 87 | 30 | 0 | 0 | 4 | 0 | 0 | 0 | 495 | 0 | 0 | 304 | 0 | 0 | 14 | 51 | 7.5 | 20 | 0 | 490 | 5 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.7 | 141 | 0 | 29 | 730 | 0 | 0 | 1 | 0 | 0 | 221 | 0 | 0 | 0 | 600 | 7 | 68 | 0 | 200 | 305 | 310 | 44 | 0 | 205 | 0 | 0 | 65 | 0 | 2 | 13 | 0 | 44 | 0 | 35 | 0 | 250 | 155 | 370 | 40 | 30 | 159 | 5 | 16 | 0 | 83 | 30 | 95 | 0 | 0 | 17 | 59 | 9.56 | 65 | 0 | 1 | 22.7 | 7 | 6394.46 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1234.2 | 0 | 0 | 0 | 1197.49 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 26.55 | 45 | 0 | 0 | 28.14 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 2.47 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.6 | 83 | 0.21 | 16 | 281 | 115 | 0 | 0 | 1170.6 | 300 | 18 | 5858.26 | 12252.72 | 102.92
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 0 | 87 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 465 | 0 | 0 | 290 | 0 | 0 | 23 | 86 | 7.8 | 20 | 0 | 485 | 17 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.57 | 140 | 0 | 29 | 730 | 0 | 0 | 18 | 0 | 0 | 219 | 0 | 0 | 0 | 600 | 16 | 100 | 0 | 200 | 300 | 295 | 44 | 0 | 193 | 0 | 0 | 65 | 0 | 24 | 13 | 0 | 46 | 0 | 53 | 0 | 262 | 95 | 397 | 40 | 30 | 157 | 8 | 16 | 0 | 83 | 30 | 95 | 0 | 0 | 17 | 59 | 15.26 | 113 | 0 | 1.6 | 34.43 | 24 | 6548.66 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1227 | 0 | 0 | 0 | 1210.77 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 41.56 | 73 | 0 | 0 | 45.73 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 3.9 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.5 | 135 | 0.36 | 16 | 269 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 6006.42 | 12555.08 | 102.91
10:00 | 0 | 5 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 73 | 15 | 0 | 0 | 18 | 0 | 0 | 0 | 480 | 0 | 0 | 302 | 0 | 0 | 28 | 86 | 7.8 | 20 | 0 | 480 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 25 | 3.33 | 139 | 0 | 29 | 730 | 0 | 0 | 18 | 0 | 0 | 216 | 0 | 0 | 0 | 600 | 18 | 50 | 0 | 170 | 315 | 310 | 44 | 0 | 185 | 0 | 0 | 65 | 0 | 28 | 13 | 0 | 48 | 0 | 64 | 0 | 275 | 90 | 397 | 40 | 30 | 154 | 10 | 16 | 0 | 83 | 30 | 96 | 0 | 0 | 17 | 79 | 19.11 | 75 | 0 | 1.9 | 40.16 | 24 | 6568.3 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1174 | 0 | 0 | 0 | 1011.46 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 52.48 | 96 | 0 | 0 | 55.65 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 4.88 | 0 | 0 | 35 | 31 | 0 | 0 | 0 | 0 | 5.7 | 170 | 0.5 | 16 | 291 | 115 | 0 | 0 | 1170.6 | 300 | 35 | 5889.27 | 12457.57 | 102.9
11:00 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 0 | 74 | 32 | 5 | 0 | 49 | 17 | 0 | 0 | 505 | 0 | 5 | 311 | 0 | 0 | 31 | 86 | 7.8 | 20 | 0 | 465 | 96 | 83 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.72 | 139 | 6 | 30 | 730 | 0 | 0 | 28 | 0 | 0 | 214 | 0 | 0 | 0 | 600 | 14 | 60 | 0 | 160 | 325 | 320 | 44 | 0 | 180 | 0 | 0 | 65 | 0 | 52 | 13 | 0 | 52 | 0 | 69 | 0 | 280 | 15 | 398 | 40 | 29 | 155 | 10 | 16 | 0 | 82 | 25 | 95 | 0 | 100 | 18 | 78 | 17.8 | 75 | 0 | 1.8 | 43.55 | 24 | 6901.67 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1200 | 0 | 0 | 0 | 1027.62 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 55.13 | 108 | 0 | 0 | 55.29 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 5.34 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 6.4 | 192 | 0.6 | 48 | 297 | 114 | 0 | 0 | 1170.6 | 300 | 35 | 6068.98 | 12970.65 | 102.89
12:00 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 35 | 19 | 133 | 69 | 135 | 4 | 55 | 68 | 0 | 0 | 510 | 0 | 35 | 309 | 0 | 0 | 32 | 123 | 8.5 | 20 | 0 | 455 | 107 | 87 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.5 | 139 | 49 | 30 | 730 | 0 | 0 | 39 | 1 | 87 | 214 | 0 | 0 | 0 | 600 | 18 | 95 | 0 | 160 | 315 | 310 | 44 | 0 | 184 | 0 | 1 | 65 | 2 | 49 | 13 | 0 | 58 | 3 | 63 | 0 | 294 | 15 | 397 | 40 | 29 | 155 | 8 | 16 | 0 | 81 | 25 | 96 | 0 | 100 | 33 | 78 | 22 | 75 | 0 | 2.3 | 53.19 | 24 | 7541.49 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 90 | 1234.2 | 0 | 0 | 0 | 1030.13 | 0 | 0 | 0 | 95 | 18 | 0 | 0 | 0 | 25 | 57.97 | 97 | 0 | 0 | 63.59 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 5.62 | 0 | 0 | 115 | 36 | 37 | 0 | 0 | 0 | 6.3 | 197 | 0.59 | 48 | 298 | 113 | 0 | 0 | 1170.6 | 300 | 35 | 6336 | 13877.49 | 102.88
13:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 35 | 149 | 94 | 229 | 49 | 55 | 162 | 0 | 0 | 500 | 0 | 35 | 290 | 0 | 0 | 30 | 123 | 8.5 | 20 | 0 | 450 | 109 | 87 | 0 | 0 | 0 | 0 | 1 | 35 | 0 | 25 | 3.4 | 139 | 64 | 28 | 730 | 9 | 0 | 45 | 15 | 88 | 212 | 0 | 0 | 0 | 600 | 18 | 123 | 0 | 190 | 276 | 275 | 44 | 0 | 194 | 0 | 21 | 65 | 31 | 43 | 13 | 17 | 62 | 43 | 53 | 0 | 300 | 16 | 392 | 39 | 28 | 154 | 10 | 16 | 0 | 81 | 28 | 95 | 0 | 100 | 35 | 86 | 20 | 75 | 0 | 2.1 | 50 | 24 | 7909 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 80 | 1234.2 | 0 | 0 | 0 | 1022.5 | 0 | 0 | 0 | 113 | 96 | 0 | 0 | 0 | 43 | 55.69 | 104 | 0 | 0 | 44.91 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 5.06 | 0 | 0 | 115 | 33 | 67 | 0 | 0 | 0 | 6.2 | 182 | 0.54 | 64 | 287 | 113 | 0 | 0 | 1170.6 | 300 | 35 | 6453.7 | 14362.7 | 102.87
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 54 | 35 | 149 | 62 | 257 | 55 | 35 | 158 | 0 | 0 | 485 | 0 | 35 | 310 | 0 | 0 | 21 | 123 | 9 | 20 | 0 | 450 | 107 | 88 | 0 | 0 | 1 | 0 | 7 | 35 | 0 | 25 | 3.03 | 140 | 72 | 21 | 880 | 16 | 0 | 43 | 15 | 88 | 212 | 0 | 0 | 0 | 600 | 15 | 133 | 0 | 210 | 315 | 280 | 44 | 0 | 209 | 0 | 16 | 65 | 98 | 37 | 13 | 17 | 62 | 43 | 56 | 0 | 300 | 30 | 391 | 39 | 28 | 140 | 6 | 16 | 0 | 81 | 25 | 96 | 0 | 100 | 35 | 87 | 16.85 | 55 | 0 | 1.7 | 41.5 | 24 | 8111.08 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 55 | 1195 | 0 | 0 | 0 | 1025.55 | 0 | 0 | 0 | 113 | 50 | 0 | 8.2 | 0 | 52.2 | 39.52 | 91 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 3.98 | 0 | 0 | 115 | 29 | 68 | 0 | 0 | 0 | 5.3 | 152 | 0.31 | 64 | 257 | 113 | 0 | 0 | 1130 | 300 | 35 | 6228.81 | 14339.89 | 102.86
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 54 | 35 | 149 | 45 | 278 | 30 | 35 | 126 | 0 | 0 | 485 | 0 | 35 | 309 | 0 | 0 | 12 | 123 | 8.5 | 20 | 0 | 445 | 109 | 88 | 0 | 0 | 0 | 0 | 7 | 35 | 0 | 25 | 1.99 | 139 | 72 | 22 | 1080 | 16 | 0 | 42 | 25.5 | 89 | 212 | 0 | 0 | 0 | 603 | 11 | 135 | 0 | 185 | 297 | 255 | 44 | 0 | 215 | 0 | 16 | 65 | 122 | 33 | 13 | 17 | 60 | 43 | 38 | 0 | 300 | 55 | 394 | 39 | 28 | 151 | 7 | 16 | 0 | 80 | 30 | 96 | 0 | 100 | 35 | 87 | 12 | 55 | 0 | 1.2 | 31.9 | 24 | 8226.09 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 1195 | 0 | 0 | 0 | 1010.41 | 0 | 0 | 0 | 113 | 35 | 0 | 8.2 | 0 | 34 | 16.68 | 48 | 0 | 0 | 37.55 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 1.8 | 0 | 0 | 70 | 21 | 49 | 0 | 0 | 0 | 3.9 | 112 | 0.35 | 64 | 276 | 108 | 0 | 0 | 1112 | 300 | 35 | 5970.89 | 14196.98 | 102.85
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 35 | 149 | 45 | 225 | 30 | 35 | 90 | 0 | 0 | 490 | 0 | 35 | 311 | 0 | 0 | 5 | 105 | 0 | 14 | 0 | 445 | 72 | 87 | 0 | 0 | 1 | 0 | 7 | 35 | 0 | 25 | 0.9 | 140 | 72 | 28 | 1080 | 16 | 0 | 42 | 25.5 | 51 | 212 | 0 | 0 | 0 | 605 | 6 | 100 | 0 | 195 | 350 | 270 | 44 | 0 | 214 | 0 | 16 | 65 | 85 | 34 | 13 | 17 | 56 | 25 | 18 | 0 | 292 | 55 | 389 | 39 | 28 | 153 | 3 | 16 | 0 | 81 | 30 | 96 | 0 | 100 | 35 | 87 | 5 | 55 | 0 | 0.6 | 16.31 | 24 | 7969.31 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 1196 | 0 | 0 | 0 | 1024.95 | 0 | 0 | 0 | 70 | 35 | 0 | 8.2 | 0 | 34 | 7.07 | 16 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 1.37 | 0 | 0 | 70 | 9 | 49 | 0 | 0 | 0 | 1.3 | 53 | 0.12 | 64 | 294 | 108 | 0 | 0 | 1102 | 300 | 35 | 5755.81 | 13725.12 | 102.84
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 35 | 120 | 45 | 210 | 30 | 35 | 90 | 0 | 0 | 480 | 0 | 35 | 300 | 0 | 0 | 1 | 105 | 8.5 | 20 | 0 | 445 | 72 | 115 | 0 | 0 | 0 | 0 | 7 | 35 | 0 | 25 | 0.06 | 141 | 71 | 28 | 1080 | 28 | 0 | 42 | 25.5 | 51 | 212 | 0 | 0 | 0 | 690 | 0 | 100 | 0 | 205 | 292 | 250 | 44 | 0 | 215 | 0 | 25 | 65 | 85 | 37 | 13 | 34 | 58 | 25 | 2 | 0 | 296 | 55 | 399 | 39 | 29 | 146 | 0 | 16 | 0 | 81 | 30 | 96 | 0 | 100 | 35 | 87 | 0.75 | 75 | 0 | 0.1 | 1.3 | 24 | 7988.21 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2.95 | 1186 | 0 | 0 | 0 | 997.05 | 0 | 0 | 0 | 70 | 35 | 0 | 8.2 | 0 | 34 | 1.52 | 4 | 0 | 0 | 2.46 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0.16 | 0 | 0 | 70 | 2 | 49 | 0 | 0 | 0 | 0 | 8 | 0.03 | 80 | 254 | 109 | 0 | 0 | 1120 | 300 | 54 | 5633.37 | 13621.58 | 102.83
18:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 36 | 122 | 94 | 245 | 35 | 55 | 126 | 0 | 0 | 495 | 0 | 35 | 317 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 450 | 90 | 206 | 0 | 0 | 0 | 24 | 7 | 54.36 | 12 | 25 | 0 | 141 | 57 | 28 | 1080 | 57 | 0 | 45 | 25.5 | 59 | 214 | 0 | 0 | 0 | 795 | 0 | 125 | 25 | 170 | 312 | 270 | 44 | 0 | 190 | 0 | 46 | 65 | 98 | 42 | 13 | 70 | 68 | 34 | 0 | 0 | 295 | 55 | 385 | 39 | 29 | 141 | 0 | 16 | 0 | 82 | 30 | 96 | 0 | 100 | 35 | 87 | 0 | 142 | 0 | 0 | 0 | 24 | 8758.78 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1200 | 0 | 0 | 0 | 1117.73 | 0 | 0 | 0 | 113 | 56 | 0 | 60 | 26 | 52.2 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 110 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 285 | 114 | 0 | 0 | 1170.6 | 300 | 137 | 6223.53 | 14982.31 | 102.83
19:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 54 | 48 | 149 | 94 | 245 | 55 | 55 | 126 | 0 | 0 | 525 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 465 | 107 | 210 | 5 | 0 | 0 | 51 | 7 | 54.36 | 24 | 25 | 0 | 141 | 73 | 28 | 1080 | 52 | 0 | 45 | 25.5 | 68 | 216 | 0 | 0 | 0 | 950 | 0 | 150 | 8 | 165 | 285 | 250 | 44 | 0 | 210 | 0 | 68 | 65 | 126 | 43 | 13 | 34 | 66 | 52.2 | 0 | 0 | 293 | 57 | 397 | 40 | 30 | 153 | 0 | 16 | 0 | 82 | 28 | 95 | 0 | 100 | 35 | 87 | 0 | 160 | 0 | 0 | 0 | 24 | 9178.98 | 915 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 1101.16 | 0 | 32 | 0 | 113 | 70 | 0 | 60 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 115 | 0 | 0 | 1159 | 300 | 137 | 6373.56 | 15552.54 | 102.82
19:30 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 54 | 54 | 114 | 94 | 210 | 30 | 55 | 90 | 0 | 0 | 490 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 465 | 72 | 175 | 20 | 0 | 0 | 51 | 7 | 54.36 | 24 | 25 | 0 | 141 | 72 | 28 | 1080 | 34 | 0 | 45 | 25.5 | 68 | 218 | 0 | 0 | 0 | 1030 | 0 | 150 | 8 | 185 | 325 | 285 | 44 | 0 | 206 | 0 | 32 | 65 | 147 | 43 | 13 | 34 | 66 | 34 | 0 | 0 | 290 | 60 | 398 | 40 | 30 | 152 | 0 | 16 | 0 | 82 | 28 | 95 | 0 | 100 | 35 | 87 | 0 | 140 | 0 | 0 | 0 | 24 | 9069.78 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1220 | 0 | 0 | 0 | 1114.2 | 0 | 32 | 0 | 113 | 35 | 0 | 60 | 31 | 34 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 115 | 0 | 0 | 1167 | 300 | 100 | 6220.2 | 15289.98
20:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 54 | 130 | 78 | 210 | 15 | 55 | 90 | 0 | 0 | 490 | 0 | 35 | 302 | 0 | 0 | 0 | 143.42 | 8.5 | 20 | 0 | 460 | 72 | 175 | 30 | 0 | 0 | 51 | 21 | 54.36 | 24 | 25 | 0 | 141 | 75 | 26 | 1080 | 16 | 0 | 45 | 25.5 | 68 | 218 | 0 | 0 | 0 | 1100 | 0 | 150 | 8 | 185 | 292 | 255 | 44 | 0 | 208 | 0 | 36 | 66 | 120 | 43 | 13 | 17 | 66 | 34 | 0 | 0 | 288 | 60 | 398 | 40 | 30 | 154 | 0 | 16 | 0 | 82 | 30 | 94 | 0 | 100 | 35 | 87 | 0 | 120 | 0 | 0 | 0 | 24 | 8973.78 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1207 | 0 | 0 | 0 | 1110.23 | 0 | 32 | 0 | 113 | 35 | 0 | 60 | 32 | 34 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 115 | 0 | 0 | 1133 | 300 | 100 | 6175.23 | 15149.01 | 102.82
21:00 | 0 | 50 | 42 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 54 | 17 | 114 | 78 | 210 | 15 | 55 | 90 | 0 | 0 | 485 | 0 | 35 | 305 | 0 | 0 | 0 | 123 | 8.5 | 21 | 0 | 460 | 72 | 175 | 18 | 0 | 0 | 50 | 21 | 54.36 | 12 | 25 | 0 | 141 | 92 | 28 | 1080 | 16 | 0 | 44 | 25.5 | 68 | 217 | 0 | 0 | 0 | 1165 | 0 | 150 | 8 | 185 | 298 | 255 | 44 | 0 | 211 | 0 | 24 | 66 | 85 | 44 | 18 | 17 | 64 | 16 | 0 | 0 | 289 | 90 | 398 | 40 | 30 | 155 | 0 | 16 | 0 | 83 | 30 | 96 | 0 | 100 | 35 | 87 | 0 | 120 | 0 | 0 | 0 | 24 | 8920.36 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1190 | 0 | 0 | 0 | 1105.81 | 0 | 32 | 0 | 113 | 35 | 0 | 60 | 32 | 16 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 70 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 278 | 115 | 0 | 0 | 1136 | 300 | 100 | 6081.81 | 15002.17 | 102.81
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 17 | 114 | 78 | 210 | 15 | 55 | 90 | 0 | 0 | 485 | 0 | 35 | 298 | 0 | 0 | 0 | 123 | 8.5 | 21 | 0 | 460 | 72 | 175 | 12 | 0 | 0 | 50 | 21 | 35 | 12 | 25 | 0 | 139 | 92 | 29 | 1080 | 16 | 0 | 40 | 17 | 68 | 218 | 0 | 0 | 0 | 1224 | 0 | 100 | 8 | 195 | 287 | 245 | 44 | 0 | 220 | 0 | 16 | 66 | 85 | 44 | 5 | 17 | 66 | 16 | 0 | 0 | 290 | 115 | 398 | 40 | 30 | 153 | 0 | 16 | 0 | 83 | 30 | 77 | 0 | 100 | 35 | 87 | 0 | 100 | 0 | 0 | 0 | 12 | 8768.5 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1178 | 0 | 0 | 0 | 1097.47 | 0 | 32 | 0 | 70 | 35 | 0 | 60 | 32 | 16 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 275 | 115 | 0 | 0 | 1125 | 300 | 100 | 5987.47 | 14755.97 | 102.81
23:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 17 | 114 | 78 | 210 | 15 | 55 | 90 | 0 | 0 | 450 | 0 | 35 | 310 | 0 | 0 | 0 | 123 | 8.5 | 21 | 0 | 450 | 72 | 135 | 12 | 0 | 0 | 50 | 21 | 35 | 12 | 25 | 0 | 139 | 93 | 29 | 1080 | 16 | 0 | 44 | 19 | 68 | 219 | 0 | 0 | 0 | 1160 | 0 | 100 | 0 | 200 | 304 | 265 | 44 | 0 | 219 | 0 | 16 | 65 | 68 | 44 | 5 | 17 | 66 | 16 | 0 | 0 | 288 | 130 | 398 | 40 | 30 | 153 | 0 | 16 | 0 | 83 | 30 | 71 | 0 | 100 | 35 | 87 | 0 | 75 | 0 | 0 | 0 | 24 | 8650.5 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1152 | 0 | 0 | 0 | 1136.95 | 0 | 32 | 0 | 70 | 35 | 0 | 60 | 32 | 16 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 278 | 115 | 0 | 0 | 1125 | 300 | 100 | 5974.95 | 14625.45 | 102.8
Total KWH | 0 | 588480 | 349920 | 0 | 0 | 0 | 0 | 0 | 8798400 | 0 | 0 | 965160 | 454320 | 2670624 | 1075680 | 2847065 | 436462 | 913468 | 1412640 | 0 | 0 | 11864575 | 0 | 494680 | 7410185 | 0 | 0 | 200053 | 2521200 | 200400 | 468720 | 0 | 11150909.09 | 1467818 | 2157818 | 104640 | 0 | 1920 | 580799 | 211272 | 591067 | 118080 | 541440 | 23398 | 3407405 | 1157526 | 683040 | 22690909.09 | 329527 | 0 | 831840 | 256069.8 | 1006145 | 5003956 | 0 | 0 | 0 | 18556362 | 121230 | 2821890 | 217455 | 4753000 | 7821800 | 7024000 | 1031304 | 0 | 5061000 | 0 | 372480 | 1546980 | 1163520 | 801360 | 282790 | 308940 | 1383360 | 389914 | 456655 | 0 | 6611000 | 3103300 | 9510000 | 957000 | 701640 | 3662018.18 | 72999 | 398784 | 0 | 1504320 | 519456 | 2191000 | 0 | 1898820 | 730080 | 1764000 | 132980 | 1785600 | 0 | 14250 | 345690 | 485280 | 186489868.16 | 21957818 | 0 | 0 | 172416 | 0 | 0 | 0 | 0 | 0 | 904032 | 518400 | 28938190 | 0 | 0 | 0 | 26917093 | 0 | 218224 | 0 | 1668576 | 787200 | 0 | 491088 | 176592 | 417926 | 355968 | 726411 | 247885 | 0 | 405008 | 0 | 0 | 0 | 0 | 0 | 0 | 7406836 | 0 | 35400 | 0 | 0 | 1303269 | 242687 | 820617 | 0 | 0 | 0 | 43404.24 | 1298880 | 3739 | 1067136 | 6895000 | 2726000 | 0 | 0 | 27803636 | 7262545.46 | 1185600 | 142997576.7 | 329487444.86

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13877.49 | MW | 12:00 Hr. | Energy Generated |  |  | 329.4874 |  | MKWHr.
| Day Peak Demand |  |  | 13877.49 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.091 |  | MKWHr.
| Evening Peak Generation |  |  | 15552.54 | MW | 19:00 Hr. | Energy Demand |  |  | 329.5784 |  | MKWHr.
| Evening Peak Demand |  |  | 15586.54 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 11724.7 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 837.92 |  | MMCFD
| Maximum Generation of the Day |  |  | 15552.54 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 7.7448 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.8932 | 0 | 14.7297 | 0 | 0 | 0.20005 | 0 | 0 | 54.8229 | Gas | 114.5087 | Gas | 393691644.5809
| Chattogram Zone |  |  | 5.687 | 41.2473 | 9.354 | 0 | 3.4074 | 0.14463 | 0 | 0.00192 | 59.8423 | Coal | 112.1466 | Coal | 873425763.7339
| Cumilla Zone |  |  | 27.7383 | 0 | 5.8581 | 0 | 0 | 0.45665 | 1.3834 | 0 | 35.4364 | HFO | 44.1674 | HFO | 880767127.778
| Mymensingh Zone |  |  | 0 | 0 | 4.765 | 0 | 0 | 0.49292 | 0 | 0 | 5.2579 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.0573 | 0 | 0 | 0 | 0 | 0.072999 | 0 | 0 | 31.1303 | Hydro | 3.4074 | Hydro | 340740.5
| Khulna Zone |  |  | 0 | 28.9382 | 1.0764 | 0 | 0 | 0.5184 | 21.9578 | 0 | 52.4909 | Solar | 4.9972 | Solar | 80471409.7944
| Barishal Zone |  |  | 2.726 | 41.9612 | 2.2527 | 0 | 0 | 0.003739 | 0 | 0 | 46.9437 | Import | 50.2583 | Import | 323093643.31
| Rajshahi Zone |  |  | 7.4068 | 0 | 4.0075 | 0 | 0 | 1.5228 | 26.9171 | 0 | 39.8542 | Wind | 0.00192 | Wind | 28454.4
| Rangpur Zone |  |  | 0 | 0 | 2.1239 | 0 | 0 | 1.585 | 0 | 0 | 3.7089
| Total |  |  | 114.5087 | 112.1466 | 44.1674 | 0 | 3.4074 | 4.9972 | 50.2583 | 0.00192 | 329.4874
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 393691644.5809 |  | Hydro | 340740.5
|  |  |  | Coal | 873425763.7339 |  | Solar | 80471409.7944
|  |  |  | HFO | 880767127.778 |  | Import | 323093643.31
|  |  |  | HSD | 0 |  | Wind | 28454.4
[5 empty] | Total: | 255,18,18,784 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9578 | Peak Hr Flow | 915.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35370000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.9171 | Peak Hr Flow | 1101.16 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1598 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3834 | Peak Hr Flow | 66.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2303 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.2583 | Peak Hr Flow | 2082.16 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5518
|  |  |  | Chattogram |  | 0 |  | 1493
|  |  |  | Cumilla |  | 0 |  | 1490
|  |  |  | Mymensingh |  | 23 |  | 1226
|  |  |  | Sylhet |  | 0 |  | 660
|  |  |  | Khulna |  | 0 |  | 1710
|  |  |  | Barishal |  | 0 |  | 465
|  |  |  | Rajshahi |  | 0 |  | 1454
|  |  |  | Rangpur |  | 0 |  | 855
|  |  |  | Total |  | 33 |  | 14871
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 500
|  |  |  | Total Unavailable Capacity |  |  |  | 800
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 10:43 |  | Sylhet 225 MW CCPP GT Synchronized with remarks:- None
| 10:43 |  | Sylhet 225 MW CCPP Synchronized with remarks:- GT
| 13:00 |  | Day Peak Generation: 14363 MW.
| 15:55 | 16:07 | Savar 132/33kV S/S T-3 LT Tripped showing Over current relay relays Due to DPBS-3 L-38
feeder fault
| 15:55 | 16:07 | Savar 132/33kV S/S T-4 LT Tripped showing Over current relay relays Due to DPBS-3 L-38
feeder fault
| 20:36 |  | Bibiyana South 400 MW Synchronized with remarks:- ST
| 03:39 |  | Shahjibazar 330 MW CCPP GT-1 was shutdown.
| 06:00 |  | Minimum Generation: 12134 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 388 | 8798400 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 436462 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 7410185 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 965160 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 94 | 1075680 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 913468 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 494680 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8.5 | 200400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 468720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 349920 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 2847065 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2670624 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 588480 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1412640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 200053 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 48 | 454320 | Machine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 1*448+1*208 | 584 | 465 | 11150909.09 | Machine Problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 525 | 11864575 | Machine Problem
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2521200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2840.92 | 54822941.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 256069.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121230 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 831840 | Machine Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 141 | 3407405 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5003956 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1006145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 7 | 211272 | Machine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 580799 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 118080 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 683040 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 5 | 104640 | Machine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 210 | 2157818 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 591067 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 73 | 1157526 | Fuel Shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 541440 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1467818 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 52 | 329527 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 950 | 18556362 | Coal Shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 1920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 22690909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3161.86 | 59842261.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 210 | 5061000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 285 | 7821800 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 7024000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 165 | 4753000 | STG Under Shutdown & Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1031304 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2821890 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 65 | 1546980 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 126 | 1163520 | Fuel Shortage
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1383360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 389914 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 282790 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 308940 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 43 | 801360 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 372480 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456655 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1579.2 | 35436448
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 132980 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 160 | 1785600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1764000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 345690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 485280 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 730080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 306 | 5257880
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 72999 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 957000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 701640 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3662018.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 95 | 2191000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 519456 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1504320 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1898820 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 398784 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 293 | 6611000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 397 | 9510000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 57 | 3103300 | ST synch process going on
Sylhet Area Total |  |  |  |  | 2325 | 1291 | 31130337.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 21957818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 172416 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 904032 | Machine Problem
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 518400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 28938190 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2259.2 | 52490856
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1159 | 27803636 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 1067136 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2726000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7262545.46 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1185600 | Machine Problem
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6895000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3739 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2098 | 46943656.46
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 355968 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 218224 | plant availability zero
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 176592 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 297 | 7406836 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 247885 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 417926 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 60 | 491088 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 787200 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1668576 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 35400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1101.16 | 26917093 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 405008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 726411 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1788.36 | 39854207
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 820617 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43404.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1303269 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 242687 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1298880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 228 | 3708857.24
Eastern Grid Total |  |  |  |  | 16961.086 | 9178.98 | 186489868.16
Western Grid Total |  |  |  |  | 11731.125 | 6373.56 | 142997576.7
National Grid Total |  |  |  |  | 28692.211 | 15552.54 | 329487444.86
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10355.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4484.3 | MW
i) Dhaka area |  |  | 5508.37 |  | MW | i) Khulna area |  |  |  | 1710 | MW
ii) Chattogram area |  |  | 1493.2 |  | MW | ii) Barishal area |  |  |  | 464.9 | MW
iii) Cumilla area |  |  | 1490.46 |  | MW | iii) Rajshahi area |  |  |  | 1454.4 | MW
iv) Mymensingh area |  |  | 1203 |  | MW | iv) Rangpur area |  |  |  | 855 | MW
v) Sylhet area |  |  | 660 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14839.33 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 00:00 | 72 | Hatirjheel | 56 | 13:00 | 143 | PHP | 11 | 00:00
2 | AKSML | 147.3 | 23:00 | 73 | Ishurdi | 72 | 18:00 | 144 | Pabna | 92 | 18:30
3 | Aftabnagar | 38 | 13:00 | 74 | Jaldhaka | 70 | 18:00 | 145 | Palashbari | 122 | 18:30
4 | Agargaon | 105 | 13:00 | 75 | Jamalpur | 134 | 18:30 | 146 | Panchagarh | 54 | 19:00
5 | Agrabad | 66 | 08:00 | 76 | Jashore | 110 | 18:00 | 147 | Patiya | 31.7 | 20:00
6 | Amnura | 37 | 14:00 | 77 | Jhenaidah | 88 | 18:30 | 148 | Patnitala | 29 | 14:00
7 | Araihazar | 114 | 19:30 | 78 | Joydebpur | 143 | 18:00 | 149 | Patuakhali | 67.5 | 18:30
8 | Ashuganj | 0.5 | 23:00 | 79 | Joypurhat | 55 | 18:00 | 150 | Payra | 34 | 22:00
9 | Ashuganj-230 | 99 | 03:00 | 80 | Juldah | 18 | 07:00 | 151 | Postogola | 61 | 13:00
10 | BSRM | 206 | 19:30 | 81 | KSRM | 38 | 11:00 | 152 | Pubail | 42 | 18:00
11 | Bagerhat | 85 | 19:00 | 82 | Kabirpur | 223 | 18:30 | 153 | Purbachal | 29 | 19:30
12 | Bajitpur | 92 | 18:00 | 83 | Kachua | 96 | 18:00 | 154 | Purbasadipur | 101 | 13:00
13 | Bakerganj | 14.4 | 19:30 | 84 | Kaliganj | 41 | 18:30 | 155 | Rahanpur | 31 | 18:00
14 | Bakulia | 92 | 23:00 | 85 | Kallyanpur | 111 | 18:00 | 156 | Rahim | 49 | 15:00
15 | Banani | 43.2 | 13:00 | 86 | Kalurghat | 30 | 00:00 | 157 | Rajbari | 81 | 18:00
16 | Bangabhaban | 3 | 00:00 | 87 | Kamrangirchar | 85 | 13:00 | 158 | Rajendrapur | 130 | 18:00
17 | Barapukuria | 58 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 90 | 18:30
18 | Barguna | 20 | 18:00 | 89 | Kasba | 39 | 19:30 | 160 | Rajshahi-230 | 92 | 13:00
19 | Barishal | 94 | 13:00 | 90 | Kazla | 120 | 13:00 | 161 | Ramganj | 110 | 18:00
20 | Barishal-230 | 100 | 18:00 | 91 | Keranigonj | 84 | 19:00 | 162 | Rampur | 44 | 00:00
21 | Baroaulia | 36 | 08:00 | 92 | Khagrachori | 36 | 17:00 | 163 | Rangamati | 17 | 18:00
22 | Baroirhat | 63 | 18:00 | 93 | Khulna | 60 | 13:00 | 164 | Rangpur | 118 | 18:30
23 | Bashundhara | 183 | 13:00 | 94 | Khulshi | 177 | 18:00 | 165 | Ruppur | 4 | 10:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 134 | 19:30 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 76 | 18:00 | 96 | Kodda | 317 | 18:00 | 167 | Saidpur | 76 | 18:30
26 | Benapole | 61 | 18:30 | 97 | Kulaura | 51 | 18:30 | 168 | Santhia | 34 | 18:00
27 | Bhaluka | 151 | 18:30 | 98 | Kurigram | 64 | 18:00 | 169 | Satkhira | 122 | 18:30
28 | Bhandaria | 53 | 21:00 | 99 | Kushtia | 134 | 18:00 | 170 | Satmasjid | 95 | 18:00
29 | Bhangura | 36 | 18:00 | 100 | Laksam | 35 | 18:00 | 171 | Savar | 193 | 12:00
30 | Bheramara(GK) | 65 | 18:00 | 101 | Lakshmipur | 51 | 18:00 | 172 | SevenRings | 7 | 00:00
31 | Bhulta | 205 | 00:00 | 102 | Lalbag | 78 | 13:00 | 173 | ShahCement | 30 | 18:30
32 | Bog-Sherpur | 68 | 18:00 | 103 | Lalmonirhat | 56 | 18:00 | 174 | Shahjadpur | 79 | 18:30
33 | Bogura | 172 | 19:30 | 104 | MI_Cement | 11.2 | 21:00 | 175 | Shahjibazar | 134 | 18:00
34 | Borhanuddin | 73 | 21:00 | 105 | Madanganj | 49 | 18:30 | 176 | Shahmirpur | 54 | 00:00
35 | Brahmanbaria | 142 | 19:30 | 106 | Madaripur | 102 | 21:00 | 177 | Shariatpur | 97 | 21:00
36 | Cantonment | 116 | 13:00 | 107 | Madartek | 78 | 00:00 | 178 | Sherpur | 156 | 18:00
37 | Chandina | 23 | 22:00 | 108 | Madunaghat | 55 | 18:00 | 179 | Shikalbaha | 25 | 00:00
38 | Chandpur | 81 | 18:00 | 109 | Magura | 62 | 18:00 | 180 | Shitalakhya | 74.8 | 12:00
39 | Chandraghona | 33 | 18:00 | 110 | Mahasthangarh | 68 | 18:00 | 181 | Sholosohor | 42 | 15:00
40 | Chapai | 71 | 18:30 | 111 | Maijdee | 38 | 21:00 | 182 | Shomvuganj | 40 | 18:30
41 | Charfasson | 31 | 22:00 | 112 | Manikganj | 132 | 18:30 | 183 | Shyampur | 148 | 12:00
42 | Charsaidpur | 40 | 00:00 | 113 | Maniknagar | 76 | 13:00 | 184 | Siddhirganj | 117 | 16:00
43 | Chauddagram | 73 | 21:00 | 114 | Matarbari | 57 | 20:00 | 185 | Sirajganj | 114 | 19:30
44 | Chhatak | 40 | 19:00 | 115 | Matuail | 76 | 12:00 | 186 | Sitakunda | 35 | 18:00
45 | Chowmuhani | 156 | 18:00 | 116 | Metrorail_Motijheel | 18 | 18:30 | 187 | Sonargaon | 117 | 10:00
46 | Chuadanga | 109 | 18:00 | 117 | Metrorail_Uttara | 7 | 18:30 | 188 | Sreemongol | 88 | 18:00
47 | Coxsbazar | 152 | 21:00 | 118 | Millgate | 87 | 15:00 | 189 | Sreepur | 130 | 18:30
48 | Cumilla(N) | 150 | 19:30 | 119 | Mirpur | 136 | 13:00 | 190 | Srinagar | 49.96 | 21:00
49 | Cumilla(S) | 139 | 19:30 | 120 | Mirsorai | 16 | 09:00 | 191 | Sunamganj | 64 | 18:00
50 | Daganbhuiyan | 42 | 18:00 | 121 | Mirzapur | 44 | 18:30 | 192 | Sylhet | 124 | 18:00
51 | Daudkandi | 124 | 19:00 | 122 | Mithapukur | 70 | 18:00 | 193 | Sylhet_(South) | 63 | 18:00
52 | DhakaUniversity | 62 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 102 | 18:00 | 124 | Mogbazar | 44.2 | 18:00 | 195 | Tangail | 180 | 18:00
54 | Dhanmondi | 75 | 13:00 | 125 | Mongla | 39 | 00:00 | 196 | Taraganj | 29 | 18:00
55 | Dohazari | 123 | 19:00 | 126 | Monirampur | 23 | 18:00 | 197 | Tasnim | 35 | 02:00
56 | Faridpur | 160 | 18:30 | 127 | Motijheel | 35 | 00:00 | 198 | Thakurgaon | 89 | 19:00
57 | Fatullah | 111 | 00:00 | 128 | Muktagacha | 41 | 18:00 | 199 | Tongi | 154 | 11:00
58 | Fenchuganj | 36 | 00:00 | 129 | Munshiganj | 108 | 20:00 | 200 | Ullahpara | 38 | 18:00
59 | Feni | 114 | 18:30 | 130 | Muradnagar | 57 | 19:30 | 201 | Ullon | 47 | 13:00
60 | GPH | 1 | 00:00 | 131 | Mymensingh | 153 | 13:00 | 202 | Uttara | 81 | 19:30
61 | Ghatail | 99 | 18:00 | 132 | Nabinagar | 104 | 18:00 | 203 | UttaraNew | 38 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 110 | 18:30 | 204 | Zigatola | 82 | 12:00
63 | Ghorashal-230 | 89 | 00:00 | 134 | Narail | 58 | 18:00
64 | Goalpara | 36 | 18:00 | 135 | Narinda | 53.5 | 13:00
65 | Gollamari | 98 | 13:00 | 136 | Narshingdi | 187 | 19:30
66 | Gopalganj | 107 | 18:30 | 137 | Natore | 139 | 18:30
67 | Gulshan | 80 | 13:00 | 138 | Nawabganj | 45.6 | 22:00
68 | Halishahar | 73 | 20:00 | 139 | Netrakona | 138 | 20:00
69 | HaripurSBU | 130 | 18:00 | 140 | New | 70.1 | 14:00
70 | Hasnabad | 109 | 20:00 | 141 | Niamatpur | 73 | 13:00
71 | Hathazari | 93 | 20:00 | 142 | Noapara | 43 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14059.8 | 0 |  | 14059.8
1:00 | 13834.58 | 4 |  | 13838.58
2:00 | 13169.58 | 4 |  | 13173.76
3:00 | 12804.97 | 0 |  | 12804.97
4:00 | 12452.86 | 0 |  | 12452.86
5:00 | 12110.54 | 0 |  | 12110.54
6:00 | 11724.7 | 0 |  | 11724.7
7:00 | 12037.9 | 0 |  | 12037.9
8:00 | 12252.72 | 0 |  | 12252.72
9:00 | 12555.08 | 0 |  | 12555.08
10:00 | 12457.57 | 0 |  | 12457.57
11:00 | 12970.65 | 0 |  | 12970.65
12:00 | 13877.49 | 0 |  | 13877.49
13:00 | 14362.7 | 0 |  | 14362.7
14:00 | 14339.89 | 0 |  | 14339.89
15:00 | 14196.98 | 0 |  | 14196.98
16:00 | 13725.12 | 0 |  | 13725.12
17:00 | 13621.58 | 0 |  | 13621.58
18:00 | 14982.31 | 50 |  | 15034.31
19:00 | 15552.54 | 33 |  | 15586.54
19:30 | 15289.98 | 0 |  | 15289.98
20:00 | 15149.01 | 0 |  | 15149.01
21:00 | 15002.17 | 0 |  | 15002.17
22:00 | 14755.97 | 0 |  | 14755.97
23:00 | 14625.45 | 0 |  | 14625.45
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 21-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 146 | 32 | 382 | 132 | 1414 | 530 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 134 | 33 | 332 | 106 | 1400 | 490
2:00 | 137 | 33 | 352 | 118 | 1450 | 478 |  | Import | 0
3:00 | 146 | 34 | 362 | 108 | 1512 | 472
4:00 | 155 | 33 | 386 | 94 | 1618 | 488 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 161 | 33 | 404 | 90 | 1668 | 490
6:00 | 165 | 30 | 422 | 90 | 1704 | 510 |  | Import | 0
7:00 | 148 | 22 | 386 | 92 | 1658 | 466
8:00 | 142 | 13 | 360 | 74 | 1654 | 434 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 161 | 25 | 404 | 84 | 1704 | 464
10:00 | 165 | 27 | 410 | 94 | 1724 | 500 |  | Import | 0
11:00 | 161 | 24 | 414 | 108 | 1728 | 516
12:00 | 150 | 13 | 410 | 112 | 1728 | 476 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 131 | 3 | 388 | 114 | 1530 | 418
14:00 | 130 | 6 | 360 | 104 | 1460 | 442 |  | Import | 0
15:00 | 121 | 9 | 332 | 108 | 1462 | 456
16:00 | 117 | 6 | 330 | 104 | 1460 | 430 | Gopalganj-Aminbazar Ckt-1 | Export | 17660000
17:00 | 109 | 9 | 304 | 116 | 1344 | 454
18:00 | 95 | -2 | 286 | 96 | 1290 | 404 |  | Import | 0
18:30 | 84 | -6 | 290 | 122 | 1222 | 388
19:00 | 88 | -4 | 290 | 130 | 1220 | 386 | Gopalganj-Aminbazar Ckt-2 | Export | 17710000
19:30 | 88 | -5 | 262 | 112 | 1178 | 404
20:00 | 87 | -5 | 272 | 120 | 1178 | 402 |  | Import | 0
21:00 | 91 | -3 | 288 | 128 | 1132 | 406
22:00 | 94 | 0 | 296 | 126 | 1114 | 420 |  | Total Export | 35370000
23:00 | 105 | 3 | 320 | 120 | 1218 | 448 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8137.5 | 5922.3 | 14059.8 | DAILY GENERATION CURVE
00:30 | 8050 | 5897.19 | 13947.19
01:00 | 7962.5 | 5872.08 | 13834.58 | 21-10-2026
01:30 | 7728.5 | 5773.58 | 13502.08
02:00 | 7494.5 | 5675.08 | 13169.58
02:30 | 7367 | 5620.275 | 12987.275
03:00 | 7239.5 | 5565.47 | 12804.97
03:30 | 7070 | 5558.915 | 12628.915
04:00 | 6900.5 | 5552.36 | 12452.86
04:30 | 6710.5 | 5571.2 | 12281.7
05:00 | 6520.5 | 5590.04 | 12110.54
05:30 | 6358.525 | 5559.095 | 11917.62
06:00 | 6196.55 | 5528.15 | 11724.7
06:30 | 6271.83 | 5609.47 | 11881.3
07:00 | 6347.11 | 5690.79 | 12037.9
07:30 | 6370.785 | 5774.525 | 12145.31
08:00 | 6394.46 | 5858.26 | 12252.72
08:30 | 6471.56 | 5932.34 | 12403.9
09:00 | 6548.66 | 6006.42 | 12555.08
09:30 | 6558.48 | 5947.845 | 12506.325
10:00 | 6568.3 | 5889.27 | 12457.57
10:30 | 6734.985 | 5979.125 | 12714.11
11:00 | 6901.67 | 6068.98 | 12970.65
11:30 | 7221.58 | 6202.49 | 13424.07
12:00 | 7541.49 | 6336 | 13877.49
12:30 | 7725.245 | 6394.85 | 14120.095
13:00 | 7909 | 6453.7 | 14362.7
13:30 | 8010.04 | 6341.255 | 14351.295
14:00 | 8111.08 | 6228.81 | 14339.89
14:30 | 8168.585 | 6099.85 | 14268.435
15:00 | 8226.09 | 5970.89 | 14196.98
15:30 | 8097.7 | 5863.35 | 13961.05
16:00 | 7969.31 | 5755.81 | 13725.12
16:30 | 7978.76 | 5694.59 | 13673.35
17:00 | 7988.21 | 5633.37 | 13621.58
17:30 | 8373.495 | 5928.45 | 14301.945
18:00 | 8758.78 | 6223.53 | 14982.31
18:30 | 8968.88 | 6298.545 | 15267.425
19:00 | 9178.98 | 6373.56 | 15552.54
19:30 | 9069.78 | 6220.2 | 15289.98
20:00 | 8973.78 | 6175.23 | 15149.01
20:30 | 8947.07 | 6128.52 | 15075.59 |  | Executive Engineer
21:00 | 8920.36 | 6081.81 | 15002.17 |  | Network Operation Division
21:30 | 8844.43 | 6034.64 | 14879.07
22:00 | 8768.5 | 5987.47 | 14755.97
22:30 | 8709.5 | 5981.21 | 14690.71
23:00 | 8650.5 | 5974.95 | 14625.45

## En-Curve
QF-LDC-12
Date | 21-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3134 | 1528.5 | 904 | 0 | 64 | 1316.5 | 141 | 5278.8 | 0 | 398 | 1295 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3189.5 | 1529.5 | 903.5 | 0 | 62 | 1283.39 | 141.5 | 5167.8 | 0 | 394.5 | 1275.5 | 0 | 0 | 0 | 2 | 21-10-2026
01:00 | 3245 | 1530.5 | 903 | 0 | 60 | 1250.28 | 142 | 5056.8 | 0 | 391 | 1256 | 0 | 0 | 0 | 4
01:30 | 3259 | 1528 | 903 | 0 | 59 | 1236.78 | 142 | 4966.8 | 0 | 270.5 | 1137 | 0 | 0 | 0 | 4 | Energy Generated | 329.4874 |  | MKWHr
02:00 | 3273 | 1525.5 | 903 | 0 | 58 | 1223.28 | 142 | 4876.8 | 0 | 150 | 1018 | 0 | 0 | 0 | 4 | Energy not Served | 0.091 |  | MKWHr
02:30 | 3309.5 | 1532 | 903.5 | 0 | 58 | 1223.475 | 142 | 4812.8 | 0 | 138 | 868 | 0 | 0 | 0 | 2 | Total Energy Requirement | 329.5784 |  | MKWHr
03:00 | 3346 | 1538.5 | 904 | 0 | 58 | 1223.67 | 142 | 4748.8 | 0 | 126 | 718 | 0 | 0 | 0 | 0
03:30 | 3346 | 1539 | 903.5 | 0 | 57 | 1226.115 | 142 | 4712.3 | 0 | 126 | 577 | 0 | 0 | 0 | 0
04:00 | 3346 | 1539.5 | 903 | 0 | 56 | 1228.56 | 142 | 4675.8 | 0 | 126 | 436 | 0 | 0 | 0 | 0
04:30 | 3355 | 1526 | 903.5 | 0 | 56 | 1238.4 | 142 | 4571.3 | 0 | 122 | 367.5 | 0 | 0 | 0 | 0
05:00 | 3364 | 1512.5 | 904 | 0 | 56 | 1248.24 | 142 | 4466.8 | 0 | 118 | 299 | 0 | 0 | 0 | 0
05:30 | 3339.5 | 1525.5 | 904 | 0 | 54 | 1242.895 | 142 | 4369.2 | 0.025 | 90 | 250.5 | 0 | 0 | 0 | 0
06:00 | 3315 | 1538.5 | 904 | 0 | 52 | 1237.55 | 142 | 4271.6 | 0.05 | 62 | 202 | 0 | 0 | 0 | 0
06:30 | 3301.5 | 1581.5 | 904 | 0 | 50 | 1240.425 | 142 | 4285.6 | 55.275 | 67.5 | 253.5 | 0 | 0 | 0 | 0
07:00 | 3288 | 1624.5 | 904 | 0 | 48 | 1243.3 | 142 | 4299.6 | 110.5 | 73 | 305 | 0 | 0 | 0 | 0
07:30 | 3215.5 | 1615.5 | 904 | 0 | 46 | 1220.395 | 141.5 | 4307.7 | 221.215 | 77 | 396.5 | 0 | 0 | 0 | 0
08:00 | 3143 | 1606.5 | 904 | 0 | 44 | 1197.49 | 141 | 4315.8 | 331.93 | 81 | 488 | 0 | 0 | 0 | 0
08:30 | 3085.5 | 1594.15 | 903.5 | 0 | 45 | 1204.13 | 140.5 | 4306.2 | 435.42 | 102.5 | 587 | 0 | 0 | 0 | 0
09:00 | 3028 | 1581.8 | 903 | 0 | 46 | 1210.77 | 140 | 4296.6 | 538.91 | 124 | 686 | 0 | 0 | 0 | 0
09:30 | 3031.5 | 1591.8 | 903.5 | 0 | 47 | 1111.115 | 139.5 | 4281.1 | 605.81 | 132 | 663 | 0 | 0 | 0 | 0
10:00 | 3035 | 1601.8 | 904 | 0 | 48 | 1011.46 | 139 | 4265.6 | 672.71 | 140 | 640 | 0 | 0 | 0 | 0
10:30 | 3045 | 1609.8 | 904 | 0 | 50 | 1019.54 | 139 | 4281.6 | 696.17 | 157.5 | 811.5 | 0 | 0 | 0 | 0
11:00 | 3055 | 1617.8 | 904 | 0 | 52 | 1027.62 | 139 | 4297.6 | 719.63 | 175 | 983 | 0 | 0 | 0 | 0
11:30 | 3051.5 | 1622.15 | 904 | 0 | 55 | 1028.875 | 139 | 4315.2 | 737.845 | 255.5 | 1315 | 0 | 0 | 0 | 0
12:00 | 3048 | 1626.5 | 904 | 0 | 58 | 1030.13 | 139 | 4332.8 | 756.06 | 336 | 1647 | 0 | 0 | 0 | 0
12:30 | 3006 | 1620.5 | 904 | 0 | 60 | 1026.315 | 139 | 4327.3 | 726.98 | 348.5 | 1961.5 | 0 | 0 | 0 | 0
13:00 | 2964 | 1614.5 | 904 | 0 | 62 | 1022.5 | 139 | 4321.8 | 697.9 | 361 | 2276 | 0 | 0 | 0 | 0
13:30 | 3012 | 1596.75 | 904 | 0 | 62 | 1024.025 | 139.5 | 4341.9 | 642.42 | 335.6 | 2292.6 | 0 | 0 | 0.5 | 0
14:00 | 3060 | 1579 | 904 | 0 | 62 | 1025.55 | 140 | 4362 | 586.94 | 310.2 | 2309.2 | 0 | 0 | 1 | 0
14:30 | 3044 | 1581.75 | 906.5 | 0 | 61 | 1017.98 | 139.5 | 4464 | 491.655 | 301.7 | 2259.85 | 0 | 0 | 0.5 | 0
15:00 | 3028 | 1584.5 | 909 | 0 | 60 | 1010.41 | 139 | 4566 | 396.37 | 293.2 | 2210.5 | 0 | 0 | 0 | 0
15:30 | 3071 | 1580.25 | 909 | 0 | 58 | 1017.68 | 139.5 | 4571.5 | 284.92 | 266.7 | 2062 | 0 | 0 | 0.5 | 0
16:00 | 3114 | 1576 | 909 | 0 | 56 | 1024.95 | 140 | 4577 | 173.47 | 240.2 | 1913.5 | 0 | 0 | 1 | 0
16:30 | 3082.5 | 1576.75 | 908.5 | 0 | 57 | 1011 | 140.5 | 4603.5 | 99.9 | 240.2 | 1953 | 0 | 0 | 0.5 | 0
17:00 | 3051 | 1577.5 | 908 | 0 | 58 | 997.05 | 141 | 4630 | 26.33 | 240.2 | 1992.5 | 0 | 0 | 0 | 0
17:30 | 3048.5 | 1597.5 | 911.5 | 0 | 63 | 1057.39 | 141 | 4730.3 | 13.165 | 410.81 | 2328.78 | 0 | 0 | 0 | 25
18:00 | 3046 | 1617.5 | 915 | 0 | 68 | 1117.73 | 141 | 4830.6 | 0 | 581.42 | 2665.06 | 0 | 0 | 0 | 50
18:30 | 3051 | 1636.5 | 915 | 0 | 67 | 1109.445 | 141 | 4930.4 | 0 | 626.92 | 2790.16 | 0 | 0 | 0 | 41.5
19:00 | 3056 | 1655.5 | 915 | 0 | 66 | 1101.16 | 141 | 5030.2 | 0 | 672.42 | 2915.26 | 0 | 0 | 0 | 33
19:30 | 3164 | 1616.5 | 918 | 0 | 66 | 1114.2 | 141 | 5104 | 0 | 681.42 | 2484.86 | 0 | 0 | 0 | 0
20:00 | 3076 | 1609.5 | 918 | 0 | 66 | 1110.23 | 141 | 5127 | 0 | 680.42 | 2420.86 | 0 | 0 | 0 | 0
20:30 | 3102 | 1612.5 | 918 | 0 | 65 | 1108.02 | 141 | 5138 | 0 | 642.21 | 2348.86 | 0 | 0 | 0 | 0
21:00 | 3128 | 1615.5 | 918 | 0 | 64 | 1105.81 | 141 | 5149 | 0 | 604 | 2276.86 | 0 | 0 | 0 | 0
21:30 | 3119.5 | 1609 | 918 | 0 | 65 | 1101.64 | 140 | 5165.5 | 0 | 579 | 2181.43 | 0 | 0 | 0 | 0
22:00 | 3111 | 1602.5 | 918 | 0 | 66 | 1097.47 | 139 | 5182 | 0 | 554 | 2086 | 0 | 0 | 0 | 0
22:30 | 3144 | 1575 | 918 | 0 | 66 | 1117.21 | 139 | 5138.5 | 0 | 554 | 2039 | 0 | 0 | 0 | 0
23:00 | 3177 | 1547.5 | 918 | 0 | 66 | 1136.95 | 139 | 5095 | 0 | 554 | 1992 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 17:00 | 371 | 00:00 | Madunaghat | 402 | 14:00 | 39 | 09:00
Amtali | 412 | 17:00 | 408 | 00:00 | Meghnaghat | 390 | 08:00 | 381 | 00:00
Ashuganj | 394 | 17:00 | 386 | 00:00 | Mirsorai | 402 | 17:00 | 389 | 00:00
Bhulta | 393 | 05:00 | 384 | 00:00 | Payra | 413 | 15:00 | 410 | 04:00
Bibiana | 388 | 08:00 | 384 | 00:00 | Rahanpur | 408 | 13:00 | 400 | 00:00
BIPTC | 401 | 05:00 | 393 | 18:00 | Rampal | 399 | 05:00 | 393 | 00:00
Bogura | 400 | 14:00 | 389 | 00:00
Gopalganj | 394 | 17:00 | 386 | 00:00
Kaliakoir | 377 | 13:00 | 368 | 11:00
Korerhat | 401 | 14:00 | 388 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 225 | 00:00 | Hasnabad | 227 | 17:00 | 221 | 00:00
AKSML | 235 | 13:00 | 225 | 00:00 | Hathazari | 236 | 13:00 | 228 | 00:00
Aminbazar | 233 | 17:00 | 226 | 00:00 | Ishurdi | 236 | 05:00 | 224 | 18:30
Ashuganj | 228 | 08:00 | 215 | 04:00 | Jhenaidah | 229 | 04:00 | 215 | 18:00
Ashuganj-400 | 228 | 08:00 | 215 | 04:00 | Kachua | 230 | 17:00 | 219 | 00:00
Baghabari | 233 | 04:00 | 224 | 18:30 | Kaliakoir | 233 | 13:00 | 227 | 11:00
Barapukuria | 233 | 12:00 | 223 | 00:00 | Keranigonj | 228 | 06:00 | 222 | 00:00
Barapukuria-230 | 233 | 12:00 | 223 | 00:00 | Khulna(S) | 231 | 05:00 | 222 | 18:30
Barapukuria(N) | 234 | 13:00 | 222 | 08:00 | Korerhat | 230 | 17:00 | 220 | 00:00
Barishal | 235 | 17:00 | 229 | 00:00 | Madunaghat | 239 | 13:00 | 232 | 00:00
Bheramara | 234 | 05:00 | 221 | 18:30 | Madunaghat-400 | 240 | 14:00 | 233 | 00:00
Bhulta | 225 | 08:00 | 219 | 00:00 | Maniknagar | 223 | 03:00 | 217 | 00:00
Bibiana | 224 | 07:00 | 218 | 00:00 | Meghnaghat | 231 | 07:00 | 227 | 00:00
BIPTC | 237 | 05:00 | 221 | 18:30 | Meghnaghat-400 | 226 | 08:00 | 220 | 00:00
Birulia | 231 | 08:00 | 225 | 00:00 | Mirsorai | 228 | 14:00 | 220 | 00:00
Bogura | 237 | 13:00 | 231 | 00:00 | Naogaon | 224 | 01:00 | 215 | 00:00
Bogura-400 | 237 | 14:00 | 230 | 00:00 | Purbasadipur | 232 | 13:00 | 218 | 08:00
Borhanuddin | 236 | 17:00 | 231 | 00:00 | Rajshahi | 231 | 04:00 | 220 | 18:00
BSRM | 229 | 17:00 | 220 | 00:00 | Rampal | 229 | 04:00 | 222 | 00:00
Charfasson | 234 | 18:00 | 229 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 16:00 | 220 | 00:00 | Rampura | 224 | 05:00 | 218 | 00:00
Cumilla(N) | 223 | 05:00 | 217 | 00:00 | Shikalbaha | 240 | 18:00 | 231 | 00:00
Faridpur | 235 | 05:00 | 230 | 00:00 | Shyampur | 226 | 08:00 | 220 | 00:00
Fenchuganj | 227 | 11:00 | 220 | 01:00 | Siddhirganj | 225 | 08:00 | 220 | 00:00
Feni | 226 | 17:00 | 218 | 00:00 | Sirajgonj | 234 | 05:00 | 230 | 01:00
Ghorashal | 230 | 03:00 | 220 | 00:00 | Sreepur | 224 | 06:00 | 216 | 18:30
Ghorashal-230 | 221 | 23:00 | 211 | 00:00 | Tongi | 225 | 13:00 | 213 | 00:00
Gopalganj | 238 | 17:00 | 233 | 00:00
GPH | 235 | 13:00 | 228 | 01:00
Haripur | 225 | 08:00 | 218 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 08:00 | 129 | 00:00 | Madanganj | 136 | 08:00 | 132 | 00:00
Agargaon | 135 | 08:00 | 130 | 00:00 | Madaripur | 134 | 10:00 | 131 | 00:00
Agrabad | 136 | 17:00 | 131 | 00:00 | Madartek | 133 | 04:00 | 128 | 11:00
AKS | 134 | 17:00 | 130 | 00:00 | Madunaghat | 138 | 15:00 | 134 | 00:00
Aminbazar | 134 | 17:00 | 129 | 00:00 | Magura | 136 | 03:00 | 124 | 18:30
Amnura | 132 | 04:00 | 129 | 08:00 | Mahasthangarh | 134 | 01:00 | 130 | 07:00
Araihazar | 125 | 04:00 | 121 | 00:00 | Maijdee | 128 | 14:00 | 123 | 00:00
Ashuganj | 134 | 08:00 | 128 | 00:00 | Manikganj | 135 | 13:00 | 126 | 00:00
Ashuganj-230 | 136 | 17:00 | 134 | 00:00 | Maniknagar | 135 | 04:00 | 131 | 00:00
Bagerhat | 130 | 08:00 | 125 | 00:00 | Matarbari | 119 | 09:00 | 109 | 00:00
Bajitpur | 130 | 04:00 | 124 | 00:00 | Matuail | 136 | 08:00 | 132 | 12:00
Bakerganj | 135 | 17:00 | 132 | 00:00 | Metrorail_Motijheel | 135 | 04:00 | 131 | 00:00
Bakulia | 135 | 13:00 | 131 | 00:00 | Metrorail_Uttara | 135 | 05:00 | 129 | 00:00
Banani | 133 | 03:00 | 129 | 00:00 | Millgate | 136 | 17:00 | 129 | 00:00
Bangabhaban | 136 | 08:00 | 130 | 12:00 | Mirpur | 133 | 17:00 | 128 | 00:00
Barapukuria | 138 | 01:00 | 128 | 08:00 | Mirzapur | 133 | 19:00 | 128 | 00:00
Barguna | 135 | 08:00 | 131 | 00:00 | Mithapukur | 133 | 14:00 | 125 | 08:00
Barishal | 135 | 13:00 | 131 | 00:00 | MI_Cement | 133 | 05:00 | 128 | 11:00
Barishal-230 | 136 | 17:00 | 131 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 135 | 07:00 | 132 | 00:00 | Mogbazar | 135 | 04:00 | 130 | 12:00
Baroirhat | 132 | 09:00 | 127 | 00:00 | Mongla | 130 | 09:00 | 124 | 00:00
Bashundhara | 135 | 05:00 | 128 | 11:00 | Monirampur | 129 | 05:00 | 121 | 19:00
BashundharaCement | 136 | 08:00 | 132 | 00:00 | Motijheel | 136 | 08:00 | 130 | 12:00
Beanibazar | 127 | 08:00 | 121 | 00:00 | Muktagacha | 131 | 08:00 | 121 | 00:00
Benapole | 135 | 05:00 | 120 | 18:30 | Munshiganj | 134 | 08:00 | 131 | 00:00
Bhaluka | 130 | 03:00 | 122 | 19:00 | Muradnagar | 128 | 06:00 | 125 | 00:00
Bhandaria | 133 | 09:00 | 128 | 00:00 | Mymensingh | 132 | 09:00 | 116 | 21:00
Bhangura | 134 | 04:00 | 128 | 18:30 | Nabinagar | 133 | 14:00 | 127 | 00:00
Bheramara | 138 | 04:00 | 130 | 18:30 | Naogaon | 135 | 01:00 | 129 | 00:00
Bheramara(GK) | 138 | 04:00 | 130 | 18:30 | Narail | 136 | 04:00 | 123 | 18:00
Bhulta | 124 | 08:00 | 120 | 00:00 | Narinda | 135 | 04:00 | 131 | 00:00
Bhulta-400 | 125 | 05:00 | 121 | 00:00 | Narshingdi | 130 | 18:00 | 119 | 00:00
Birulia | 136 | 08:00 | 131 | 00:00 | Natore | 134 | 04:00 | 129 | 18:30
Bog-Sherpur | 136 | 14:00 | 131 | 08:00 | Nawabganj | 134 | 05:00 | 130 | 00:00
Bogura | 136 | 03:00 | 133 | 00:00 | Netrakona | 119 | 03:00 | 110 | 18:30
Bogura-230 | 138 | 13:00 | 133 | 08:00 | New | 137 | 17:00 | 130 | 00:00
Brahmanbaria | 132 | 07:00 | 125 | 00:00 | Niamatpur | 134 | 05:00 | 131 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 134 | 03:00 | 130 | 00:00 | Noapara | 131 | 05:00 | 125 | 18:30
Chandina | 130 | 06:00 | 125 | 00:00 | Pabna | 136 | 05:00 | 128 | 18:30
Chandpur | 132 | 17:00 | 123 | 00:00 | Palashbari | 131 | 13:00 | 125 | 08:00
Chandraghona | 138 | 17:00 | 133 | 00:00 | Panchagarh | 139 | 13:00 | 129 | 08:00
Chapai | 133 | 01:00 | 129 | 11:00 | Patiya | 134 | 18:00 | 129 | 00:00
Charsaidpur | 135 | 08:00 | 132 | 00:00 | Patnitala | 133 | 04:00 | 130 | 00:00
Chauddagram | 130 | 08:00 | 124 | 00:00 | Patuakhali | 136 | 17:00 | 131 | 00:00
Chhatak | 123 | 08:00 | 115 | 00:00 | Payra | 136 | 18:00 | 134 | 00:00
Chowmuhani | 129 | 16:00 | 123 | 00:00 | PHP | 132 | 17:00 | 127 | 00:00
Chuadanga | 136 | 05:00 | 124 | 18:30 | Postogola | 134 | 04:00 | 130 | 00:00
Coxsbazar | 118 | 07:00 | 107 | 00:00 | Pubail | 131 | 19:00 | 127 | 00:00
Cumilla(N) | 130 | 04:00 | 126 | 00:00 | Purbachal | 134 | 07:00 | 129 | 12:00
Cumilla(S) | 132 | 00:00 | 125 | 00:00 | Purbasadipur | 135 | 13:00 | 126 | 08:00
Daganbhuiyan | 130 | 14:00 | 125 | 00:00 | Rahanpur | 136 | 01:00 | 133 | 00:00
Daudkandi | 128 | 05:00 | 123 | 00:00 | Rahanpur-400 | 137 | 05:00 | 134 | 00:00
DhakaUniversity | 133 | 03:00 | 129 | 12:00 | Rahim | 135 | 02:00 | 133 | 00:00
Dhamrai | 133 | 04:00 | 127 | 00:00 | Rajbari | 133 | 04:00 | 129 | 18:30
Dhanmondi | 136.5 | 05:00 | 133 | 12:00 | Rajendrapur | 132 | 05:00 | 125 | 18:30
Dohazari | 130 | 17:00 | 123 | 00:00 | Rajshahi | 133 | 04:00 | 128 | 00:00
Faridpur | 135 | 06:00 | 131 | 00:00 | Rajshahi-230 | 133 | 05:00 | 128 | 12:00
Fatullah | 135 | 04:00 | 129 | 00:00 | Ramganj | 128 | 17:00 | 120 | 00:00
Fenchuganj | 133 | 06:00 | 129 | 00:00 | Rampur | 136 | 09:00 | 131 | 00:00
Feni | 130 | 13:00 | 126 | 00:00 | Rampura | 134 | 08:00 | 129 | 12:00
Feni-230 | 131 | 14:00 | 126 | 00:00 | Rangamati | 137 | 17:00 | 132 | 00:00
Ghatail | 129 | 09:00 | 120 | 07:00 | Rangpur | 133 | 14:00 | 122 | 08:00
Ghorashal | 132 | 17:00 | 127 | 00:00 | Ruppur | 136 | 01:00 | 130 | 18:30
Goalpara | 133 | 05:00 | 128 | 18:30 | Saidpur | 134 | 13:00 | 126 | 07:00
Gollamari | 133 | 04:00 | 127 | 18:30 | Santhia | 135 | 04:00 | 129 | 18:30
Gopalganj | 133 | 15:00 | 129 | 00:00 | Satkhira | 130 | 05:00 | 120 | 18:30
Gopalganj-400 | 134 | 06:00 | 131 | 00:00 | Satmasjid | 134 | 03:00 | 130 | 00:00
Gulshan | 133 | 05:00 | 129 | 00:00 | Savar | 134 | 13:00 | 129 | 00:00
Halishahar | 137 | 17:00 | 132 | 00:00 | SevenRings | 133 | 16:00 | 128 | 00:00
Haripur | 136 | 08:00 | 13 | 17:00 | ShahCement | 135 | 08:00 | 132 | 00:00
HaripurSBU | 136 | 08:00 | 133 | 00:00 | Shahjadpur | 134 | 00:00 | 131 | 19:00
Hasnabad | 135 | 04:00 | 130 | 00:00 | Shahjibazar | 133 | 08:00 | 123 | 00:00
Hathazari | 137 | 09:00 | 133 | 00:00 | Shahmirpur | 136 | 17:00 | 131 | 00:00
Hatirjheel | 134 | 05:00 | 129 | 00:00 | Shariatpur | 133 | 05:00 | 129 | 00:00
Ishurdi | 138 | 04:00 | 131 | 18:30 | Sherpur | 130 | 09:00 | 115 | 07:00
Jaldhaka | 132 | 11:00 | 29 | 18:00 | Shikalbaha | 126 | 17:00 | 121 | 04:00
Jamalpur | 136 | 19:00 | 120 | 07:00 | Shikalbaha-230 | 137 | 16:00 | 132 | 00:00
Jashore | 137 | 05:00 | 122 | 18:30 | Shitalakhya | 133 | 05:00 | 128 | 11:00
Jhenaidah | 139 | 05:00 | 128 | 18:30 | Sholosohor | 138 | 17:00 | 132 | 00:00
Jhenaidah-230 | 140 | 05:00 | 129 | 18:00 | Shomvuganj | 122 | 03:00 | 119 | 00:00
Joydebpur | 130 | 18:00 | 124 | 00:00 | Shyampur | 134 | 01:00 | 131 | 11:00
Joypurhat | 132 | 01:00 | 130 | 00:00 | Shyampur-230 | 136 | 05:00 | 131 | 11:00
Juldah | 135 | 09:00 | 131 | 00:00 | Siddhirganj | 136 | 03:00 | 133 | 00:00
Kabirpur | 137 | 13:00 | 127 | 00:00 | Sirajganj | 133 | 05:00 | 126 | 18:30
Kachua | 131 | 17:00 | 124 | 00:00 | Sitakunda | 136 | 10:00 | 132 | 00:00
Kaliakoir | 139 | 19:00 | 127 | 23:00 | Sonargaon | 133 | 05:00 | 130 | 00:00
Kaliganj | 138 | 05:00 | 127 | 18:30 | Sreemongol | 131 | 08:00 | 123 | 00:00
Kallyanpur | 133 | 13:00 | 128 | 00:00 | Sreepur | 133 | 05:00 | 127 | 18:30
Kalurghat | 138 | 17:00 | 134 | 04:00 | Srinagar | 134 | 04:00 | 130 | 00:00
Kamrangirchar | 135 | 07:00 | 126 | 00:00 | SSM | 140 | 08:00 | 135 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 120 | 06:00 | 113 | 00:00
Kasba | 128 | 06:00 | 122 | 00:00 | Sylhet | 126 | 09:00 | 121 | 00:00
Kazla | 135 | 08:00 | 130 | 00:00 | Sylhet_(South) | 128 | 09:00 | 122 | 00:00
Keranigonj | 135 | 05:00 | 131 | 00:00 | Tangail | 129 | 19:00 | 123 | 00:00
Khagrachori | 135 | 13:00 | 131 | 00:00 | Taraganj | 132 | 12:00 | 123 | 07:00
Khulna | 133 | 04:00 | 126 | 18:30 | Tasnim | 134 | 08:00 | 130 | 00:00
Khulna(S) | 134 | 05:00 | 128 | 18:30 | Thakurgaon | 139 | 13:00 | 127 | 08:00
Khulshi | 135 | 15:00 | 130 | 00:00 | TK | 137 | 10:00 | 133 | 00:00
Kishoreganj | 128 | 04:00 | 122 | 18:30 | Tongi | 139 | 23:00 | 130 | 00:00
Kodda | 138 | 13:00 | 121 | 13:00 | Ullahpara | 134 | 04:00 | 128 | 18:30
Korerhat | 134 | 15:00 | 129 | 00:00 | Ullon | 134 | 08:00 | 129 | 00:00
KSRM | 136 | 17:00 | 132 | 00:00 | Uttara | 134 | 14:00 | 127 | 00:00
Kulaura | 133 | 09:00 | 127 | 00:00 | UttaraNew | 135 | 05:00 | 129 | 00:00
Kurigram | 129 | 03:00 | 122 | 07:00 | Zigatola | 135 | 05:00 | 131 | 00:00
Kushtia | 138 | 05:00 | 130 | 18:30
Laksam | 130 | 17:00 | 124 | 00:00
Lakshmipur | 128 | 17:00 | 122 | 00:00
Lalbag | 135 | 08:00 | 130 | 00:00
Lalmonirhat | 157 | 17:00 | 122 | 09:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division