## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-10-2026 | [28 empty] | Date: | 22-10-2026 | [28 empty] | Date: | 22-10-2026 | [28 empty] | Date: | 22-10-2026 | [28 empty] | Date: | 22-10-2026 | [16 empty] | Date: | 22-10-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 143.420 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 54 | 17 | 114 | 78 | 210 | 15 | 55 | 90 | 0 | 0 | 455 | 0 | 35 | 310 | 0 | 0 | 0 | 123 | 8.5 | 21 | 0 | 470 | 72 | 135 | 12 | 0 | 0 | 50 | 21 | 35 | 12 | 25 | 0 | 138 | 93 | 29 | 1080 | 16 | 0 | 46 | 25.5 | 68 | 218 | 0 | 0 | 0 | 1034 | 0 | 100 | 0 | 195 | 305 | 265 | 44 | 0 | 220 | 0 | 16 | 65 | 68 | 38 | 5 | 17 | 66 | 16 | 0 | 0 | 286 | 160 | 398 | 40 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 72 | 0 | 100 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8550 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1155 | 0 | 0 | 0 | 1060.76 | 0 | 32 | 0 | 70 | 35 | 0 | 60 | 32 | 16 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 275 | 115 | 0 | 0 | 1138 | 300 | 100 | 5916.76 | 14466.76 | 102.8
01:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35 | 17 | 114 | 78 | 210 | 15 | 35 | 90 | 0 | 0 | 470 | 0 | 35 | 310 | 0 | 0 | 0 | 123 | 9.5 | 21 | 0 | 470 | 68 | 100 | 12 | 0 | 0 | 0 | 13 | 0 | 12 | 25 | 0 | 138 | 92 | 29 | 1080 | 16 | 0 | 46 | 25.5 | 68 | 219 | 0 | 0 | 0 | 815 | 0 | 100 | 15 | 55 | 310 | 310 | 44 | 0 | 201 | 0 | 16 | 65 | 68 | 0 | 9 | 17 | 62 | 16 | 0 | 0 | 276 | 200 | 398 | 40 | 30 | 157 | 0 | 8 | 0 | 83 | 30 | 70 | 0 | 100 | 35 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8069 | 918 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1202 | 0 | 0 | 0 | 1022.09 | 0 | 32 | 0 | 70 | 35 | 0 | 60 | 32 | 16 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1143 | 300 | 100 | 5946.09 | 14015.09 | 102.79
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 35 | 17 | 114 | 78 | 210 | 15 | 35 | 90 | 0 | 0 | 475 | 0 | 35 | 300 | 0 | 0 | 0 | 105 | 9.5 | 21 | 0 | 470 | 63 | 51 | 10 | 0 | 0 | 0 | 13 | 0 | 0 | 25 | 0 | 138 | 93 | 29 | 1080 | 0 | 0 | 50 | 25.5 | 68 | 220 | 0 | 0 | 0 | 700 | 0 | 97 | 53 | 2 | 305 | 300 | 44 | 8 | 196 | 0 | 16 | 65 | 68 | 0 | 7 | 0 | 30 | 16 | 0 | 0 | 266 | 265 | 398 | 40 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 110 | 0 | 100 | 35 | 59 | 0 | 45 | 0 | 0 | 0 | 24 | 7850 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1234.2 | 0 | 0 | 0 | 1014.78 | 0 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1020 | 300 | 100 | 5692.98 | 13542.98 | 102.79
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 17 | 114 | 15 | 210 | 0 | 35 | 35 | 0 | 0 | 475 | 0 | 35 | 305 | 0 | 0 | 0 | 68 | 9.5 | 21 | 0 | 470 | 61 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 139 | 93 | 29 | 1080 | 0 | 0 | 50 | 0 | 68 | 220 | 0 | 0 | 0 | 603 | 0 | 100 | 55 | 85 | 305 | 300 | 44 | 10 | 199 | 0 | 0 | 65 | 17 | 0 | 7 | 0 | 58 | 0 | 0 | 0 | 257 | 330 | 398 | 40 | 30 | 156 | 0 | 16 | 0 | 11 | 30 | 110 | 0 | 100 | 35 | 59 | 0 | 35 | 0 | 0 | 0 | 24 | 7513.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1007.2 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1020 | 300 | 100 | 5497.4 | 13010.9 | 102.78
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 17 | 114 | 15 | 30 | 0 | 35 | 0 | 0 | 0 | 470 | 0 | 0 | 310 | 0 | 0 | 0 | 68 | 9.5 | 21 | 0 | 475 | 30 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 140 | 34 | 29 | 1080 | 0 | 0 | 44 | 0 | 0 | 223 | 0 | 0 | 0 | 605 | 0 | 100 | 20 | 195 | 310 | 310 | 44 | 10 | 197 | 0 | 0 | 65 | 0 | 0 | 7 | 0 | 58 | 0 | 0 | 0 | 254 | 400 | 398 | 40 | 30 | 154 | 0 | 16 | 0 | 55 | 30 | 0 | 0 | 100 | 35 | 59 | 0 | 35 | 0 | 0 | 0 | 24 | 7176.5 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1006.68 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1020 | 300 | 17 | 5388.88 | 12565.38 | 102.78
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 80 | 15 | 30 | 0 | 35 | 0 | 0 | 0 | 480 | 0 | 0 | 310 | 0 | 0 | 0 | 68 | 9.5 | 21 | 0 | 470 | 31 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 140 | 0 | 29 | 930 | 0 | 0 | 44 | 0 | 0 | 223 | 0 | 0 | 0 | 611 | 0 | 100 | 0 | 195 | 300 | 305 | 44 | 0 | 198 | 0 | 0 | 65 | 0 | 0 | 7 | 0 | 56 | 0 | 0 | 0 | 257 | 400 | 398 | 40 | 30 | 157 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 0 | 35 | 0 | 0 | 0 | 24 | 6950.5 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 1011.81 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1020 | 300 | 17 | 5396.81 | 12347.31 | 102.77
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 90 | 60 | 15 | 0 | 35 | 0 | 0 | 0 | 470 | 0 | 0 | 298 | 0 | 0 | 0 | 51 | 9.5 | 21 | 0 | 470 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0.01 | 140 | 0 | 29 | 800 | 0 | 0 | 44 | 0 | 0 | 223 | 0 | 0 | 0 | 600 | 0 | 100 | 0 | 205 | 290 | 290 | 44 | 0 | 192 | 0 | 0 | 65 | 0 | 0 | 7 | 0 | 54 | 0 | 0 | 0 | 251 | 400 | 398 | 40 | 30 | 154 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 0.03 | 65 | 0 | 0 | 0 | 24 | 6758.54 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 1010.14 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 0 | 0 | 1020 | 300 | 17 | 5375.14 | 12133.68 | 102.77
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 17 | 114 | 60 | 0 | 0 | 17 | 0 | 0 | 0 | 480 | 0 | 0 | 323 | 0 | 0 | 5 | 80 | 9.5 | 21 | 0 | 470 | 15 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 25 | 0.68 | 140 | 0 | 24 | 780 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 600 | 5 | 20 | 0 | 175 | 344 | 335 | 44 | 0 | 202 | 0 | 0 | 65 | 0 | 0 | 9 | 0 | 50 | 0 | 13 | 0 | 246 | 400 | 398 | 40 | 30 | 157 | 1 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 3.26 | 65 | 0 | 0.2 | 2.61 | 24 | 6773.25 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1213 | 0 | 0 | 0 | 1010.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 10 | 0 | 0 | 8.15 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0.77 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 29 | 0.07 | 0 | 297 | 115 | 0 | 0 | 1170.6 | 300 | 0 | 5491.31 | 12264.56 | 102.76
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 17 | 131 | 45 | 45 | 4 | 24 | 72 | 0 | 0 | 470 | 0 | 17 | 311 | 0 | 0 | 11 | 86 | 9.5 | 21 | 0 | 450 | 45 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.57 | 140 | 6 | 16 | 780 | 0 | 0 | 16 | 2 | 15 | 220 | 0 | 0 | 0 | 600 | 9 | 63 | 0 | 145 | 307 | 300 | 44 | 0 | 219 | 0 | 0 | 65 | 7 | 8 | 7 | 0 | 54 | 8 | 33 | 0 | 245 | 400 | 398 | 40 | 30 | 156 | 5 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 10.01 | 65 | 0 | 1.1 | 23.49 | 24 | 7037.67 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 36.85 | 1234.2 | 0 | 0 | 0 | 809.69 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 8 | 25.23 | 42 | 0 | 0 | 28.49 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.55 | 0 | 0 | 50 | 15 | 49 | 0 | 0 | 0 | 2.6 | 84 | 0.2 | 32 | 286 | 115 | 0 | 0 | 1165 | 300 | 11 | 5605.81 | 12643.48 | 102.75
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 3 | 116 | 15 | 45 | 15 | 55 | 72 | 0 | 0 | 405 | 0 | 17 | 297 | 0 | 0 | 22 | 68 | 9.5 | 21 | 0 | 450 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.51 | 140 | 34 | 11 | 780 | 0 | 0 | 24 | 8 | 51 | 218 | 0 | 0 | 0 | 600 | 15 | 120 | 0 | 180 | 299 | 255 | 44 | 0 | 194 | 0 | 0 | 65 | 17 | 44 | 9 | 0 | 52 | 8 | 51 | 0 | 241 | 396 | 398 | 40 | 0 | 156 | 7 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 59 | 15.76 | 45 | 0 | 1.6 | 38.09 | 6 | 7051.46 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 58 | 1178 | 0 | 0 | 0 | 812.46 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 8 | 39.66 | 62 | 0 | 0 | 44.23 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 3.87 | 0 | 0 | 50 | 25 | 49 | 0 | 0 | 0 | 4.4 | 134 | 0.38 | 32 | 254 | 115 | 0 | 0 | 1145 | 300 | 17 | 5678 | 12729.46 | 102.75
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 114 | 15 | 45 | 15 | 55 | 68 | 0 | 0 | 425 | 0 | 17 | 297 | 0 | 0 | 28 | 68 | 9.5 | 21 | 0 | 450 | 66 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3.13 | 141 | 32 | 8 | 780 | 0 | 0 | 24 | 8 | 49 | 217 | 0 | 0 | 0 | 690 | 18 | 120 | 0 | 180 | 294 | 290 | 44 | 0 | 189 | 0 | 0 | 65 | 17 | 40 | 9 | 0 | 54 | 8 | 66 | 0 | 244 | 393 | 398 | 40 | 0 | 156 | 10 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 35 | 58 | 19 | 45 | 0 | 2.1 | 42.87 | 6 | 7217.6 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 1150 | 0 | 0 | 0 | 816.84 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 8 | 43.01 | 89 | 0 | 0 | 54.14 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 4.74 | 0 | 0 | 50 | 31 | 34 | 0 | 0 | 0 | 5.7 | 168 | 0.51 | 32 | 255 | 114 | 0 | 0 | 1134 | 300 | 17 | 5758.94 | 12976.54 | 102.74
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 17 | 114 | 15 | 45 | 15 | 55 | 67 | 0 | 0 | 465 | 0 | 17 | 306 | 0 | 0 | 31 | 68 | 9.5 | 21 | 0 | 445 | 58 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.45 | 139 | 33 | 5 | 780 | 0 | 0 | 24 | 8 | 48 | 214 | 0 | 0 | 0 | 875 | 19 | 120 | 0 | 200 | 319 | 315 | 44 | 0 | 202 | 0 | 0 | 65 | 16 | 36 | 9 | 0 | 64 | 8 | 48 | 0 | 240 | 388 | 395 | 40 | 0 | 156 | 11 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 35 | 59 | 21.21 | 45 | 0 | 2.2 | 49.58 | 6 | 7533.94 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 84 | 1150 | 0 | 0 | 0 | 818.41 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 8 | 54.36 | 96 | 0 | 0 | 62.06 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 5.63 | 0 | 0 | 50 | 34 | 34 | 0 | 0 | 0 | 6.5 | 190 | 0.58 | 32 | 275 | 113 | 0 | 0 | 1128 | 300 | 17 | 5826.54 | 13360.48 | 102.73
12:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 25 | 127 | 15 | 95 | 18 | 55 | 98 | 0 | 0 | 470 | 0 | 35 | 316 | 0 | 0 | 31 | 68 | 9.5 | 20 | 0 | 440 | 81 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.62 | 137 | 36 | 0 | 780 | 0 | 0 | 0 | 8 | 50 | 213 | 0 | 0 | 0 | 1090 | 3 | 127 | 0 | 200 | 331 | 330 | 44 | 0 | 206 | 0 | 0 | 66 | 23 | 35 | 9 | 0 | 70 | 25 | 64 | 0 | 242 | 386 | 387 | 39 | 0 | 153 | 6 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 35 | 87 | 21.55 | 65 | 0 | 2.3 | 50.6 | 6 | 8031.57 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 82 | 1234.2 | 0 | 0 | 0 | 813.94 | 0 | 0 | 0 | 90 | 35 | 0 | 0 | 0 | 8 | 54.87 | 70 | 0 | 0 | 62.62 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 5.51 | 0 | 0 | 70 | 35 | 34 | 0 | 0 | 0 | 6.5 | 195 | 0.57 | 48 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 17 | 6047.81 | 14079.38 | 102.73
13:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 36 | 149 | 62 | 195 | 30 | 55 | 144 | 0 | 0 | 465 | 0 | 35 | 300 | 0 | 0 | 29 | 123 | 9.5 | 20 | 0 | 435 | 97 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 3.32 | 138 | 50 | 0 | 780 | 0 | 0 | 2 | 8 | 59 | 212 | 0 | 0 | 0 | 1177 | 18 | 127 | 0 | 190 | 304 | 300 | 44 | 0 | 179 | 0 | 3 | 65 | 75 | 35 | 8 | 0 | 68 | 25 | 58 | 0 | 245 | 386 | 394 | 39 | 0 | 153 | 10 | 16 | 0 | 80 | 30 | 0 | 0 | 100 | 35 | 87 | 19.5 | 75 | 0 | 2.1 | 46.39 | 16 | 8454.81 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 80 | 1234.2 | 0 | 0 | 0 | 820.92 | 0 | 0 | 0 | 113 | 55 | 0 | 8.2 | 0 | 8 | 53.83 | 95 | 0 | 0 | 53.8 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 3.29 | 0 | 0 | 115 | 34 | 34 | 0 | 0 | 0 | 6.7 | 167 | 0.56 | 48 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 17 | 6120.1 | 14574.91 | 102.72
14:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 54 | 149 | 62 | 245 | 30 | 55 | 133 | 0 | 0 | 458 | 0 | 35 | 294 | 0 | 0 | 23 | 123 | 9.5 | 20 | 0 | 435 | 91 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 2.17 | 138 | 92 | 0 | 780 | 0 | 0 | 23 | 8 | 64 | 214 | 0 | 0 | 0 | 1160 | 15 | 130 | 0 | 170 | 311 | 270 | 44 | 0 | 205 | 0 | 17 | 42 | 111 | 28 | 8 | 0 | 72 | 25 | 50 | 0 | 244 | 384 | 340 | 39 | 0 | 150 | 3 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 35 | 86 | 16.85 | 75 | 0 | 1.7 | 38.23 | 24 | 8443.45 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 65 | 1234.2 | 0 | 0 | 0 | 814.28 | 0 | 0 | 0 | 113 | 70 | 0 | 8.5 | 0 | 8 | 46.8 | 87 | 0 | 0 | 50.27 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 4.45 | 0 | 0 | 115 | 28 | 34 | 0 | 0 | 0 | 5.2 | 157 | 0.46 | 48 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 17 | 6045.76 | 14489.21 | 102.72
15:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 0 | 147 | 62 | 246 | 30 | 55 | 162 | 0 | 0 | 467 | 0 | 55 | 303 | 0 | 0 | 18 | 123 | 9.5 | 20 | 0 | 440 | 96 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 1.8 | 140 | 95 | 0 | 780 | 0 | 0 | 47 | 8 | 71 | 212 | 0 | 0 | 0 | 1224 | 12 | 135 | 0 | 170 | 313 | 310 | 45 | 0 | 205 | 0 | 16 | 0 | 120 | 26 | 8 | 0 | 70 | 25 | 30 | 0 | 248 | 386 | 392 | 39 | 0 | 149 | 6 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 35 | 87 | 10.98 | 75 | 0 | 1.2 | 27.64 | 24 | 8606.12 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 48 | 1234.2 | 0 | 0 | 0 | 821.01 | 0 | 0 | 0 | 113 | 70 | 0 | 8.5 | 0 | 8 | 34.4 | 65 | 0 | 0 | 35.36 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 3.21 | 0 | 0 | 115 | 21 | 34 | 0 | 0 | 0 | 3.1 | 114 | 0.29 | 48 | 307 | 107 | 0 | 0 | 1170.6 | 300 | 17 | 5951.67 | 14557.79 | 102.71
16:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 39 | 146 | 62 | 250 | 30 | 55 | 162 | 0 | 0 | 463 | 0 | 55 | 309 | 0 | 0 | 9 | 123 | 9 | 20 | 0 | 445 | 90 | 52 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 0.81 | 141 | 91 | 0 | 780 | 0 | 0 | 47 | 8 | 87 | 212 | 0 | 0 | 0 | 1224 | 6 | 133 | 0 | 165 | 335 | 325 | 51 | 0 | 208 | 0 | 17 | 0 | 115 | 26 | 8 | 0 | 68 | 25 | 18 | 0 | 246 | 385 | 367 | 39 | 0 | 152 | 3 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 35 | 87 | 5.73 | 75 | 0 | 0.5 | 11.07 | 18 | 8632.11 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 23 | 1218 | 0 | 0 | 0 | 825.28 | 0 | 0 | 0 | 113 | 70 | 0 | 8.5 | 0 | 8 | 17.9 | 32 | 0 | 0 | 18.95 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 1.53 | 0 | 0 | 115 | 9 | 34 | 0 | 0 | 0 | 1.8 | 57 | 0.14 | 48 | 267 | 106 | 0 | 0 | 1100 | 300 | 17 | 5665.1 | 14297.21 | 102.71
17:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 54 | 135 | 62 | 230 | 30 | 55 | 162 | 0 | 0 | 469 | 0 | 55 | 288 | 0 | 0 | 1 | 123 | 7.5 | 21 | 0 | 445 | 95 | 169 | 0 | 0 | 0 | 0 | 2 | 35 | 0 | 25 | 0.09 | 141 | 92 | 2 | 1080 | 0 | 0 | 50 | 8 | 91 | 212 | 0 | 0 | 0 | 1224 | 1 | 140 | 0 | 155 | 298 | 255 | 44 | 0 | 170 | 0 | 17 | 0 | 114 | 26 | 8 | 0 | 66 | 25 | 2 | 0 | 241 | 397 | 397 | 39 | 0 | 149 | 0 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 35 | 97 | 0.98 | 75 | 0 | 0.1 | 2.04 | 0 | 8862.71 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 3 | 1148 | 0 | 0 | 0 | 815.74 | 0 | 0 | 0 | 113 | 70 | 0 | 8.5 | 0 | 8 | 2.02 | 6 | 0 | 0 | 2.66 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0.19 | 0 | 0 | 115 | 2 | 34 | 0 | 0 | 0 | 0.3 | 7 | 0.02 | 48 | 267 | 108 | 0 | 0 | 1050 | 300 | 35 | 5399.43 | 14262.14 | 102.7
18:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 54 | 54 | 148 | 107 | 146 | 40 | 55 | 162 | 0 | 0 | 452 | 0 | 55 | 308 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 450 | 95 | 187 | 0 | 0 | 0 | 50 | 13 | 54.36 | 37 | 25 | 0 | 142 | 92 | 3 | 1080 | 69 | 0 | 50 | 13 | 105 | 214 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 190 | 305 | 300 | 44 | 0 | 208 | 0 | 30 | 0 | 123 | 26 | 8 | 114 | 78 | 52.2 | 0 | 0 | 244 | 397 | 386 | 40 | 0 | 146 | 0 | 16 | 0 | 81 | 30 | 0 | 0 | 101 | 35 | 96 | 0 | 151 | 0 | 0 | 0 | 0 | 9500.98 | 918 | 0 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1148 | 0 | 0 | 0 | 811.41 | 0 | 0 | 0 | 113 | 94 | 0 | 100 | 28 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 275 | 108 | 0 | 0 | 1170.6 | 300 | 137 | 5860.01 | 15360.99 | 102.7
19:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 54 | 149 | 126 | 147 | 55 | 55 | 162 | 0 | 0 | 478 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 455 | 109 | 207 | 42 | 0 | 0 | 50 | 20 | 54.36 | 37 | 25 | 0 | 142 | 92 | 18 | 1080 | 158 | 0 | 50 | 25.5 | 105 | 215 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 185 | 292 | 265 | 51 | 0 | 217 | 0 | 102 | 0 | 159 | 26 | 10 | 114 | 70 | 52.2 | 0 | 0 | 243 | 400 | 397 | 40 | 0 | 152 | 0 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 35 | 87 | 0 | 161 | 0 | 0 | 0 | 18 | 9849.48 | 775 | 0 | 21 | 34 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1222 | 0 | 0 | 0 | 810.42 | 0 | 32 | 0 | 113 | 113 | 0 | 100 | 32 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 137 | 5932.02 | 15781.5 | 102.69
19:30 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 54 | 54 | 149 | 127 | 147 | 55 | 55 | 162 | 0 | 0 | 486 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 455 | 109 | 207 | 66 | 0 | 0 | 50 | 20 | 54.36 | 37 | 25 | 0 | 142 | 92 | 25 | 1080 | 88 | 0 | 45 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 185 | 299 | 255 | 51 | 0 | 198 | 0 | 115 | 0 | 171 | 26 | 10 | 70 | 74 | 52.2 | 0 | 0 | 243 | 399 | 398 | 40 | 0 | 146 | 0 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 35 | 87 | 0 | 162 | 0 | 0 | 0 | 20 | 9765.48 | 775 | 0 | 23 | 40 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1230 | 0 | 0 | 0 | 816.83 | 0 | 32 | 0 | 113 | 113 | 0 | 100 | 32 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 137 | 5956.43 | 15721.91
20:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 54 | 54 | 149 | 112 | 147 | 30 | 55 | 162 | 0 | 0 | 480 | 0 | 55 | 309 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 460 | 107 | 207 | 66 | 0 | 0 | 50 | 20 | 54.36 | 37 | 25 | 0 | 142 | 92 | 29 | 1080 | 34 | 0 | 46 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 195 | 300 | 265 | 51 | 0 | 205 | 0 | 105 | 0 | 171 | 26 | 10 | 45 | 70 | 52.2 | 0 | 0 | 244 | 396 | 398 | 40 | 0 | 138 | 0 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 35 | 87 | 0 | 125 | 0 | 0 | 0 | 22 | 9610.48 | 775 | 0 | 31 | 45 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1230 | 0 | 0 | 0 | 815.87 | 0 | 32 | 0 | 113 | 70 | 0 | 100 | 32 | 8 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 108 | 0 | 0 | 1170.6 | 300 | 137 | 5921.47 | 15531.95 | 102.69
21:00 | 0 | 50 | 42 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 54 | 141 | 78 | 147 | 30 | 55 | 162 | 0 | 0 | 485 | 0 | 55 | 306 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 460 | 107 | 194 | 69 | 0 | 0 | 50 | 20 | 54.36 | 12 | 25 | 0 | 142 | 92 | 29 | 1080 | 34 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 137 | 0 | 205 | 308 | 265 | 51 | 0 | 200 | 0 | 34 | 0 | 171 | 27 | 10 | 34 | 70 | 52.2 | 0 | 0 | 243 | 396 | 398 | 40 | 0 | 140 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 87 | 0 | 125 | 0 | 0 | 0 | 20 | 9438.48 | 918 | 0 | 29 | 40 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 817 | 0 | 32 | 0 | 113 | 70 | 0 | 100 | 32 | 25 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 113 | 0 | 0 | 1170.6 | 300 | 102 | 6000.8 | 15439.28 | 102.68
22:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 54 | 118 | 78 | 147 | 30 | 55 | 162 | 0 | 0 | 485 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 7 | 21 | 0 | 465 | 109 | 212 | 73 | 0 | 0 | 50 | 20 | 35 | 12 | 25 | 0 | 142 | 93 | 29 | 1080 | 34 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 135 | 0 | 180 | 277 | 240 | 51 | 0 | 182 | 0 | 34 | 0 | 170 | 26 | 10 | 34 | 70 | 52.2 | 0 | 0 | 242 | 400 | 398 | 40 | 0 | 153 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 87 | 0 | 125 | 0 | 0 | 0 | 23 | 9289.12 | 917 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1234.2 | 0 | 0 | 0 | 805.88 | 0 | 32 | 0 | 113 | 70 | 0 | 50 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 113 | 0 | 0 | 1170.6 | 300 | 54 | 5924.88 | 15214 | 102.68
23:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35 | 54 | 112 | 78 | 98 | 30 | 55 | 108 | 0 | 0 | 485 | 0 | 55 | 318 | 0 | 0 | 0 | 123 | 8.5 | 21 | 0 | 470 | 107 | 87 | 72 | 0 | 0 | 50 | 20 | 35 | 12 | 25 | 0 | 141 | 93 | 29 | 1080 | 34 | 0 | 50 | 25.5 | 105 | 219 | 0 | 0 | 0 | 1224 | 0 | 132 | 0 | 145 | 310 | 270 | 51 | 0 | 215 | 0 | 34 | 0 | 120 | 21 | 10 | 34 | 72 | 25 | 0 | 0 | 242 | 400 | 398 | 40 | 0 | 156 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 35 | 88 | 0 | 85 | 0 | 0 | 0 | 0 | 8996 | 918 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1203 | 0 | 0 | 0 | 816.51 | 0 | 32 | 0 | 113 | 70 | 0 | 50 | 31 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 276 | 115 | 0 | 0 | 1170.6 | 300 | 54 | 5861.31 | 14857.31 | 102.67
Total KWH | 0 | 987840 | 385440 | 0 | 0 | 0 | 0 | 0 | 8920800 | 0 | 0 | 789480 | 815760 | 3020832 | 1434720 | 3161455 | 532951 | 1157967 | 2355840 | 0 | 0 | 11338414 | 0 | 832715 | 7420012 | 0 | 0 | 203255 | 2605200 | 222000 | 508320 | 0 | 10932272.73 | 1895618 | 2170364 | 420480 | 0 | 4800 | 352877 | 148647 | 593283 | 165120 | 588480 | 21360 | 3412369 | 1585745 | 392640 | 22370909.09 | 530255 | 0 | 903360 | 288036 | 1570691 | 5178483 | 0 | 0 | 0 | 22658179 | 123525 | 2840290 | 150545 | 4038000 | 7804400 | 7126000 | 1080424 | 30240 | 4886000 | 0 | 532800 | 897199 | 1856160 | 500640 | 187340 | 418380 | 1534080 | 510010 | 433864 | 0 | 5966000 | 8931900 | 9559000 | 944000 | 285600 | 3669545.46 | 67667 | 391608 | 0 | 1870080 | 716064 | 310000 | 0 | 2408580 | 869760 | 1750800 | 139132 | 1850400 | 0 | 14700 | 329690 | 427200 | 198328593.28 | 21902545 | 0 | 130560 | 268800 | 0 | 0 | 0 | 0 | 0 | 1182528 | 568080 | 29054540 | 0 | 0 | 0 | 21272000 | 0 | 227154 | 0 | 2070336 | 1254816 | 0 | 588192 | 232931 | 304968 | 363992 | 699400 | 258300 | 0 | 399744 | 0 | 0 | 0 | 0 | 0 | 0 | 7480436 | 0 | 34740 | 0 | 0 | 1903969 | 238523 | 942374 | 0 | 0 | 0 | 42874.68 | 1308240 | 3750 | 1063392 | 7025000 | 2692000 | 0 | 0 | 27178182 | 7316363.64 | 1196400 | 139205130.32 | 337533723.6

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-10-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-10-2026 | during | 23-10-2026 | during | 23-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 383 | 350 | 412 | 412 | 392 | 392 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 18 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 310 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 126 | 133 | 133 | 133 | 133 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9.5 | 7 | 33 | 33 | 5.5 | 5.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 19 | 19 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 42 | 52.19 | 52.19 | 24 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 147 | 300 | 300 | 98 | 98 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 127 | 149 | 149 | 149 | 115 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 88 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 98 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 25 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP | 1*448+1*208 | 584 | 584 | 440 | 455 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 470 | 478 | 583 | 583 | 525 | 525 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 143.42 | 68 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6204.914 | 2280.5 | 2751.42 | 5566.8 | 5536.8 | 2610.92 | 2797.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 17 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 3 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 137 | 142 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 215 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 20 | 14 | 24 | 14 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 37 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 18 | 42 | 42 | 30 | 42 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 0 | 42 | 95.1 | 95.1 | 34 | 52 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.62 | 0 | 3.8 | 0 | 3.8 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 207 | 300 | 300 | 51 | 212 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 35 | 54.36 | 54.36 | 54.36 | 36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 36 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 81 | 109 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 158 | 163 | 163 | 35 | 146 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1090 | 1224 | 1224 | 1224 | 740 | 1172 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 780 | 1080 | 1150 | 1150 | 790 | 1080 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2513.62 | 3653.86 | 3885.76 | 3924.96 | 2356.8 | 3463.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 206 | 217 | 221.25 | 221.25 | 205 | 205 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 331 | 292 | 350.01 | 350.01 | 350.01 | 350.01 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 330 | 265 | 342.01 | 342.01 | 306 | 306 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 200 | 185 | 280 | 280 | 200 | 200 | STG Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 45 | 45 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 55 | 55 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 44 | 44 | Engine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 127 | 140 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 20 | 20 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 66 | 0 | 163 | 163 | 65 | 65 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 23 | 159 | 200 | 200 | 135 | 124 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 70 | 70 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 10 | 24.5 | 24.5 | 11 | 11 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 35 | 26 | 113 | 113 | 73 | 68 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 102 | 115 | 115 | 51 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1530 | 1683.2 | 2555.44 | 2485.44 | 1939.21 | 1917.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-10-2026 | during | 23-10-2026 | during | 23-10-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.55 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 161 | 200 | 200 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 87 | 115 | 115 | 59 | 95 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.6 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 267.45 | 301 | 673.6 | 601.5 | 308.1 | 322
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 30 | 30 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 100 | 100 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 83 | 83 | 11 | 11 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 13 | 13 | plant availability zero
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 242 | 243 | 341 | 341 | 260 | 260 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 397 | 400 | 400 | 400 | 400 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 386 | 400 | 383 | 383 | 260 | 260 | STG Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1440 | 1460 | 1586 | 1586 | 1361 | 1361
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 775 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 34 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 85 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1222 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2284.2 | 2137 | 2254.2 | 2164.2 | 1729.2 | 1639.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | 1170.6 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 48 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 107 | 108 | 120 | 120 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 300 | 300 | 300 | 300 | 300 | 300 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 137 | 150 | 150 | 35 | 100 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1950.17 | 2086.6 | 2158.6 | 2157.6 | 1944.6 | 2008.6
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 54.87 | 0 | 57 | 0 | 57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 32 | 32 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 | 40 | 40 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 333 | 243 | 413.79 | 413.79 | 300 | 300 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 34 | 34 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113 | 55 | 113 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.51 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 813.94 | 810.42 | 800 | 800 | 1200 | 1400 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.62 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 70 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1472.94 | 1483.42 | 2607.69 | 2383.99 | 1993.9 | 2141.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 110 | 113 | 113 | 34 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.5 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 115 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 195 | 0 | 189.93 | 0 | 189.93 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 340.5 | 225 | 486.93 | 262 | 396.93 | 251
System Total |  |  |  |  | 28843.2 | 28692.211 | 14079.38 | 15781.5 | 21775.02 | 21102.49 | 14640.66 | 15901.99
Forecast Scenario (23-10-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15190 |  | 0 |  | 15190
|  |  |  | 1:00 | 14600 |  | 0 |  | 14600
|  |  |  | 2:00 | 14250 |  | 0 |  | 14250
|  |  |  | 3:00 | 13990 |  | 0 |  | 13990
|  |  |  | 4:00 | 13720 |  | 0 |  | 13720
|  |  |  | 5:00 | 13200 |  | 0 |  | 13200
|  |  |  | 6:00 | 12420 |  | 0 |  | 12420
|  |  |  | 7:00 | 12210 |  | 0 |  | 12210
|  |  |  | 8:00 | 12040 |  | 0 |  | 12040
|  |  |  | 9:00 | 11710 |  | 0 |  | 11710
|  |  |  | 10:00 | 11710 |  | 0 |  | 11710
|  |  |  | 11:00 | 12000 |  | 0 |  | 12000
|  |  |  | 12:00 | 12690 |  | 0 |  | 12690
|  |  |  | 13:00 | 13320 |  | 0 |  | 13320
|  |  |  | 14:00 | 12630 |  | 0 |  | 12630
|  |  |  | 15:00 | 12490 |  | 0 |  | 12490
|  |  |  | 16:00 | 12130 |  | 0 |  | 12130
|  |  |  | 17:00 | 11800 |  | 0 |  | 11800
|  |  |  | 18:00 | 12630 |  | 0 |  | 12630
|  |  |  | 18:30 | 13385 |  | 0 |  | 13385
|  |  |  | 19:00 | 14140 |  | 0 |  | 14140
|  |  |  | 19:30 | 14170 |  | 0 |  | 14170
|  |  |  | 20:00 | 14320 |  | 0 |  | 14320
|  |  |  | 21:00 | 14360 |  | 0 |  | 14360
|  |  |  | 22:00 | 14600 |  | 0 |  | 14600
|  |  |  | 23:00 | 14680 |  | 0 |  | 14680
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 12690.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14360.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14360.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 316.83 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:36 hrs on 23-10-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-10-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14079.38 | MW | 12:00 Hr. | Energy Generated |  |  | 337.5337 |  | MKWHr.
| Day Peak Demand |  |  | 14087.38 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.221 |  | MKWHr.
| Evening Peak Generation |  |  | 15781.5 | MW | 19:00 Hr. | Energy Demand |  |  | 337.7547 |  | MKWHr.
| Evening Peak Demand |  |  | 15849.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 12133.68 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 832.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 15781.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 8.0558 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.3418 | 0 | 18.0802 | 0 | 0 | 0.20325 | 0 | 0 | 57.6253 | Gas | 116.3379 | Gas | 398577306.1073
| Chattogram Zone |  |  | 5.5711 | 45.0291 | 11.213 | 0 | 3.4124 | 0.14489 | 0 | 0.0048 | 65.3752 | Coal | 115.6032 | Coal | 903402016.8685
| Cumilla Zone |  |  | 26.2001 | 0 | 6.6583 | 0 | 0 | 0.43386 | 1.5341 | 0 | 34.8264 | HFO | 52.4743 | HFO | 1059358892.66
| Mymensingh Zone |  |  | 0 | 0 | 4.8982 | 0 | 0 | 0.48352 | 0 | 0 | 5.3817 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.0524 | 0 | 0 | 0 | 0 | 0.067667 | 0 | 0 | 35.12 | Hydro | 3.4124 | Hydro | 341236.9
| Khulna Zone |  |  | 0 | 29.0545 | 1.5819 | 0 | 0 | 0.56808 | 21.9025 | 0 | 53.1071 | Solar | 4.9925 | Solar | 80526624.8708
| Barishal Zone |  |  | 2.692 | 41.5195 | 2.2598 | 0 | 0 | 0.00375 | 0 | 0 | 46.4751 | Import | 44.7086 | Import | 276831132.2
| Rajshahi Zone |  |  | 7.4804 | 0 | 4.9367 | 0 | 0 | 1.4979 | 21.272 | 0 | 35.187 | Wind | 0.0048 | Wind | 71136
| Rangpur Zone |  |  | 0 | 0 | 2.8463 | 0 | 0 | 1.5896 | 0 | 0 | 4.436
| Total |  |  | 116.3379 | 115.6032 | 52.4743 | 0 | 3.4124 | 4.9925 | 44.7086 | 0.0048 | 337.5337
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 398577306.1073 |  | Hydro | 341236.9
|  |  |  | Coal | 903402016.8685 |  | Solar | 80526624.8708
|  |  |  | HFO | 1059358892.66 |  | Import | 276831132.2
|  |  |  | HSD | 0 |  | Wind | 71136
[5 empty] | Total: | 271,91,08,345 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9025 | Peak Hr Flow | 775.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34624000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.272 | Peak Hr Flow | 810.42 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1122 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5341 | Peak Hr Flow | 70.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2129 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.7086 | Peak Hr Flow | 1655.42 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 24 |  | 5736
|  |  |  | Chattogram |  | 0 |  | 1565
|  |  |  | Cumilla |  | 5 |  | 1571
|  |  |  | Mymensingh |  | 34 |  | 1221
|  |  |  | Sylhet |  | 0 |  | 670
|  |  |  | Khulna |  | 0 |  | 1758
|  |  |  | Barishal |  | 0 |  | 480
|  |  |  | Rajshahi |  | 2 |  | 1432
|  |  |  | Rangpur |  | 0 |  | 871
|  |  |  | Total |  | 65 |  | 15304
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-2 |  |  | 40
[7 empty] | 4 | Khulna 330 MW CCPP GT |  |  | 220
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 500
|  |  |  | Total Unavailable Capacity |  |  |  | 800
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:27 | 10:57 | New Tongi S/S Tr-2(4161-3) Scheduled S/D Due to Maintenance for overheating on Red Phase
of DS-411M of T-2.
| 09:27 | 16:05 | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to Annual maintenance
| 09:27 | 16:06 | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to Annual maintenance.
| 09:59 |  | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Breaker
pole replacement work and from Purbasadipur 230/132/33kV end Due to 132kV CB replacement
Work at saidpur Grid S/S of 132kV Saidpur Ckt-1. Load served by Saidpur Ckt-2
| 12:00 |  | Day peak generation is 14080 MW.
| 19:00 |  | Evening Peak Generation: 15782 MW.
| 19:05 | 20:05 | Chowmuhani 230/132/33kV S/S TR3-435T LT Forced S/D Due to TR-03 X-former 33kV side R
phase Red hot Maintenance.
| 19:05 | 20:05 | Chowmuhani 230/132/33kV S/S TR3-435T HT Forced S/D Due to TR-03 X-former 33kV side R
phase Red hot Maintenance.
| 06:00 |  | Minimum generation 11971 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-10-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8920800 | Gas Shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 532951 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas Shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7420012 | Gas Shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 789480 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 1434720 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1157967 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 832715 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7 | 222000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 508320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 385440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 147 | 3161455 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3020832 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 987840 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2355840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 203255 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 815760 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 1*448+1*208 | 584 | 455 | 10932272.73 | Machine Problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 478 | 11338414 | Machine Problem
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas Shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 143.42 | 143.42 | 2605200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6204.914 | 2751.42 | 57625273.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 288036 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123525 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 903360 | 33kV Feeder Problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 142 | 3412369 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5178483 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1570691 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 20 | 148647 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 352877 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 165120 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 392640 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 42 | 420480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21360 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 207 | 2170364 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 593283 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1585745 | Machine Problem
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 588480 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 1895618 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 158 | 530255 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 22658179 | Coal Shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 4800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 22370909.09 | Coal Shortage
Chattogram Area Total |  |  |  |  | 4885.967 | 3653.86 | 65375221.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 217 | 4886000 | Gas Shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 292 | 7804400 | Gas Shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 265 | 7126000 | Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 185 | 4038000 | STG Under Shutdown & Gas Shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas Shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 30240 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 150545 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1080424 | Engine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 2840290 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Machine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 897199 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 159 | 1856160 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 70 | 1534080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 510010 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 10 | 187340 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 418380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 500640 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 102 | 532800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 433864 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1683.2 | 34826372
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 139132 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 161 | 1850400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1750800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 329690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 427200 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 869760 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 301 | 5381682
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 67667 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 944000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 285600 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3669545.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 310000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716064 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1870080 | Gas Shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2408580 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 391608 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 243 | 5966000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 397 | 9559000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 8931900 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1460 | 35120044.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 775 | 21902545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 130560 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 34 | 268800 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1182528 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 568080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Atomizing air Compressor system's HX problem.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1222 | 29054540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2137 | 53107053
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1170.6 | 27178182 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1063392 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 108 | 2692000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 300 | 7316363.64 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 0 | Major Inspection
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1196400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7025000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3750 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2086.6 | 46475087.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 363992 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 227154 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 232931 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 243 | 7480436 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 258300 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 304968 | Fuel Shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 588192 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1254816 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 2070336 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 34740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 810.42 | 21272000 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 399744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 699400 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1483.42 | 35187009
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas Shortage
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 942374 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42874.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1903969 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 238523 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1308240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 225 | 4435980.68
Eastern Grid Total |  |  |  |  | 16961.086 | 9849.48 | 198328593.28
Western Grid Total |  |  |  |  | 11731.125 | 5932.02 | 139205130.32
National Grid Total |  |  |  |  | 28692.211 | 15781.5 | 337533723.6
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-10-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10700.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4538.1 | MW
i) Dhaka area |  |  | 5711.73 |  | MW | i) Khulna area |  |  |  | 1757.5 | MW
ii) Chattogram area |  |  | 1565.1 |  | MW | ii) Barishal area |  |  |  | 480 | MW
iii) Cumilla area |  |  | 1566.48 |  | MW | iii) Rajshahi area |  |  |  | 1429.6 | MW
iv) Mymensingh area |  |  | 1187 |  | MW | iv) Rangpur area |  |  |  | 871 | MW
v) Sylhet area |  |  | 670 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15238.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 72 | Hatirjheel | 61 | 13:00 | 143 | PHP | 13 | 17:00
2 | AKSML | 156.4 | 05:00 | 73 | Ishurdi | 76 | 18:30 | 144 | Pabna | 91 | 18:00
3 | Aftabnagar | 58 | 18:00 | 74 | Jaldhaka | 67 | 18:00 | 145 | Palashbari | 120 | 18:00
4 | Agargaon | 108 | 13:00 | 75 | Jamalpur | 121 | 19:00 | 146 | Panchagarh | 54 | 19:00
5 | Agrabad | 66 | 18:00 | 76 | Jashore | 115 | 18:30 | 147 | Patiya | 31 | 18:00
6 | Amnura | 38 | 18:00 | 77 | Jhenaidah | 93 | 18:00 | 148 | Patnitala | 34 | 08:00
7 | Araihazar | 113 | 23:00 | 78 | Joydebpur | 153 | 18:00 | 149 | Patuakhali | 69.3 | 22:00
8 | Ashuganj | 0.56 | 19:30 | 79 | Joypurhat | 54 | 00:00 | 150 | Payra | 34 | 21:00
9 | Ashuganj-230 | 97 | 00:00 | 80 | Juldah | 19.5 | 23:00 | 151 | Postogola | 62 | 13:00
10 | BSRM | 204 | 19:30 | 81 | KSRM | 44 | 16:00 | 152 | Pubail | 44 | 18:00
11 | Bagerhat | 87 | 18:00 | 82 | Kabirpur | 251 | 19:30 | 153 | Purbachal | 29 | 18:00
12 | Bajitpur | 93 | 19:30 | 83 | Kachua | 98 | 19:00 | 154 | Purbasadipur | 103 | 18:30
13 | Bakerganj | 14 | 18:30 | 84 | Kaliganj | 42 | 18:00 | 155 | Rahanpur | 32 | 18:00
14 | Bakulia | 94 | 18:00 | 85 | Kallyanpur | 111 | 13:00 | 156 | Rahim | 46 | 14:00
15 | Banani | 46 | 13:00 | 86 | Kalurghat | 39 | 22:00 | 157 | Rajbari | 81.5 | 18:30
16 | Bangabhaban | 5 | 12:00 | 87 | Kamrangirchar | 78 | 12:00 | 158 | Rajendrapur | 124 | 18:00
17 | Barapukuria | 58 | 18:30 | 88 | Kaptai | N/A | N/A | 159 | Rajshahi | 89 | 20:00
18 | Barguna | 22 | 20:00 | 89 | Kasba | 39 | 19:00 | 160 | Rajshahi-230 | 90 | 13:00
19 | Barishal | 98 | 13:00 | 90 | Kazla | 119 | 13:00 | 161 | Ramganj | 110 | 19:00
20 | Barishal-230 | 102 | 18:00 | 91 | Keranigonj | 86 | 13:00 | 162 | Rampur | 46 | 00:00
21 | Baroaulia | 39 | 09:00 | 92 | Khagrachori | 38 | 18:00 | 163 | Rangamati | 20 | 18:00
22 | Baroirhat | 64 | 18:00 | 93 | Khulna | 61 | 13:00 | 164 | Rangpur | 114 | 19:00
23 | Bashundhara | 201 | 13:00 | 94 | Khulshi | 177 | 12:00 | 165 | Ruppur | 4.2 | 15:00
24 | BashundharaCement | 0 | 00:00 | 95 | Kishoreganj | 137 | 18:00 | 166 | SSM | 0 | 00:00
25 | Beanibazar | 76 | 18:00 | 96 | Kodda | 315 | 19:00 | 167 | Saidpur | 99 | 18:30
26 | Benapole | 63 | 18:30 | 97 | Kulaura | 57 | 18:00 | 168 | Santhia | 34 | 18:00
27 | Bhaluka | 152 | 18:00 | 98 | Kurigram | 58 | 19:00 | 169 | Satkhira | 127 | 22:00
28 | Bhandaria | 57 | 22:00 | 99 | Kushtia | 139 | 18:00 | 170 | Satmasjid | 97 | 13:00
29 | Bhangura | 37 | 18:00 | 100 | Laksam | 35 | 04:00 | 171 | Savar | 201 | 15:00
30 | Bheramara(GK) | 64 | 18:00 | 101 | Lakshmipur | 48 | 00:00 | 172 | SevenRings | 5.65 | 23:00
31 | Bhulta | 197 | 23:00 | 102 | Lalbag | 76 | 14:00 | 173 | ShahCement | 21 | 00:00
32 | Bog-Sherpur | 68 | 18:00 | 103 | Lalmonirhat | 62 | 18:00 | 174 | Shahjadpur | 74 | 18:30
33 | Bogura | 166 | 23:00 | 104 | MI_Cement | 11.3 | 00:00 | 175 | Shahjibazar | 148 | 18:00
34 | Borhanuddin | 75 | 21:00 | 105 | Madanganj | 52 | 15:00 | 176 | Shahmirpur | 68 | 18:00
35 | Brahmanbaria | 153 | 19:00 | 106 | Madaripur | 105 | 22:00 | 177 | Shariatpur | 99 | 22:00
36 | Cantonment | 122 | 13:00 | 107 | Madartek | 78 | 00:00 | 178 | Sherpur | 148 | 18:00
37 | Chandina | 24 | 18:00 | 108 | Madunaghat | 56 | 18:00 | 179 | Shikalbaha | 24 | 14:00
38 | Chandpur | 85 | 20:00 | 109 | Magura | 64 | 18:00 | 180 | Shitalakhya | 78.8 | 12:00
39 | Chandraghona | 34 | 18:00 | 110 | Mahasthangarh | 70 | 18:00 | 181 | Sholosohor | 47 | 18:00
40 | Chapai | 71 | 19:00 | 111 | Maijdee | 38 | 22:00 | 182 | Shomvuganj | 36 | 21:00
41 | Charfasson | 32 | 22:00 | 112 | Manikganj | 137 | 19:30 | 183 | Shyampur | 158 | 10:00
42 | Charsaidpur | 39 | 00:00 | 113 | Maniknagar | 74 | 00:00 | 184 | Siddhirganj | 121 | 11:00
43 | Chauddagram | 77 | 18:00 | 114 | Matarbari | 60 | 19:00 | 185 | Sirajganj | 108 | 19:00
44 | Chhatak | 40 | 21:00 | 115 | Matuail | 78 | 12:00 | 186 | Sitakunda | 35 | 18:00
45 | Chowmuhani | 171 | 18:00 | 116 | Metrorail_Motijheel | 18 | 13:00 | 187 | Sonargaon | 123 | 16:00
46 | Chuadanga | 110 | 18:00 | 117 | Metrorail_Uttara | 5 | 19:00 | 188 | Sreemongol | 86 | 19:30
47 | Coxsbazar | 154 | 19:30 | 118 | Millgate | 89 | 15:00 | 189 | Sreepur | 130 | 18:00
48 | Cumilla(N) | 158 | 18:30 | 119 | Mirpur | 138 | 18:00 | 190 | Srinagar | 48.7 | 22:00
49 | Cumilla(S) | 153 | 18:00 | 120 | Mirsorai | 12 | 18:30 | 191 | Sunamganj | 62 | 19:30
50 | Daganbhuiyan | 41 | 00:00 | 121 | Mirzapur | 50 | 18:30 | 192 | Sylhet | 122 | 18:00
51 | Daudkandi | 126 | 21:00 | 122 | Mithapukur | 105 | 18:00 | 193 | Sylhet_(South) | 65 | 18:30
52 | DhakaUniversity | 60 | 13:00 | 123 | Modern | N/A | N/A | 194 | TK | 0 | 00:00
53 | Dhamrai | 100 | 16:00 | 124 | Mogbazar | 56.7 | 12:00 | 195 | Tangail | 182 | 18:30
54 | Dhanmondi | 85 | 13:00 | 125 | Mongla | 37 | 18:00 | 196 | Taraganj | 30 | 18:00
55 | Dohazari | 124 | 20:00 | 126 | Monirampur | 23 | 18:30 | 197 | Tasnim | 38 | 17:00
56 | Faridpur | 167 | 19:00 | 127 | Motijheel | 35 | 07:00 | 198 | Thakurgaon | 95 | 18:30
57 | Fatullah | 132 | 16:00 | 128 | Muktagacha | 40 | 18:00 | 199 | Tongi | 164 | 11:00
58 | Fenchuganj | 45 | 18:00 | 129 | Munshiganj | 111 | 23:00 | 200 | Ullahpara | 39 | 18:00
59 | Feni | 112 | 18:00 | 130 | Muradnagar | 59 | 19:00 | 201 | Ullon | 46 | 00:00
60 | GPH | 1 | 01:00 | 131 | Mymensingh | 160 | 18:00 | 202 | Uttara | 91 | 18:00
61 | Ghatail | 96 | 18:00 | 132 | Nabinagar | 112 | 12:00 | 203 | UttaraNew | 38 | 13:00
62 | Ghorashal | 0 | 00:00 | 133 | Naogaon | 111 | 18:30 | 204 | Zigatola | 82 | 13:00
63 | Ghorashal-230 | 104 | 13:00 | 134 | Narail | 59 | 18:30
64 | Goalpara | 36 | 00:00 | 135 | Narinda | 56 | 13:00
65 | Gollamari | 94 | 00:00 | 136 | Narshingdi | 189 | 19:00
66 | Gopalganj | 109 | 22:00 | 137 | Natore | 136 | 19:00
67 | Gulshan | 88 | 13:00 | 138 | Nawabganj | 46.6 | 22:00
68 | Halishahar | 80 | 16:00 | 139 | Netrakona | 134 | 20:00
69 | HaripurSBU | 131 | 19:00 | 140 | New | 69 | 08:00
70 | Hasnabad | 103 | 18:00 | 141 | Niamatpur | 72 | 13:00
71 | Hathazari | 96 | 18:00 | 142 | Noapara | 44 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-10-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14466.76 | 0 |  | 14466.76
1:00 | 14015.09 | 0 |  | 14015.09
2:00 | 13542.98 | 0 |  | 13542.98
3:00 | 13010.9 | 0 |  | 13010.9
4:00 | 12565.38 | 0 |  | 12565.38
5:00 | 12347.31 | 0 |  | 12347.31
6:00 | 12133.68 | 0 |  | 12133.68
7:00 | 12264.56 | 0 |  | 12264.56
8:00 | 12643.48 | 0 |  | 12643.48
9:00 | 12729.46 | 0 |  | 12729.46
10:00 | 12976.54 | 0 |  | 12976.54
11:00 | 13360.48 | 0 |  | 13360.48
12:00 | 14079.38 | 8 |  | 14087.38
13:00 | 14574.91 | 0 |  | 14574.91
14:00 | 14489.21 | 0 |  | 14489.21
15:00 | 14557.79 | 0 |  | 14557.79
16:00 | 14297.21 | 0 |  | 14297.21
17:00 | 14262.14 | 8 |  | 14270.14
18:00 | 15360.99 | 84 |  | 15448.99
19:00 | 15781.5 | 65 |  | 15849.5
19:30 | 15721.91 | 40 |  | 15763.71
20:00 | 15531.95 | 20 |  | 15552.95
21:00 | 15439.28 | 20 |  | 15460.28
22:00 | 15214 | 12 |  | 15226.54
23:00 | 14857.31 | 4 |  | 14861.31
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-10-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8550 | 5916.76 | 14466.76 | DAILY GENERATION CURVE
00:30 | 8309.5 | 5931.425 | 14240.925
01:00 | 8069 | 5946.09 | 14015.09 | 22-10-2026
01:30 | 7959.5 | 5819.535 | 13779.035
02:00 | 7850 | 5692.98 | 13542.98
02:30 | 7681.75 | 5595.19 | 13276.94
03:00 | 7513.5 | 5497.4 | 13010.9
03:30 | 7345 | 5443.14 | 12788.14
04:00 | 7176.5 | 5388.88 | 12565.38
04:30 | 7063.5 | 5392.845 | 12456.345
05:00 | 6950.5 | 5396.81 | 12347.31
05:30 | 6854.52 | 5385.975 | 12240.495
06:00 | 6758.54 | 5375.14 | 12133.68
06:30 | 6765.895 | 5433.225 | 12199.12
07:00 | 6773.25 | 5491.31 | 12264.56
07:30 | 6905.46 | 5548.56 | 12454.02
08:00 | 7037.67 | 5605.81 | 12643.48
08:30 | 7044.565 | 5641.905 | 12686.47
09:00 | 7051.46 | 5678 | 12729.46
09:30 | 7134.53 | 5718.47 | 12853
10:00 | 7217.6 | 5758.94 | 12976.54
10:30 | 7375.77 | 5792.74 | 13168.51
11:00 | 7533.94 | 5826.54 | 13360.48
11:30 | 7782.755 | 5937.175 | 13719.93
12:00 | 8031.57 | 6047.81 | 14079.38
12:30 | 8243.19 | 6083.955 | 14327.145
13:00 | 8454.81 | 6120.1 | 14574.91
13:30 | 8449.13 | 6082.93 | 14532.06
14:00 | 8443.45 | 6045.76 | 14489.21
14:30 | 8524.785 | 5998.715 | 14523.5
15:00 | 8606.12 | 5951.67 | 14557.79
15:30 | 8619.115 | 5808.385 | 14427.5
16:00 | 8632.11 | 5665.1 | 14297.21
16:30 | 8747.41 | 5532.265 | 14279.675
17:00 | 8862.71 | 5399.43 | 14262.14
17:30 | 9181.845 | 5629.72 | 14811.565
18:00 | 9500.98 | 5860.01 | 15360.99
18:30 | 9675.23 | 5896.015 | 15571.245
19:00 | 9849.48 | 5932.02 | 15781.5
19:30 | 9765.48 | 5956.43 | 15721.91
20:00 | 9610.48 | 5921.47 | 15531.95
20:30 | 9524.48 | 5961.135 | 15485.615 |  | Executive Engineer
21:00 | 9438.48 | 6000.8 | 15439.28 |  | Network Operation Division
21:30 | 9363.8 | 5962.84 | 15326.64
22:00 | 9289.12 | 5924.88 | 15214
22:30 | 9142.56 | 5893.095 | 15035.655
23:00 | 8996 | 5861.31 | 14857.31

## En-Curve
QF-LDC-12
Date | 22-10-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3217 | 1573.5 | 918 | 0 | 66 | 1060.76 | 138 | 4982 | 0 | 554 | 1957.5 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3192 | 1582.5 | 918 | 0 | 64 | 1041.425 | 138 | 4914.5 | 0 | 525 | 1865.5 | 0 | 0 | 0 | 0 | 22-10-2026
01:00 | 3167 | 1591.5 | 918 | 0 | 62 | 1022.09 | 138 | 4847 | 0 | 496 | 1773.5 | 0 | 0 | 0 | 0
01:30 | 3180 | 1614.5 | 917.5 | 0 | 46 | 1018.435 | 138 | 4744.1 | 0 | 407 | 1713.5 | 0 | 0 | 0 | 0 | Energy Generated | 337.5337 |  | MKWHr
02:00 | 3193 | 1637.5 | 917 | 0 | 30 | 1014.78 | 138 | 4641.2 | 0 | 318 | 1653.5 | 0 | 0 | 0 | 0 | Energy not Served | 0.221 |  | MKWHr
02:30 | 3275 | 1599 | 917.5 | 0 | 44 | 1010.99 | 138.5 | 4592.7 | 0 | 204.5 | 1494.75 | 0 | 0 | 0 | 0 | Total Energy Requirement | 337.7547 |  | MKWHr
03:00 | 3357 | 1560.5 | 918 | 0 | 58 | 1007.2 | 139 | 4544.2 | 0 | 91 | 1336 | 0 | 0 | 0 | 0
03:30 | 3406 | 1562.5 | 917.5 | 0 | 58 | 1006.94 | 139.5 | 4545.2 | 0 | 91 | 1061.5 | 0 | 0 | 0 | 0
04:00 | 3455 | 1564.5 | 917 | 0 | 58 | 1006.68 | 140 | 4546.2 | 0 | 91 | 787 | 0 | 0 | 0 | 0
04:30 | 3457 | 1569 | 917.5 | 0 | 57 | 1009.245 | 140 | 4471.1 | 0 | 91 | 744.5 | 0 | 0 | 0 | 0
05:00 | 3459 | 1573.5 | 918 | 0 | 56 | 1011.81 | 140 | 4396 | 0 | 91 | 702 | 0 | 0 | 0 | 0
05:30 | 3441.5 | 1564 | 917.5 | 0 | 55 | 1010.975 | 140 | 4328 | 0.02 | 105 | 678.5 | 0 | 0 | 0 | 0
06:00 | 3424 | 1554.5 | 917 | 0 | 54 | 1010.14 | 140 | 4260 | 0.04 | 119 | 655 | 0 | 0 | 0 | 0
06:30 | 3485 | 1557 | 917.5 | 0 | 52 | 1010.165 | 140 | 4310.3 | 54.155 | 133.5 | 539 | 0 | 0 | 0.5 | 0
07:00 | 3546 | 1559.5 | 918 | 0 | 50 | 1010.19 | 140 | 4360.6 | 108.27 | 148 | 423 | 0 | 0 | 1 | 0
07:30 | 3451 | 1538.5 | 918 | 0 | 52 | 909.94 | 140 | 4362.9 | 219.68 | 159.5 | 702 | 0 | 0 | 0.5 | 0
08:00 | 3356 | 1517.5 | 918 | 0 | 54 | 809.69 | 140 | 4365.2 | 331.09 | 171 | 981 | 0 | 0 | 0 | 0
08:30 | 3323 | 1481.5 | 918 | 0 | 53 | 811.075 | 140 | 4311.1 | 427.795 | 147 | 1074 | 0 | 0 | 0 | 0
09:00 | 3290 | 1445.5 | 918 | 0 | 52 | 812.46 | 140 | 4257 | 524.5 | 123 | 1167 | 0 | 0 | 0 | 0
09:30 | 3311.5 | 1455 | 917.5 | 0 | 53 | 814.65 | 140.5 | 4283 | 591.85 | 123 | 1163 | 0 | 0 | 0 | 0
10:00 | 3333 | 1464.5 | 917 | 0 | 54 | 816.84 | 141 | 4309 | 659.2 | 123 | 1159 | 0 | 0 | 0 | 0
10:30 | 3366 | 1478.5 | 917 | 0 | 59 | 817.625 | 140 | 4408.5 | 688.885 | 123 | 1170 | 0 | 0 | 0 | 0
11:00 | 3399 | 1492.5 | 917 | 0 | 64 | 818.41 | 139 | 4508 | 718.57 | 123 | 1181 | 0 | 0 | 0 | 0
11:30 | 3413 | 1488.5 | 917.5 | 0 | 67 | 816.175 | 138 | 4694.9 | 706.355 | 157 | 1321.5 | 0 | 0 | 0 | 4
12:00 | 3427 | 1484.5 | 918 | 0 | 70 | 813.94 | 137 | 4881.8 | 694.14 | 191 | 1462 | 0 | 0 | 0 | 8
12:30 | 3360.5 | 1480 | 918 | 0 | 69 | 817.43 | 137.5 | 4925.3 | 687.315 | 272.6 | 1659.5 | 0 | 0 | 0 | 4
13:00 | 3294 | 1475.5 | 918 | 0 | 68 | 820.92 | 138 | 4968.8 | 680.49 | 354.2 | 1857 | 0 | 0 | 0 | 0
13:30 | 3215.5 | 1470.5 | 918 | 0 | 70 | 817.6 | 138 | 4960.3 | 637.31 | 354.35 | 1950.5 | 0 | 0 | 0 | 0
14:00 | 3137 | 1465.5 | 918 | 0 | 72 | 814.28 | 138 | 4951.8 | 594.13 | 354.5 | 2044 | 0 | 0 | 0 | 0
14:30 | 3176.5 | 1474.5 | 918 | 0 | 71 | 817.645 | 139 | 4983.8 | 513.055 | 363.5 | 2066.5 | 0 | 0 | 0 | 0
15:00 | 3216 | 1483.5 | 918 | 0 | 70 | 821.01 | 140 | 5015.8 | 431.98 | 372.5 | 2089 | 0 | 0 | 0 | 0
15:30 | 3215.5 | 1487.25 | 918 | 0 | 69 | 823.145 | 140.5 | 4952.4 | 323.705 | 372.5 | 2125.5 | 0 | 0 | 0 | 0
16:00 | 3215 | 1491 | 918 | 0 | 68 | 825.28 | 141 | 4889 | 215.43 | 372.5 | 2162 | 0 | 0 | 0 | 0
16:30 | 3144 | 1487.25 | 917.5 | 0 | 67 | 820.51 | 141 | 4979 | 122.915 | 373.5 | 2227 | 0 | 0 | 0 | 4
17:00 | 3073 | 1483.5 | 917 | 0 | 66 | 815.74 | 141 | 5069 | 30.4 | 374.5 | 2292 | 0 | 0 | 0 | 8
17:30 | 3137.5 | 1477.75 | 917.5 | 0 | 72 | 813.575 | 141.5 | 5133.3 | 15.2 | 537.46 | 2565.78 | 0 | 0 | 0 | 46
18:00 | 3202 | 1472 | 918 | 0 | 78 | 811.41 | 142 | 5197.6 | 0 | 700.42 | 2839.56 | 0 | 0 | 0 | 84
18:30 | 3177 | 1502.5 | 846.5 | 0 | 74 | 810.915 | 142 | 5250.6 | 0 | 752.92 | 3014.81 | 0 | 0 | 0 | 74.5
19:00 | 3152 | 1533 | 775 | 0 | 70 | 810.42 | 142 | 5303.6 | 0 | 805.42 | 3190.06 | 0 | 0 | 0 | 65
19:30 | 3118 | 1542 | 775 | 0 | 74 | 816.83 | 142 | 5311.6 | 0 | 814.42 | 3128.06 | 0 | 0 | 0 | 40
20:00 | 3147 | 1538 | 775 | 0 | 70 | 815.87 | 142 | 5311.6 | 0 | 812.42 | 2920.06 | 0 | 0 | 0 | 20
20:30 | 3159.5 | 1541.5 | 846.5 | 0 | 70 | 816.435 | 142 | 5313.7 | 0 | 772.92 | 2823.06 | 0 | 0 | 0 | 20
21:00 | 3172 | 1545 | 918 | 0 | 70 | 817 | 142 | 5315.8 | 0 | 733.42 | 2726.06 | 0 | 0 | 0 | 20
21:30 | 3130.5 | 1553.5 | 917.5 | 0 | 70 | 811.44 | 142 | 5315.8 | 0 | 688.92 | 2696.98 | 0 | 0 | 0 | 16
22:00 | 3089 | 1562 | 917 | 0 | 70 | 805.88 | 142 | 5315.8 | 0 | 644.42 | 2667.9 | 0 | 0 | 0 | 12
22:30 | 3140.5 | 1566.75 | 917.5 | 0 | 71 | 811.195 | 141.5 | 5284.7 | 0 | 616.21 | 2486.3 | 0 | 0 | 0 | 8
23:00 | 3192 | 1571.5 | 918 | 0 | 72 | 816.51 | 141 | 5253.6 | 0 | 588 | 2304.7 | 0 | 0 | 0 | 4
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 22-10-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 107 | 4 | 326 | 120 | 1288 | 438 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 118 | 7 | 362 | 108 | 1388 | 408
2:00 | 113 | 6 | 364 | 104 | 1340 | 404 |  | Import | 0
3:00 | 119 | 9 | 370 | 106 | 1382 | 420
4:00 | 135 | 19 | 368 | 102 | 1414 | 448 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 140 | 21 | 382 | 102 | 1474 | 458
6:00 | 146 | 19 | 400 | 94 | 1538 | 456 |  | Import | 0
7:00 | 120 | 8 | 316 | 82 | 1474 | 436
8:00 | 115 | 13 | 284 | 98 | 1436 | 434 | Sirajganj-Sreepur Ckt-1 | Export | 1463000
9:00 | 148 | 26 | 378 | 118 | 1532 | 498
10:00 | 161 | 32 | 392 | 116 | 1576 | 528 |  | Import | 0
11:00 | 157 | 30 | 372 | 116 | 1516 | 545
12:00 | 138 | 23 | 356 | 142 | 1400 | 510 | Sirajganj-Sreepur Ckt-2 | Export | 1461000
13:00 | 113 | 13 | 300 | 132 | 1392 | 500
14:00 | 109 | 10 | 306 | 134 | 1368 | 456 |  | Import | 0
15:00 | 113 | 17 | 298 | 136 | 1376 | 486
16:00 | 109 | 17 | 280 | 136 | 1268 | 518 | Gopalganj-Aminbazar Ckt-1 | Export | 15790000
17:00 | 93 | 16 | 250 | 136 | 1180 | 508
18:00 | 78 | 17 | 200 | 150 | 1014 | 474 |  | Import | 0
18:30 | 43 | 18 | 114 | 148 | 886 | 438
19:00 | 48 | 23 | 154 | 174 | 920 | 452 | Gopalganj-Aminbazar Ckt-2 | Export | 15910000
19:30 | 57 | 25 | 184 | 174 | 986 | 464
20:00 | 54 | 24 | 174 | 180 | 990 | 454 |  | Import | 0
21:00 | 77 | 16 | 216 | 166 | 1038 | 470
22:00 | 88 | 21 | 248 | 162 | 1044 | 470 |  | Total Export | 34624000
23:00 | 97 | 24 | 258 | 162 | 1060 | 494 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-10-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 05:00 | 371 | 11:00 | Madunaghat | 401 | 09:00 | 394 | 13:00
Amtali | 413 | 02:00 | 408 | 12:00 | Meghnaghat | 392 | 02:00 | 380 | 12:00
Ashuganj | 403 | 6:00 | 388 | 12:00 | Mirsorai | 401 | 08:00 | 392 | 12:00
Bhulta | 395 | 06:00 | 379 | 12:00 | Payra | 415 | 03:00 | 408 | 12:00
Bibiana | 389 | 01:00 | 383 | 17:00 | Rahanpur | 412 | 02:00 | 404 | 12:00
BIPTC | 401 | 20:00 | 393 | 11:00 | Rampal | 402 | 05:00 | 390 | 12:00
Bogura | 403 | 02:00 | 392 | 18:30
Gopalganj | 396 | 02:00 | 386 | 12:00
Kaliakoir | 381 | 02:00 | 363 | 12:00
Korerhat | 401 | 08:00 | 391 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 02:00 | 223 | 12:00 | Hasnabad | 227 | 02:00 | 219 | 12:00
AKSML | 236 | 08:00 | 230 | 00:00 | Hathazari | 235 | 09:00 | 229 | 11:00
Aminbazar | 235 | 03:00 | 225 | 11:00 | Ishurdi | 236 | 05:00 | 224 | 12:00
Ashuganj | 229 | 06:00 | 221 | 19:00 | Jhenaidah | 229 | 05:00 | 214 | 12:00
Ashuganj-400 | N/A | N/A | N/A | N/A | Kachua | 227 | 08:00 | 221 | 23:00
Baghabari | 232 | 05:00 | 225 | 12:00 | Kaliakoir | 236 | 02:00 | 223 | 12:00
Barapukuria | 235 | 05:00 | 221 | 07:00 | Keranigonj | 231 | 02:00 | 220 | 12:00
Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 231 | 05:00 | 220 | 18:30
Barapukuria(N) | 238 | 02:00 | 224 | 07:00 | Korerhat | 228 | 07:00 | 221 | 23:00
Barishal | 236 | 02:00 | 229 | 23:00 | Madunaghat | 238 | 09:00 | 233 | 04:00
Bheramara | 234 | 05:00 | 221 | 12:00 | Madunaghat-400 | 239 | 09:00 | 235 | 13:00
Bhulta | 226 | 06:00 | 216 | 12:00 | Maniknagar | 223 | 01:00 | 215 | 13:00
Bibiana | 224 | 06:00 | 218 | 18:00 | Meghnaghat | 232 | 06:00 | 223 | 12:00
BIPTC | 237 | 05:00 | 221 | 12:00 | Meghnaghat-400 | 228 | 06:00 | 219 | 12:00
Birulia | 235 | 02:00 | 223 | 12:00 | Mirsorai | 227 | 08:00 | 222 | 12:00
Bogura | 240 | 02:00 | 231 | 07:00 | Naogaon | 228 | 02:00 | 216 | 12:00
Bogura-400 | 239 | 02:00 | 232 | 18:30 | Purbasadipur | 236 | 02:00 | 220 | 07:00
Borhanuddin | 236 | 05:00 | 231 | 12:00 | Rajshahi | 234 | 06:00 | 221 | 12:00
BSRM | 229 | 08:00 | 222 | 12:00 | Rampal | 231 | 06:00 | 220 | 18:00
Charfasson | 233 | 07:00 | 229 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 07:00 | 221 | 12:00 | Rampura | 225 | 05:00 | 213 | 12:00
Cumilla(N) | 225 | 05:00 | 218 | 12:00 | Shikalbaha | 240 | 18:30 | 233 | 07:00
Faridpur | 236 | 05:00 | 230 | 12:00 | Shyampur | 228 | 02:00 | 218 | 12:00
Fenchuganj | 227 | 06:00 | 218 | 11:00 | Siddhirganj | 224 | 03:00 | 219 | 12:00
Feni | 225 | 06:00 | 219 | 12:00 | Sirajgonj | 237 | 05:00 | 230 | 00:00
Ghorashal | 225 | 02:00 | 220 | 00:00 | Sreepur | 224 | 06:00 | 217 | 12:00
Ghorashal-230 | 227 | 02:00 | 208 | 12:00 | Tongi | 227 | 04:00 | 212 | 11:00
Gopalganj | 239 | 06:00 | 232 | 12:00
GPH | 234 | 08:00 | 228 | 12:00
Haripur | 226 | 06:00 | 217 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 127 | 12:00 | Madanganj | 136 | 06:00 | 130 | 12:00
Agargaon | 136 | 02:00 | 129 | 12:00 | Madaripur | 135 | 06:00 | 130 | 18:30
Agrabad | 136 | 18:30 | 130 | 12:00 | Madartek | 134 | 06:00 | 126 | 12:00
AKS | 134 | 18:30 | 130 | 12:00 | Madunaghat | 138 | 07:00 | 134 | 04:00
Aminbazar | 135 | 01:00 | 129 | 12:00 | Magura | 136 | 06:00 | 126 | 12:00
Amnura | 135 | 01:00 | 128 | 12:00 | Mahasthangarh | 136 | 05:00 | 131 | 07:00
Araihazar | 128 | 06:00 | 120 | 15:00 | Maijdee | 128 | 09:00 | 123 | 23:00
Ashuganj | 134 | 02:00 | 128 | 18:00 | Manikganj | 134 | 06:00 | 127 | 11:00
Ashuganj-230 | 137 | 03:00 | 134 | 18:00 | Maniknagar | 136 | 05:00 | 128 | 13:00
Bagerhat | 131 | 06:00 | 123 | 18:00 | Matarbari | 120 | 18:00 | 109 | 00:00
Bajitpur | 130 | 05:00 | 123 | 21:00 | Matuail | 136.5 | 05:00 | 130 | 12:00
Bakerganj | 134 | 00:00 | 131 | 11:00 | Metrorail_Motijheel | 136 | 05:00 | 128 | 13:00
Bakulia | 136 | 18:00 | 131 | 12:00 | Metrorail_Uttara | 138 | 02:00 | 126 | 11:00
Banani | 134 | 05:00 | 126 | 12:00 | Millgate | 138 | 01:00 | 127 | 12:00
Bangabhaban | 136 | 05:00 | 128 | 12:00 | Mirpur | 134 | 02:00 | 127 | 12:00
Barapukuria | 138 | 05:00 | 128 | 07:00 | Mirzapur | 134 | 02:00 | 127 | 11:00
Barguna | 134 | 08:00 | 130 | 13:00 | Mithapukur | 134 | 02:00 | 128 | 07:00
Barishal | 136 | 05:00 | 132 | 12:00 | MI_Cement | 134.7 | 04:00 | 126 | 11:00
Barishal-230 | 136 | 02:00 | 132 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 136 | 18:30 | 132 | 12:00 | Mogbazar | 135 | 06:00 | 128 | 13:00
Baroirhat | 132 | 08:00 | 129 | 12:00 | Mongla | 130 | 07:00 | 123 | 18:00
Bashundhara | 139 | 02:00 | 127 | 11:00 | Monirampur | 131 | 06:00 | 118 | 18:30
BashundharaCement | 136 | 06:00 | 130 | 12:00 | Motijheel | 136 | 05:00 | 128 | 12:00
Beanibazar | 126 | 07:00 | 119 | 19:30 | Muktagacha | 131 | 06:00 | 120 | 07:00
Benapole | 135 | 05:00 | 119 | 18:00 | Munshiganj | 135 | 05:00 | 129 | 12:00
Bhaluka | 130 | 05:00 | 122 | 12:00 | Muradnagar | 129 | 06:00 | 123 | 12:00
Bhandaria | 135 | 04:00 | 127 | 22:00 | Mymensingh | 131 | 06:00 | 116 | 18:00
Bhangura | 135 | 02:00 | 129 | 07:00 | Nabinagar | 136 | 04:00 | 124 | 12:00
Bheramara | 138 | 02:00 | 131 | 12:00 | Naogaon | 137 | 02:00 | 130 | 12:00
Bheramara(GK) | 138 | 04:00 | 130 | 12:00 | Narail | 136 | 06:00 | 124 | 14:00
Bhulta | 123 | 08:00 | 120 | 12:00 | Narinda | 136 | 05:00 | 128 | 13:00
Bhulta-400 | 126 | 05:00 | 120 | 12:00 | Narshingdi | 130 | 01:00 | 118 | 11:00
Birulia | 137 | 02:00 | 131 | 12:00 | Natore | 135 | 04:00 | 129 | 12:00
Bog-Sherpur | 137 | 02:00 | 131 | 07:00 | Nawabganj | 136 | 06:00 | 129 | 12:00
Bogura | 138 | 03:00 | 133 | 07:00 | Netrakona | 122 | 06:00 | 109 | 18:00
Bogura-230 | 140 | 02:00 | 133 | 07:00 | New | 139 | 05:00 | 127 | 11:00
Brahmanbaria | 133 | 06:00 | 125 | 19:00 | Niamatpur | 136 | 06:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 136 | 02:00 | 129 | 11:00 | Noapara | 132 | 06:00 | 124 | 18:00
Chandina | 130 | 06:00 | 126 | 12:00 | Pabna | 136 | 05:00 | 129 | 12:00
Chandpur | 134 | 18:30 | 125 | 03:00 | Palashbari | 132 | 05:00 | 125 | 07:00
Chandraghona | 137 | 08:00 | 134 | 12:00 | Panchagarh | 142 | 02:00 | 131 | 07:00
Chapai | 134 | 02:00 | 130 | 00:00 | Patiya | 134 | 09:00 | 128 | 13:00
Charsaidpur | 136 | 02:00 | 130 | 12:00 | Patnitala | 135 | 05:00 | 130 | 00:00
Chauddagram | 130 | 08:00 | 126 | 12:00 | Patuakhali | 134 | 00:00 | 131 | 12:00
Chhatak | 124 | 07:00 | 115 | 18:00 | Payra | 136 | 00:00 | 134 | 11:00
Chowmuhani | 128 | 07:00 | 124 | 12:00 | PHP | 131 | 06:00 | 128 | 13:00
Chuadanga | 136 | 05:00 | 125 | 12:00 | Postogola | 135 | 03:00 | 128 | 12:00
Coxsbazar | 120 | 04:00 | 113 | 21:00 | Pubail | 131 | 00:00 | 125 | 11:00
Cumilla(N) | 130 | 05:00 | 125 | 13:00 | Purbachal | 134 | 05:00 | 126 | 13:00
Cumilla(S) | 133 | 05:00 | 125 | 22:00 | Purbasadipur | 137 | 02:00 | 127 | 07:00
Daganbhuiyan | 129 | 08:00 | 126 | 12:00 | Rahanpur | 138 | 04:00 | 134 | 12:00
Daudkandi | 129 | 04:00 | 123 | 12:00 | Rahanpur-400 | 138 | 02:00 | 135 | 07:00
DhakaUniversity | 134 | 05:00 | 127 | 12:00 | Rahim | 137 | 05:00 | 131 | 12:00
Dhamrai | 134 | 03:00 | 125 | 12:00 | Rajbari | 134 | 06:00 | 128 | 18:30
Dhanmondi | 136 | 03:00 | 131 | 12:00 | Rajendrapur | 133 | 05:00 | 126 | 19:00
Dohazari | 130 | 18:00 | 123 | 13:00 | Rajshahi | 133 | 03:00 | 126 | 12:00
Faridpur | 135 | 05:00 | 131 | 12:00 | Rajshahi-230 | 134 | 02:00 | 128 | 12:00
Fatullah | 136 | 06:00 | 127 | 12:00 | Ramganj | 127 | 18:30 | 123 | 00:00
Fenchuganj | 134 | 05:00 | 128 | 21:00 | Rampur | 136 | 18:30 | 131 | 12:00
Feni | 130 | 08:00 | 126 | 16:00 | Rampura | 134 | 05:00 | 127 | 12:00
Feni-230 | 131 | 08:00 | 127 | 12:00 | Rangamati | 136 | 01:00 | 132 | 12:00
Ghatail | 129 | 06:00 | 122 | 7:00 | Rangpur | 134 | 09:00 | 126 | 07:00
Ghorashal | 133 | 05:00 | 127 | 11:00 | Ruppur | 137 | 00:00 | 132 | 12:00
Goalpara | 135 | 05:00 | 127 | 13:00 | Saidpur | 135 | 06:00 | 128 | 07:00
Gollamari | 134 | 06:00 | 128 | 12:00 | Santhia | 136 | 05:00 | 129 | 12:00
Gopalganj | 133 | 02:00 | 128 | 18:00 | Satkhira | 130 | 05:00 | 119 | 18:30
Gopalganj-400 | 135 | 02:00 | 131 | 13:00 | Satmasjid | 136 | 02:00 | 129 | 12:00
Gulshan | 134 | 05:00 | 126 | 12:00 | Savar | 134 | 07:00 | 128 | 12:00
Halishahar | 136 | 18:00 | 131 | 12:00 | SevenRings | 135 | 02:00 | 127 | 11:00
Haripur | 137 | 06:00 | 131 | 12:00 | ShahCement | 136 | 05:00 | 130 | 12:00
HaripurSBU | 136 | 02:00 | 131 | 12:00 | Shahjadpur | 133 | 00:00 | 132 | 07:00
Hasnabad | 136 | 04:00 | 130 | 15:00 | Shahjibazar | 132 | 06:00 | 125 | 19:00
Hathazari | 136 | 00:00 | 135 | 01:00 | Shahmirpur | 136 | 18:30 | 132 | 12:00
Hatirjheel | 134 | 04:00 | 126 | 12:00 | Shariatpur | 133 | 05:00 | 129 | 13:00
Ishurdi | 138 | 02:00 | 132 | 12:00 | Sherpur | 131 | 06:00 | 118 | 11:00
Jaldhaka | 132 | 03:00 | 124 | 18:30 | Shikalbaha | 126 | 18:00 | 121 | 14:00
Jamalpur | 133 | 19:30 | 122 | 07:00 | Shikalbaha-230 | 137 | 18:30 | 133 | 13:00
Jashore | 137 | 06:00 | 120 | 18:30 | Shitalakhya | 134.7 | 04:00 | 126 | 11:00
Jhenaidah | 139 | 04:00 | 129 | 12:00 | Sholosohor | 137 | 07:00 | 132 | 13:00
Jhenaidah-230 | 140 | 05:00 | 128 | 12:00 | Shomvuganj | 127 | 06:00 | 117 | 21:00
Joydebpur | 129 | 00:00 | 123 | 11:00 | Shyampur | 135 | 06:00 | 130 | 12:00
Joypurhat | 135 | 05:00 | 130 | 07:00 | Shyampur-230 | 137 | 02:00 | 130 | 13:00
Juldah | 136 | 18:30 | 131 | 12:00 | Siddhirganj | 137 | 05:00 | 131 | 12:00
Kabirpur | 137 | 03:00 | 124 | 12:00 | Sirajganj | 134 | 02:00 | 127 | 12:00
Kachua | 130 | 18:30 | 126 | 12:00 | Sitakunda | 136 | 08:00 | 132 | 13:00
Kaliakoir | 139 | 01:00 | 130 | 04:00 | Sonargaon | 134 | 05:00 | 128 | 13:00
Kaliganj | 138 | 05:00 | 128 | 12:00 | Sreemongol | 131 | 06:00 | 123 | 19:30
Kallyanpur | 134 | 03:00 | 128 | 12:00 | Sreepur | 133 | 05:00 | 127 | 12:00
Kalurghat | 137 | 00:00 | 134 | 12:00 | Srinagar | 136 | 08:00 | 129 | 12:00
Kamrangirchar | 137 | 03:00 | 125 | 12:00 | SSM | 140 | 00:00 | 138 | 13:00
Kaptai | 139 | 1:00 | 136 | 13:00 | Sunamganj | 120 | 05:00 | 113 | 19:30
Kasba | 128 | 07:00 | 122 | 22:00 | Sylhet | 126 | 08:00 | 121 | 21:00
Kazla | 136 | 06:00 | 128 | 13:00 | Sylhet_(South) | 128 | 06:00 | 122 | 18:30
Keranigonj | 137 | 06:00 | 130 | 12:00 | Tangail | 130 | 06:00 | 123 | 12:00
Khagrachori | 135 | 03:00 | 131 | 12:00 | Taraganj | 134 | 09:00 | 127 | 07:00
Khulna | 133 | 05:00 | 125 | 18:00 | Tasnim | 134 | 05:00 | 128 | 15:00
Khulna(S) | 135 | 06:00 | 126 | 18:30 | Thakurgaon | 142 | 02:00 | 129 | 07:00
Khulshi | 135 | 18:00 | 129 | 12:00 | TK | 137 | 04:00 | 136 | 00:00
Kishoreganj | 130 | 06:00 | 121 | 19:00 | Tongi | 141 | 04:00 | 130 | 11:00
Kodda | 136 | 01:00 | 120 | 10:00 | Ullahpara | 135 | 04:00 | 129 | 11:00
Korerhat | 136 | 07:00 | 130 | 12:00 | Ullon | 133 | 02:00 | 127 | 12:00
KSRM | 138 | 18:30 | 132 | 12:00 | Uttara | 138 | 02:00 | 125 | 12:00
Kulaura | 133 | 05:00 | 127 | 18:30 | UttaraNew | 138 | 02:00 | 126 | 12:00
Kurigram | 131 | 08:00 | 121 | 07:00 | Zigatola | 136 | 04:00 | 130 | 12:00
Kushtia | 138 | 04:00 | 129 | 12:00
Laksam | 129 | 18:30 | 125 | 04:00
Lakshmipur | 127 | 08:00 | 123 | 12:00
Lalbag | 136 | 05:00 | 128 | 13:00
Lalmonirhat | 130 | 04:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division