## Forecast
6086.1 |  |  |  |  | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-12-05 | Wednesday
|  | Date (day): | 2018-12-05 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10546 | MW |  |  | (b) At Evening Peak Hour : |  | 11487 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-12-04 | 2018-12-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 67 | 67 | 67 | 67 |  | 18
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 340 | 330 | 330
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 364 | 245 | 412 | 0
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 360 | 360 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 35 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Gas shortage
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Contract expired
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 40 | 48 | 48 |  | 3
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 1 | 0 | 133 | 133 |  | 16 | Engine problem
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 47 | 47 | 47 |  | 61 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 49 | 49 | 49 |  | 31 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 25 | 25 | 25 |  | 8 | Engine problem
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 51 | 51 | 51 |  | 1
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 152 | 300 | 300
35 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 15 | 47 | 149 | 149 |  | 0
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 1756 | 2334 | 3640 | 3907 | 923 | 498
39 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 140 | 150 | 150 | 30 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 130 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
41 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 |  | 0
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 102 | 102 |  | 128
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 148 | 130 | 0 | 130
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 40 | 40 | 40 |  | 11 | Engine problem
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 90 | 90 |  | 10 | Engine problem
| Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 0 | 0 | 74 | 100 | 100 | 100 |  |  | On test
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 10 | 14 | 14
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 6 | 55 | 92 | 92 |  | 16 | Engine problem
| Chattogram area Total |  |  |  |  | 1661 | 1581 | 557 | 860 | 858 | 968 | 210 | 430
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 181 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 265 | 265 | 265 |  | 95 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 334 | 305 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 40 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 15 | 51 | 51 | 51
| Midland 150MW |  | HFO | IPP | 23*7.015 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 40 | 85 | 85 | 85
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 100 | 100 |  | 63
| Chandpur Desh 200MW |  | HFO | IPP | 0 | 0 | 0 | 80 | 186 | 190 | 190 |  |  | On test
65 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
66 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 92 | 118 | 90 | 117
67 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
68 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
69 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 22 | 22
70 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2601 | 2541 | 1380 | 1556 | 1957 | 2034 | 449 | 158
71 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 129 | 118 | 112 | 112
72 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
73 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 78 | 78 | 78 |  | 17 | Engine problem.
74 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 2 | 0
75 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 100 | 200 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 159.6 | 318 | 414 | 412 | 0 | 17
76 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 27 | 27 | 27
77 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 76 | 76 | 76 | 76
78 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
79 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 300 | 308 | 310 | 310 |  | 20 | Machine problem
80 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 53 | 51 | 51
81 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 25 | 50 | 44 | 44
82 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
83 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 41 | 66 | 66
84 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 86 | 86 | 86
85 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 49 | 50 | 50
86 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 100 | 80 | 130 | 130
87 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 20 | 20
88 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 41 | 48 | 50 | 50
89 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 0 | 25
90 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
91 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 851 | 1014 | 1094 | 1119 | 0 | 361
92 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 568 | 687 | 598 | 696
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 83 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 0 | 30
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 80
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
99 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
101 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2278 | 2209 | 568 | 1005 | 958 | 1196 | 0 | 410
102 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
103 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
104 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 26 | 26 | 26 |  | 7 | Engine problem
105 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 185 | 188 | 190 | 190
106 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 42 | 79 | 80 | 80
| Barisal Area Total |  |  |  |  | 472 | 462 | 240 | 341 | 406 | 436 | 0 | 7
107 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 70 | 70 | 70
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
108 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
109 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 48
110 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
111 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
112 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30
113 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 197 | 184 | 197 | 197 |  |  | FGMO
114 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 192 | 187 | 220 | 220 | 0 |  | FGMO
115 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 |  |  | Gas shortage
116 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 250 | 293 | 292 | 292
117 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
118 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
119 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
120 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
121 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 52 | 52 | 52
122 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 749 | 957 | 1069 | 1229 | 0 | 105
123 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
124 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124
125 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
126 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 149 | 150 | 186 | 209 | 85
| Total |  |  |  |  | 17340 | 16742 | 6410.6 | 8534 | 10546 | 11487 | 1791 | 2071
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5933.5985 | 7899 | 9761.2906 | 10632.2724
A. |  | 2018-12-04 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8534 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4933 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8534 | MW
3 | Day peak Generation : |  |  | 6410.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7899 | MW
4 | Evening peak Generation : |  |  | 8534 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 152.7255 | MKWHr | By Solar | 0.12727 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 120.1457 | MKWHr |  | By Oil: | 12.5026 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6631 | MKWHr |  | By Hydro: | 0.955 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1791 | MW | Dhaka | 3001 | 3001 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2071 | MW | Chittagong | 849 | 849 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3862 | MW | Khulna | 956 | 956 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1029.5 | MMCFD |  |  | Rajshahi | 819 | 819 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 85497171.634 | ii) Oil : | Taka | 85062831.93 | Comilla | 676 | 676 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14139566 | Total | Taka | 184699569.564 | Mymensingh | 572 | 572 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 2.573 | MKWHr. | Sylhet | 303 | 303 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -350 | MW at | 19:00 | hrs | Barisal | 200 | 200 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -500 | MW at | 8:00 | hrs | Rangpur | 523 | 523 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.3° C |  |  | Total | 7899 | 7899 |  | 0
B. |  | 2018-12-05 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 24.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11487 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 2687 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 157.4859 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5000 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.2371 | MKWHr. | ii) HVDC Flow at Peak Time |  | 687 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0947 | MKWHr. | iii) Maximum HVDC Flow : |  | 687 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.12 |  | (b) Today: | 100.05 |  | (c) Rule Curve: |  | 105.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-12-04
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 67 | 0 | 120 | 0 | 200 | 0 | 0 | 350 | 363 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 39 | 0 | 150 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 22 | 10 | 100 | 0 | 100 | 265 | 305 | 178 | 8 | 100 | 40 | 5 | 5 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 135 | 0 | 0 | 0 | 26 | 76 | 5 | 5 | 130 | 300 | 54 | 10 | 5 | 100 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 0 |  | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 176 | 0 | 179 | 0 | 11 | 0 | 0 | 0 | 194 | 0 |  | 4177 | 1332 | 5509 | 3672 | 347 | 1195 | 30 | 150 | 39 | 0 | 76 | 0 | 0 | 100.16
2:00 | 67 | 0 | 120 | 0 | 200 | 0 | 0 | 350 | 327 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 39 | 0 | 150 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | 100 | 0 | 100 | 267 | 305 | 197 | 8 | 90 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 136 | 0 | 0 | 0 | 26 | 76 | 5 | 5 | 100 | 300 | 56 | 5 | 5 | 80 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 0 |  | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 178 | 0 | 180 | 0 | 11 | 0 | 0 | 0 | 143 | 0 |  | 4039 | 1251 | 5290 | 3615 | 347 | 1037 | 30 | 150 | 39 | 0 | 72 | 0 | 0 | 100.16
3:00 | 67 | 0 | 120 | 0 | 170 | 0 | 0 | 350 | 247 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | 100 | 0 | 100 | 270 | 305 | 205 | 8 | 90 | 20 | 5 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 117 | 0 | 0 | 0 | 26 | 76 | 5 | 5 | 100 | 298 | 63 | 5 | 5 | 80 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 0 |  | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 174 | 0 | 176 | 0 | 11 | 0 | 0 | 0 | 128 | 0 |  | 3839 | 1228 | 5067 | 3555 | 347 | 871 | 30 | 150 | 40 | 0 | 74 | 0 | 0 | 100.16
4:00 | 67 | 0 | 119 | 0 | 170 | 0 | 0 | 360 | 236 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | 100 | 0 | 100 | 270 | 327 | 195 | 8 | 90 | 20 | 5 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 9 | 72 | 115 | 0 | 0 | 0 | 26 | 76 | 5 | 5 | 100 | 300 | 63 | 5 | 5 | 80 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 164 | 0 | 163 | 0 | 11 | 0 | 0 | 0 | 111 | 0 |  | 3821 | 1194 | 5015 | 3554 | 346 | 823 | 30 | 150 | 40 | 0 | 72 | 0 | 0 | 100.16
5:00 | 67 | 0 | 120 | 0 | 170 | 0 | 0 | 370 | 235 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | 100 | 0 | 100 | 267 | 309 | 198 | 8 | 0 | 20 | 5 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 9 | 70 | 115 | 0 | 0 | 0 | 10 | 63 | 5 | 5 | 130 | 300 | 69 | 5 | 5 | 80 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 26 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 167 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 112 | 0 |  | 3737 | 1196 | 4933 | 3435 | 346 | 853 | 39 | 150 | 40 | 0 | 70 | 0 | 0 | 100.16
6:00 | 67 | 0 | 119 | 0 | 200 | 0 | 0 | 382 | 236 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 0 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 37 | 100 | 0 | 100 | 267 | 301 | 198 | 8 | 0 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 7 | 0 | 0 | 9 | 70 | 160 | 0 | 0 | 0 | 26 | 76 | 5 | 5 | 163 | 299 | 68 | 5 | 5 | 100 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 55 | 0 | 0 |  | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 178 | 0 | 178 | 0 | 11 | 0 | 0 | 0 | 120 | 0 |  | 3982 | 1233 | 5215 | 3618 | 346 | 923 | 68 | 150 | 40 | 0 | 70 | 0 | 0 | 100.12
7:00 | 67 | 0 | 120 | 0 | 250 | 0 | 0 | 382 | 275 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 16 | 0 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 22 | 36 | 100 | 0 | 100 | 265 | 301 | 201 | 8 | 0 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 16 | 8 | 0 | 15 | 72 | 163 | 0 | 0 | 0.1 | 27 | 76 | 5 | 5 | 163 | 304 | 69 | 5 | 5 | 98 | 0 | 39 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.5 | 0 | 105 | 0 | 0 |  | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 193 | 0 | 195 | 0 | 11 | 0 | 0 | 0 | 113 | 0 |  | 4296.6 | 1257 | 5553.6 | 3772 | 345 | 1055 | 118 | 150 | 40 | 0 | 72 | 1.6 | 0 | 100.11
8:00 | 67 | 0 | 120 | 0 | 250 | 0 | 0 | 370 | 384 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 17 | 2 | 0 | 40 | 0 | 150 | 120 | 0 | 0 | 0 | 150 | 0 | 0 | 2 | 0 | 0 | 0 | 6 | 0 | 22 | 19 | 120 | 0 | 135 | 270 | 301 | 189 | 8 | 0 | 40 | 5 | 5 | 6 | 50 | 0 | 0 | 16 | 8 | 0 | 15 | 76 | 148 | 0 | 22 | 0.6 | 27 | 76 | 5 | 5 | 130 | 300 | 61 | 50 | 46 | 78 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.4 | 14 | 118 | 0 | 0 |  | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 189 | 0 | 191 | 0 | 11 | 0 | 0 | 0 | 256 | 0 |  | 4559 | 1456 | 6015 | 3787 | 343 | 1397 | 213 | 150 | 40 | 0 | 76 | 9 | 0 | 100.11
9:00 | 67 | 0 | 120 | 0 | 250 | 0 | 0 | 358 | 260 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 0 | 25 | 24 | 33 | 8 | 40 | 0 | 41 | 0 | 150 | 120 | 0 | 0 | 0 | 150 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 0 | 22 | 5 | 120 | 0 | 120 | 270 | 301 | 184 | 45 | 0 | 37 | 5 | 5 | 26 | 11 | 0 | 0 | 16 | 8 | 0 | 15 | 82 | 133 | 0 | 22 | 1.2 | 26 | 76 | 5 | 5 | 100 | 300 | 68 | 10 | 10 | 78 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 2 | 13.2 | 20 | 120 | 0 | 0 |  | 523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 18 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 183 | 0 | 185 | 0 | 50 | 0 | 0 | 0 | 255 | 0 |  | 4340.4 | 1617 | 5957.4 | 3654 | 523 | 1182 | 311 | 150 | 41 | 0 | 82 | 14.4 | 0 | 100.11
10:00 | 67 | 0 | 120 | 0 | 200 | 0 | 0 | 350 | 260 | 0 | 0 | 300 | 0 | 2 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 10 | 25 | 24 | 33 | 8 | 8 | 0 | 40 | 0 | 150 | 100 | 0 | 0 | 0 | 152 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 0 | 22 | 4 | 100 | 0 | 100 | 260 | 309 | 204 | 45 | 0 | 37 | 5 | 5 | 15 | 11 | 0 | 0 | 16 | 8 | 0 | 15 | 82 | 132 | 0 | 22 | 1.8 | 26 | 76 | 5 | 5 | 100 | 301 | 65 | 0 | 5 | 78 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 17.2 | 20 | 80 | 0 | 0 |  | 684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 18 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 184 | 0 | 187 | 0 | 52 | 0 | 0 | 0 | 250 | 0 |  | 4128 | 1792 | 5920 | 3575 | 684 | 1104 | 266 | 150 | 40 | 0 | 82 | 19 | 0 | 100.11
11:00 | 67 | 0 | 140 | 0 | 200 | 0 | 0 | 380 | 320 | 0 | 0 | 340 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 24 | 33 | 8 | 8 | 0 | 40 | 0 | 140 | 100 | 0 | 0 | 0 | 152 | 0 | 0 | 17 | 0 | 0 | 0 | 6 | 0 | 22 | 5 | 100 | 0 | 100 | 260 | 320 | 204 | 45 | 0 | 37 | 5 | 5 | 15 | 11 | 0 | 0 | 19 | 8 | 0 | 18 | 90 | 130 | 0 | 22 | 2 | 26 | 76 | 5 | 5 | 163 | 298 | 66 | 5 | 5 | 78 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 19.1 | 43 | 80 | 0 | 0 |  | 684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 12 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 16 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 196 | 0 | 52 | 0 | 0 | 0 | 250 | 0 |  | 4401.1 | 1841 | 6242.1 | 3718 | 684 | 1277 | 262 | 150 | 40 | 0 | 90 | 21.1 | 0 | 100.1
12:00 | 67 | 0 | 140 | 0 | 200 | 0 | 0 | 370 | 360 | 0 | 0 | 430 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 22 | 33 | 8 | 8 | 0 | 40 | 0 | 130 | 100 | 0 | 0 | 0 | 148 | 0 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 22 | 5 | 120 | 0 | 100 | 260 | 334 | 202 | 45 | 0 | 37 | 5 | 5 | 15 | 40 | 0 | 0 | 19 | 8 | 0 | 18 | 92 | 129 | 0 | 22 | 1.6 | 26 | 76 | 31 | 25 | 130 | 300 | 64 | 5 | 45 | 100 | 0 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 0 | 74 | 80 | 0 | 0 |  | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 16 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 192 | 0 | 42 | 0 | 0 | 0 | 250 | 0 |  | 4703.6 | 1707 | 6410.6 | 3736 | 568 | 1514 | 308 | 150 | 40 | 1 | 92 | 1.6 | 0 | 100.1
13:00 | 67 | 0 | 141 | 0 | 200 | 0 | 0 | 370 | 310 | 0 | 0 | 400 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 24 | 33 | 8 | 8 | 0 | 40 | 0 | 130 | 100 | 0 | 0 | 0 | 150 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 8 | 100 | 0 | 100 | 255 | 320 | 180 | 45 | 0 | 40 | 5 | 5 | 35 | 40 | 0 | 0 | 19 | 8 | 33 | 18 | 90 | 121 | 0 | 22 | 1.9 | 26 | 76 | 50 | 50 | 100 | 311 | 64 | 5 | 47 | 80 | 18 | 42 | 10 | 0 | 15 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 17.5 | 80 | 50 | 0 | 0 |  | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 199 | 0 | 190 | 0 | 42 | 0 | 0 | 0 | 290 | 0 |  | 4673.4 | 1738 | 6411.4 | 3735 | 568 | 1523 | 284 | 150 | 40 | 2 | 90 | 19.4 | 0 | 100.1
14:00 | 67 | 0 | 140 | 0 | 200 | 0 | 0 | 359 | 270 | 0 | 0 | 340 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 24 | 33 | 8 | 8 | 0 | 40 | 0 | 120 | 100 | 0 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 3 | 100 | 0 | 100 | 255 | 301 | 183 | 11 | 0 | 20 | 5 | 5 | 51 | 10 | 0 | 0 | 19 | 8 | 33 | 18 | 94 | 123 | 0 | 22 | 1.3 | 26 | 76 | 50 | 20 | 100 | 311 | 63 | 5 | 48 | 78 | 19 | 42 | 10 | 0 | 15 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 15 | 100 | 50 | 0 | 0 |  | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 174 | 0 | 182 | 0 | 44 | 0 | 0 | 0 | 290 | 0 |  | 4437.3 | 1742 | 6179.3 | 3623 | 606 | 1341 | 304 | 150 | 40 | 5 | 94 | 16.3 | 0 | 0
15:00 | 67 | 0 | 63 | 0 | 200 | 0 | 0 | 375 | 270 | 0 | 0 | 340 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 23 | 33 | 8 | 8 | 0 | 40 | 0 | 120 | 100 | 0 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 3 | 100 | 0 | 100 | 250 | 342 | 204 | 8 | 0 | 40 | 5 | 5 | 51 | 11 | 0 | 0 | 19 | 8 | 33 | 18 | 88 | 119 | 0 | 22 | 0 | 25 | 75 | 53 | 20 | 100 | 311 | 63 | 5 | 48 | 80 | 19 | 10 | 10 | 0 | 15 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 10.6 | 100 | 50 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 149 | 0 | 0 | 140 | 0 | 192 | 0 | 43 | 0 | 0 | 0 | 290 | 0 |  | 4408.6 | 1797 | 6205.6 | 3610 | 687 | 1309 | 304 | 149 | 40 | 8 | 88 | 10.6 | 0 | 0
16:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 383 | 270 | 0 | 0 | 370 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 23 | 33 | 8 | 8 | 0 | 40 | 0 | 120 | 100 | 0 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 0 | 7 | 6 | 0 | 22 | 3 | 100 | 0 | 100 | 255 | 316 | 191 | 8 | 0 | 40 | 5 | 5 | 51 | 11 | 0 | 0 | 19 | 8 | 33 | 18 | 82 | 120 | 0 | 22 | 0.4 | 27 | 75 | 53 | 20 | 100 | 310 | 64 | 5 | 48 | 80 | 19 | 10 | 10 | 0 | 15 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 5 | 100 | 50 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 186 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 158 | 0 | 195 | 0 | 42 | 0 | 0 | 0 | 290 | 0 |  | 4480.4 | 1838 | 6318.4 | 3687 | 687 | 1341 | 311 | 150 | 40 | 15 | 82 | 5.4 | 0 | 0
17:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 385 | 300 | 0 | 0 | 400 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 31 | 0 | 0 | 36 | 18 | 36 | 19 | 25 | 24 | 33 | 16 | 8 | 0 | 40 | 0 | 120 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 23 | 50 | 20 | 2 | 22 | 11 | 100 | 0 | 100 | 255 | 323 | 193 | 8 | 0 | 40 | 5 | 5 | 51 | 11 | 0 | 1 | 19 | 8 | 33 | 18 | 94 | 119 | 14 | 22 | 0 | 27 | 76 | 11 | 20 | 100 | 309 | 64 | 5 | 48 | 80 | 19 | 11 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 21 | 0 | 15 | 0.2 | 100 | 50 | 0 | 0 |  | 687 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 9 | 44 | 0 | 187 | 20 | 33 | 0 | 0 | 55 | 0 | 0 | 30 | 12 | 0 | 0 | 8 | 13 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 182 | 0 | 194 | 0 | 43 | 0 | 0 | 0 | 242 | 105 |  | 4767.2 | 2060 | 6827.2 | 3758 | 687 | 1328 | 651 | 150 | 40 | 119 | 94 | 0.2 | 0 | 0
18:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 369 | 353 | 0 | 0 | 400 | 0 | 7 | 12 | 44 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 47 | 0 | 18 | 54 | 54 | 36 | 19 | 25 | 24 | 33 | 16 | 51 | 0 | 40 | 0 | 120 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 68 | 50 | 55 | 28 | 22 | 4 | 100 | 0 | 100 | 255 | 327 | 197 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 16 | 19 | 8 | 33 | 22 | 116 | 118 | 78 | 22 | 0 | 27 | 76 | 51 | 35 | 130 | 308 | 65 | 86 | 48 | 80 | 19 | 46 | 10 | 0 | 25 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 43 | 0 | 100 | 119 | 0 | 0 |  | 687 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 28 | 60 | 40 | 188 | 26 | 48 | 0 | 0 | 70 | 0 | 0 | 51 | 50 | 0 | 0 | 43 | 32 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 187 | 0 | 189 | 0 | 45 | 0 | 0 | 0 | 290 | 105 |  | 5830 | 2382 | 8212 | 3771 | 687 | 1705 | 1504 | 150 | 40 | 239 | 116 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 364 | 360 | 0 | 0 | 400 | 0 | 0 | 35 | 55 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 47 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 40 | 0 | 140 | 130 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 68 | 50 | 55 | 50 | 22 | 10 | 100 | 0 | 100 | 265 | 305 | 181 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 22 | 118 | 118 | 78 | 22 | 0 | 27 | 76 | 53 | 50 | 130 | 308 | 41 | 86 | 49 | 80 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 152 | 0 | 0 | 100 | 0 | 47 | 0 | 100 | 186 | 0 | 0 |  | 687 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 30 | 60 | 40 | 188 | 26 | 48 | 0 | 0 | 70 | 0 | 0 | 51 | 50 | 0 | 0 | 52 | 32 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 184 | 0 | 187 | 0 | 79 | 0 | 0 | 0 | 293 | 105 |  | 6082 | 2452 | 8534 | 3763 | 687 | 1775 | 1761 | 149 | 40 | 241 | 118 | 0 | 0 | 0
19:30 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 367 | 360 | 0 | 0 | 400 | 0 | 0 | 48 | 55 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 46 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 40 | 0 | 150 | 130 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 51 | 50 | 12 | 50 | 22 | 26 | 100 | 0 | 100 | 260 | 331 | 193 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 22 | 116 | 107 | 78 | 22 | 0 | 26 | 76 | 53 | 50 | 130 | 308 | 63 | 86 | 49 | 77 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 150 | 0 | 0 | 50 | 0 | 17 | 0 | 100 | 190 | 0 | 0 |  | 687 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 34 | 56 | 40 | 186 | 25 | 48 | 0 | 0 | 65 | 0 | 0 | 8 | 50 | 0 | 0 | 52 | 31 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 178 | 0 | 178 | 0 | 85 | 0 | 0 | 0 | 292 | 105 |  | 6023 | 2340 | 8363 | 3794 | 687 | 1795 | 1602 | 149 | 40 | 180 | 116 | 0 | 0 | 0
20:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 356 | 360 | 0 | 0 | 400 | 0 | 0 | 48 | 55 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 44 | 54 | 55 | 0 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 40 | 0 | 150 | 130 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 51 | 10 | 12 | 50 | 22 | 30 | 100 | 0 | 100 | 260 | 312 | 188 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 22 | 118 | 106 | 78 | 22 | 0 | 25 | 76 | 53 | 50 | 130 | 310 | 60 | 86 | 49 | 77 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 150 | 0 | 0 | 50 | 0 | 15 | 0 | 100 | 194 | 0 | 0 |  | 687 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 34 | 48 | 40 | 184 | 26 | 48 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 31 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 177 | 0 | 180 | 0 | 85 | 0 | 0 | 0 | 292 | 105 |  | 5867 | 2329 | 8196 | 3760 | 687 | 1800 | 1478 | 149 | 40 | 164 | 118 | 0 | 0 | 0
21:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 350 | 360 | 0 | 0 | 400 | 0 | 0 | 48 | 55 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 46 | 0 | 46 | 54 | 55 | 0 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 41 | 0 | 150 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 51 | 10 | 12 | 46 | 22 | 34 | 100 | 0 | 100 | 260 | 305 | 188 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 22 | 108 | 108 | 77 | 22 | 0 | 25 | 76 | 53 | 50 | 130 | 312 | 68 | 86 | 49 | 77 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 55 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 192 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 40 | 188 | 25 | 48 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 182 | 0 | 85 | 0 | 0 | 0 | 292 | 105 |  | 5618 | 2225 | 7843 | 3638 | 687 | 1803 | 1332 | 149 | 41 | 85 | 108 | 0 | 0 | 0
22:00 | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 350 | 363 | 0 | 0 | 400 | 0 | 0 | 15 | 55 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 46 | 54 | 55 | 0 | 22 | 25 | 24 | 33 | 25 | 25 | 0 | 41 | 0 | 150 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 28 | 10 | 10 | 37 | 22 | 38 | 100 | 0 | 100 | 265 | 301 | 181 | 8 | 0 | 40 | 5 | 5 | 51 | 86 | 0 | 0 | 19 | 8 | 33 | 22 | 98 | 109 | 40 | 22 | 0 | 27 | 76 | 53 | 50 | 100 | 312 | 49 | 86 | 49 | 78 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 50 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 178 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 169 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 173 | 0 | 177 | 0 | 91 | 0 | 0 | 0 | 293 | 6 |  | 5305 | 1960 | 7265 | 3576 | 687 | 1787 | 898 | 150 | 41 | 28 | 98 | 0 | 0 | 100.08
23:00 | 67 | 0 | 0 | 0 | 320 | 0 | 0 | 350 | 362 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 42 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 39 | 100 | 0 | 100 | 265 | 301 | 181 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 90 | 110 | 0 | 22 | 0 | 27 | 76 | 53 | 50 | 100 | 312 | 64 | 86 | 49 | 79 | 20 | 47 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 101 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 174 | 0 | 177 | 0 | 91 | 0 | 0 | 0 | 292 | 0 |  | 4613 | 1873 | 6486 | 3456 | 687 | 1753 | 308 | 150 | 42 | 0 | 90 | 0 | 0 | 100.07
24:00 | 67 | 0 | 0 | 0 | 320 | 0 | 0 | 350 | 364 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 25 | 0 | 0 | 42 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 10 | 100 | 0 | 100 | 265 | 301 | 182 | 8 | 0 | 40 | 5 | 5 | 6 | 50 | 0 | 0 | 19 | 8 | 8 | 22 | 84 | 113 | 0 | 22 | 0 | 27 | 76 | 5 | 5 | 100 | 311 | 66 | 5 | 49 | 77 | 0 | 7 | 0 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 101 | 0 | 0 |  | 687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 175 | 0 | 176 | 0 | 45 | 0 | 0 | 0 | 291 | 0 |  | 4158 | 1800 | 5958 | 3384 | 687 | 1357 | 254 | 150 | 42 | 0 | 84 | 0 | 0 | 100.12
KWH | 1478000 | 0 | 1871000 | 0 | 5958345 | 0 | 0 | 8840090 | 7479000 | 0 | 0 | 8822225 | 0 | 72960 | 173088 | 424477 | 0 | 0 | 0 | 0 | 0 | 350640 | 12960 | 0 | 257280 | 0 | 222096 | 472680 | 474403 | 94000 | 239760 | 600000 | 545220 | 826100 | 374700 | 387840 | 0 | 955000 | 0 | 3300000 | 2400000 | 131040 | 0 | 0 | 3094801 | 0 | 0 | 581280 | 0 | 288224 | 194520 | 284160 | 221760 | 440880 | 451680 | 2530816 | 0 | 2454410 | 6491000 | 7562500 | 4655000 | 368000 | 443990 | 848448 | 150720 | 120000 | 776313 | 173088 | 0 | 107650 | 334620 | 149040 | 370200 | 442340 | 2094720 | 2917280 | 408000 | 375228 | 10900 | 612000 | 1798800 | 621000 | 500000 | 3161078 | 6623200 | 1491000 | 725760 | 720360 | 2033490 | 221000 | 526440 | 116280 | 0 | 430248 | 252192 | 0 | 584620 | 0 | 0 | 513600 | 0 | 259200 | 116370 | 1323840 | 2160000 | 0 | 0 |  | 13237090 | 0 | 0 | 0 | 176640 | 0 | 0 | 0 | 117600 | 214400 | 192000 | 4348547 | 426300 | 214080 | 0 | 0 | 1350000 | 0 | 0 | 113480 | 346120 | 0 | 0 | 497280 | 98859 | 323760 | 77832 | 107172 | 0 | 0 | 3663100 | 0 | 0 | 4562709 | 0 | 4605682 | 0 | 1024512 | 0 | 0 | 0 | 5601545 | 531840 |  | 110894950 | 41830548 | 152725498 | 87979808 | 13237090 | 32165893 | 11657094 | 3663100 | 955000 | 845523 | 2094720 | 127270 | 0
Fuel Cost | 1271080 | 0 | 1609060 | 0 | 3813340.8 | 0 | 0 | 5392454.9 | 4562190 | 0 | 0 | 5910890.75 | 0 | 458188.8 | 1156227.84 | 2593554.47 | 0 | 0 | 0 | 0 | 0 | 2310717.6 | 125323.2 | 0 | 1541107.2 | 0 | 1481380.32 | 3370208.4 | 2965018.75 | 589380 | 179820 | 450000 | 0 | 0 | 0 | 3668966.4 | 0 | 0 | 0 | 3630000 | 2640000 | 1240948.8 | 0 | 0 | 3559021.15 | 0 | 0 | 5109451.2 | 0 | 2804419.52 | 1204078.8 | 1835673.6 | 1450310.4 | 374748 | 0 | 2303042.56 | 0 | 2233513.1 | 4024420 | 5218125 | 3258500 | 253920 | 426230.4 | 568460.16 | 129619.2 | 110400 | 636576.66 | 164433.6 | 0 | 798763 | 257657.4 | 111780 | 285054 | 331755 | 14327884.8 | 2187960 | 3749520 | 288925.56 | 0 | 636480 | 1870752 | 596160 | 450000 | 2465640.84 | 4636240 | 1699740 | 776563.2 | 792396 | 2318178.6 | 282880 | 489589.2 | 108140.4 | 0 | 322686 | 191665.92 | 0 | 4244341.2 | 0 | 0 | 3672240 | 0 | 0 | 0 | 0 | 20174400 | 0 | 0 |  | 67509159 | 0 | 0 | 0 | 1464345.6 | 0 | 0 | 0 | 1324176 | 2525632 | 1512960 | 3000497.43 | 422037 | 1584192 | 0 | 0 | 1417500 | 0 | 0 | 1016780.8 | 2993938 | 0 | 0 | 4933017.6 | 1163570.43 | 356136 | 73162.08 | 81129.204 | 0 | 0 | 14139566 | 0 | 0 | 3102642.12 | 0 | 3223977.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 154692194.7 | 111844418.664 | 266536613.364 | 67199316.704 | 67509159 | 18297854.93 | 76102929.98 | 14139566 | 0 | 8959901.95 | 14327884.8 | 0 | 0
Yesterday Day Peak | 67 | 0 | 140 | 0 | 200 | 0 | 0 | 370 | 360 | 0 | 0 | 430 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 19 | 25 | 22 | 33 | 8 | 8 | 0 | 40 | 0 | 130 | 100 | 0 | 0 | 0 | 148 | 0 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 22 | 5 | 120 | 0 | 100 | 260 | 334 | 202 | 45 | 0 | 37 | 5 | 5 | 15 | 40 | 0 | 0 | 19 | 8 | 0 | 18 | 92 | 129 | 0 | 22 | 1.6 | 26 | 76 | 31 | 25 | 130 | 300 | 64 | 5 | 45 | 100 | 0 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 0 | 74 | 80 | 0 | 0 |  | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 16 | 0 | 22 | 5 | 0 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 192 | 0 | 42 | 0 | 0 | 0 | 250 | 0 |  | 6410.6 | DayPeak
Yesterday Evening Peak | 67 | 0 | 0 | 0 | 340 | 0 | 0 | 364 | 360 | 0 | 0 | 400 | 0 | 0 | 35 | 55 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 47 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 40 | 0 | 140 | 130 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 68 | 50 | 55 | 50 | 22 | 10 | 100 | 0 | 100 | 265 | 305 | 181 | 8 | 0 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 22 | 118 | 118 | 78 | 22 | 0 | 27 | 76 | 53 | 50 | 130 | 308 | 41 | 86 | 49 | 80 | 20 | 48 | 10 | 0 | 25 | 11 | 0 | 152 | 0 | 0 | 100 | 0 | 47 | 0 | 100 | 186 | 0 | 0 |  | 687 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 30 | 60 | 40 | 188 | 26 | 48 | 0 | 0 | 70 | 0 | 0 | 51 | 50 | 0 | 0 | 52 | 32 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 184 | 0 | 187 | 0 | 79 | 0 | 0 | 0 | 293 | 105 |  | 8534 | EvPeak
Forecast for Evening | 67 | 0 | 0 | 0 | 330 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 47 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 42 | 60 | 150 | 0 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 85 | 68 | 90 | 92 | 50 | 22 | 14 | 100 | 0 | 100 | 265 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 8 | 33 | 22 | 117 | 112 | 78 | 22 | 0 | 27 | 76 | 51 | 44 | 163 | 310 | 66 | 86 | 50 | 130 | 20 | 50 | 10 | 0 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 190 | 0 |  |  | 696 | 30 | 0 | 0 | 115 | 0 | 0 | 0 | 30 | 80 | 40 | 190 | 26 | 110 | 30 | 0 | 70 | 50 | 48 | 100 | 50 | 50 | 30 | 52 | 32 | 22 | 5 | 11 | 0 | 0 | 150 | 18 | 18 | 197 | 0 | 220 | 0 | 80 | 100 | 0 | 0 | 292 | 105
Forecast for Day | 67 | 0 | 0 | 0 | 330 | 0 | 0 | 245 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 47 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 25 | 51 | 0 | 42 | 60 | 150 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 40 | 85 | 68 | 90 | 92 | 50 | 22 | 14 | 100 | 0 | 100 | 265 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 22 | 90 | 112 | 78 | 22 | 2 | 27 | 76 | 51 | 44 | 163 | 310 | 66 | 86 | 50 | 130 | 20 | 50 | 10 | 0 | 0 | 11 | 200 | 300 | 300 | 0 | 200 | 100 | 149 | 20 | 100 | 190 | 0 |  |  | 598 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 26 | 110 | 0 | 0 | 70 | 0 | 0 | 100 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 |  | 0 | 197 | 0 | 220 | 0 | 80 | 100 | 0 | 0 | 292 | 105
Generation at 08:00(Today) | 67 | 0 | 0 | 0 | 330 | 0 | 0 | 245 | 320 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 23 | 0 | 0 | 42 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 22 | 14 | 100 | 0 | 100 | 265 | 360 | 202 | 8 | 0 | 40 | 5 | 5 | 22 | 40 | 0 | 0 | 16 | 8 | 33 | 18 | 72 | 112 | 0 | 22 | 0.4 | 27 | 76 | 51 | 40 | 100 | 312 | 69 | 86 | 47 | 78 | 20 | 46 | 10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.9 | 90 | 34 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 188 | 0 | 190 | 0 | 60 | 0 | 0 | 0 | 292 | 0 | 0
199
| Minimum Generation |  | 4933 | 5:00
| Highest Generation |  | 8534 | 19:00
| Day Peak Generation |  | 6410.6 | 12:00
| Evening Peak Generation |  | 8534 | 19:00
| HVDC Max Flow |  | 687 | 15:00
| HVDC EvPeak Flow |  | 687 | 19:00
| Load factor L.F |  | 74.57%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-12-05
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-12-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6410.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5000 | MW
Evening Peak Generation : |  | 8534 | MW Hour : | 19:00 | Available Max Generation : |  | 11487 | MW
E.P. Demand (at gen end) : |  | 8534 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 8534 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2687 | MW
Total Gen. (MKWH) : |  | 152.7255 | System Load Factor : | 74.57% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -500 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-12-05
Actual : | 100.05 | Ft.(MSL) , | Rule curve : | 105.6 | Ft.( MSL )
Gas Consumed : | Total = | 1029.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 85497171.634
|  | Coal : | 14139566 | Oil : | 85062831.93 | Total : | 184699569.564
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3047.5336 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1029.8021 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 921.5053 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 832.2448 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 752.3153 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 607.0754 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 347.8472 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 156.5279 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 468.1665 |  |  | 0 | 0%
Total | 0 |  | 8163.0181 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Ghorasal Max
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Ghorasal Regent 108
|  |  |  | 3) Ghorasal Unit-3,4,5 |  | 12) Siddhirganj GT-1,2
4) Tongi GT
5) Bheramara-410 MW ST
6) Baghabari 100 MW
7) Siddhirganj ST 210 MW
8) Siddhirganj 335 MW
9) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Kaptai-Hathazari 132 kV Ckt-2 was under shut down from 08:25 to 15:34 for A/M.
b) Julda-Shahmirpur 132 kV Ckt-2 was under shut down from 08:26 to 20:40 for A/M.
c) Aminbazar 230/132 kV TR-1 transformer was under shut down from 09:56 to 15:59 for A/M.
d) New Tongi-Tongi 132 kV Ckt-2 was under shut down from 08:44 to 14:59 for A/M.
e) Joydevpur 132/33 kV T-2 transformer was under shut down from 09:33 to 14:14 for A/M.
f) Haripur-Bhulta-Rampura 230 kV Ckt-2 was under shut down from 08:53 to 16:13 for A/M.
g) Bhulta-Rampura 230 kV Ckt-3 was under shut down from 09:10 to 13:58 for A/M.
h) Dohazari-Sikalbaha 132 kV Ckt-1 is under shut down since 09:26 for D/W.
i) Manikganj-Kabirpur 132 kV Ckt-2 with T-2 transformer was under shut down from 08:26 to 16:35 for A/M.
j) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 08:42 to 14:0 for A/M.
k) Sylhet-Chatak 132 kV Ckt-2 was under shut down from 08:58 to 11:59 for A/M.
l) Sreemongal-Fenchuganj 132 kV Ckt-1 was under shut down from 09:28 to 16:30 for A/M.
m) Sikalbaha-TK Chemical 132 kV Ckt was under shut down from 09:25 to 15:15 for D/W.
n) Bhulta 400/230 kV T-1 & T-2 transformers were under shut down at 10:00 & 12:51 for D/W and were
switched on at 12:37 & 15:24 respectively.
o) Biyanibazar 132/33 kV T-2 transformer was under shut down from 10:00 to 13:15 for D/W.
p) Natore-Ishurdi 132 kV Ckt-2 was under shut down from 08:11 to 16:25 for A/M.
q) Palashbari 132/33 kV T-3 transformer was under shut down from 09:14 to 14:50 for A/M.
r) Barishal-Bhola 230 kV Ckt-2 was under shut down from 08:51 to 16:31 for A/M.
s) Noapara 132/33 kV T-4 transformer was under shut down from 09:02 to 12:48 for A/M.
t) Jessore 132/33 kV T-1 transformer was under shut down from 08:18 to 15:37 for A/M.
u) Barishal 132/33 kV T-2 transformer was under shut down from 08:32 to 09:12 for new auxiliary transformer |  |  |  | About 20 MW power interruption occurred under Barishal S/ S
connection. |  |  |  | area from 08:32 to 09:12.
v) Meghnaghat-Cumilla(N) 230 kV Ckt-2 was under shut down from 08:55 to 16:58 for A/M.
w) Fenchuganj P/S-Sylhet 132 kV Ckt-1 & 2 were under shut down from 12:11 & 13:15 to 13:07 & 14:16 for A/M.
x) Khulna © 132/33 kV T-3 transformer was under shut down from 10:25 to 14:57 for relay test.
y) Bheramara HVDC P1 tripped at 10:59 due to converter transformer trip and was switched on at 13:35.
z) Baghabari-71 MW was synchronized at 10:03.
aa) Raozan #2 was forced shut down at 20:52 due to boiler problem.
ab) Sikalbaha-150 MW GT was shut down at 22:56 due to heat exchanger leakage.
ac) Haripur EGCB-412 MW CCPP ST tripped at 00:51(5/12/18) due to pre heater leakage.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-12-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 67 | 1478000
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 1871000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 5958345
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 364 | 8840090 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 360 | 7479000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8822225
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 72960 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 35 | 173088 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 424477
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 239760
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 350640
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 222096
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 472680
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 12960 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 474403
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 94000 | Low demand
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 47 | 257280 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1145220 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 826100
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 374700 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 387840
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 152 | 584620 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 47 | 259200 | Low demand
| Dhaka area Total |  |  |  | 5848 | 2334 | 40820684
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 140 | 3300000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 130 | 2400000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 131040
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 116370 | Reserve
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 221760
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 955000 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Combustion inspection.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3094801 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 581280 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 288224
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 194520 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 0 | 100 | 1323840 | On test
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 440880
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 451680
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 55 | 284160 | Low demand
| Chattogram area Total |  |  |  | 1581 | 860 | 13783555
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2530816 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2454410 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 181 | 4655000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 6491000 | ST Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7562500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 848448 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 150720 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 368000 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 776313
| Midland 150MW |  | IPP | 23*7.015 | 0 | 0 | 0 | On test
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 173088
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 443990 | Machine problem
| Chandpur Desh 200MW |  | IPP | 0 | 0 | 186 | 2160000 | On Test
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 334620
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 149040 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 118 | 2094720
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 370200
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 25 | 107650 | Line over load
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 442340
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2541 | 1556 | 32232855
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 118 | 2917280 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 375228
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 78 | 408000 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 10900
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 100 | 513600 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 318 | 4225008
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 27 | 612000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 76 | 1798800
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3161078 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 308 | 6623200
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 621000
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 500000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 252192
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 41 | 1491000
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 725760
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 720360
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 80 | 2033490
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 20 | 221000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 48 | 526440
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 430248
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 116280
| Sylhet Area Total |  |  |  | 1549 | 1014 | 19832848
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 687 | 13237090
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 176640 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 30 | 117600
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 214400
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 192000
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 531840
| Khulna Area Total |  |  |  | 2209 | 1005 | 14469570
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 48 | 214080 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 426300 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 188 | 4348547
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 79 | 1024512 | Machine problem
| Barisal Area Total |  |  |  | 462 | 341 | 6013439
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 70 | 1350000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 346120
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4562709 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4605682 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 293 | 5601545 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 32 | 98859
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 323760
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 77832 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 107172
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 497280
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 51 | 113480 | Low demand
| Rajshahi Area Total |  |  |  | 1546 | 957 | 17684439
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3663100
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 149 | 3663100
| Total |  |  |  | 16742 | 8534 | 152725498
| Eastern Grid Total |  |  |  | 12041 | 6082 | 110894950
| Western Grid Total |  |  |  | 4701 | 2452 | 41830548
| National Grid Total |  |  |  | 16742 | 8534 | 152725498
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-12-04 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5401 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2498 | MW
i) Dhaka area |  |  | 3001 | MW | i) Khulna area |  |  | 956 | MW
ii) Chittagong area |  |  | 849 | MW | ii) Rajshahi area |  |  | 819 | MW
iii) Comilla area |  |  | 676 | MW | iii) Barisal area |  |  | 200 | MW
iv) Mymensingh area |  |  | 572 | MW | iv) Rangpur area |  |  | 523 | MW
v) Sylhet area |  |  | 303 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7899 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 1100 | Netrokona | 58 | 1800 | Goalpara | 31 | 1830
Munsiganj | 70 | 1900 | Jamalpur | 89 | 1900 | Central s/s | 54 | 1800
Sonargaon | 51 | 1900 | Sherpur | 64 | 1800 | Noapara | 68 | 1900
Shyampur | 148 | 1000 | Srimongal | 25 | 1830 | Jessore | 104 | 1900
Bhulta | 143 | 1830 | Shahjibazar | 79 | 1830 | Jhenida | 73 | 1800
Madanganj | 44 | 1800 | Fenchuganj | 28 | 1830 | Bottail | 78 | 1800
Shitalakhya | 84 | 1700 | Kulawara | 28 | 1830 | G.K Project | 32 | 1800
Rahim steel | 12 | 1200 | Sylhet | 90 | 1830 | Faridpur | 118 | 1900
Matuail | 82 | 1000 | Chatak | 19 | 1800 | Madaripur | 89 | 2000
Ghorasal | 59 | 1900 | Sunamganj | 23 | 2000 | Gopalganj | 52 | 1900
Narsingdi | 96 | 1800 | Biani Bazar | 28 | 1930 | Bagerhat | 61 | 1900
Haripur (SBU) | 97 | 1000 | Comilla (S) | 118 | 1830 | Mongla | 32 | 800
Ullon | 56 | 1800 | Comilla(N) | 69 | 1800 | Satkhira | 63 | 1830
Hasnabad | 143 | 1800 | Chandpur | 76 | 2000 | Gallamari | 28 | 1830
Magbazar | 87 | 1800 | Feni | 81 | 1800 | Magura | 34 | 1800
Maniknagar | 72 | 1500 | Chowmuhani | 126 | 1900 | Chuadanga | 68 | 1900
Bangabhaban | 24 | 1500 | Ashuganj | 39 | 1900 | Barisal | 86 | 1900
Narinda | 66 | 1300 | Daudkandi | 80 | 1930 | Patuakhali | 62 | 1930
Dhanmondi | 86 | 1300 | B.Baria | 84 | 2000 | Bhandaria | 38 | 1900
Lalbag | 72 | 1800 | Ramganj | 24 | 2000 | Ishurdi | 38 | 1800
Madartek | 40 | 1830 | Madunaghat | 46 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 83 | 1800 | Hathazari | 70 | 1800 | Natore | 82 | 1800
Kalyanpur | 81 | 1800 | Khulshi | 172 | 1300 | Bogra | 174 | 1800
Gulshan | 88 | 1800 | Halishahar | 97 | 1100 | Noagaon | 82 | 1900
Uttara | 58 | 1800 | Baraulia | 125 | 100 | Rajshahi | 95 | 1830
Uttara(New) | 5 | 1800 | Sikalbaha | 26 | 1900 | C.Nawabganj | 46 | 1830
Kamrangirchar | 70 | 1300 | Dohazari | 68 | 1800 | Amnura | 27 | 1800
Savar | 106 | 1800 | Cox'sbazar | 55 | 1800 | Pabna | 72 | 1800
Bhasantec | 108 | 1800 | Chandraghona | 19 | 1800 | Shahjadpur | 73 | 1800
Agargaon | 39 | 1300 | Kaptai | 3.2 | 1830 | Serajganj | 69 | 1830
Satmosjid | 63 | 1800 | A. Khaer Stl. | 8 | 1200 | Niyamatpur | 38 | 1830
Tongi | 83 | 1100 | Bakulia | 75 | 1800 | Joypurhat | 39 | 1830
Kabirpur | 125 | 1800 | Julda | 17 | 900 | Rangpur | 101 | 1830
Basundhara | 90 | 1800 | TK chemical | 4.8 | 1100 | Lalmonirhat | 73 | 1800
Manikganj | 58 | 1830 | Modern Steel | 13 | 1700 | Saidpur | 102 | 1830
Joydevpur | 185 | 1900 | Shahmirpur | 19.5 | 1800 | Purbasadipur | 72 | 1930
New Tongi | 99 | 1200 | Khagrachhari | 14 | 1800 | Thakurgaon | 57 | 1800
Korda | 211 | 1000 | Matarbari | 19 | 1830 | Palashbari | 81 | 1830
Dhamrai | 40 | 1800 | Baroiar Hat | 19 | 1800 | Barapukuria | 37 | 1800
Tangail | 117 | 1800 | Rangamati | 8 | 1800 | Panchagar | 32 | 1830
Mymensing | 180 | 1900 | Abul Khair 230 | 13 | 1830
Kishorganj | 66 | 1830 | BSRM | 103 | 200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-12-04
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 396 | 24:00 | 381 | 14:00 | Kaliakoir | 381 | 3:00 | 364 | 12:00
Bheramara | 412 | 3:00 | 400 | 12:00 | Bhulta | 401 | 2:00 | 389 | 16:00
Ashuganj(N) | 404 | 3:00 | 392 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 18:00 | 213 | 11:00
Ishurdi | 237 | 2:00 | 225 | 7:00 | Megnaghat | 230 | 7:00 | 223 | 12:00
Ashuganj | 239 | 20:00 | 232 | 10:00 | Fenchuganj | 242 | 22:00 | 235 | 10:00
Serajganj | 226 | 1:00 | 223 | 19:00 | Siddhirganj | 230 | 1:00 | 220 | 15:00
Baghabari | 230 | 1:00 | 222 | 18:00 | Maniknagar | 228 | 3:00 | 219 | 15:00
Barapukuria | 234 | 1:00 | 221 | 18:00 | Old Airport | 229 | 2:00 | 218 | 11:00
Bogra | 229 | 1:00 | 218 | 18:00 | Barisal | 236 | 17:00 | 225 | 12:00
Khulna South | 238 | 17:00 | 222 | 7:00 | AKSML | 224 | 19:00 | 216 | 10:00
Rampura | 228 | 1:00 | 220 | 11:00 | BSRM | 226 | 18:00 | 218 | 11:00
Haripur | 228 | 1:00 | 220 | 10:00 | Bibiyana | 238 | 2:00 | 230 | 12:00
Hasnabad | 230 | 3:00 | 218 | 12:00 | Bhulta | 230 | 2:00 | 221 | 12:00
Aminbazar | 228 | 1:00 | 218 | 12:00 | Ashuganj (S) | 240 | 3:00 | 233 | 10:00
Tongi | 227 | 19:30 | 218 | 11:00 | Kaliakoir | 232 | 3:00 | 220 | 12:00
Comilla (N) | 236 | 7:00 | 231 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 100 | 128 | 1100 | Ramganj | 135 | 900 | 132 | 700
Munsiganj | 137 | 2000 | 128 | 1200 | Madanhat | 134 | 1900 | 129 | 1100
Megnaghat | 133 | 100 | 128 | 1200 | Hathazari | 134 | 1830 | 128 | 1000
Shyampur | 128 | 100 | 123 | 1100 | Khulshi | 131 | 1830 | 124 | 1000
Bhulta | 133 | 1800 | 128 | 1100 | Halishahar | 135 | 1900 | 126 | 1000
Madanganj | 136 | 700 | 128 | 1200 | Baraulia | 132 | 1830 | 125 | 1100
Shitalakhya | 140 | 1900 | 128 | 1200 | Sikalbaha | 133 | 1900 | 127 | 1300
Rahim steal | 134 | 100 | 129 | 1200 | Dohazari | 132 | 1830 | 126 | 900
Matuail | 133 | 100 | 127 | 1200 | Cox'sbazar | 128 | 1900 | 122 | 1000
Ghorasal | 138 | 900 | 135 | 100 | Chandraghona | 133 | 1800 | 129 | 1300
Narsinghdi | 136 | 2000 | 133 | 100 | Kaptai | 135 | 1900 | 128 | 1500
Haripur (SBU) | 137 | 1000 | 129 | 1200 | A. Khaer Stl. | 131 | 1800 | 126 | 1000
Ullon | 136 | 100 | 130 | 1000 | Bakulia | 131 | 1800 | 124 | 1000
Hasnabad | 137 | 500 | 129 | 1200 | Julda | 133 | 1800 | 124 | 1000
Magbazar | 136 | 100 | 130 | 1200 | TK Chemical | 132 | 500 | 128 | 1400
Maniknagar | 137 | 300 | 131 | 1200 | Modern Steel | 132 | 1900 | 125 | 1100
Bangabhaban | 137 | 300 | 126 | 1100 | Shahmirpur | 132 | 1800 | 124 | 1000
Narinda | 137 | 300 | 129 | 1200 | Khagrachhari | 133 | 1900 | 127 | 1000
Dhanmondi | 136 | 100 | 130 | 1000 | Matarbari | 120 | 500 | 122 | 1600
Lalbag | 137 | 300 | 126 | 1100 | Baroiar Hat | 133 | 100 | 129 | 1500
Madartek | 137 | 300 | 129 | 1200 | Rangamati | 133 | 1900 | 127 | 1000
Mirpur | 137 | 600 | 129 | 1300 | Goalpara | 136 | 1700 | 125 | 1200
Kalyanpur | 139 | 600 | 131 | 1200 | Central s/s | 136 | 1700 | 125 | 1200
Gulshan | 136 | 600 | 128 | 1200 | Noapara | 135 | 1700 | 123 | 1300
Uttara | 138 | 400 | 130 | 1200 | Jessore | 130 | 300 | 122 | 1200
Uttara(New) | 136 | 600 | 128 | 1200 | Jhenida | 134 | 100 | 125 | 800
Kamrangirchar | 136 | 600 | 125 | 1200 | Bottail | 138 | 200 | 130 | 1300
Savar | 135 | 600 | 128 | 1200 | G.K.Project | 142 | 100 | 134 | 1200
Bhasantec | 140 | 400 | 131 | 1200 | Faridpur | 135 | 300 | 129 | 1200
Agargaon | 140 | 300 | 132 | 1200 | Madaripur | 135 | 400 | 130 | 800
Satmosjid | 139 | 600 | 132 | 1200 | Gopalganj | 140 | 1700 | 127 | 2100
Tongi | 133 | 800 | 132 | 1700 | Bagerhat | 138 | 1700 | 124 | 1100
Kabirpur | 137 | 300 | 130 | 1500 | Mongla | 135 | 1700 | 121 | 1200
Basundhara | 134 | 300 | 125 | 1500 | Satkhira | 136 | 1700 | 125 | 1200
Manikganj | 141 | 500 | 130 | 1300 | Gallamari | 136 | 200 | 126 | 1200
Joydevpur | 138 | 100 | 132 | 1000 | Magura | 135 | 300 | 125 | 700
New Tongi | 139 | 500 | 131 | 1500 | Chuadanga | 132 | 100 | 125 | 800
Kodda | 136 | 100 | 130 | 1000 | Barisal | 136 | 1600 | 132 | 1000
Dhamrai | 137 | 300 | 130 | 1600 | Patuakhali | 135 | 1700 | 128 | 800
Tangail | 138 | 400 | 133 | 1600 | Bhandaria | 137 | 1700 | 127 | 1200
Mymensing | 137 | 400 | 132 | 1500 | Ishurdi | 141 | 100 | 133 | 1800
Kishorganj | 136 | 200 | 132 | 1500 | Ruppur Paromanobik | 140 | 1800 | 134 | 1200
Netrokona | 137 | 500 | 131 | 1600 | Natore | 138 | 100 | 131 | 1200
Jamalpur | 137 | 1800 | 126 | 1600 | Bogra | 137 | 100 | 127 | 1800
Sherpur | 137 | 1800 | 134 | 1600 | Noagaon | 134 | 600 | 125 | 1800
Srimongal | 140 | 2200 | 136 | 1700 | Rajshahi | 134 | 100 | 127 | 1300
Shahjibazar | 139 | 2200 | 135 | 1500 | C.Nawabganj | 130 | 1800 | 125 | 1300
Fenchuganj | 136 | 2200 | 132 | 1500 | Amnura | 134 | 1200 | 125 | 800
Khulawara | 135 | 200 | 132 | 1300 | Pabna | 137 | 100 | 130 | 1800
Sylhet | 136 | 1930 | 133 | 1700 | Shahjadpur | 143 | 100 | 137 | 1100
Chatak | 136 | 200 | 132 | 1100 | Serajganj | 138 | 100 | 130 | 1800
Sunamganj | 135 | 100 | 132 | 1000 | Niyamatpur | 135 | 400 | 122 | 1800
Biani Bazar | 136 | 2200 | 133 | 100 | Joypurhat | 137 | 100 | 125 | 1830
Cumilla(s) | 132 | 100 | 128 | 800 | Rangpur | 131 | 400 | 114 | 1800
Cumilla(n) | 142 | 2200 | 138 | 1500 | Lalmonirhat | 129 | 500 | 105 | 1800
Chandpur | 143 | 800 | 135 | 1700 | Saidpur | 133 | 500 | 119 | 1800
Feni | 135 | 2200 | 129 | 1600 | Purbasadipur | 130 | 100 | 110 | 1800
Chowmuhani | 133 | 400 | 129 | 1200 | Thakurgaon | 130 | 400 | 100 | 1800
Ashuganj | 140 | 100 | 137 | 1700 | Palashbari | 130 | 100 | 116 | 1800
Daudkandi | 135 | 1800 | 131 | 1200 | Barapukuria | 134 | 100 | 121 | 1800
B.Baria | 140 | 2200 | 134 | 1100 | Panchagar | 126 | 300 | 97 | 1800

## L-Curve
Date | 2018-12-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 120 | 4158 | 1800 | 5958 |  |  |  | QF-LDC-12
0:30 | 75 | 4167.5 | 1566 | 5733.5 | Date: | 2018-12-04
1:00 | 30 | 4177 | 1332 | 5509
1:30 | 20 | 4108 | 1291.5 | 5399.5
2:00 | 10 | 4039 | 1251 | 5290
2:30 | 165 | 3939 | 1239.5 | 5178.5 | [5 empty] | Gen. at Eve. Peak | 8534 | 8534 MW (19:00 )
3:00 | 320 | 3839 | 1228 | 5067 | [6 empty] | 19:00
3:30 | 310 | 3830 | 1211 | 5041 | [5 empty] | Gen. at Day Peak | 6410.6 | 6410.6 MW (12:00 )
4:00 | 300 | 3821 | 1194 | 5015 | [6 empty] | 12:00
4:30 | 310 | 3779 | 1195 | 4974 | [5 empty] | Highest Generation | 8534
5:00 | 320 | 3737 | 1196 | 4933 | [6 empty] | 19:00
5:30 | 340 | 3859.5 | 1214.5 | 5074
6:00 | 360 | 3982 | 1233 | 5215
6:30 | 415 | 4139.3 | 1245 | 5384.3
7:00 | 470 | 4296.6 | 1257 | 5553.6
7:30 | 485 | 4427.8 | 1356.5 | 5784.3
8:00 | 500 | 4559 | 1456 | 6015
8:30 | 280 | 4449.7 | 1536.5 | 5986.2
9:00 | 60 | 4340.4 | 1617 | 5957.4
9:30 | 210 | 4234.2 | 1704.5 | 5938.7
10:00 | 360 | 4128 | 1792 | 5920
10:30 | 350 | 4264.55 | 1816.5 | 6081.05
11:00 | 340 | 4401.1 | 1841 | 6242.1
11:30 | 170 | 4552.35 | 1774 | 6326.35
12:00 | 0 | 4703.6 | 1707 | 6410.6
12:30 | 40 | 4688.5 | 1722.5 | 6411
13:00 | 80 | 4673.4 | 1738 | 6411.4
13:30 | 65 | 4555.35 | 1740 | 6295.35
14:00 | 50 | 4437.3 | 1742 | 6179.3
14:30 | 170 | 4422.95 | 1769.5 | 6192.45
15:00 | 290 | 4408.6 | 1797 | 6205.6
15:30 | 290 | 4444.5 | 1817.5 | 6262
16:00 | 290 | 4480.4 | 1838 | 6318.4
16:30 | 285 | 4623.8 | 1949 | 6572.8
17:00 | 280 | 4767.2 | 2060 | 6827.2
17:30 | 300 | 5298.6 | 2221 | 7519.6
18:00 | 320 | 5830 | 2382 | 8212
18:30 | 335 | 5956 | 2417 | 8373
19:00 | 350 | 6082 | 2452 | 8534
19:30 | 340 | 6023 | 2340 | 8363
20:00 | 360 | 5867 | 2329 | 8196 |  |  |  | Executive Engineer
20:30 | 330 | 5742.5 | 2277 | 8019.5 |  |  |  | Network Operation Division
21:00 | 300 | 5618 | 2225 | 7843
21:30 | 290 | 5461.5 | 2092.5 | 7554
22:00 | 280 | 5305 | 1960 | 7265 |  |  |  |  | Page 6 of 7
22:30 | 190 | 4959 | 1916.5 | 6875.5
23:00 | 100 | 4613 | 1873 | 6486
23:30 | 110 | 4385.5 | 1836.5 | 6222
24:00 | 120 | 4158 | 1800 | 5958
8534 MW (19:00 )
6410.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-12-04 |  | Energy | 152725498
[10 empty] | 2018-12-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3384 | 687 | 1357 | 254 | 150 | 42 | 0 | 0 | 84
0:30 | 3528 | 517 | 1276 | 142 | 150 | 40.5 | 0 | 0 | 80 | Date: | 2018-12-04
1:00 | 3672 | 347 | 1195 | 30 | 150 | 39 | 0 | 0 | 76
1:30 | 3643.5 | 347 | 1116 | 30 | 150 | 39 | 0 | 0 | 74 | [7 empty] | Total Energy | 152.7255 | Total Energy Gen 152.725 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.725 MKWHr
2:00 | 3615 | 347 | 1037 | 30 | 150 | 39 | 0 | 0 | 72 | [7 empty] | Energy not Served | 0
2:30 | 3585 | 347 | 954 | 30 | 150 | 39.5 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 152.7255
3:00 | 3555 | 347 | 871 | 30 | 150 | 40 | 0 | 0 | 74
3:30 | 3554.5 | 346.5 | 847 | 30 | 150 | 40 | 0 | 0 | 73 | [6 empty] | Shortage
4:00 | 3554 | 346 | 823 | 30 | 150 | 40 | 0 | 0 | 72
4:30 | 3494.5 | 346 | 838 | 34.5 | 150 | 40 | 0 | 0 | 71
5:00 | 3435 | 346 | 853 | 39 | 150 | 40 | 0 | 0 | 70
5:30 | 3526.5 | 346 | 888 | 53.5 | 150 | 40 | 0 | 0 | 70
6:00 | 3618 | 346 | 923 | 68 | 150 | 40 | 0 | 0 | 70
6:30 | 3695 | 345.5 | 989 | 93 | 150 | 40 | 0 | 0 | 71 |  |  |  |  | Coal
7:00 | 3772 | 345 | 1055 | 118 | 150 | 40 | 0 | 0 | 72
7:30 | 3779.5 | 344 | 1226 | 165.5 | 150 | 40 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3787 | 343 | 1397 | 213 | 150 | 40 | 0 | 0 | 76
8:30 | 3720.5 | 433 | 1289.5 | 262 | 150 | 40.5 | 0 | 0 | 79
9:00 | 3654 | 523 | 1182 | 311 | 150 | 41 | 0 | 0 | 82
9:30 | 3614.5 | 603.5 | 1143 | 288.5 | 150 | 40.5 | 0 | 0 | 82
10:00 | 3575 | 684 | 1104 | 266 | 150 | 40 | 0 | 0 | 82
10:30 | 3646.5 | 684 | 1190.5 | 264 | 150 | 40 | 0 | 0 | 86
11:00 | 3718 | 684 | 1277 | 262 | 150 | 40 | 0 | 0 | 90
11:30 | 3727 | 626 | 1395.5 | 285 | 150 | 40 | 0.5 | 0 | 91
12:00 | 3736 | 568 | 1514 | 308 | 150 | 40 | 1 | 0 | 92
12:30 | 3735.5 | 568 | 1518.5 | 296 | 150 | 40 | 1.5 | 0 | 91
13:00 | 3735 | 568 | 1523 | 284 | 150 | 40 | 2 | 0 | 90
13:30 | 3735 | 568 | 1523 | 284 | 150 | 40 | 2 | 0 | 90
14:00 | 3735 | 568 | 1523 | 284 | 150 | 40 | 2 | 0 | 90
14:30 | 3672.5 | 627.5 | 1416 | 294 | 149.5 | 40 | 5 | 0 | 89
15:00 | 3610 | 687 | 1309 | 304 | 149 | 40 | 8 | 0 | 88
15:30 | 3648.5 | 687 | 1325 | 307.5 | 149.5 | 40 | 11.5 | 0 | 85
16:00 | 3687 | 687 | 1341 | 311 | 150 | 40 | 15 | 0 | 82
16:30 | 3722.5 | 687 | 1334.5 | 481 | 150 | 40 | 67 | 0 | 88
17:00 | 3758 | 687 | 1328 | 651 | 150 | 40 | 119 | 0 | 94
17:30 | 3764.5 | 687 | 1516.5 | 1077.5 | 150 | 40 | 179 | 0 | 105
18:00 | 3771 | 687 | 1705 | 1504 | 150 | 40 | 239 | 0 | 116
18:30 | 3767 | 687 | 1740 | 1632.5 | 149.5 | 40 | 240 | 0 | 117
19:00 | 3763 | 687 | 1775 | 1761 | 149 | 40 | 241 | 0 | 118
19:30 | 3794 | 687 | 1795 | 1602 | 149 | 40 | 180 | 0 | 116
20:00 | 3760 | 687 | 1800 | 1478 | 149 | 40 | 164 | 0 | 118
20:30 | 3699 | 687 | 1801.5 | 1405 | 149 | 40.5 | 124.5 | 0 | 113
21:00 | 3638 | 687 | 1803 | 1332 | 149 | 41 | 85 | 0 | 108
21:30 | 3607 | 687 | 1795 | 1115 | 149.5 | 41 | 56.5 | 0 | 103
22:00 | 3576 | 687 | 1787 | 898 | 150 | 41 | 28 | 0 | 98
22:30 | 3516 | 687 | 1770 | 603 | 150 | 41.5 | 14 | 0 | 94
23:00 | 3456 | 687 | 1753 | 308 | 150 | 42 | 0 | 0 | 90
23:30 | 3420 | 687 | 1555 | 281 | 150 | 42 | 0 | 0 | 87 | Max Temp. in Dhaka |  | 28.3° C
24:00 | 3384 | 687 | 1357 | 254 | 150 | 42 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 152.725 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.725 MKWHr
Note on W13: Author:

## Generation
2018-12-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 41 | 41 | 42 | 42 | 955000
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 | 130 | 130 | 120 | 120 | 120 | 120 | 120 |  | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 3300000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 |  | 130 | 130 | 130 | 0 |  |  |  | 2400000
5 | Raozan 25 MW (RPCL) | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 131040
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.5 | 8.4 | 13.2 | 17.2 | 19.1 | 0 | 17.5 | 15 | 10.6 | 5 | 0.2 | 0 |  | 0 | [6 empty] | 116370
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 130 | 130 | 130 | 130 | 133 | 150 | 150 | 150 | 152 | 152 | 148 | 150 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 0 |  | 3094801
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 23 | 68 |  | 68 | 51 | 51 | 51 | 28 | 0 |  | 288224
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [16 empty] | 0 | 95 |  | 152 | 150 | 150 | 55 | 50 | 0 |  | 584620
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 45 | 45 | 11 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 368000
20 | Ghorasal ST: Unit-1,2 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1478000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 120 | 120 | 120 | 119 | 120 | 119 | 120 | 120 | 120 | 120 | 140 | 140 | 141 | 140 | 63 | 0 | 0 | [9 empty] | 1871000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 200 | 200 | 170 | 170 | 170 | 200 | 250 | 250 | 250 | 200 | 200 | 200 | 200 | 200 | 200 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 320 | 320 | 5958345
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 100 | 100 | 120 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2530816
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2454410
32 | Ashuganj Engines TSK | 40 | 40 | 20 | 20 | 20 | 40 | 40 | 40 | 37 | 37 | 37 | 37 | 40 | 20 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 848448
33 | Ashuganj CCPP 225 MW | 178 | 197 | 205 | 195 | 198 | 198 | 201 | 189 | 184 | 204 | 204 | 202 | 180 | 183 | 204 | 191 | 193 | 197 |  | 181 | 193 | 188 | 188 | 181 | 181 | 182 | 4655000
34 | Ashuganj CCPP(South) | 305 | 305 | 305 | 327 | 309 | 301 | 301 | 301 | 301 | 309 | 320 | 334 | 320 | 301 | 342 | 316 | 323 | 327 |  | 305 | 331 | 312 | 305 | 301 | 301 | 301 | 7562500
| Ashuganj CCPP(North) | 265 | 267 | 270 | 270 | 267 | 267 | 265 | 270 | 270 | 260 | 260 | 260 | 255 | 255 | 250 | 255 | 255 | 255 |  | 265 | 260 | 260 | 260 | 265 | 265 | 265 | 6491000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 150720
36 | Chandpur CCPP | 100 | 90 | 90 | 90 | 0 | [21 empty] | 443990
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 350 | 350 | 350 | 360 | 370 | 382 | 382 | 370 | 358 | 350 | 380 | 370 | 370 | 359 | 375 | 383 | 385 | 369 |  | 364 | 367 | 356 | 350 | 350 | 350 | 350 | 8840090
40 | Meghnaghat CCPP 450MW | 400 | 370 | 300 | 280 | 280 | 280 | 350 | 400 | 350 | 300 | 340 | 430 | 400 | 340 | 340 | 370 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 8822225
41 | Haripur Power CCPP 360MW | 363 | 327 | 247 | 236 | 235 | 236 | 275 | 384 | 260 | 260 | 320 | 360 | 310 | 270 | 270 | 270 | 300 | 353 |  | 360 | 360 | 360 | 360 | 363 | 362 | 364 | 7479000
42 | Mymensingh RPCL 210MW | 135 | 136 | 117 | 115 | 115 | 160 | 163 | 148 | 133 | 132 | 130 | 129 | 121 | 123 | 119 | 120 | 119 | 118 |  | 118 | 107 | 106 | 108 | 109 | 110 | 113 | 2917280
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 26 | 26 | 26 | 26 | 10 | 26 | 27 | 27 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 27 | 27 | 27 |  | 27 | 26 | 25 | 25 | 27 | 27 | 27 | 612000
45 | Fenchugonj CCPP-2 | 76 | 76 | 76 | 76 | 63 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1798800
46 | Shajibazar 330 MW | 300 | 300 | 298 | 300 | 300 | 299 | 304 | 300 | 300 | 301 | 298 | 300 | 311 | 311 | 311 | 310 | 309 | 308 |  | 308 | 308 | 310 | 312 | 312 | 312 | 311 | 6623200
47 | Shahjibazar GT: Unit- 8, 9 | 54 | 56 | 63 | 63 | 69 | 68 | 69 | 61 | 68 | 65 | 66 | 64 | 64 | 63 | 63 | 64 | 64 | 65 |  | 41 | 63 | 60 | 68 | 49 | 64 | 66 | 1491000
48 | Shahjibazar 86MW | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 10 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 5 | 725760
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 46 | 10 | 5 | 5 | 45 | 47 | 48 | 48 | 48 | 48 | 48 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 720360
50 | Sylhet GT 150 MW | 100 | 80 | 80 | 80 | 80 | 100 | 98 | 78 | 78 | 78 | 78 | 100 | 80 | 78 | 80 | 80 | 80 | 80 |  | 80 | 77 | 77 | 77 | 78 | 79 | 77 | 2033490
51 | Sylhet GT 20 MW | [12 empty] | 18 | 19 | 19 | 19 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 221000
52 | Sylhet (EPL) 50MW | 7 | 7 | 7 | 7 | 7 | 7 | 39 | 7 | 7 | 7 | 7 | 41 | 42 | 42 | 10 | 10 | 11 | 46 |  | 48 | 48 | 48 | 48 | 48 | 47 | 7 | 526440
53 | Sylhet (Desh) 10MW | [12 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 116280
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252192
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 31 | 50 | 50 | 53 | 53 | 11 | 51 |  | 53 | 53 | 53 | 53 | 53 | 53 | 5 | 621000
56 | Shahjahanulla 25 MW | [12 empty] | 15 | 15 | 15 | 15 | 23 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 430248
57 | Summit Bibiana- 2
58 | Southern 55MW | [16 empty] | 36 | 36 |  | 36 | 36 | 0 | 0 |  |  |  | 94000
59 | Sikalbaha (Energis) | [7 empty] | 2 | 16 | 16 | 17 | 32 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 581280
60 | Barabkunda (Regent) | 22 | 0 |  |  |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 440880
61 | Narshingdi (Doreen) | [8 empty] | 0 | 10 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 239760
62 | Tangail (Doreen) 22MW | [6 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 375228
63 | Tripura | 76 | 72 | 74 | 72 | 70 | 70 | 72 | 76 | 82 | 82 | 90 | 92 | 90 | 94 | 88 | 82 | 94 | 116 |  | 118 | 116 | 118 | 108 | 98 | 90 | 84 | 2094720
64 | Malancha, Ctg. EPZ (United) | 10 | 10 | 10 | 10 | 10 | 37 | 36 | 19 | 5 | 4 | 5 | 5 | 8 | 3 | 3 | 3 | 11 | 4 |  | 10 | 26 | 30 | 34 | 38 | 39 | 10 | 451680
65 | Feni (Doreen) 22MW |  |  |  |  | 0 | 7 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 334620
66 | Feni, Mohipal (Doreen) | [5 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 149040
67 | Jangalia (Summit) 33MW | [12 empty] | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 370200
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 9 | 9 | 9 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 442340
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 24 | 24 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 545220
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826100
72 | Summit Rupganj | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 374700
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [16 empty] | 0 | 0
78 | Gazipur (RPCL) | [7 empty] | 2 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 51 |  | 51 | 51 | 51 | 51 | 25 | 0 |  | 387840
79 | Kodda 149MW | [10 empty] | 0 | 1 | 2 | 5 | 8 | [11 empty] | 12960
80 | Jamalpur 95MW | [16 empty] | 14 | 78 |  | 78 | 78 | 78 | 77 | 40 | 0 |  | 408000
81 | Lakdhanvi 52 MW | [16 empty] | 1 | 16 |  | 25 | 25 | 25 | 25 | 0 |  |  | 107650
82 | Madanganj 102MW | [16 empty] | 0 | 12 |  | 35 | 48 | 48 | 48 | 15 | 0 |  | 173088
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 11 | 11 | 11 | 40 | 40 | 10 | 11 | 11 | 11 | 85 |  | 85 | 85 | 85 | 85 | 86 | 85 | 50 | 173088
85 | Keraniganj (Powerpac) 100MW | [16 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [9 empty] | 2 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 0 | 0 | 0 |  |  |  |  | 72960
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [15 empty] | 7 | 50 | 50 |  | 50 | 50 | 10 | 10 | 10 | 0 |  | 194520
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 50 | 20 | 20 | 20 | 20 | 35 |  | 50 | 50 | 50 | 50 | 50 | 50 | 5 | 500000
93 | Ashuganj (Midland) 51MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 26 | 15 | 15 | 15 | 35 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 6 | 776313
94 | Gagnagar (Orion) | [15 empty] | 0 | 10 | 80 |  | 102 | 102 | 48 | 50 | 7 | 0 |  | 350640
95 | Patenga 50MW | [16 empty] | 2 | 28 |  | 50 | 50 | 50 | 46 | 37 | 0 |  | 221760
96 | Chattogram ECPV 108 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 20 | 55 |  | 55 | 12 | 12 | 12 | 10 | 6 | 6 | 284160
97 | Katpotti 51 MW | [16 empty] | 0 | 18 |  | 40 | 40 | 44 | 46 | 46 | 0 |  | 222096
98 | Bosila 108MW | [16 empty] | 31 | 47 |  | 47 | 46 | 46 | 46 | 46 | 0 |  | 257280
99 | Madanganj-55 MW | [9 empty] | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 44 |  | 55 | 55 | 55 | 55 | 55 | 0 |  | 424477
100 | Northern 55 MW | [7 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 55 | 55 | 55 | 55 | 55 | 0 |  | 474403
101 | Kushiara 163 MW CCPP GT | 130 | 100 | 100 | 100 | 130 | 163 | 163 | 130 | 100 | 100 | 163 | 130 | 100 | 100 | 100 | 100 | 100 | 130 |  | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 3161078
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.6 | 1.2 | 1.8 | 2 | 1.6 | 1.9 | 1.3 | 0 | 0.4 | 0 | 0 | [8 empty] | 10900
103 | Banco Energy 54MW | [7 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 472680
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 21 | 100 |  | 100 | 50 | 50 | 50 | 7 | 7 | 7 | 513600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [7 empty] | 0 | 2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 43 |  | 47 | 17 | 15 | 0 |  |  |  | 259200
115 | Juldah 100 MW Unit-3 | [7 empty] | 14 | 20 | 20 | 43 | 74 | 80 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1323840
116 | Chandpur Desh 200MW | 17 | 17 | 17 | 17 | 26 | 55 | 105 | 118 | 120 | 80 | 80 | 80 | 50 | 50 | 50 | 50 | 50 | 119 |  | 186 | 190 | 194 | 192 | 178 | 101 | 101 | 2160000
117 | Midland 150MW
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4177 | 4039 | 3839 | 3821 | 3737 | 3982 | 4296.6 | 4559 | 4340.4 | 4128 | 4401.1 | 4703.6 | 4673.4 | 4437.3 | 4408.6 | 4480.4 | 4767.2 | 5830 |  | 6082 | 6023 | 5867 | 5618 | 5305 | 4613 | 4158 | 110894950
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [16 empty] | 19 | 66 |  | 83 | 33 | 33 | 0 |  |  |  | 176640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 9 | 28 |  | 30 | 34 | 34 | 34 | 0 |  |  | 117600
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [16 empty] | 105 | 105 |  | 105 | 105 | 105 | 105 | 6 | 0 |  | 531840
130
131
132
133
| Summit Barisal 110 MW | [16 empty] | 33 | 48 |  | 48 | 48 | 48 | 48 | 0 |  |  | 214080
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 50 | 52 | 52 | 42 | 42 | 44 | 43 | 42 | 43 | 45 |  | 79 | 85 | 85 | 85 | 91 | 91 | 45 | 1024512
| Bhola CCPP 194MW | 189 | 157 | 158 | 165 | 165 | 165 | 166 | 187 | 169 | 186 | 185 | 185 | 185 | 184 | 184 | 186 | 187 | 188 |  | 188 | 186 | 184 | 188 | 169 | 184 | 189 | 4348547
140 | Bhola (Venture) 33MW | 21 | 20 | 19 | 19 | 19 | 20 | 19 | 10 | 10 | 12 | 12 | 13 | 12 | 10 | 10 | 13 | 20 | 26 |  | 26 | 25 | 26 | 25 | 24 | 23 | 22 | 426300
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [16 empty] | 0 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 192000
143 | Gopalganj Peaking | [15 empty] | 15 | 44 | 60 |  | 60 | 56 | 48 | 0 |  |  |  | 214400
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 347 | 347 | 347 | 346 | 346 | 346 | 345 | 343 | 523 | 684 | 684 | 568 | 568 | 606 | 687 | 687 | 687 | 687 |  | 687 | 687 | 687 | 687 | 687 | 687 | 687 | 13237090
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 |  | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 3663100
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 0 | 0 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 70 |  | 70 | 65 | 70 | 70 | 60 | 60 | 50 | 1350000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [16 empty] | 0 | 0 |  | 0
157 | Sirajgonj Unit-1 225MW (Gas) | 176 | 178 | 174 | 164 | 167 | 178 | 193 | 189 | 183 | 184 | 197 | 197 | 199 | 174 | 140 | 158 | 182 | 187 |  | 184 | 178 | 177 | 180 | 173 | 174 | 175 | 4562709
158 | Sirajgonj Unit-1 225MW (Oil) | [19 empty] | 0
| Sirajgonj Unit-2 225MW (Gas) | 179 | 180 | 176 | 163 | 161 | 178 | 195 | 191 | 185 | 187 | 196 | 192 | 190 | 182 | 192 | 195 | 194 | 189 |  | 187 | 178 | 180 | 182 | 177 | 177 | 176 | 4605682
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 194 | 143 | 128 | 111 | 112 | 120 | 113 | 256 | 255 | 250 | 250 | 250 | 290 | 290 | 290 | 290 | 242 | 290 |  | 293 | 292 | 292 | 292 | 293 | 292 | 291 | 5601545
161 | Bera Peaking
162 | Bogra (GBB) | [8 empty] | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 323760
163 | Bogra (EPL) | [8 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 77832
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | [6 empty] | 0 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 107172
165 | Amnura 50MW | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 50 |  | 50 | 50 | 50 | 50 | 0 |  |  | 346120
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking | [16 empty] | 13 | 32 |  | 32 | 31 | 31 | 0 |  |  |  | 98859
169 | Rajlanka 52 MW | [6 empty] | 0 | 52 | 52 | 52 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 43 |  | 52 | 52 | 52 | 52 | 52 | 0 |  | 497280
170 | Chapainawabganj-100 MW | [16 empty] | 30 | 51 |  | 51 | 8 | 0 | 0 |  |  |  | 113480
171
172
173 | Rangpur GT
175 | Saidpur GT
176
177
178
178 | Western Zone Total | 1332 | 1251 | 1228 | 1194 | 1196 | 1233 | 1257 | 1456 | 1617 | 1792 | 1841 | 1707 | 1738 | 1742 | 1797 | 1838 | 2060 | 2382 |  | 2452 | 2340 | 2329 | 2225 | 1960 | 1873 | 1800 | 41830548