## Forecast
6086.1 |  |  |  |  | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-11-28 | Wednesday
|  | Date (day): | 2018-11-28 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10932 | MW |  |  | (b) At Evening Peak Hour : |  | 11468 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-11-27 | 2018-11-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | Unit-2 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 340 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 60 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 94 | 101 | 101 | 7
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 40 | 0 | 0 | 0 |  |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 232 | 95 | 300 | 300 |  |  | ST under maint.
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 322 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 380 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 70 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 32 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 67 | 0 | 0 | 0 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 150 | 225 | 225
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Contract expired
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 14 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 43 | 48 |  | 3
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
25 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 133 | 133 |  | 16 | Engine problem
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 47 | 47 | 47 |  | 61 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 48 | 49 | 49 |  | 31 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 25 |  | 8 | Engine problem
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 32 | 0 | 43 | 43 |  | 9 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 12 | 120 | 300 | 300
35 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 31 | 97 | 133 | 133 |  | 16 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 1938 | 2329 | 4044 | 4149 | 315 | 560
39 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 160 | 160 | 160 | 20 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
41 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.58 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 44 | 71 | 160 | 160 |  | 70
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 202 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 80 | 130 | 131 | 150
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 32 | 40 | 40 |  | 11 | Engine problem
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 55 | 80 | 80
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 15 | 100 | 100
| Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 0 | 0 | 50 | 90 | 100 | 100 |  |  | On test
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 11 | 10 | 10
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 92 | 92 |  | 16 | Engine problem
| Chattogram area Total |  |  |  |  | 1661 | 1581 | 590.58 | 923 | 1266 | 1265 | 200 | 137
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 90 | 120 | 90 | 90 | 39 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 338 | 305 | 305 | 305 |  | 55 | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 20 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 54 | 51 | 51
| Midland 150MW |  | HFO | IPP | 23*7.015 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 150 | 150 |  | 13
| Chandpur Desh 200MW |  | HFO | IPP | 0 | 0 | 0 | 0 | 145 | 200 | 200 |  |  | On test
65 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
66 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 86 | 120 | 96 | 121
67 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
68 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 44 | 52 | 52
69 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 21 | 22 | 22
70 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2601 | 2541 | 1342 | 1609 | 1851 | 1926 | 339 | 428
71 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 88 | 71 | 55 | 70
72 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
73 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 79 | 79 | 79 |  | 16 | Engine problem.
74 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
75 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 151 | 180 | 185
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 119.1 | 323 | 338 | 356 | 0 | 16
76 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 25 | 26 | 26 | 26
77 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 63 | 63 | 76 | 76
78 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
79 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Uner maint.
80 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
81 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
82 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 8 | 11
83 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 54 | 66 | 66
84 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 86 | 86 | 86
85 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 47 | 50 | 50
86 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 98 | 78 | 79 | 79
87 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
88 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 48 | 50 | 50
89 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 25 | 25 | 25
90 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 250 | 0 | 0 |  |  | Under maint.
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0
91 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 883 | 947 | 754 | 757 | 0 | 330
92 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 687 | 686 | 694 | 694
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 17 | 0 | 30
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 75 | 75
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 293 | 305 | 310 | 310 |  | 100 | ST under maint.
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
99 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
101 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2278 | 2209 | 980 | 1213 | 1439 | 1499 | 0 | 100
102 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
103 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
104 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 25 | 26 | 26 |  | 7 | Engine problem
105 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 191 | 115 | 119 | 145
106 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 31 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 241 | 318 | 350 | 406 | 0 | 7
107 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 30 | 70 | 70
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 51 | 0 | 0 |  | 100 | Under maint.
108 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
109 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 50
110 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
111 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
112 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 0 | 40
113 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 188 | 176 | 210 | 210 |  |  | FGMO
114 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 192 | 180 | 185 | 35 |  | FGMO
115 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 |  |  | Gas shortage
116 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | On test.
117 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 39
118 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
119 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
120 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
121 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
122 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 93 | 93
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 477 | 691 | 740 | 924 | 35 | 108
123 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
124 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150 | 124
125 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
126 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 149 | 150 | 186 | 209 | 85
| Total |  |  |  |  | 17340 | 16742 | 6719.68 | 8502 | 10932 | 11468 | 1098 | 1771
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6365.5967 | 8054 | 10355.9548 | 10863.7111
A. |  | 2018-11-27 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8502 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5135 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8502 | MW
3 | Day peak Generation : |  |  | 6719.68 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8054 | MW
4 | Evening peak Generation : |  |  | 8502 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 158.4283 | MKWHr | By Solar | 0.15017 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 124.5351 | MKWHr |  | By Oil: | 11.7248 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6599 | MKWHr |  | By Hydro: | 1.1848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1098 | MW | Dhaka | 3057 | 3057 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1771 | MW | Chittagong | 914 | 914 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2869 | MW | Khulna | 974 | 974 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1110.43 | MMCFD |  |  | Rajshahi | 800 | 800 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 93851607.228 | ii) Oil : | Taka | 77760834.07 | Comilla | 701 | 701 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14127214 | Total | Taka | 185739655.298 | Mymensingh | 577 | 577 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 1.3225 | MKWHr. | Sylhet | 312 | 312 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -380 | MW at | 19:00 | hrs | Barisal | 205 | 205 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -420 | MW at | 18:30 | hrs | Rangpur | 514 | 514 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 8054 | 8054 |  | 0
B. |  | 2018-11-28 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 28.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11468 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6900 | MW
4 | Reserve(Generation end) |  |  |  | 2668 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 163.9813 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5262 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.0538 | MKWHr. | ii) HVDC Flow at Peak Time |  | 686 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1197 | MKWHr. | iii) Maximum HVDC Flow : |  | 693 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.5 |  | (b) Today: | 100.43 |  | (c) Rule Curve: |  | 106.3
.

## YesterdayGen
2018-11-27
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 0 | 120 | 0 | 380 | 12 | 0 | 300 | 326 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 45 | 30 | 160 | 0 | 0 | 197 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 100 | 90 | 100 | 0 | 305 | 182 | 8 | 88 | 40 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 78 | 105 | 0 | 0 | 0 | 26 | 63 | 9 | 51 | 100 | 0 | 61 | 5 | 47 | 78 | 0 | 47 | 0 | 280 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 498 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 21 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 146 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4393 | 1403 | 5796 | 3646 | 498 | 1327 | 22 | 150 | 75 | 0 | 78 | 0 | 0 | 100.5
2:00 | 37 | 0 | 120 | 0 | 380 | 12 | 0 | 300 | 300 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 42 | 0 | 160 | 0 | 0 | 200 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 100 | 90 | 100 | 0 | 272 | 182 | 8 | 87 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 74 | 106 | 0 | 0 | 0 | 26 | 63 | 5 | 5 | 100 | 0 | 65 | 5 | 20 | 78 | 0 | 7 | 0 | 275 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 20 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 152 | 0 | 148 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4066 | 1415 | 5481 | 3520 | 497 | 1176 | 22 | 150 | 42 | 0 | 74 | 0 | 0 | 100.5
3:00 | 37 | 0 | 119 | 0 | 280 | 12 | 0 | 220 | 302 | 0 | 20 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 42 | 0 | 160 | 0 | 0 | 201 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 80 | 90 | 80 | 0 | 276 | 196 | 8 | 88 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 105 | 0 | 0 | 0 | 26 | 63 | 5 | 5 | 100 | 0 | 63 | 5 | 5 | 78 | 0 | 5 | 0 | 285 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 152 | 0 | 138 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 3835 | 1448 | 5283 | 3361 | 497 | 1139 | 22 | 150 | 42 | 0 | 72 | 0 | 0 | 100.5
4:00 | 37 | 0 | 121 | 0 | 280 | 12 | 0 | 220 | 282 | 0 | 20 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 25 | 0 | 0 | 42 | 0 | 160 | 0 | 0 | 201 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 90 | 80 | 0 | 264 | 187 | 8 | 88 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 70 | 106 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 100 | 0 | 64 | 5 | 5 | 78 | 0 | 5 | 0 | 305 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 159 | 0 | 136 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3742 | 1454 | 5196 | 3296 | 497 | 1119 | 22 | 150 | 42 | 0 | 70 | 0 | 0 | 100.5
5:00 | 37 | 0 | 119 | 0 | 240 | 12 | 0 | 220 | 251 | 0 | 20 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 40 | 0 | 160 | 0 | 0 | 201 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 80 | 90 | 80 | 0 | 253 | 183 | 8 | 88 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 70 | 106 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 100 | 0 | 50 | 5 | 5 | 79 | 0 | 5 | 0 | 285 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 159 | 0 | 136 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3685 | 1450 | 5135 | 3236 | 497 | 1120 | 22 | 150 | 40 | 0 | 70 | 0 | 0 | 100.5
6:00 | 37 | 0 | 118 | 0 | 240 | 12 | 0 | 250 | 282 | 0 | 20 | 380 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 40 | 0 | 160 | 0 | 0 | 209 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 80 | 90 | 80 | 0 | 290 | 203 | 8 | 88 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 106 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 130 | 0 | 67 | 5 | 5 | 80 | 0 | 5 | 0 | 280 | 0 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 497 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 164 | 0 | 136 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3896 | 1521 | 5417 | 3439 | 497 | 1197 | 22 | 150 | 40 | 0 | 72 | 0 | 0 | 100.5
7:00 | 37 | 0 | 120 | 0 | 300 | 12 | 0 | 280 | 340 | 0 | 20 | 380 | 0 | 0 | 0 | 0 | 135 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 40 | 0 | 160 | 0 | 0 | 207 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 80 | 90 | 80 | 0 | 334 | 205 | 8 | 88 | 10 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 108 | 0 | 0 | 0.1 | 26 | 60 | 5 | 5 | 130 | 0 | 68 | 5 | 5 | 78 | 0 | 7 | 0 | 300 | 0 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 4.27 | 0 | 0 | 0 | 0 |  | 497 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 167 | 0 | 141 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4174.37 | 1554 | 5728.37 | 3689 | 497 | 1257 | 19 | 150 | 40 | 0 | 72 | 4.37 | 0 | 100.49
8:00 | 37 | 0 | 120 | 0 | 380 | 12 | 0 | 211 | 342 | 0 | 20 | 380 | 0 | 0 | 0 | 0 | 180 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 11 | 0 | 40 | 0 | 160 | 0 | 0 | 210 | 0 | 111 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 7 | 80 | 90 | 80 | 0 | 334 | 201 | 8 | 89 | 35 | 5 | 5 | 12 | 50 | 0 | 0 | 22 | 5 | 8 | 14 | 76 | 107 | 0 | 22 | 0.8 | 26 | 63 | 43 | 30 | 130 | 0 | 68 | 5 | 47 | 80 | 0 | 45 | 0 | 290 | 22 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 10 | 41 | 0 | 0 | 0 |  | 497 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 8 | 0 | 0 | 150 | 0 | 0 | 177 | 0 | 177 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4667.8 | 1629 | 6296.8 | 3985 | 497 | 1466 | 72 | 150 | 40 | 0 | 76 | 10.8 | 0 | 100.49
9:00 | 37 | 0 | 0 | 0 | 380 | 51 | 0 | 20 | 365 | 0 | 40 | 450 | 0 | 0 | 0 | 0 | 235 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 25 | 25 | 30 | 0 | 42 | 0 | 160 | 0 | 0 | 194 | 0 | 110 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 120 | 90 | 135 | 0 | 305 | 185 | 8 | 89 | 37 | 5 | 5 | 35 | 85 | 0 | 0 | 22 | 5 | 0 | 14 | 78 | 107 | 0 | 22 | 1.5 | 24 | 63 | 45 | 47 | 163 | 0 | 62 | 5 | 48 | 78 | 0 | 45 | 0 | 260 | 24 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 1 | 14.92 | 50 | 0 | 0 | 0 |  | 533 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 192 | 0 | 195 | 0 | 28 | 0 | 0 | 0 | 0 | 0 |  | 4726.42 | 1690 | 6416.42 | 3781 | 533 | 1693 | 124 | 149 | 42 | 0 | 78 | 16.42 | 0 | 100.49
10:00 | 37 | 0 | 0 | 0 | 380 | 51 | 0 | 30 | 323 | 0 | 40 | 450 | 0 | 2 | 0 | 0 | 180 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 25 | 25 | 30 | 0 | 42 | 0 | 160 | 0 | 0 | 195 | 0 | 110 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 120 | 90 | 135 | 0 | 305 | 184 | 8 | 88 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 8 | 14 | 82 | 95 | 0 | 22 | 2 | 24 | 63 | 45 | 50 | 100 | 0 | 56 | 5 | 47 | 78 | 19 | 43 | 9 | 245 | 24 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 24 | 18.33 | 50 | 0 | 0 | 0 |  | 693 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 173 | 0 | 177 | 0 | 32 | 0 | 0 | 0 | 0 | 0 |  | 4600.33 | 1815 | 6415.33 | 3665 | 693 | 1599 | 165 | 149 | 42 | 0 | 82 | 20.33 | 0 | 100.49
11:00 | 37 | 0 | 0 | 0 | 380 | 94 | 0 | 76 | 281 | 0 | 40 | 420 | 0 | 7 | 0 | 0 | 120 | 0 | 67 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 25 | 25 | 30 | 0 | 42 | 0 | 160 | 0 | 0 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 120 | 90 | 135 | 0 | 305 | 185 | 8 | 87 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 8 | 14 | 84 | 89 | 0 | 22 | 2.2 | 21 | 63 | 48 | 50 | 100 | 0 | 61 | 5 | 47 | 80 | 19 | 41 | 10 | 265 | 24 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 31 | 19.58 | 50 | 0 | 0 | 0 |  | 687 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 185 | 0 | 178 | 0 | 31 | 0 | 0 | 0 | 0 | 0 |  | 4564.78 | 1840 | 6404.78 | 3639 | 687 | 1592 | 189 | 150 | 42 | 0 | 84 | 21.78 | 0 | 100.48
12:00 | 37 | 0 | 0 | 0 | 380 | 94 | 0 | 232 | 322 | 0 | 40 | 420 | 0 | 7 | 0 | 0 | 120 | 0 | 67 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 17 | 25 | 32 | 0 | 44 | 0 | 160 | 0 | 0 | 203 | 0 | 80 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 90 | 135 | 0 | 338 | 202 | 8 | 140 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 0 | 8 | 13 | 86 | 88 | 0 | 22 | 2.1 | 25 | 63 | 50 | 50 | 100 | 0 | 63 | 5 | 47 | 98 | 19 | 42 | 10 | 280 | 23 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 31 | 19.58 | 50 | 0 | 0 | 0 |  | 687 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 188 | 0 | 199 | 0 | 31 | 0 | 0 | 0 | 0 | 0 |  | 4872.68 | 1847 | 6719.68 | 3876 | 687 | 1653 | 203 | 149 | 44 | 0 | 86 | 21.68 | 0 | 100.48
13:00 | 37 | 0 | 0 | 0 | 380 | 94 | 0 | 134 | 351 | 0 | 40 | 450 | 0 | 7 | 0 | 15 | 218 | 0 | 57 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 25 | 25 | 30 | 0 | 40 | 0 | 160 | 0 | 0 | 203 | 0 | 145 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 120 | 90 | 135 | 0 | 305 | 185 | 8 | 135 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 26 | 14 | 86 | 85 | 0 | 22 | 2 | 27 | 63 | 50 | 50 | 163 | 0 | 54 | 86 | 47 | 48 | 19 | 44 | 10 | 275 | 24 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 31 | 18.3 | 50 | 0 | 0 | 0 |  | 687 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 193 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 183 | 0 | 89 | 0 | 0 | 0 | 0 | 0 |  | 5089.3 | 1932 | 7021.3 | 3862 | 687 | 1911 | 266 | 149 | 40 | 0 | 86 | 20.3 | 0 | 100.48
14:00 | 37 | 0 | 0 | 0 | 380 | 94 | 50 | 22 | 222 | 0 | 40 | 340 | 0 | 7 | 0 | 15 | 140 | 0 | 35 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 25 | 25 | 32 | 0 | 40 | 0 | 160 | 0 | 0 | 202 | 0 | 100 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 120 | 90 | 135 | 0 | 305 | 185 | 8 | 140 | 37 | 25 | 5 | 54 | 52 | 0 | 0 | 22 | 11 | 26 | 14 | 92 | 79 | 0 | 22 | 1.7 | 25 | 63 | 50 | 47 | 100 | 0 | 56 | 50 | 47 | 47 | 19 | 44 | 10 | 250 | 25 | 8 | 0 | 15 | 0 | 0 | 7 | 0 | 31 | 15.77 | 50 | 0 | 0 | 0 |  | 686 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 174 | 0 | 178 | 0 | 90 | 0 | 0 | 0 | 0 | 0 |  | 4518.47 | 1926 | 6444.47 | 3575 | 686 | 1588 | 297 | 149 | 40 | 0 | 92 | 17.47 | 0 | 100.47
15:00 | 37 | 0 | 0 | 0 | 380 | 94 | 76 | 38 | 262 | 0 | 40 | 350 | 0 | 7 | 0 | 15 | 140 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 25 | 25 | 34 | 0 | 40 | 0 | 160 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 120 | 90 | 135 | 0 | 345 | 194 | 8 | 140 | 37 | 5 | 5 | 54 | 52 | 0 | 0 | 22 | 11 | 33 | 14 | 90 | 82 | 0 | 22 | 1.2 | 26 | 62 | 50 | 47 | 130 | 0 | 63 | 50 | 47 | 88 | 19 | 44 | 10 | 260 | 25 | 8 | 0 | 15 | 0 | 0 | 7 | 0 | 31 | 11.3 | 50 | 0 | 0 | 0 |  | 687 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 192 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 187 | 0 | 189 | 0 | 52 | 0 | 0 | 0 | 0 | 0 |  | 4724.5 | 1893 | 6617.5 | 3717 | 687 | 1641 | 281 | 149 | 40 | 0 | 90 | 12.5 | 0 | 100.47
16:00 | 37 | 0 | 0 | 0 | 330 | 94 | 77 | 98 | 272 | 0 | 0 | 350 | 0 | 0 | 0 | 15 | 140 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 22 | 25 | 23 | 25 | 25 | 38 | 0 | 42 | 0 | 160 | 0 | 0 | 216 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 120 | 90 | 135 | 0 | 342 | 204 | 8 | 140 | 37 | 5 | 5 | 54 | 50 | 0 | 0 | 22 | 0 | 33 | 15 | 90 | 82 | 0 | 22 | 0.8 | 26 | 62 | 50 | 50 | 130 | 0 | 63 | 50 | 47 | 88 | 19 | 44 | 10 | 255 | 25 | 8 | 0 | 15 | 0 | 0 | 7 | 0 | 31 | 5.4 | 50 | 0 | 0 | 0 |  | 686 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 191 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 8 | 0 | 0 | 145 | 0 | 0 | 182 | 0 | 185 | 0 | 13 | 0 | 0 | 0 | 0 | 0 |  | 4722.2 | 1812 | 6534.2 | 3685 | 686 | 1610 | 256 | 145 | 42 | 14 | 90 | 6.2 | 0 | 100.47
17:00 | 37 | 0 | 0 | 0 | 250 | 94 | 60 | 100 | 292 | 0 | 0 | 350 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 44 | 0 | 4 | 54 | 48 | 17 | 22 | 25 | 23 | 25 | 25 | 0 | 0 | 42 | 0 | 160 | 0 | 25 | 202 | 0 | 100 | 0 | 0 | 32 | 0 | 34 | 0 | 0 | 27 | 19 | 3 | 120 | 120 | 135 | 0 | 253 | 184 | 8 | 138 | 37 | 5 | 5 | 54 | 85 | 0 | 3 | 22 | 8 | 33 | 15 | 94 | 81 | 7 | 22 | 0 | 26 | 62 | 50 | 50 | 163 | 0 | 47 | 86 | 47 | 69 | 19 | 45 | 10 | 240 | 25 | 8 | 0 | 28 | 0 | 0 | 7 | 0 | 36 | 0.16 | 50 | 28 | 0 | 0 |  | 687 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 40 | 167 | 18 | 16 | 0 | 50 | 30 | 0 | 0 | 4 | 12 | 0 | 0 | 37 | 12 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 174 | 0 | 51 | 0 | 0 | 0 | 0 | 35 |  | 4821.16 | 1985 | 6806.16 | 3393 | 687 | 1743 | 612 | 149 | 42 | 86 | 94 | 0.16 | 0 | 100.47
18:00 | 37 | 0 | 0 | 0 | 380 | 87 | 60 | 99 | 352 | 0 | 0 | 450 | 0 | 4 | 14 | 55 | 150 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 47 | 0 | 46 | 54 | 55 | 36 | 22 | 25 | 23 | 25 | 25 | 13 | 0 | 42 | 30 | 160 | 0 | 25 | 214 | 0 | 133 | 0 | 0 | 32 | 55 | 51 | 15 | 12 | 44 | 19 | 2 | 120 | 120 | 135 | 0 | 331 | 203 | 8 | 140 | 37 | 5 | 5 | 54 | 85 | 8 | 25 | 22 | 11 | 33 | 21 | 122 | 71 | 50 | 22 | 0 | 26 | 63 | 50 | 50 | 163 | 0 | 62 | 86 | 47 | 133 | 19 | 47 | 10 | 260 | 25 | 11 | 0 | 57 | 0 | 0 | 100 | 0 | 68 | 0 | 90 | 94 | 0 | 0 |  | 686 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 7 | 61 | 40 | 135 | 25 | 54 | 0 | 50 | 30 | 0 | 0 | 52 | 50 | 0 | 11 | 43 | 38 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 175 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 6078 | 2324 | 8402 | 3797 | 686 | 1969 | 1308 | 149 | 72 | 299 | 122 | 0 | 0 | 100.47
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 0 | 0 | 0 | 340 | 94 | 60 | 95 | 322 | 0 | 0 | 380 | 0 | 70 | 32 | 55 | 150 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 23 | 25 | 25 | 0 | 0 | 41 | 30 | 160 | 0 | 25 | 202 | 0 | 130 | 0 | 0 | 32 | 55 | 51 | 15 | 12 | 50 | 19 | 11 | 120 | 120 | 135 | 0 | 305 | 184 | 8 | 140 | 37 | 20 | 5 | 54 | 85 | 0 | 44 | 22 | 11 | 33 | 21 | 120 | 71 | 79 | 22 | 0 | 26 | 63 | 50 | 50 | 130 | 0 | 54 | 86 | 47 | 78 | 19 | 48 | 10 | 250 | 25 | 11 | 0 | 120 | 0 | 0 | 151 | 0 | 97 | 0 | 90 | 145 | 0 | 0 |  | 686 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 17 | 60 | 40 | 115 | 25 | 80 | 0 | 51 | 30 | 0 | 0 | 52 | 50 | 0 | 14 | 52 | 39 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 176 | 0 | 192 | 0 | 98 | 0 | 0 | 0 | 0 | 105 |  | 6131 | 2371 | 8502 | 3627 | 686 | 1860 | 1685 | 149 | 71 | 304 | 120 | 0 | 0 | 0
19:30 | 37 | 0 | 0 | 0 | 340 | 94 | 40 | 95 | 318 | 0 | 0 | 380 | 0 | 100 | 48 | 55 | 150 | 0 | 0 | 0 | 0 | 102 | 10 | 0 | 47 | 0 | 48 | 54 | 55 | 36 | 22 | 25 | 23 | 25 | 25 | 10 | 0 | 41 | 30 | 160 | 0 | 25 | 201 | 0 | 131 | 0 | 0 | 32 | 55 | 51 | 15 | 12 | 50 | 22 | 15 | 120 | 120 | 135 | 0 | 305 | 184 | 8 | 140 | 37 | 20 | 5 | 54 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 122 | 72 | 79 | 22 | 0 | 27 | 63 | 50 | 50 | 100 | 0 | 55 | 86 | 47 | 80 | 20 | 48 | 10 | 280 | 25 | 11 | 0 | 120 | 0 | 0 | 150 | 0 | 84 | 0 | 90 | 145 | 0 | 0 |  | 686 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 40 | 133 | 26 | 80 | 0 | 50 | 30 | 0 | 0 | 52 | 50 | 0 | 0 | 52 | 39 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 174 | 0 | 177 | 0 | 98 | 0 | 0 | 0 | 0 | 105 |  | 6167 | 2316 | 8483 | 3634 | 686 | 1841 | 1736 | 149 | 71 | 244 | 122 | 0 | 0 | 0
20:00 | 37 | 0 | 0 | 0 | 340 | 94 | 40 | 99 | 320 | 0 | 0 | 380 | 0 | 75 | 66 | 55 | 150 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 47 | 0 | 47 | 54 | 55 | 17 | 22 | 25 | 23 | 25 | 25 | 33 | 0 | 41 | 30 | 160 | 0 | 25 | 203 | 0 | 130 | 0 | 0 | 32 | 55 | 34 | 15 | 12 | 50 | 22 | 12 | 120 | 120 | 135 | 0 | 305 | 184 | 8 | 137 | 37 | 20 | 5 | 54 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 120 | 72 | 79 | 22 | 0 | 26 | 63 | 50 | 50 | 100 | 0 | 52 | 86 | 47 | 78 | 20 | 48 | 10 | 255 | 25 | 11 | 0 | 150 | 0 | 0 | 150 | 0 | 80 | 0 | 90 | 146 | 0 | 0 |  | 686 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 40 | 132 | 26 | 80 | 0 | 50 | 60 | 0 | 0 | 26 | 50 | 0 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 174 | 0 | 177 | 0 | 98 | 0 | 0 | 0 | 0 | 105 |  | 6131 | 2274 | 8405 | 3660 | 686 | 1815 | 1759 | 149 | 71 | 145 | 120 | 0 | 0 | 0
21:00 | 37 | 0 | 0 | 0 | 340 | 97 | 40 | 99 | 352 | 0 | 0 | 400 | 0 | 40 | 75 | 55 | 150 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 47 | 0 | 48 | 54 | 55 | 17 | 22 | 25 | 23 | 25 | 25 | 43 | 0 | 42 | 30 | 160 | 0 | 25 | 202 | 0 | 130 | 0 | 0 | 32 | 55 | 34 | 15 | 12 | 50 | 22 | 13 | 120 | 120 | 135 | 0 | 305 | 184 | 8 | 135 | 40 | 20 | 5 | 54 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 110 | 54 | 79 | 22 | 0 | 26 | 63 | 50 | 50 | 100 | 0 | 87 | 86 | 47 | 98 | 20 | 49 | 10 | 270 | 25 | 11 | 0 | 115 | 0 | 0 | 150 | 0 | 27 | 0 | 90 | 146 | 0 | 0 |  | 686 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 135 | 23 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 175 | 0 | 177 | 0 | 98 | 0 | 0 | 0 | 0 | 105 |  | 6128 | 2138 | 8266 | 3652 | 686 | 1884 | 1624 | 149 | 72 | 89 | 110 | 0 | 0 | 0
22:00 | 37 | 0 | 0 | 0 | 340 | 98 | 40 | 99 | 343 | 0 | 0 | 400 | 0 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 47 | 0 | 47 | 54 | 18 | 0 | 16 | 25 | 23 | 25 | 25 | 43 | 0 | 42 | 30 | 160 | 0 | 0 | 202 | 0 | 130 | 0 | 0 | 40 | 0 | 34 | 0 | 0 | 19 | 22 | 21 | 120 | 120 | 135 | 0 | 309 | 189 | 8 | 140 | 40 | 20 | 5 | 54 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 52 | 79 | 22 | 0 | 26 | 63 | 50 | 50 | 130 | 0 | 67 | 86 | 47 | 98 | 20 | 47 | 10 | 260 | 25 | 11 | 0 | 12 | 0 | 0 | 70 | 0 | 0 | 0 | 84 | 100 | 0 | 0 |  | 686 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 139 | 22 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 175 | 0 | 177 | 0 | 97 | 0 | 0 | 0 | 0 | 0 |  | 5448 | 1953 | 7401 | 3642 | 686 | 1900 | 816 | 149 | 72 | 34 | 102 | 0 | 0 | 0
23:00 | 37 | 0 | 0 | 0 | 300 | 101 | 40 | 99 | 322 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 47 | 54 | 0 | 0 | 16 | 25 | 23 | 25 | 25 | 0 | 0 | 42 | 30 | 160 | 0 | 0 | 202 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 22 | 24 | 120 | 120 | 135 | 0 | 310 | 193 | 8 | 141 | 40 | 20 | 5 | 54 | 85 | 0 | 0 | 22 | 11 | 33 | 15 | 90 | 52 | 48 | 22 | 0 | 26 | 63 | 50 | 50 | 130 | 0 | 68 | 86 | 47 | 80 | 20 | 46 | 10 | 120 | 25 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 40 | 0 | 0 |  | 687 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 136 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 177 | 0 | 179 | 0 | 97 | 0 | 0 | 0 | 0 | 0 |  | 4790 | 1930 | 6720 | 3585 | 687 | 1745 | 375 | 149 | 72 | 17 | 90 | 0 | 0 | 0
24:00 | 37 | 0 | 0 | 0 | 300 | 94 | 40 | 160 | 331 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 23 | 25 | 25 | 0 | 0 | 42 | 0 | 160 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 120 | 120 | 135 | 0 | 305 | 187 | 8 | 140 | 40 | 20 | 5 | 54 | 85 | 0 | 0 | 22 | 11 | 0 | 15 | 84 | 52 | 0 | 22 | 0 | 26 | 63 | 50 | 50 | 130 | 0 | 67 | 86 | 47 | 80 | 20 | 47 | 0 | 95 | 25 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 686 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 187 | 0 | 189 | 0 | 94 | 0 | 0 | 0 | 0 | 0 |  | 4428 | 1859 | 6287 | 3603 | 686 | 1685 | 37 | 150 | 42 | 0 | 84 | 0 | 0 | 0
KWH | 874000 | 0 | 930000 | 0 | 7961609 | 1420773 | 744800 | 3703000 | 7424000 | 0 | 416000 | 9199500 | 0 | 274560 | 218664 | 404642 | 3591347 | 0 | 1306000 | 0 | 0 | 610128 | 53280 | 0 | 290880 | 0 | 300096 | 420120 | 400235 | 113570 | 289224 | 600000 | 524700 | 613500 | 609900 | 468576 | 0 | 953280 | 231500 | 3900000 | 0 | 124920 | 4848666 | 0 | 2681513 | 0 | 0 | 500160 | 200040 | 244851 | 69600 | 50880 | 243840 | 361488 | 361920 | 2659334 | 2364905 | 2835094 | 0 | 7333000 | 4635000 | 217454 | 2700660 | 703152 | 295680 | 120000 | 900454 | 218664 | 6008 | 187368 | 355212 | 128160 | 399200 | 386270 | 2119680 | 2072720 | 476160 | 365580 | 13550 | 562000 | 1427232 | 882000 | 902000 | 3188364 | 0 | 1449000 | 988800 | 880200 | 2001000 | 281000 | 821880 | 147240 | 6840500 | 518448 | 235104 | 0 | 785345 | 0 | 0 | 789600 | 0 | 531360 | 136620 | 925440 | 855840 | 0 | 0 |  | 15053818 | 0 | 6959808 | 0 | 0 | 0 | 0 | 0 | 43200 | 161152 | 341250 | 3015000 | 464800 | 313440 | 0 | 170000 | 1200000 | 0 | 0 | 141528 | 209720 | 0 | 21542 | 365760 | 102469 | 412800 | 81936 | 177444 | 0 | 0 | 3659900 | 0 | 0 | 4458891 | 0 | 4282355 | 0 | 1134862 | 0 | 0 | 0 | 0 | 478560 |  | 115178040 | 43250235 | 158428275 | 86886516 | 15053818 | 37648627 | 10750714 | 3659900 | 1184780 | 974070 | 2119680 | 150170 | 0
Fuel Cost | 751640 | 0 | 799800 | 0 | 5095429.76 | 1150826.13 | 700112 | 2258830 | 4528640 | 0 | 569920 | 6163665 | 0 | 1724236.8 | 1460675.52 | 2472362.62 | 2334375.55 | 0 | 1449660 | 0 | 0 | 4020743.52 | 515217.6 | 0 | 1742371.2 | 0 | 2001640.32 | 2995455.6 | 2501468.75 | 712083.9 | 216918 | 450000 | 0 | 0 | 0 | 4432728.96 | 0 | 0 | 0 | 4290000 | 0 | 1182992.4 | 3200119.56 | 0 | 3083739.95 | 0 | 0 | 4396406.4 | 2154430.8 | 2382400.23 | 430824 | 328684.8 | 1594713.6 | 307264.8 | 0 | 2419993.94 | 2152063.55 | 2579935.54 | 0 | 5059770 | 3244500 | 150043.26 | 2592633.6 | 471111.84 | 254284.8 | 110400 | 738372.28 | 207730.8 | 65126.72 | 1390270.56 | 273513.24 | 96120 | 307384 | 289702.5 | 14498611.2 | 1554540 | 4375910.4 | 281496.6 | 0 | 584480 | 1484321.28 | 846720 | 811800 | 2486923.92 | 0 | 1651860 | 1058016 | 968220 | 2281140 | 359680 | 764348.4 | 136933.2 | 4377920 | 388836 | 178679.04 | 0 | 5701604.7 | 0 | 0 | 5645640 | 0 | 0 | 0 | 0 | 7993545.6 | 0 | 0 |  | 76774471.8 | 0 | 4663071.36 | 0 | 0 | 0 | 0 | 0 | 486432 | 1898370.56 | 2689050 | 2080350 | 460152 | 2319456 | 0 | 178500 | 1260000 | 0 | 0 | 1268090.88 | 1814078 | 0 | 229422.3 | 3628339.2 | 1206060.13 | 454080 | 77019.84 | 134325.108 | 0 | 0 | 14127214 | 0 | 0 | 3032045.88 | 0 | 2997648.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 155234560.74 | 121778177.558 | 277012738.298 | 67405399.598 | 76774471.8 | 26446207.63 | 67555282.85 | 14127214 | 0 | 10205551.22 | 14498611.2 | 0 | 0
Yesterday Day Peak | 37 | 0 | 0 | 0 | 380 | 94 | 0 | 232 | 322 | 0 | 40 | 420 | 0 | 7 | 0 | 0 | 120 | 0 | 67 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 23 | 17 | 25 | 32 | 0 | 44 | 0 | 160 | 0 | 0 | 203 | 0 | 80 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 90 | 135 | 0 | 338 | 202 | 8 | 140 | 37 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 0 | 8 | 13 | 86 | 88 | 0 | 22 | 2.1 | 25 | 63 | 50 | 50 | 100 | 0 | 63 | 5 | 47 | 98 | 19 | 42 | 10 | 280 | 23 | 8 | 0 | 12 | 0 | 0 | 7 | 0 | 31 | 19.58 | 50 | 0 | 0 | 0 |  | 687 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 188 | 0 | 199 | 0 | 31 | 0 | 0 | 0 | 0 | 0 |  | 6719.68 | DayPeak
Yesterday Evening Peak | 37 | 0 | 0 | 0 | 340 | 94 | 60 | 95 | 322 | 0 | 0 | 380 | 0 | 70 | 32 | 55 | 150 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 23 | 25 | 25 | 0 | 0 | 41 | 30 | 160 | 0 | 25 | 202 | 0 | 130 | 0 | 0 | 32 | 55 | 51 | 15 | 12 | 50 | 19 | 11 | 120 | 120 | 135 | 0 | 305 | 184 | 8 | 140 | 37 | 20 | 5 | 54 | 85 | 0 | 44 | 22 | 11 | 33 | 21 | 120 | 71 | 79 | 22 | 0 | 26 | 63 | 50 | 50 | 130 | 0 | 54 | 86 | 47 | 78 | 19 | 48 | 10 | 250 | 25 | 11 | 0 | 120 | 0 | 0 | 151 | 0 | 97 | 0 | 90 | 145 | 0 | 0 |  | 686 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 17 | 60 | 40 | 115 | 25 | 80 | 0 | 51 | 30 | 0 | 0 | 52 | 50 | 0 | 14 | 52 | 39 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 176 | 0 | 192 | 0 | 98 | 0 | 0 | 0 | 0 | 105 |  | 8502 | EvPeak
Forecast for Evening | 37 | 0 | 0 | 0 | 380 | 101 | 40 | 300 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 225 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 47 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 25 | 43 | 0 | 100 | 60 | 160 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 40 | 80 | 51 | 100 | 92 | 50 | 22 | 10 | 120 | 90 | 135 | 0 | 305 | 221 | 8 | 150 | 40 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 121 | 70 | 79 | 22 | 0 | 26 | 76 | 51 | 44 | 163 | 0 | 66 | 86 | 50 | 79 | 20 | 50 | 10 | 0 | 25 | 11 | 200 | 300 | 300 | 100 | 185 | 100 | 133 | 0 | 100 | 200 | 0 |  |  | 694 | 30 | 310 | 0 | 115 | 0 | 0 | 0 | 30 | 75 | 40 | 145 | 26 | 110 | 30 | 0 | 70 | 50 | 50 | 93 | 50 | 50 | 40 | 52 | 39 | 22 | 5 | 8 | 0 | 0 | 150 | 18 | 18 | 210 | 0 | 185 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 37 | 0 | 0 | 0 | 380 | 101 | 40 | 300 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 225 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 47 | 0 | 43 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 25 | 43 | 0 | 100 | 60 | 160 | 0 | 25 | 225 | 0 | 131 | 0 | 0 | 40 | 80 | 51 | 100 | 92 | 50 | 22 | 10 | 120 | 90 | 135 | 0 | 305 | 221 | 8 | 150 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 96 | 55 | 79 | 22 | 2 | 26 | 76 | 51 | 44 | 163 | 0 | 66 | 86 | 50 | 79 | 20 | 50 | 10 | 0 | 25 | 8 | 200 | 300 | 300 | 0 | 180 | 100 | 133 | 20 | 100 | 200 | 0 |  |  | 694 | 0 | 310 | 0 | 115 | 0 | 0 | 0 | 0 | 75 | 40 | 119 | 26 | 110 | 0 | 0 | 70 | 0 | 0 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 150 |  | 0 | 210 | 0 | 180 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 37 | 0 | 0 | 0 | 300 | 101 | 40 | 250 | 344 | 0 | 0 | 360 | 0 | 0 | 4 | 0 | 150 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 47 | 0 | 0 | 54 | 36 | 0 | 0 | 25 | 23 | 25 | 25 | 10 | 0 | 42 | 0 | 160 | 0 | 25 | 202 | 0 | 131 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 120 | 120 | 135 | 0 | 250 | 182 | 8 | 134 | 37 | 5 | 5 | 35 | 85 | 0 | 3 | 22 | 5 | 17 | 10 | 72 | 53 | 43 | 22 | 0.8 | 26 | 63 | 45 | 40 | 130 | 0 | 53 | 86 | 47 | 80 | 20 | 45 | 10 | 0 | 24 | 8 | 0 | 12 | 0 | 0 | 48 | 0 | 0 | 10.5 | 77 | 18 | 0 | 0 | 0 | 347 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 119 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 80 | 0 | 187 | 0 | 51 | 0 | 0 | 0 | 0 | 78 | 0
199
| Minimum Generation |  | 5135 | 5:00
| Highest Generation |  | 8502 | 19:00
| Day Peak Generation |  | 6719.68 | 12:00
| Evening Peak Generation |  | 8502 | 19:00
| HVDC Max Flow |  | 693 | 10:00
| HVDC EvPeak Flow |  | 686 | 19:00
| Load factor L.F |  | 77.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-11-28
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-11-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6719.68 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5262 | MW
Evening Peak Generation : |  | 8502 | MW Hour : | 19:00 | Available Max Generation : |  | 11468 | MW
E.P. Demand (at gen end) : |  | 8502 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 8502 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2668 | MW
Total Gen. (MKWH) : |  | 158.4283 | System Load Factor : | 77.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -420 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-11-28
Actual : | 100.43 | Ft.(MSL) , | Rule curve : | 106.3 | Ft.( MSL )
Gas Consumed : | Total = | 1110.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93851607.228
|  | Coal : | 14127214 | Oil : | 77760834.07 | Total : | 185739655.298
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3115.7455 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1053.4925 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 942.8192 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 851.535 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 769.7304 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 621.1299 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 355.0694 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 160.1297 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 479.0091 |  |  | 0 | 0%
Total | 0 |  | 8348.6608 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Ashuganj (North)
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Bheramara-410 MW ST
3) Ghorasal Unit-2,3,5
4) Tongi GT
5) Shajibazar 330 MW
6) Baghabari 100 MW
7) Ashuganj (S) ST
8) Siddhirganj ST 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Ghorasal Unit-4 tripped at 08:11 due to gas pressure inlet valve problem.
b) Siddhirganj GT-2 was shut down at 10:33 due to gas shortage.
c) Raozan-Hathazari 230 kV Ckt-1 was under shut down from 09:06 to 16:08 for A/M.
d) Bakulia-Modern steel 132 kV Ckt-1 was under shut down from 09:05 to 14:39 for A/M.
e) Agargaon-Cantonment 132 kV Ckt-1 was under shut down from 09:00 to 10:33 for A/M.
f) Agargaon-Cantonment 132 kV Ckt-2 was under shut down from 10:34 to 10:58 for A/M.
g) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 08:47 to 13:40 for A/M.
h) Joydevpur-Kodda 132 kV Ckt-2 was under shut down from 08:46 to 15:56 for A/M.
i) Mymensingh 132/33 kV T3 transformer was under shut down from 09:13 to 15:20 for A/M.
j) Sherpur 132/33 kV T2 transformer was under shut down from 08:11 to 16:17 for A/M.
k) Manikganj 132/33 kV T3 transformer & Manikganj-Kabirpur 132 kV Ckt-1 were under shut down from
08:15 to 17:37 for A/M.
l) B.Baria 132/33 kV T2 transformer was under shut down from 08:50 to 15:25 for A/M.
m) Bogura-Sirajganj 132 kV Ckt-2 was under shut down from 08:14 to 16:02 for A/M.
n) Ishurdi-Bagabari 230 kV Ckt-2 was under shut down from 08:41 to 19:14 for A/M.
o) Khulna(C ) 132/33 kV T1 transformer was under shut down from 07:01 to 15:41 for A/M.
p) Noapara 132/33 kV T1 transformer was under shut down from 08:54 to 14:23 for A/M.
q) Bheramara HVDC-Khulna(S) 230 kV Ckt-1 was under shut down from 09:10 to 16:57 for A/M.
r) Saidpur 132/33 kV T2, T4 & 33 kv bus were under shut down from 08:50 to 17:50 for D/W.
s) Mirpur-Uttara 132 kV Ckt was under shut down from 10:15 to 19:21 for A/M.
t) Madunaghat-Khulshi 132 kV Ckt-2 tripped at 11:49 showing Dist. Trip,E/F, Dist. B-phase at Madunaghat
end & Dist. Protection trip, inst. E/F at Khulshi end and was switched on at 12:04.
u) Bhola 225 MW ST tripped at 17:16 due to internal fault.
v) Bakulia 132/33 kV T2 transformer tripped at 16:49 showing Diff. discrepnncy relay failure and was |  |  |  | About 40MW Power interruption occurred under Bakulia S/S
switched on at 19:13. |  |  |  | area from 16:49 to 19:13.
w) Haripur EGCB 412 MW ST was shut down at 19:49 for test purpose and was synchronized at 20:36,and
FSD at 21:50.
x) Siddhirganj Peaking GT1 was shut down at 14:06 due to gas shortage.
y) Baghabari 100 MW was shut down at 20:16 due to vibration high.
z) After maintenance Aminbazar-Savar 132 kV Ckt-2 was switched on at 22:52.
aa) Sirajganj Unit-1 CCPP ST tripped at 01:24 (28/11/2018) due to mal-function of L.P steam valve and was
synchronized at 07:22.
ab) Fenchuganj-Kulaura 132 kV Ckt-1 & 2 tripped at 01:40(28/11/2018) from Fenchuganj end showing |  |  |  | About 20MW Power interruption occurred under Kulaura S/S
Dist Z2 3-phase, Gen trip due to 132 kV B-phase PT of bus-1 at Kulaura got burst and were switched on |  |  |  | area from 01:40 to 04:04(28/11/2018).
at 04:04.
ac) Fenchuganj-Sylhet 132 kV Ckt tripped at 01:40 (28/11/2018) from Sylhet end showing Dist C-phase
and was switched on at 01:57.At the same time Fenchuganj Energy Prima, Fenchuganj Barakatullah & Sylhet
Energy Prima P/S got tripped
ad) Summit Bibiyana -2 CCPP ST & GT were shut down at 06:37 & 06:40 (28/11/2018) respectively due to HGPI.
ae) Khulna(C ) 132/33 kV T2 transformer was shut down at 07:02(28/11/2018) for A/M.
af) Barisal (Old) 132/33 kV T2 transformer was shut down at 07:18 to 09:40(28/11/2018) for D/W by |  |  |  | About 10MW Power interruption occurred under Barisal (Old) S/S
Distr. Utility. |  |  |  | area from 07:18 to 09:40 (28/11/2018)
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-11-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 874000 | #2 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 930000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 7961609 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 60 | 744800 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 94 | 1420773 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 416000 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 95 | 3703000 | Load decrease due to ST sync.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 322 | 7424000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 380 | 9199500 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 70 | 274560 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 32 | 218664 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 404642
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 289224
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 1306000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 150 | 3591347 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 610128
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 47 | 300096
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 420120
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 53280 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 400235
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 113570 | Low demand
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 47 | 290880 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1124700 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 613500 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 609900 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 468576 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 120 | 785345 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 97 | 531360 | Low demand
| Dhaka area Total |  |  |  | 5848 | 2329 | 45079809
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 160 | 3900000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 124920
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 136620
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 243840
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 71 | 1184780 | Unit-2,5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4848666 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2681513 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 500160 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 55 | 200040 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 51 | 244851
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 15 | 69600 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 0 | 90 | 925440 | On test
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 361488
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 11 | 361920
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 12 | 50880 | Low demand
| Chattogram area Total |  |  |  | 1581 | 923 | 15834718
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2659334 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2364905 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 2835094
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4635000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7333000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 37 | 703152 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 20 | 295680 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 54 | 900454
| Midland 150MW |  | IPP | 23*7.015 | 0 | 0 | 0 | On test
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 218664
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 6008 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 2700660
| Chandpur Desh 200MW |  | IPP | 0 | 0 | 145 | 855840 | On Test
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 355212
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 128160
** | Tripura |  | Imported power | 0 | 160 | 120 | 2119680
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 399200
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 44 | 187368 | Low demand
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 386270
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2541 | 1609 | 29421135
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 71 | 2072720 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 365580
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 79 | 476160 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 13550
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 151 | 789600 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 323 | 3717610
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 26 | 562000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1427232
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3188364 | Frequency Control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 882000
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 902000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 235104
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 54 | 1449000
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 988800
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 880200
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 2001000
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 281000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 48 | 821880
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 518448
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 250 | 6840500 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 147240
| Sylhet Area Total |  |  |  | 1549 | 947 | 21124768
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 686 | 15053818
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 17 | 43200 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 161152 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 305 | 6959808
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 341250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 478560
| Khulna Area Total |  |  |  | 2209 | 1213 | 23037788
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 313440 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 25 | 464800 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 115 | 3015000 | ST under maint.
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 1134862
| Barisal Area Total |  |  |  | 462 | 318 | 4928102
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 30 | 1200000 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 51 | 170000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 209720
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 14 | 21542 | Low demand
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 176 | 4458891 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4282355
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 39 | 102469
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 412800
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 81936 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 177444 | Engine problem
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 365760
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 52 | 141528 | Low demand
| Rajshahi Area Total |  |  |  | 1546 | 691 | 11624445
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3659900
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 149 | 3659900
| Total |  |  |  | 16742 | 8502 | 158428275
| Eastern Grid Total |  |  |  | 12041 | 6131 | 115178040
| Western Grid Total |  |  |  | 4701 | 2371 | 43250235
| National Grid Total |  |  |  | 16742 | 8502 | 158428275
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-11-27 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5561 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2493 | MW
i) Dhaka area |  |  | 3057 | MW | i) Khulna area |  |  | 974 | MW
ii) Chittagong area |  |  | 914 | MW | ii) Rajshahi area |  |  | 800 | MW
iii) Comilla area |  |  | 701 | MW | iii) Barisal area |  |  | 205 | MW
iv) Mymensingh area |  |  | 577 | MW | iv) Rangpur area |  |  | 514 | MW
v) Sylhet area |  |  | 312 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8054 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 104 | 1800 | Netrokona | 58 | 1800 | Goalpara | 19 | 1830
Munsiganj | 76 | 2000 | Jamalpur | 87 | 1830 | Central s/s | 63 | 1830
Sonargaon | 45 | 1900 | Sherpur | 64 | 1800 | Noapara | 67 | 1900
Shyampur | 150 | 800 | Srimongal | 24 | 1800 | Jessore | 106 | 1830
Bhulta | 151 | 1830 | Shahjibazar | 81 | 1830 | Jhenida | 72 | 1800
Madanganj | 57 | 1400 | Fenchuganj | 28 | 1900 | Bottail | 70 | 1800
Shitalakhya | 81 | 900 | Kulawara | 29 | 1800 | G.K Project | 44 | 1800
Rahim steel | 12 | 1830 | Sylhet | 89 | 1830 | Faridpur | 116 | 2000
Matuail | 80 | 800 | Chatak | 19 | 1830 | Madaripur | 92 | 1830
Ghorasal | 58 | 1800 | Sunamganj | 24 | 1830 | Gopalganj | 59 | 1800
Narsingdi | 104 | 2000 | Biani Bazar | 28 | 1800 | Bagerhat | 41 | 1700
Haripur (SBU) | 97 | 1900 | Comilla (S) | 122 | 1800 | Mongla | 30 | 100
Ullon | 56 | 1930 | Comilla(N) | 69 | 1900 | Satkhira | 64 | 1900
Hasnabad | 141 | 1800 | Chandpur | 77 | 1830 | Gallamari | 35 | 1300
Magbazar | 103 | 1200 | Feni | 87 | 1930 | Magura | 35 | 1900
Maniknagar | 71 | 1200 | Chowmuhani | 122 | 1830 | Chuadanga | 66 | 1900
Bangabhaban | 24 | 1000 | Ashuganj | 41 | 1900 | Barisal | 86 | 1830
Narinda | 70 | 1800 | Daudkandi | 82 | 1930 | Patuakhali | 61 | 1930
Dhanmondi | 84 | 1800 | B.Baria | 86 | 1830 | Bhandaria | 37 | 1830
Lalbag | 88 | 1800 | Ramganj | 24 | 1800 | Ishurdi | 41 | 1800
Madartek | 43 | 2000 | Madunaghat | 46.5 | 1800 | Ruppur Paromanobik | 1 | 2000
Mirpur | 81 | 1800 | Hathazari | 78 | 2000 | Natore | 82 | 1800
Kalyanpur | 87 | 1900 | Khulshi | 166 | 1400 | Bogra | 174 | 1830
Gulshan | 98 | 1300 | Halishahar | 109 | 1800 | Noagaon | 42 | 1830
Uttara | 61 | 1800 | Baraulia | 143 | 500 | Rajshahi | 99 | 1830
Uttara(New) | 6 | 1800 | Sikalbaha | 30 | 1900 | C.Nawabganj | 47 | 1800
Kamrangirchar | 64 | 1800 | Dohazari | 60 | 1800 | Amnura | 24 | 2000
Savar | 114 | 1800 | Cox'sbazar | 67 | 1830 | Pabna | 75 | 1830
Bhasantec | 123 | 1800 | Chandraghona | 18 | 1800 | Shahjadpur | 66 | 1800
Agargaon | 41 | 2000 | Kaptai | 3.5 | 1800 | Serajganj | 65 | 1830
Satmosjid | 68 | 1800 | A. Khaer Stl. | 16 | 1700 | Niyamatpur | 37 | 1800
Tongi | 106 | 126 | Bakulia | 80 | 1930 | Joypurhat | 39 | 1900
Kabirpur | 154 | 1830 | Julda | 22 | 900 | Rangpur | 96 | 1830
Basundhara | 100 | 1900 | TK chemical | 5.6 | 1200 | Lalmonirhat | 69 | 1800
Manikganj | 65 | 1830 | Modern Steel | 16 | 1100 | Saidpur | 96 | 1830
Joydevpur | 177 | 1200 | Shahmirpur | 21.5 | 1800 | Purbasadipur | 67 | 1830
New Tongi | 88 | 1100 | Khagrachhari | 14 | 1900 | Thakurgaon | 53 | 1800
Korda | 200 | 1830 | Matarbari | 18 | 1830 | Palashbari | 75 | 1830
Dhamrai | 46 | 1800 | Baroiar Hat | 18 | 1800 | Barapukuria | 40 | 1800
Tangail | 119 | 1930 | Rangamati | 8 | 1800 | Panchagar | 34 | 1800
Mymensing | 188 | 1830 | Abul Khair 230 | 181 | 2300
Kishorganj | 80 | 1900 | BSRM | 104 | 900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-11-27
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 394 | 5:00 | 383 | 12:00 | Kaliakoir | 379 | 1:00 | 362 | 12:00
Bheramara | 407 | 2:00 | 396 | 18:00 | Bhulta | 392 | 4:00 | 378 | 16:00
Ashuganj(N) | 393 | 6:00 | 380 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 219 | 5:00 | 208 | 16:00
Ishurdi | 236 | 1:00 | 225 | 11:00 | Megnaghat | 230 | 1:00 | 220 | 13:00
Ashuganj | 236 | 7:00 | 230 | 16:00 | Fenchuganj | 239 | 1:00 | 232 | 10:00
Serajganj | 230 | 2:00 | 221 | 11:00 | Siddhirganj | 229 | 1:00 | 219 | 12:00
Baghabari | 230 | 1:00 | 223 | 12:00 | Maniknagar | 225 | 1:00 | 216 | 15:00
Barapukuria | 233 | 2:00 | 223 | 18:00 | Old Airport | 227 | 5:00 | 215 | 16:00
Bogra | 229 | 1:00 | 219 | 18:00 | Barisal | 232 | 17:00 | 222 | 12:00
Khulna South | 238 | 5:00 | 215 | 12:00 | AKSML | 221 | 18:30 | 209 | 12:00
Rampura | 227 | 5:00 | 220 | 10:00 | BSRM | 223 | 18:30 | 213 | 12:00
Haripur | 225 | 7:00 | 217 | 16:00 | Bibiyana | 235 | 1:00 | 229 | 11:00
Hasnabad | 225 | 3:00 | 218 | 11:00 | Bhulta | 227 | 2:00 | 217 | 16:00
Aminbazar | 227 | 5:00 | 216 | 16:00 | Ashuganj (S) | 236 | 2:00 | 229 | 11:00
Tongi | 226 | 7:00 | 215 | 11:00 | Kaliakoir | 231 | 5:00 | 219 | 12:00
Comilla (N) | 235 | 23:00 | 225 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 600 | 125 | 1600 | Ramganj | 133 | 900 | 130 | 2100
Munsiganj | 136 | 2000 | 124 | 1500 | Madanhat | 132 | 1930 | 127 | 1500
Megnaghat | 131 | 2000 | 127 | 1700 | Hathazari | 132 | 1900 | 125 | 1600
Shyampur | 130 | 600 | 120 | 1500 | Khulshi | 129 | 1900 | 122 | 1200
Bhulta | 132 | 100 | 127 | 1200 | Halishahar | 132 | 1900 | 124 | 1200
Madanganj | 135 | 600 | 127 | 1200 | Baraulia | 130 | 1830 | 123 | 1200
Shitalakhya | 138 | 1800 | 127 | 1100 | Sikalbaha | 131 | 1830 | 125 | 1600
Rahim steal | 132 | 100 | 126 | 1500 | Dohazari | 129 | 1700 | 125 | 1200
Matuail | 131 | 600 | 125 | 1400 | Cox'sbazar | 126 | 800 | 121 | 1200
Ghorasal | 135 | 100 | 134 | 1800 | Chandraghona | 133 | 1900 | 126 | 1200
Narsinghdi | 137 | 1700 | 132 | 100 | Kaptai | 132 | 1900 | 126 | 1200
Haripur (SBU) | 132 | 100 | 131 | 700 | A. Khaer Stl. | 128 | 1700 | 124 | 1200
Ullon | 134 | 200 | 127 | 1200 | Bakulia | 129 | 1900 | 123 | 1200
Hasnabad | 135 | 700 | 128 | 1000 | Julda | 130 | 1800 | 123 | 1200
Magbazar | 136 | 500 | 127 | 1100 | TK Chemical | 133 | 1900 | 128 | 1100
Maniknagar | 135 | 100 | 129 | 1600 | Modern Steel | 130 | 1700 | 123 | 1500
Bangabhaban | 135 | 500 | 122 | 1600 | Shahmirpur | 130 | 1900 | 123 | 1200
Narinda | 124 | 100 | 126 | 1600 | Khagrachhari | 132 | 1900 | 125 | 1200
Dhanmondi | 134 | 200 | 127 | 1200 | Matarbari | 125 | 400 | 121 | 1600
Lalbag | 135 | 500 | 122 | 1600 | Baroiar Hat | 133 | 1900 | 125 | 1200
Madartek | 124 | 100 | 126 | 1600 | Rangamati | 132 | 1900 | 125 | 1200
Mirpur | 136 | 300 | 131 | 1200 | Goalpara | 137 | 1700 | 124 | 1200
Kalyanpur | 137 | 200 | 131 | 1200 | Central s/s | 137 | 1700 | 123 | 1200
Gulshan | 134 | 200 | 127 | 1200 | Noapara | 136 | 1700 | 121 | 1200
Uttara | 137 | 300 | 127 | 1200 | Jessore | 132 | 1700 | 120 | 1200
Uttara(New) | 135 | 300 | 127 | 1200 | Jhenida | 134 | 1700 | 125 | 1200
Kamrangirchar | 134 | 500 | 126 | 1200 | Bottail | 137 | 1700 | 130 | 1200
Savar | 133 | 500 | 126 | 1200 | G.K.Project | 141 | 1700 | 137 | 1200
Bhasantec | 138 | 500 | 130 | 1200 | Faridpur | 135 | 1700 | 128 | 2100
Agargaon | 137 | 300 | 130 | 1200 | Madaripur | 137 | 1700 | 129 | 2100
Satmosjid | 138 | 500 | 130 | 1200 | Gopalganj | 141 | 1700 | 127 | 2100
Tongi | 137 | 2300 | 130 | 1100 | Bagerhat | 136 | 1700 | 120 | 1200
Kabirpur | 136 | 300 | 128 | 1200 | Mongla | 134 | 1700 | 119 | 1200
Basundhara | 131 | 400 | 122 | 1600 | Satkhira | 136 | 1700 | 123 | 1200
Manikganj | 141 | 600 | 131 | 1600 | Gallamari | 137 | 1700 | 124 | 1200
Joydevpur | 143 | 1300 | 132 | 2200 | Magura | 135 | 1700 | 125 | 1200
New Tongi | 138 | 300 | 129 | 1200 | Chuadanga | 131 | 1700 | 122 | 1200
Kodda | 140 | 700 | 129 | 2100 | Barisal | 138 | 4700 | 133 | 1200
Dhamrai | 137 | 200 | 128 | 1600 | Patuakhali | 135 | 400 | 127 | 1200
Tangail | 137 | 400 | 128 | 1600 | Bhandaria | 137 | 1700 | 125 | 1200
Mymensing | 136 | 400 | 129 | 1200 | Ishurdi | 141 | 100 | f | 1200
Kishorganj | 136 | 400 | 130 | 1200 | Ruppur Paromanobik | 142 | 100 | 136 | 1800
Netrokona | 136 | 300 | 130 | 1200 | Natore | 138 | 100 | 131 | 1200
Jamalpur | 138 | 1830 | 125 | 1200 | Bogra | 137 | 500 | 130 | 1800
Sherpur | 137 | 2000 | 123 | 1200 | Noagaon | 134 | 500 | 127 | 1800
Srimongal | 140 | 900 | 137 | 1600 | Rajshahi | 135 | 1700 | 126 | 1200
Shahjibazar | 139 | 1700 | 136 | 1200 | C.Nawabganj | 133 | 1930 | 125 | 1200
Fenchuganj | 138 | 1700 | 134 | 1500 | Amnura | 132 | 500 | 124 | 1200
Khulawara | 137 | 400 | 134 | 1600 | Pabna | 136 | 100 | 130 | 1800
Sylhet | 136 | 100 | 135 | 1000 | Shahjadpur | 143 | 600 | 136 | 1830
Chatak | 136 | 100 | 134 | 1600 | Serajganj | 136 | 400 | 130 | 1800
Sunamganj | 136 | 100 | 134 | 1000 | Niyamatpur | 133 | 100 | 125 | 1800
Biani Bazar | 137 | 2400 | 135 | 1100 | Joypurhat | 136 | 200 | 127 | 1800
Cumilla(s) | 132 | 2000 | 127 | 1700 | Rangpur | 130 | 600 | 119 | 1800
Cumilla(n) | 140 | 700 | 136 | 1000 | Lalmonirhat | 130 | 600 | 114 | 1800
Chandpur | 141 | 2200 | 135 | 700 | Saidpur | 130 | 600 | 121 | 1800
Feni | 133 | 1900 | 128 | 1100 | Purbasadipur | 132 | 500 | 120 | 1830
Chowmuhani | 131 | 700 | 125 | 1200 | Thakurgaon | 134 | 100 | 107 | 1800
Ashuganj | 140 | 600 | 137 | 1500 | Palashbari | 131 | 500 | 121 | 1830
Daudkandi | 134 | 2000 | 127 | 1600 | Barapukuria | 133 | 600 | 123 | 1800
B.Baria | 139 | 2100 | 136 | 1500 | Panchagar | 126 | 500 | 107 | 1830

## L-Curve
Date | 2018-11-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 160 | 4428 | 1859 | 6287 |  |  |  | QF-LDC-12
0:30 | 215 | 4410.5 | 1631 | 6041.5 | Date: | 2018-11-27
1:00 | 270 | 4393 | 1403 | 5796
1:30 | 235 | 4229.5 | 1409 | 5638.5
2:00 | 200 | 4066 | 1415 | 5481
2:30 | 180 | 3950.5 | 1431.5 | 5382 | [5 empty] | Gen. at Eve. Peak | 8502 | 8502 MW (19:00 )
3:00 | 160 | 3835 | 1448 | 5283 | [6 empty] | 19:00
3:30 | 90 | 3788.5 | 1451 | 5239.5 | [5 empty] | Gen. at Day Peak | 6719.68 | 6719.68 MW (12:00 )
4:00 | 20 | 3742 | 1454 | 5196 | [6 empty] | 12:00
4:30 | 20 | 3713.5 | 1452 | 5165.5 | [5 empty] | Highest Generation | 8502
5:00 | 20 | 3685 | 1450 | 5135 | [6 empty] | 19:00
5:30 | 35 | 3790.5 | 1485.5 | 5276
6:00 | 50 | 3896 | 1521 | 5417
6:30 | 95 | 4035.185 | 1537.5 | 5572.685
7:00 | 140 | 4174.37 | 1554 | 5728.37
7:30 | 170 | 4421.085 | 1591.5 | 6012.585
8:00 | 200 | 4667.8 | 1629 | 6296.8
8:30 | 200 | 4697.11 | 1659.5 | 6356.61
9:00 | 200 | 4726.42 | 1690 | 6416.42
9:30 | 230 | 4663.375 | 1752.5 | 6415.875
10:00 | 260 | 4600.33 | 1815 | 6415.33
10:30 | 265 | 4582.555 | 1827.5 | 6410.055
11:00 | 270 | 4564.78 | 1840 | 6404.78
11:30 | 245 | 4718.73 | 1843.5 | 6562.23
12:00 | 220 | 4872.68 | 1847 | 6719.68
12:30 | 210 | 4980.99 | 1889.5 | 6870.49
13:00 | 200 | 5089.3 | 1932 | 7021.3
13:30 | 280 | 4803.885 | 1929 | 6732.885
14:00 | 360 | 4518.47 | 1926 | 6444.47
14:30 | 355 | 4621.485 | 1909.5 | 6530.985
15:00 | 350 | 4724.5 | 1893 | 6617.5
15:30 | 350 | 4723.35 | 1852.5 | 6575.85
16:00 | 350 | 4722.2 | 1812 | 6534.2
16:30 | 273 | 4771.68 | 1898.5 | 6670.18
17:00 | 196 | 4821.16 | 1985 | 6806.16
17:30 | 258 | 5449.58 | 2154.5 | 7604.08
18:00 | 320 | 6078 | 2324 | 8402
18:30 | 350 | 6104.5 | 2347.5 | 8452
19:00 | 380 | 6131 | 2371 | 8502
19:30 | 380 | 6167 | 2316 | 8483
20:00 | 380 | 6131 | 2274 | 8405 |  |  |  | Executive Engineer
20:30 | 375 | 6129.5 | 2206 | 8335.5 |  |  |  | Network Operation Division
21:00 | 370 | 6128 | 2138 | 8266
21:30 | 310 | 5788 | 2045.5 | 7833.5
22:00 | 250 | 5448 | 1953 | 7401 |  |  |  |  | Page 6 of 7
22:30 | 155 | 5119 | 1941.5 | 7060.5
23:00 | 60 | 4790 | 1930 | 6720
23:30 | 110 | 4609 | 1894.5 | 6503.5
24:00 | 160 | 4428 | 1859 | 6287
8502 MW (19:00 )
6719.68 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-11-27 |  | Energy | 158428275
[10 empty] | 2018-11-27 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3603 | 686 | 1685 | 37 | 150 | 42 | 0 | 0 | 84
0:30 | 3624.5 | 592 | 1506 | 29.5 | 150 | 58.5 | 0 | 0 | 81 | Date: | 2018-11-27
1:00 | 3646 | 498 | 1327 | 22 | 150 | 75 | 0 | 0 | 78
1:30 | 3583 | 497.5 | 1251.5 | 22 | 150 | 58.5 | 0 | 0 | 76 | [7 empty] | Total Energy | 158.4283 | Total Energy Gen 158.428 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 158.428 MKWHr
2:00 | 3520 | 497 | 1176 | 22 | 150 | 42 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3440.5 | 497 | 1157.5 | 22 | 150 | 42 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 158.4283
3:00 | 3361 | 497 | 1139 | 22 | 150 | 42 | 0 | 0 | 72
3:30 | 3328.5 | 497 | 1129 | 22 | 150 | 42 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3296 | 497 | 1119 | 22 | 150 | 42 | 0 | 0 | 70
4:30 | 3266 | 497 | 1119.5 | 22 | 150 | 41 | 0 | 0 | 70
5:00 | 3236 | 497 | 1120 | 22 | 150 | 40 | 0 | 0 | 70
5:30 | 3337.5 | 497 | 1158.5 | 22 | 150 | 40 | 0 | 0 | 71
6:00 | 3439 | 497 | 1197 | 22 | 150 | 40 | 0 | 0 | 72
6:30 | 3564 | 497 | 1227 | 20.5 | 150 | 40 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3689 | 497 | 1257 | 19 | 150 | 40 | 0 | 0 | 72
7:30 | 3837 | 497 | 1361.5 | 45.5 | 150 | 40 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3985 | 497 | 1466 | 72 | 150 | 40 | 0 | 0 | 76
8:30 | 3883 | 515 | 1579.5 | 98 | 149.5 | 41 | 0 | 0 | 77
9:00 | 3781 | 533 | 1693 | 124 | 149 | 42 | 0 | 0 | 78
9:30 | 3723 | 613 | 1646 | 144.5 | 149 | 42 | 0 | 0 | 80
10:00 | 3665 | 693 | 1599 | 165 | 149 | 42 | 0 | 0 | 82
10:30 | 3652 | 690 | 1595.5 | 177 | 149.5 | 42 | 0 | 0 | 83
11:00 | 3639 | 687 | 1592 | 189 | 150 | 42 | 0 | 0 | 84
11:30 | 3757.5 | 687 | 1622.5 | 196 | 149.5 | 43 | 0 | 0 | 85
12:00 | 3876 | 687 | 1653 | 203 | 149 | 44 | 0 | 0 | 86
12:30 | 3869 | 687 | 1782 | 234.5 | 149 | 42 | 0 | 0 | 86
13:00 | 3862 | 687 | 1911 | 266 | 149 | 40 | 0 | 0 | 86
13:30 | 3862 | 687 | 1911 | 266 | 149 | 40 | 0 | 0 | 86
14:00 | 3862 | 687 | 1911 | 266 | 149 | 40 | 0 | 0 | 86
14:30 | 3789.5 | 687 | 1776 | 273.5 | 149 | 40 | 0 | 0 | 88
15:00 | 3717 | 687 | 1641 | 281 | 149 | 40 | 0 | 0 | 90
15:30 | 3701 | 686.5 | 1625.5 | 268.5 | 147 | 41 | 7 | 0 | 90
16:00 | 3685 | 686 | 1610 | 256 | 145 | 42 | 14 | 0 | 90
16:30 | 3539 | 686.5 | 1676.5 | 434 | 147 | 42 | 50 | 0 | 92
17:00 | 3393 | 687 | 1743 | 612 | 149 | 42 | 86 | 0 | 94
17:30 | 3595 | 686.5 | 1856 | 960 | 149 | 57 | 192.5 | 0 | 108
18:00 | 3797 | 686 | 1969 | 1308 | 149 | 72 | 299 | 0 | 122
18:30 | 3712 | 686 | 1914.5 | 1496.5 | 149 | 71.5 | 301.5 | 0 | 121
19:00 | 3627 | 686 | 1860 | 1685 | 149 | 71 | 304 | 0 | 120
19:30 | 3634 | 686 | 1841 | 1736 | 149 | 71 | 244 | 0 | 122
20:00 | 3660 | 686 | 1815 | 1759 | 149 | 71 | 145 | 0 | 120
20:30 | 3656 | 686 | 1849.5 | 1691.5 | 149 | 71.5 | 117 | 0 | 115
21:00 | 3652 | 686 | 1884 | 1624 | 149 | 72 | 89 | 0 | 110
21:30 | 3647 | 686 | 1892 | 1220 | 149 | 72 | 61.5 | 0 | 106
22:00 | 3642 | 686 | 1900 | 816 | 149 | 72 | 34 | 0 | 102
22:30 | 3613.5 | 686.5 | 1822.5 | 595.5 | 149 | 72 | 25.5 | 0 | 96
23:00 | 3585 | 687 | 1745 | 375 | 149 | 72 | 17 | 0 | 90
23:30 | 3594 | 686.5 | 1715 | 206 | 149.5 | 57 | 8.5 | 0 | 87 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 3603 | 686 | 1685 | 37 | 150 | 42 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 158.428 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 158.428 MKWHr
Note on W13: Author:

## Generation
2018-11-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 45 | 42 | 42 | 42 | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 44 | 40 | 40 | 40 | 42 | 42 | 42 |  | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 953280
2 | Kaptai Unit-4 & 5 | 30 | 0 | [14 empty] | 0 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 231500
3 | Chattogram ST-1 (Raozan) | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3900000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [15 empty] | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 0 |  |  | 124920
| Teknaf Solartech 20MW | [5 empty] | 0 | 4.27 | 10 | 14.92 | 18.33 | 19.58 | 19.58 | 18.3 | 15.77 | 11.3 | 5.4 | 0.16 | 0 | [8 empty] | 136620
6 | Sikalbaha 225MW (Gas) | 197 | 200 | 201 | 201 | 201 | 209 | 207 | 210 | 194 | 195 | 203 | 203 | 203 | 202 | 203 | 216 | 202 | 214 |  | 202 | 201 | 203 | 202 | 202 | 202 | 203 | 4848666
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 132 | 80 | 80 | 80 | 80 | 100 | 130 | 111 | 110 | 110 | 90 | 80 | 145 | 100 | 130 | 130 | 100 | 133 |  | 130 | 131 | 130 | 130 | 130 | 130 | 130 | 2681513
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [15 empty] | 0 | 34 | 51 |  | 51 | 51 | 34 | 34 | 34 | 17 | 0 | 244851
12 | Hathazari peaking | [16 empty] | 0 | 55 |  | 55 | 55 | 55 | 55 |  |  |  | 200040
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 8 |  | 0 | [6 empty] | 6008
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 80 | 70 | 80 | 80 | 80 | 80 | 80 | 160 | 140 | 90 | 67 | 67 | 57 | 35 | 0 | [11 empty] | 1306000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 120 | 120 | 120 | 135 | 180 | 235 | 180 | 120 | 120 | 218 | 140 | 140 | 140 | 120 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3591347
18 | Summit Gazipur -2 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 15 | 15 | 28 | 57 |  | 120 | 120 | 150 | 115 | 12 | 12 | 12 | 785345
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 874000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 120 | 120 | 119 | 121 | 119 | 118 | 120 | 120 | 0 | [17 empty] | 930000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 380 | 380 | 280 | 280 | 240 | 240 | 300 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 330 | 250 | 380 |  | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 7961609
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2659334
29 | Ashuganj ST: Unit- 4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2364905
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2835094
32 | Ashuganj Engines TSK | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 40 | 40 | 40 | 40 | 703152
33 | Ashuganj CCPP 225 MW | 182 | 182 | 196 | 187 | 183 | 203 | 205 | 201 | 185 | 184 | 185 | 202 | 185 | 185 | 194 | 204 | 184 | 203 |  | 184 | 184 | 184 | 184 | 189 | 193 | 187 | 4635000
34 | Ashuganj CCPP(South) | 305 | 272 | 276 | 264 | 253 | 290 | 334 | 334 | 305 | 305 | 305 | 338 | 305 | 305 | 345 | 342 | 253 | 331 |  | 305 | 305 | 305 | 305 | 309 | 310 | 305 | 7333000
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5 | 5 | 5 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 295680
36 | Chandpur CCPP | 88 | 87 | 88 | 88 | 88 | 88 | 88 | 89 | 89 | 88 | 87 | 140 | 135 | 140 | 140 | 140 | 138 | 140 |  | 140 | 140 | 137 | 135 | 140 | 141 | 140 | 2700660
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | [10 empty] | 416000
39 | Haripur 412 MW CCPP | 300 | 300 | 220 | 220 | 220 | 250 | 280 | 211 | 20 | 30 | 76 | 232 | 134 | 22 | 38 | 98 | 100 | 99 |  | 95 | 95 | 99 | 99 | 99 | 99 | 160 | 3703000
40 | Meghnaghat CCPP 450MW | 370 | 370 | 340 | 320 | 350 | 380 | 380 | 380 | 450 | 450 | 420 | 420 | 450 | 340 | 350 | 350 | 350 | 450 |  | 380 | 380 | 380 | 400 | 400 | 400 | 380 | 9199500
41 | Haripur Power CCPP 360MW | 326 | 300 | 302 | 282 | 251 | 282 | 340 | 342 | 365 | 323 | 281 | 322 | 351 | 222 | 262 | 272 | 292 | 352 |  | 322 | 318 | 320 | 352 | 343 | 322 | 331 | 7424000
42 | Mymensingh RPCL 210MW | 105 | 106 | 105 | 106 | 106 | 106 | 108 | 107 | 107 | 95 | 89 | 88 | 85 | 79 | 82 | 82 | 81 | 71 |  | 71 | 72 | 72 | 54 | 52 | 52 | 52 | 2072720
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 26 | 26 | 26 | 10 | 10 | 10 | 26 | 26 | 24 | 24 | 21 | 25 | 27 | 25 | 26 | 26 | 26 | 26 |  | 26 | 27 | 26 | 26 | 26 | 26 | 26 | 562000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 40 | 40 | 40 | 60 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 62 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1427232
46 | Shajibazar 330 MW
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 65 | 63 | 64 | 50 | 67 | 68 | 68 | 62 | 56 | 61 | 63 | 54 | 56 | 63 | 63 | 47 | 62 |  | 54 | 55 | 52 | 87 | 67 | 68 | 67 | 1449000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 86 | 50 | 50 | 50 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 988800
49 | Shahjibazar (EPL) 50MW | 47 | 20 | 5 | 5 | 5 | 5 | 5 | 47 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 880200
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 79 | 80 | 78 | 80 | 78 | 78 | 80 | 98 | 48 | 47 | 88 | 88 | 69 | 133 |  | 78 | 80 | 78 | 98 | 98 | 80 | 80 | 2001000
51 | Sylhet GT 20 MW | [8 empty] | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 281000
52 | Sylhet (EPL) 50MW | 47 | 7 | 5 | 5 | 5 | 5 | 7 | 45 | 45 | 43 | 41 | 42 | 44 | 44 | 44 | 44 | 45 | 47 |  | 48 | 48 | 48 | 49 | 47 | 46 | 47 | 821880
53 | Sylhet (Desh) 10MW | [8 empty] | 0 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 147240
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235104
55 | Fenchugonj (Barakatullah) 51MW | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 43 | 45 | 45 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 882000
56 | Shahjahanulla 25 MW | [6 empty] | 0 | 22 | 24 | 24 | 24 | 23 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 518448
57 | Summit Bibiana- 2 | 280 | 275 | 285 | 305 | 285 | 280 | 300 | 290 | 260 | 245 | 265 | 280 | 275 | 250 | 260 | 255 | 240 | 260 |  | 250 | 280 | 255 | 270 | 260 | 120 | 95 | 6840500
58 | Southern 55MW | [15 empty] | 0 | 17 | 36 |  | 36 | 36 | 17 | 17 | 0 |  |  | 113570
59 | Sikalbaha (Energis) | [6 empty] | 0 | 1 | 24 | 40 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 40 | 16 | 0 | 500160
60 | Barabkunda (Regent) | 22 | 0 |  |  |  |  | 0 | 16 | 20 | 22 | 20 | 0 | 20 | 20 | 19 | 19 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 361488
61 | Narshingdi (Doreen) | [6 empty] | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 16 | 16 | 0 | 289224
62 | Tangail (Doreen) 22MW | [6 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 365580
63 | Tripura | 78 | 74 | 72 | 70 | 70 | 72 | 72 | 76 | 78 | 82 | 84 | 86 | 86 | 92 | 90 | 90 | 94 | 122 |  | 120 | 122 | 120 | 110 | 102 | 90 | 84 | 2119680
64 | Malancha, Ctg. EPZ (United) | 15 | 13 | 13 | 12 | 34 | 25 | 3 | 7 | 3 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 3 | 2 |  | 11 | 15 | 12 | 13 | 21 | 24 | 22 | 361920
65 | Feni (Doreen) 22MW | [6 empty] | 0 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 355212
66 | Feni, Mohipal (Doreen) | [6 empty] | 0 | 5 | 5 | 11 | 11 | 0 | 11 | 11 | 11 | 0 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 128160
67 | Jangalia (Summit) 33MW | [7 empty] | 8 | 0 | 8 | 8 | 8 | 26 | 26 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 399200
68 | Summit Cumilla 25MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 14 | 14 | 13 | 14 | 14 | 14 | 15 | 15 | 21 |  | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 386270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 10 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 524700
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 613500
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 609900
73 | Ghorashal (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 51 | 51 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 87 |  | 94 | 94 | 94 | 97 | 98 | 101 | 94 | 1420773
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [7 empty] | 11 | 30 | 30 | 30 | 32 | 30 | 32 | 34 | 38 | 0 | 13 |  | 0 | 10 | 33 | 43 | 43 | 0 |  | 468576
79 | Kodda 149MW | [16 empty] | 0 | 16 |  | 16 | 10 | 0 | 0 |  |  |  | 53280
80 | Jamalpur 95MW | [15 empty] | 0 | 7 | 50 |  | 79 | 79 | 79 | 79 | 79 | 48 | 0 | 476160
81 | Lakdhanvi 52 MW | [15 empty] | 0 | 3 | 25 |  | 44 | 52 | 52 | 52 | 0 | 0 |  | 187368
82 | Madanganj 102MW | [16 empty] | 0 | 14 |  | 32 | 48 | 66 | 75 | 0 | 0 |  | 218664
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 50 | 85 | 85 | 85 | 85 | 85 | 52 | 52 | 50 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 218664
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [8 empty] | 0 | 2 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 4 |  | 70 | 100 | 75 | 40 | 0 |  |  | 274560
88 | Ghorashal 78MW (MAX) | [12 empty] | 0 | 50 | 76 | 77 | 60 | 60 |  | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 744800
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [16 empty] | 0 | 15 |  | 15 | 15 | 15 | 15 | 0 | 0 |  | 69600
92 | Fenchuganj (EPL) 44MW | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 47 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 902000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 35 | 51 | 51 | 51 | 51 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 900454
94 | Gagnagar (Orion) | [10 empty] | 2 | 14 | 24 | 24 | 24 | 24 | 32 | 80 |  | 102 | 102 | 102 | 102 | 40 | 0 | 0 | 610128
95 | Patenga 50MW | [15 empty] | 0 | 27 | 44 |  | 50 | 50 | 50 | 50 | 19 | 0 |  | 243840
96 | Chattogram ECPV 108 MW | [16 empty] | 0 | 12 |  | 12 | 12 | 12 | 12 | 0 |  |  | 50880
97 | Katpotti 51 MW | [15 empty] | 0 | 4 | 46 |  | 47 | 48 | 47 | 48 | 47 | 47 | 0 | 300096
98 | Bosila 108MW | [15 empty] | 0 | 44 | 47 |  | 47 | 47 | 47 | 47 | 47 | 38 | 0 | 290880
99 | Madanganj-55 MW | [11 empty] | 0 | 15 | 15 | 15 | 15 | 30 | 55 |  | 55 | 55 | 55 | 55 | 55 | 0 | 0 | 404642
100 | Northern 55 MW | [10 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 48 | 55 |  | 55 | 55 | 55 | 55 | 18 | 0 |  | 400235
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 100 | 100 | 100 | 163 | 100 | 130 | 130 | 163 | 163 |  | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 3188364
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.8 | 1.5 | 2 | 2.2 | 2.1 | 2 | 1.7 | 1.2 | 0.8 | 0 | [9 empty] | 13550
103 | Banco Energy 54MW | [14 empty] | 0 | 18 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 18 | 420120
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 100 |  | 151 | 150 | 150 | 150 | 70 | 7 | 7 | 789600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [8 empty] | 1 | 24 | 31 | 31 | 31 | 31 | 31 | 31 | 36 | 68 |  | 97 | 84 | 80 | 27 | 0 |  |  | 531360
115 | Juldah 100 MW Unit-3 | [6 empty] | 0 | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 |  | 90 | 90 | 90 | 90 | 84 | 30 | 0 | 925440
116 | Chandpur Desh 200MW | [15 empty] | 0 | 28 | 94 |  | 145 | 145 | 146 | 146 | 100 | 40 | 0 | 855840
117 | Midland 150MW
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4393 | 4066 | 3835 | 3742 | 3685 | 3896 | 4174.37 | 4667.8 | 4726.42 | 4600.33 | 4564.78 | 4872.68 | 5089.3 | 4518.47 | 4724.5 | 4722.2 | 4821.16 | 6078 |  | 6131 | 6167 | 6131 | 6128 | 5448 | 4790 | 4428 | 115178040
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 3 | 7 |  | 17 | 17 | 17 | 0 |  |  |  | 43200
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [15 empty] | 0 | 35 | 105 |  | 105 | 105 | 105 | 105 | 0 |  |  | 478560
130
131
132
133
| Summit Barisal 110 MW | [15 empty] | 0 | 16 | 54 |  | 80 | 80 | 80 | 48 | 16 | 0 |  | 313440
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 11 | 11 | 10 | 11 | 11 | 11 | 12 | 12 | 28 | 32 | 31 | 31 | 89 | 90 | 52 | 13 | 51 | 96 |  | 98 | 98 | 98 | 98 | 97 | 97 | 94 | 1134862
| Bhola CCPP 194MW | 107 | 127 | 202 | 202 | 198 | 204 | 201 | 197 | 175 | 178 | 193 | 191 | 193 | 183 | 192 | 191 | 167 | 135 |  | 115 | 133 | 132 | 135 | 139 | 136 | 136 | 3015000
140 | Bhola (Venture) 33MW | 21 | 20 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 16 | 17 | 19 | 19 | 18 | 16 | 17 | 18 | 25 |  | 25 | 26 | 26 | 23 | 22 | 23 | 20 | 464800
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [11 empty] | 0 | 40 | 40 | 40 | 0 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 341250
143 | Gopalganj Peaking | [14 empty] | 0 | 14 | 33 | 61 |  | 60 | 20 | 13 | 0 |  |  |  | 161152
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 498 | 497 | 497 | 497 | 497 | 497 | 497 | 497 | 533 | 693 | 687 | 687 | 687 | 686 | 687 | 686 | 687 | 686 |  | 686 | 686 | 686 | 686 | 686 | 687 | 686 | 15053818
147 | Bheramara 360 MW | 260 | 260 | 220 | 220 | 220 | 280 | 307 | 308 | 305 | 302 | 304 | 293 | 296 | 297 | 298 | 296 | 250 | 300 |  | 305 | 303 | 304 | 305 | 305 | 304 | 305 | 6959808
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 145 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 3659900
153 | Baghabari GT 71MW | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 55 | 60 | 50 | 40 | 40 | 30 | 30 |  | 30 | 30 | 60 | 60 | 60 | 60 | 60 | 1200000
156 | Baghabari GT 100MW | [15 empty] | 0 | 50 | 50 |  | 51 | 50 | 50 |  |  |  |  | 170000
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas) | 160 | 152 | 152 | 159 | 159 | 164 | 167 | 177 | 192 | 173 | 185 | 188 | 181 | 174 | 187 | 182 | 182 | 182 |  | 176 | 174 | 174 | 175 | 175 | 177 | 187 | 4458891
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 146 | 148 | 138 | 136 | 136 | 136 | 141 | 177 | 195 | 177 | 178 | 199 | 183 | 178 | 189 | 185 | 174 | 175 |  | 192 | 177 | 177 | 177 | 177 | 179 | 189 | 4282355
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 412800
163 | Bogra (EPL) | [7 empty] | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 81936
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 177444
165 | Amnura 50MW | [15 empty] | 0 | 12 | 50 |  | 50 | 50 | 50 | 50 | 0 |  |  | 209720
166 | Katakhali (Northern)
167 | Katakhali Peaking | [16 empty] | 0 | 11 |  | 14 | 0 | [5 empty] | 21542
168 | Santahar Peaking | [15 empty] | 0 | 12 | 38 |  | 39 | 39 | 0 |  |  |  |  | 102469
169 | Rajlanka 52 MW | [12 empty] | 0 | 26 | 8 | 8 | 37 | 43 |  | 52 | 52 | 52 | 52 | 52 | 43 | 0 | 365760
170 | Chapainawabganj-100 MW | [15 empty] | 0 | 4 | 52 |  | 52 | 52 | 26 |  |  |  |  | 141528
171
172
173 | Rangpur GT
175 | Saidpur GT
176
177
178
178 | Western Zone Total | 1403 | 1415 | 1448 | 1454 | 1450 | 1521 | 1554 | 1629 | 1690 | 1815 | 1840 | 1847 | 1932 | 1926 | 1893 | 1812 | 1985 | 2324 |  | 2371 | 2316 | 2274 | 2138 | 1953 | 1930 | 1859 | 43250235