## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-11-14 | Wednesday
|  | Date (day): | 2018-11-14 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9865 | MW |  |  | (b) At Evening Peak Hour : |  | 10320 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-11-13 | 2018-11-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 254 | 247 | 255 | 255 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 220 | 220 | 220 | 220 | 145 |  | Gas shortage
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2018-01-12
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 361 | 351 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-2 under maint.
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 88 | 35 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 81 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 44 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 87 | 100 | 100 | 110 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 75 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Gas shortage
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 46 | 46 | 46
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 38 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 133 | 133 | 133 |  | 16 | Engine problem
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 46 | 46 | 47 | 47 |  | 61 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 50 | 50 | 50 |  | 30 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 168 | 268 | 300 | 300
35 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 53 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 51 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 87 | 105 | 133 | 133
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 2178 | 2781 | 3390 | 3490 | 803 | 1297
39 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint. |  | 2018-04-11
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
41 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.2 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 110 | 110 |  | 120 | #2,5 Under maint.
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 202 | 202 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 40 | 50 | 50
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 84 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 76 | 100 | 100
| Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 0 | 0 | 100 | 100 | 100 | 100 |  |  | On test
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 6 | 12 | 12
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 52 | 105 | 105 | 105
| Chattogram area Total |  |  |  |  | 1661 | 1581 | 623.2 | 831 | 955 | 935 | 510 | 160
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 110 | 90 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 120 | 120
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 192 | 221 | 221
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 350 | 360 | 360 |  | 0
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 316 | 301 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 30 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 16 | 16 | 179 |  | Gas shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| Midland 150MW |  | HFO | IPP | 23*7.015 | 0 | 0 | 7 | 5 | 0 | 0 |  |  | On test
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST Under maint.
| Chandpur Desh 200MW |  | HFO | IPP | 0 | 0 | 0 | 0 | 201 | 200 | 200 |  |  | On test
65 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
66 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 92 | 124 | 103 | 127
67 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
68 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
69 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 13 | 22 | 22
70 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2601 | 2541 | 1583 | 1843 | 2093 | 2167 | 441 | 73
71 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 48 | 49 | 50 | 50 | 152 |  | Gas shortage
72 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
73 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 79 | 79 | 79 | 79 |  | 16 | Engine problem.
74 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 2 | 0
75 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 150 | 185 | 190 | 190
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 299.2 | 333 | 341 | 339 | 152 | 16
76 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 57 | 26 | 26
77 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 63 | 77 | 77 | 77
78 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
79 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Uner maint. |  | 24/12/2018
80 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 38 | 50 | 50
81 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 42 | 44 | 44
82 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
83 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 57 | 35 | 35
84 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
85 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 34 | 40 | 42 | 42
86 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 90 | 130 | 130
87 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
88 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 48 | 48 | 48
89 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 25 | 25 | 25
90 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 260 | 341 | 341 |  |  | FGMO
91 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 907 | 1004 | 1088 | 1088 | 0 | 350
92 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 552 | 553 | 563 | 563
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 100 | 99 | 99 |  | 16 | Engine problem
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 0 | 25
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 6 | 35 | 75 | 75
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
99 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 96 | 96
101 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2278 | 2209 | 719 | 954 | 978 | 1035 | 0 | 426
102 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 54 | 110 | 110
103 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
104 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 20 | 25 | 25 |  | 8 | Engine problem
105 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 62 | 65 | 68 | 68 |  |  | GT-1 & ST under maint.
106 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 222 | 234 | 298 | 328 | 0 | 8
107 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 50 | 50
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
108 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
109 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 48 | 0 | 55
110 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
111 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 50 | 50 |  | 0
112 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37
113 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
114 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 220 | 220 | 220
115 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 3 | 6 | 20 | 20 | 121 |  | Gas shortage
116 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | On test.
117 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 0 | 38
118 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
119 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
120 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
121 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 44 | 52 | 52
122 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 93 | 93 |  | 11 | Engine problem
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 326 | 676 | 573 | 753 | 331 | 116
123 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
124 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 149 | 149 | 125
125 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
126 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 150 | 149 | 185 | 210 | 85
| Total |  |  |  |  | 17340 | 16742 | 7006.4 | 8806 | 9865 | 10320 | 2447 | 2531
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6666.662 | 8379 | 9386.6494 | 9819.5866
A. |  | 2018-11-13 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8806 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 5492 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8806 | MW
3 | Day peak Generation : |  |  | 7006.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8379 | MW
4 | Evening peak Generation : |  |  | 8806 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 165.3463 | MKWHr | By Solar | 0.10688 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 98.2229 | MKWHr |  | By Oil: | 47.0577 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.65 | MKWHr |  | By Hydro: | 1.6344 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2447 | MW | Dhaka | 3351 | 3351 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2531 | MW | Chittagong | 1003 | 1003 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4978 | MW | Khulna | 950 | 950 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 853.15 |  | MMCFD |  |  | Rajshahi | 818 | 818 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 72347330.694 | ii) Oil : | Taka | 356145956.52 | Comilla | 669 | 669 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14089000 | Total | Taka | 442582287.214 | Mymensingh | 558 | 558 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.4115 | MKWHr. | Sylhet | 331 | 331 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -720 | MW at | 18:00 | hrs | Barisal | 201 | 201 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -780 | MW at | 19:30 | hrs | Rangpur | 498 | 498 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 8379 | 8379 |  | 0
B. |  | 2018-11-14 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10320 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
4 | Reserve(Generation end) |  |  |  | 1220 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 170.8666 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5459 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.4415 | MKWHr. | ii) HVDC Flow at Peak Time |  | 553 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.233 | MKWHr. | iii) Maximum HVDC Flow : |  | 554 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.65 |  | (b) Today: | 101.55 |  | (c) Rule Curve: |  | 107.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-11-13
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 253 | 0 | 250 | 0 | 0 | 0 | 356 | 0 | 0 | 225 | 0 | 0 | 16 | 55 | 0 | 0 | 92 | 0 | 0 | 102 | 0 | 0 | 8 | 21 | 39 | 54 | 18 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 40 | 0 | 17 | 15 | 0 | 0 | 22 | 34 | 110 | 0 | 100 | 130 | 334 | 202 | 16 | 87 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 12 | 80 | 50 | 78 | 20 | 0 | 57 | 63 | 53 | 51 | 130 | 0 | 67 | 86 | 40 | 80 | 0 | 48 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 17 | 0 | 100 | 160 | 0 |  | 552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 20 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4932 | 1185 | 6117 | 2429 | 552 | 1635 | 967 | 149 | 70 | 235 | 80 | 0 | 0 | 101.67
2:00 | 35 | 0 | 257 | 0 | 250 | 0 | 0 | 0 | 335 | 0 | 0 | 225 | 0 | 0 | 16 | 55 | 0 | 0 | 92 | 0 | 0 | 102 | 0 | 0 | 8 | 21 | 39 | 54 | 18 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 17 | 15 | 0 | 0 | 22 | 26 | 110 | 0 | 100 | 20 | 309 | 190 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 12 | 78 | 50 | 78 | 20 | 0 | 57 | 63 | 53 | 51 | 130 | 0 | 67 | 86 | 40 | 80 | 0 | 48 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 100 | 150 | 0 |  | 553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4730 | 1172 | 5902 | 2285 | 553 | 1611 | 937 | 149 | 70 | 219 | 78 | 0 | 0 | 101.67
3:00 | 35 | 0 | 259 | 0 | 250 | 0 | 0 | 0 | 315 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 92 | 0 | 0 | 80 | 0 | 0 | 8 | 10 | 39 | 54 | 18 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 17 | 15 | 0 | 0 | 22 | 32 | 110 | 0 | 100 | 25 | 342 | 206 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 25 | 22 | 8 | 33 | 12 | 76 | 50 | 78 | 20 | 0 | 57 | 63 | 53 | 51 | 163 | 0 | 67 | 86 | 40 | 80 | 0 | 48 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 0 | 100 | 150 | 0 |  | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 52 | 0 | 14 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4697 | 1030 | 5727 | 2335 | 437 | 1607 | 816 | 149 | 70 | 237 | 76 | 0 | 0 | 101.66
4:00 | 35 | 0 | 258 | 0 | 250 | 0 | 0 | 0 | 351 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 87 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 39 | 54 | 18 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 22 | 32 | 110 | 0 | 100 | 35 | 309 | 190 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 8 | 22 | 8 | 33 | 12 | 74 | 50 | 78 | 20 | 0 | 57 | 63 | 53 | 51 | 163 | 0 | 67 | 86 | 40 | 80 | 0 | 49 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 0 | 100 | 135 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 52 | 0 | 12 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4595 | 1020 | 5615 | 2311 | 408 | 1672 | 729 | 149 | 70 | 202 | 74 | 0 | 0 | 101.66
5:00 | 35 | 0 | 257 | 0 | 250 | 0 | 0 | 0 | 351 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 87 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 39 | 54 | 18 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 22 | 42 | 110 | 0 | 100 | 75 | 316 | 191 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 12 | 74 | 50 | 64 | 20 | 0 | 57 | 63 | 53 | 51 | 130 | 0 | 67 | 86 | 40 | 80 | 0 | 48 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 0 | 80 | 90 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 12 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4454 | 1038 | 5492 | 2402 | 408 | 1630 | 556 | 149 | 70 | 203 | 74 | 0 | 0 | 101.65
6:00 | 35 | 0 | 259 | 0 | 250 | 0 | 0 | 0 | 363 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 37 | 21 | 39 | 54 | 36 | 0 | 22 | 25 | 25 | 25 | 33 | 2 | 0 | 38 | 30 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 22 | 40 | 110 | 0 | 100 | 95 | 309 | 193 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 22 | 8 | 33 | 12 | 70 | 51 | 70 | 20 | 0 | 57 | 63 | 53 | 51 | 163 | 0 | 67 | 86 | 40 | 0 | 0 | 48 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 89 | 128 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 12 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 201 | 0 | 95 | 0 | 0 | 0 | 0 | 0 |  | 4527 | 1056 | 5583 | 2357 | 408 | 1654 | 676 | 149 | 68 | 201 | 70 | 0 | 0 | 101.65
7:00 | 35 | 0 | 260 | 0 | 250 | 0 | 0 | 0 | 361 | 0 | 0 | 225 | 0 | 2 | 9 | 8 | 0 | 0 | 87 | 0 | 0 | 8 | 5 | 0 | 47 | 21 | 37 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 33 | 27 | 0 | 40 | 30 | 0 | 0 | 8 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 0 | 44 | 0 | 2 | 22 | 37 | 110 | 0 | 100 | 115 | 338 | 205 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 14 | 22 | 8 | 33 | 9 | 70 | 50 | 79 | 20 | 0.2 | 57 | 63 | 53 | 51 | 163 | 0 | 67 | 86 | 40 | 0 | 0 | 48 | 10 | 295 | 24 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 33 | 2 | 91 | 166 | 0 |  | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 52 | 0 | 21 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 94 | 0 | 0 | 0 | 0 | 17 |  | 4783.2 | 1098 | 5881.2 | 2383 | 408 | 1666 | 927 | 149 | 70 | 206 | 70 | 2.2 | 0 | 101.64
8:00 | 35 | 0 | 260 | 0 | 220 | 0 | 0 | 0 | 284 | 0 | 0 | 225 | 0 | 7 | 56 | 55 | 0 | 0 | 83 | 0 | 4 | 50 | 16 | 0 | 47 | 21 | 32 | 54 | 55 | 36 | 0 | 25 | 21 | 25 | 33 | 34 | 0 | 40 | 30 | 0 | 0 | 16 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 33 | 28 | 22 | 11 | 110 | 0 | 100 | 120 | 268 | 182 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 39 | 22 | 8 | 0 | 9 | 72 | 51 | 79 | 20 | 0.9 | 57 | 63 | 53 | 51 | 100 | 0 | 67 | 86 | 40 | 0 | 0 | 47 | 10 | 240 | 25 | 8 | 0 | 90 | 0 | 0 | 80 | 0 | 40 | 8.9 | 91 | 166 | 0 |  | 417 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 181 | 0 | 95 | 0 | 0 | 0 | 0 | 53 |  | 4844.8 | 1196 | 6040.8 | 2220 | 417 | 1448 | 1438 | 149 | 70 | 217 | 72 | 9.8 | 0 | 101.64
9:00 | 35 | 0 | 256 | 0 | 220 | 0 | 0 | 0 | 314 | 0 | 0 | 225 | 0 | 7 | 95 | 55 | 0 | 0 | 92 | 0 | 7 | 65 | 16 | 0 | 47 | 10 | 37 | 54 | 55 | 36 | 22 | 25 | 21 | 25 | 33 | 34 | 0 | 38 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 32 | 0 | 0 | 50 | 33 | 50 | 22 | 5 | 110 | 0 | 100 | 160 | 294 | 196 | 16 | 90 | 40 | 5 | 5 | 51 | 50 | 0 | 52 | 22 | 0 | 8 | 9 | 82 | 50 | 79 | 20 | 1.5 | 57 | 63 | 53 | 51 | 100 | 0 | 65 | 50 | 40 | 0 | 0 | 45 | 10 | 270 | 25 | 8 | 0 | 120 | 0 | 0 | 80 | 0 | 56 | 16 | 92 | 145 | 0 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 94 | 0 | 0 | 0 | 0 | 53 |  | 5059.5 | 1327 | 6386.5 | 2322 | 552 | 1426 | 1551 | 150 | 68 | 218 | 82 | 17.5 | 0 | 101.63
10:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 359 | 0 | 0 | 225 | 0 | 7 | 87 | 55 | 0 | 0 | 87 | 0 | 7 | 65 | 16 | 0 | 46 | 11 | 39 | 54 | 55 | 36 | 22 | 25 | 21 | 25 | 33 | 38 | 0 | 38 | 30 | 0 | 0 | 16 | 0 | 202 | 0 | 0 | 0 | 32 | 0 | 0 | 50 | 33 | 50 | 22 | 3 | 110 | 0 | 100 | 265 | 287 | 182 | 16 | 155 | 40 | 5 | 5 | 51 | 50 | 0 | 52 | 22 | 8 | 8 | 11 | 88 | 48 | 79 | 20 | 1.9 | 57 | 63 | 47 | 48 | 100 | 0 | 41 | 50 | 35 | 0 | 0 | 45 | 10 | 300 | 24 | 8 | 0 | 125 | 0 | 0 | 80 | 0 | 64 | 6 | 82 | 184 | 2 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 56 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 95 | 0 | 0 | 0 | 0 | 53 |  | 5265.9 | 1316 | 6581.9 | 2429 | 552 | 1486 | 1584 | 149 | 68 | 218 | 88 | 7.9 | 0 | 101.63
11:00 | 35 | 0 | 243 | 0 | 220 | 0 | 0 | 0 | 358 | 0 | 0 | 225 | 0 | 58 | 82 | 55 | 0 | 0 | 62 | 0 | 7 | 75 | 16 | 0 | 46 | 21 | 39 | 36 | 55 | 49 | 0 | 25 | 21 | 25 | 33 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 33 | 50 | 19 | 3 | 110 | 0 | 100 | 325 | 342 | 201 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 8 | 86 | 48 | 79 | 20 | 2.1 | 57 | 63 | 47 | 51 | 163 | 0 | 64 | 84 | 35 | 0 | 0 | 46 | 10 | 270 | 24 | 8 | 0 | 112 | 0 | 0 | 120 | 0 | 48 | 20 | 92 | 0 | 5 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 95 | 0 | 0 | 0 | 0 | 100 |  | 5368.1 | 1383 | 6751.1 | 2508 | 552 | 1592 | 1554 | 149 | 70 | 218 | 86 | 22.1 | 0 | 101.62
12:00 | 35 | 0 | 254 | 0 | 220 | 0 | 0 | 0 | 361 | 0 | 0 | 225 | 0 | 88 | 81 | 55 | 0 | 0 | 35 | 0 | 24 | 102 | 16 | 0 | 46 | 21 | 38 | 54 | 55 | 55 | 16 | 25 | 24 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 52 | 50 | 12 | 3 | 110 | 0 | 100 | 360 | 316 | 182 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 9 | 92 | 48 | 79 | 20 | 2.2 | 55 | 63 | 50 | 48 | 163 | 0 | 57 | 84 | 34 | 0 | 0 | 44 | 10 | 270 | 24 | 5 | 0 | 168 | 0 | 0 | 150 | 0 | 87 | 19.2 | 100 | 0 | 7 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 6 | 40 | 62 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 96 | 0 | 3 | 0 | 0 | 105 |  | 5590.4 | 1416 | 7006.4 | 2464 | 552 | 1593 | 1841 | 149 | 70 | 224 | 92 | 21.4 | 0 | 101.62
13:00 | 35 | 0 | 248 | 0 | 220 | 0 | 0 | 0 | 330 | 0 | 0 | 225 | 0 | 100 | 90 | 55 | 0 | 0 | 32 | 0 | 40 | 102 | 16 | 0 | 46 | 21 | 40 | 36 | 55 | 55 | 16 | 25 | 20 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 16 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 52 | 50 | 19 | 3 | 110 | 0 | 100 | 355 | 316 | 182 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 18 | 98 | 49 | 79 | 20 | 2 | 55 | 51 | 50 | 51 | 130 | 0 | 52 | 86 | 35 | 0 | 0 | 46 | 10 | 290 | 24 | 8 | 0 | 200 | 0 | 0 | 150 | 0 | 87 | 19.6 | 72 | 106 | 7 |  | 553 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 40 | 61 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 12 | 0 | 0 | 105 |  | 5667.6 | 1437 | 7104.6 | 2467 | 553 | 1558 | 1963 | 149 | 70 | 225 | 98 | 21.6 | 0 | 101.61
14:00 | 35 | 0 | 243 | 0 | 220 | 0 | 0 | 0 | 282 | 0 | 0 | 225 | 0 | 100 | 97 | 55 | 0 | 0 | 35 | 0 | 24 | 102 | 16 | 0 | 46 | 21 | 39 | 36 | 55 | 55 | 16 | 25 | 20 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 55 | 50 | 19 | 8 | 110 | 0 | 100 | 350 | 331 | 193 | 16 | 90 | 37 | 5 | 5 | 51 | 30 | 0 | 52 | 22 | 8 | 33 | 13 | 68 | 47 | 72 | 20 | 1.6 | 55 | 51 | 22 | 25 | 100 | 0 | 63 | 50 | 20 | 0 | 0 | 20 | 10 | 275 | 24 | 8 | 0 | 200 | 0 | 0 | 100 | 0 | 85 | 6.4 | 73 | 110 | 0 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 40 | 62 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 61 | 0 | 11 | 0 | 0 | 105 |  | 5310 | 1366 | 6676 | 2451 | 552 | 1250 | 1904 | 149 | 70 | 224 | 68 | 8 | 0 | 101.61
15:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 343 | 0 | 0 | 225 | 0 | 100 | 97 | 55 | 0 | 0 | 60 | 0 | 24 | 102 | 16 | 0 | 46 | 21 | 39 | 36 | 55 | 55 | 16 | 25 | 20 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 71 | 50 | 22 | 3 | 110 | 0 | 100 | 350 | 327 | 187 | 16 | 90 | 40 | 5 | 5 | 51 | 30 | 0 | 52 | 22 | 8 | 33 | 13 | 100 | 47 | 72 | 19 | 0.9 | 55 | 51 | 22 | 25 | 130 | 0 | 63 | 50 | 20 | 0 | 0 | 22 | 10 | 315 | 24 | 8 | 0 | 200 | 0 | 0 | 100 | 0 | 85 | 5.4 | 100 | 110 | 0 |  | 554 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 40 | 64 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 60 | 0 | 7 | 0 | 0 | 105 |  | 5534.3 | 1327 | 6861.3 | 2467 | 554 | 1376 | 1915 | 150 | 70 | 223 | 100 | 6.3 | 0 | 101.61
16:00 | 35 | 0 | 246 | 0 | 220 | 0 | 0 | 0 | 350 | 0 | 0 | 225 | 0 | 82 | 70 | 55 | 0 | 0 | 82 | 0 | 24 | 59 | 16 | 0 | 46 | 21 | 39 | 54 | 55 | 55 | 16 | 25 | 20 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 214 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 71 | 50 | 22 | 4 | 95 | 0 | 100 | 350 | 345 | 176 | 16 | 90 | 40 | 5 | 5 | 51 | 30 | 0 | 25 | 19 | 8 | 33 | 13 | 92 | 45 | 72 | 20 | 0.4 | 51 | 51 | 22 | 25 | 163 | 0 | 63 | 50 | 20 | 28 | 0 | 22 | 10 | 295 | 24 | 8 | 0 | 190 | 0 | 0 | 108 | 0 | 83 | 1.7 | 92 | 110 | 0 |  | 553 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 12 | 40 | 64 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 62 | 0 | 7 | 0 | 0 | 105 |  | 5481.1 | 1330 | 6811.1 | 2497 | 553 | 1399 | 1806 | 150 | 70 | 242 | 92 | 2.1 | 0 | 101.6
17:00 | 35 | 0 | 245 | 0 | 220 | 0 | 0 | 0 | 312 | 70 | 0 | 225 | 0 | 57 | 70 | 55 | 0 | 0 | 27 | 0 | 32 | 60 | 100 | 6 | 46 | 21 | 39 | 54 | 55 | 55 | 16 | 25 | 20 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 12 | 34 | 50 | 90 | 50 | 22 | 9 | 90 | 0 | 100 | 350 | 279 | 188 | 16 | 90 | 30 | 5 | 5 | 51 | 30 | 25 | 34 | 22 | 8 | 33 | 13 | 104 | 48 | 79 | 20 | 0 | 55 | 78 | 22 | 25 | 100 | 0 | 40 | 50 | 20 | 48 | 0 | 21 | 10 | 265 | 24 | 8 | 0 | 195 | 0 | 0 | 120 | 0 | 87 | 0.2 | 92 | 195 | 0 |  | 553 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 12 | 12 | 40 | 48 | 17 | 16 | 0 | 0 | 0 | 0 | 24 | 60 | 50 | 16 | 15 | 52 | 23 | 21 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 62 | 0 | 7 | 0 | 0 | 105 |  | 5616.2 | 1479 | 7095.2 | 2386 | 553 | 1271 | 2043 | 150 | 70 | 518 | 104 | 0.2 | 0 | 101.6
18:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 351 | 110 | 0 | 225 | 0 | 35 | 80 | 55 | 0 | 0 | 87 | 0 | 75 | 102 | 133 | 44 | 46 | 46 | 40 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 84 | 51 | 76 | 105 | 50 | 22 | 6 | 90 | 0 | 100 | 350 | 301 | 192 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 8 | 33 | 13 | 124 | 49 | 79 | 20 | 0 | 57 | 77 | 38 | 42 | 163 | 0 | 57 | 86 | 40 | 90 | 0 | 48 | 10 | 260 | 25 | 11 | 20 | 268 | 53 | 50 | 185 | 51 | 105 | 0 | 100 | 201 | 5 |  | 553 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 25 | 35 | 40 | 65 | 20 | 54 | 0 | 0 | 0 | 50 | 48 | 93 | 50 | 43 | 37 | 44 | 47 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 96 | 6 | 0 | 0 | 105 |  | 6792 | 2014 | 8806 | 2644 | 553 | 1573 | 2837 | 150 | 70 | 855 | 124 | 0 | 0 | 101.6
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 357 | 110 | 0 | 225 | 0 | 18 | 100 | 55 | 0 | 0 | 92 | 0 | 100 | 50 | 133 | 80 | 46 | 10 | 40 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 75 | 51 | 78 | 106 | 50 | 22 | 25 | 90 | 0 | 100 | 350 | 301 | 204 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 8 | 33 | 21 | 122 | 49 | 79 | 20 | 0 | 57 | 77 | 50 | 48 | 163 | 0 | 67 | 86 | 40 | 98 | 0 | 48 | 10 | 270 | 25 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 129 | 0 | 100 | 202 | 5 |  | 553 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 29 | 50 | 40 | 67 | 25 | 110 | 0 | 0 | 60 | 50 | 0 | 93 | 50 | 43 | 40 | 52 | 47 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 0 | 7 | 0 | 0 | 105 |  | 6728 | 2023 | 8751 | 2750 | 553 | 1631 | 2656 | 150 | 70 | 819 | 122 | 0 | 0 | 101.59
19:30 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 357 | 110 | 0 | 225 | 0 | 16 | 100 | 55 | 0 | 0 | 97 | 0 | 100 | 50 | 133 | 86 | 46 | 0 | 40 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 75 | 51 | 78 | 106 | 50 | 22 | 26 | 90 | 0 | 100 | 350 | 301 | 198 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 122 | 50 | 79 | 20 | 0 | 57 | 77 | 50 | 48 | 163 | 0 | 67 | 86 | 41 | 130 | 0 | 48 | 10 | 305 | 25 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 66 | 0 | 100 | 177 | 13 |  | 553 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 29 | 8 | 40 | 67 | 26 | 110 | 0 | 0 | 60 | 50 | 0 | 93 | 50 | 43 | 0 | 52 | 47 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 96 | 0 | 7 | 0 | 0 | 105 |  | 6664 | 1943 | 8607 | 2785 | 553 | 1670 | 2570 | 150 | 70 | 687 | 122 | 0 | 0 | 0
20:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 356 | 110 | 0 | 225 | 0 | 16 | 100 | 55 | 0 | 0 | 97 | 0 | 100 | 50 | 133 | 85 | 46 | 0 | 40 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 75 | 51 | 78 | 106 | 50 | 22 | 32 | 90 | 0 | 100 | 350 | 301 | 211 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 122 | 49 | 79 | 20 | 0 | 57 | 77 | 50 | 48 | 163 | 0 | 64 | 86 | 41 | 100 | 0 | 48 | 10 | 300 | 25 | 11 | 0 | 274 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 172 | 5 |  | 553 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 29 | 9 | 40 | 61 | 25 | 110 | 0 | 0 | 60 | 0 | 0 | 93 | 50 | 43 | 0 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 96 | 0 | 7 | 0 | 0 | 105 |  | 6693 | 1886 | 8579 | 2758 | 553 | 1669 | 2620 | 150 | 70 | 637 | 122 | 0 | 0 | 0
21:00 | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 329 | 30 | 0 | 225 | 0 | 16 | 100 | 55 | 0 | 0 | 95 | 0 | 40 | 50 | 133 | 50 | 46 | 0 | 39 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 45 | 25 | 51 | 78 | 106 | 50 | 22 | 31 | 90 | 0 | 100 | 350 | 301 | 225 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 118 | 50 | 79 | 20 | 0 | 57 | 77 | 49 | 48 | 130 | 0 | 67 | 86 | 41 | 100 | 0 | 48 | 10 | 300 | 25 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 131 | 0 | 100 | 142 | 0 |  | 553 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 28 | 9 | 40 | 67 | 25 | 110 | 0 | 0 | 50 | 0 | 0 | 93 | 50 | 0 | 0 | 52 | 47 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 96 | 0 | 7 | 0 | 0 | 105 |  | 6350 | 1830 | 8180 | 2770 | 553 | 1607 | 2326 | 150 | 70 | 586 | 118 | 0 | 0 | 0
22:00 | 35 | 0 | 248 | 0 | 220 | 0 | 0 | 0 | 330 | 0 | 0 | 225 | 0 | 10 | 98 | 55 | 0 | 0 | 93 | 0 | 0 | 50 | 64 | 0 | 46 | 0 | 39 | 54 | 55 | 17 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 50 | 0 | 34 | 78 | 66 | 50 | 22 | 37 | 90 | 0 | 100 | 350 | 320 | 225 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 21 | 108 | 50 | 78 | 20 | 0 | 55 | 77 | 50 | 48 | 130 | 0 | 67 | 86 | 42 | 100 | 0 | 48 | 10 | 275 | 25 | 11 | 0 | 258 | 0 | 0 | 140 | 0 | 132 | 0 | 100 | 145 | 0 |  | 554 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 32 | 67 | 25 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 96 | 0 | 7 | 0 | 0 | 107 |  | 5988 | 1561 | 7549 | 2783 | 554 | 1591 | 1995 | 150 | 70 | 298 | 108 | 0 | 0 | 101.58
23:00 | 35 | 0 | 245 | 0 | 220 | 0 | 0 | 0 | 330 | 0 | 0 | 225 | 0 | 0 | 98 | 55 | 0 | 0 | 87 | 0 | 0 | 50 | 0 | 0 | 47 | 0 | 39 | 54 | 36 | 0 | 16 | 25 | 25 | 25 | 25 | 26 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 50 | 0 | 34 | 78 | 32 | 52 | 22 | 39 | 90 | 0 | 100 | 350 | 323 | 200 | 16 | 88 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 16 | 100 | 50 | 78 | 20 | 0 | 55 | 77 | 50 | 45 | 100 | 0 | 67 | 86 | 42 | 78 | 0 | 49 | 10 | 275 | 25 | 11 | 0 | 255 | 0 | 0 | 100 | 0 | 15 | 0 | 100 | 140 | 0 |  | 553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 22 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 18 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 220 | 0 | 96 | 0 | 7 | 0 | 0 | 67 |  | 5570 | 1420 | 6990 | 2723 | 553 | 1554 | 1607 | 149 | 70 | 234 | 100 | 0 | 0 | 101.58
24:00 | 35 | 0 | 253 | 0 | 220 | 0 | 0 | 0 | 331 | 0 | 0 | 225 | 0 | 0 | 85 | 55 | 0 | 0 | 83 | 0 | 0 | 50 | 0 | 0 | 47 | 0 | 39 | 54 | 18 | 0 | 16 | 25 | 25 | 25 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 50 | 0 | 17 | 78 | 0 | 52 | 22 | 42 | 100 | 0 | 120 | 350 | 272 | 183 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 9 | 90 | 50 | 78 | 20 | 0 | 55 | 77 | 50 | 45 | 100 | 0 | 59 | 86 | 42 | 78 | 0 | 48 | 10 | 295 | 25 | 11 | 0 | 125 | 0 | 0 | 100 | 0 | 15 | 0 | 100 | 140 | 0 |  | 554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 21 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 18 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 0 | 12 | 0 | 0 | 5 |  | 5311 | 1346 | 6657 | 2691 | 554 | 1575 | 1310 | 149 | 70 | 218 | 90 | 0 | 0 | 101.58
KWH | 884000 | 0 | 6031000 | 0 | 5505181 | 0 | 0 | 0 | 8052000 | 418900 | 0 | 5213125 | 0 | 774720 | 1594560 | 1186333 | 0 | 0 | 1989000 | 0 | 649260 | 1665648 | 845280 | 300387 | 876480 | 333380 | 936192 | 1216440 | 1012553 | 756000 | 355140 | 575000 | 534960 | 602300 | 721200 | 710424 | 0 | 911000 | 723400 | 0 | 0 | 417600 | 0 | 4803704 | 0 | 0 | 0 | 995040 | 306348 | 377257 | 1181520 | 1086720 | 876480 | 510960 | 527040 | 2511044 | 0 | 2414338 | 6205800 | 7542500 | 4734000 | 434909 | 2151580 | 859248 | 152640 | 120000 | 1244524 | 1594560 | 116040 | 1023259 | 507276 | 200880 | 783200 | 343260 | 2232960 | 1198730 | 1855680 | 447696 | 12650 | 1292000 | 1600080 | 1091400 | 1081000 | 3420581 | 0 | 1489000 | 1873920 | 827640 | 1154820 | 0 | 1031800 | 252180 | 7476300 | 571056 | 219936 | 11520 | 3512726 | 30651 | 27411 | 2412000 | 27645 | 1594080 | 94230 | 2236800 | 3129000 | 36800 |  | 12441454 | 0 | 0 | 0 | 592250 | 0 | 0 | 0 | 105120 | 130560 | 948750 | 1298000 | 442520 | 839040 | 0 | 0 | 310000 | 121560 | 90611 | 452508 | 1038000 | 207985 | 62797 | 1226400 | 221058 | 463680 | 109152 | 190782 | 0 | 0 | 3650000 | 0 | 0 | 0 | 0 | 4720909 | 0 | 2161106 | 100800 | 197900 | 0 | 0 | 1585440 |  | 131637882 | 33708382 | 165346264 | 60652776 | 12441454 | 37570077 | 39424874 | 3650000 | 1634400 | 7632843 | 2232960 | 106880 | 0
Fuel Cost | 760240 | 0 | 5186660 | 0 | 3523315.84 | 0 | 0 | 0 | 4911720 | 4025629 | 0 | 3492793.75 | 0 | 4865241.6 | 10651660.8 | 7248494.63 | 0 | 0 | 2207790 | 0 | 4057875 | 10976620.32 | 8173857.6 | 1913465.19 | 5250115.2 | 5330746.2 | 6244400.64 | 8673217.2 | 6328456.25 | 4740120 | 266355 | 431250 | 0 | 0 | 0 | 6720611.04 | 0 | 0 | 0 | 0 | 0 | 3954672 | 0 | 65570559.6 | 0 | 0 | 0 | 8746401.6 | 3299367.96 | 3670710.61 | 7313608.8 | 7020211.2 | 5732179.2 | 434316 | 0 | 2285050.04 | 0 | 2197047.58 | 3847596 | 5204325 | 3313800 | 300087.21 | 2065516.8 | 575696.16 | 131270.4 | 110400 | 1020509.68 | 1514832 | 1257873.6 | 7592581.78 | 390602.52 | 150660 | 603064 | 257445 | 15273446.4 | 899047.5 | 17053699.2 | 344725.92 | 0 | 1343680 | 1664083.2 | 1047744 | 972900 | 2668053.18 | 0 | 1697460 | 2005094.4 | 910404 | 1316494.8 | 0 | 959574 | 234527.4 | 4784832 | 428292 | 167151.36 | 199641.6 | 25502390.76 | 531181.83 | 467357.55 | 17245800 | 471347.25 | 0 | 0 | 0 | 29224860 | 343712 |  | 63451415.4 | 0 | 0 | 0 | 4909752.5 | 0 | 0 | 0 | 1183651.2 | 1537996.8 | 7476150 | 895620 | 438094.8 | 6208896 | 0 | 0 | 325500 | 1391862 | 971349.92 | 4054471.68 | 8978700 | 1851066.5 | 668788.05 | 12165888 | 2601852.66 | 510048 | 102602.88 | 144421.974 | 0 | 0 | 14089000 | 0 | 0 | 0 | 0 | 3304636.3 | 0 | 0 | 1746864 | 0 | 0 | 0 | 0 |  | 382298520.35 | 139008628.664 | 521307149.014 | 46231842.994 | 63451415.4 | 26115487.7 | 261763614.84 | 14089000 | 0 | 94382341.68 | 15273446.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 254 | 0 | 220 | 0 | 0 | 0 | 361 | 0 | 0 | 225 | 0 | 88 | 81 | 55 | 0 | 0 | 35 | 0 | 24 | 102 | 16 | 0 | 46 | 21 | 38 | 54 | 55 | 55 | 16 | 25 | 24 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 0 | 50 | 52 | 50 | 12 | 3 | 110 | 0 | 100 | 360 | 316 | 182 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 9 | 92 | 48 | 79 | 20 | 2.2 | 55 | 63 | 50 | 48 | 163 | 0 | 57 | 84 | 34 | 0 | 0 | 44 | 10 | 270 | 24 | 5 | 0 | 168 | 0 | 0 | 150 | 0 | 87 | 19.2 | 100 | 0 | 7 |  | 552 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 6 | 40 | 62 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 96 | 0 | 3 | 0 | 0 | 105 |  | 7006.4 | DayPeak
Yesterday Evening Peak | 35 | 0 | 247 | 0 | 220 | 0 | 0 | 0 | 351 | 110 | 0 | 225 | 0 | 35 | 80 | 55 | 0 | 0 | 87 | 0 | 75 | 102 | 133 | 44 | 46 | 46 | 40 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 84 | 51 | 76 | 105 | 50 | 22 | 6 | 90 | 0 | 100 | 350 | 301 | 192 | 16 | 90 | 30 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 8 | 33 | 13 | 124 | 49 | 79 | 20 | 0 | 57 | 77 | 38 | 42 | 163 | 0 | 57 | 86 | 40 | 90 | 0 | 48 | 10 | 260 | 25 | 11 | 20 | 268 | 53 | 50 | 185 | 51 | 105 | 0 | 100 | 201 | 5 |  | 553 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 25 | 35 | 40 | 65 | 20 | 54 | 0 | 0 | 0 | 50 | 48 | 93 | 50 | 43 | 37 | 44 | 47 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 96 | 6 | 0 | 0 | 105 |  | 8806 | EvPeak
Forecast for Evening | 35 | 0 | 255 | 0 | 220 | 0 | 0 | 0 | 360 | 110 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 102 | 133 | 100 | 47 | 46 | 40 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 43 | 0 | 80 | 30 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 0 | 50 | 85 | 51 | 100 | 105 | 50 | 22 | 12 | 100 | 0 | 120 | 360 | 360 | 221 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 8 | 33 | 22 | 127 | 50 | 79 | 20 | 0 | 26 | 77 | 50 | 44 | 163 | 0 | 35 | 86 | 42 | 130 | 0 | 48 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 133 | 0 | 100 | 200 |  |  | 563 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 25 | 75 | 40 | 68 | 25 | 110 | 30 | 0 | 50 | 50 | 55 | 93 | 50 | 50 | 37 | 52 | 38 | 22 | 5 | 11 | 0 | 0 | 149 | 17 | 19 | 0 | 0 | 220 | 0 | 95 | 96 | 20 | 0 | 0 | 105
Forecast for Day | 35 | 0 | 255 | 0 | 220 | 0 | 0 | 0 | 360 | 110 | 0 | 225 | 0 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 100 | 102 | 133 | 100 | 47 | 46 | 40 | 54 | 55 | 55 | 22 | 25 | 25 | 25 | 25 | 43 | 0 | 80 | 30 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 0 | 50 | 85 | 51 | 100 | 105 | 50 | 22 | 12 | 100 | 0 | 120 | 360 | 360 | 221 | 16 | 90 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 8 | 33 | 22 | 103 | 50 | 79 | 20 | 2 | 26 | 77 | 50 | 44 | 163 | 0 | 35 | 86 | 42 | 130 | 0 | 48 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 0 | 190 | 100 | 133 | 20 | 100 | 200 |  |  | 563 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 75 | 40 | 68 | 25 | 110 | 0 | 0 | 50 | 0 | 0 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 149 |  | 0 | 0 | 0 | 220 | 0 | 95 | 96 | 20 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 255 | 0 | 220 | 0 | 0 | 0 | 344 | 0 | 0 | 225 | 0 | 0 | 15 | 55 | 0 | 0 | 97 | 0 | 0 | 50 | 0 | 0 | 47 | 10 | 39 | 54 | 55 | 17 | 0 | 25 | 25 | 25 | 25 | 30 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 7 | 6 | 22 | 12 | 100 | 0 | 120 | 350 | 290 | 182 | 16 | 90 | 37 | 5 | 5 | 51 | 85 | 0 | 22 | 22 | 8 | 33 | 8 | 78 | 50 | 78 | 20 | 0.5 | 26 | 77 | 50 | 40 | 100 | 0 | 35 | 86 | 42 | 98 | 0 | 47 | 10 | 285 | 16 | 8 | 0 | 62 | 0 | 0 | 100 | 0 | 15 | 2.3 | 100 | 110 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 16 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 0 | 14 | 0 | 0 | 53 | 0
199
| Minimum Generation |  | 5492 | 5:00
| Highest Generation |  | 8806 | 18:00
| Day Peak Generation |  | 7006.4 | 12:00
| Evening Peak Generation |  | 8806 | 18:00
| HVDC Max Flow |  | 554 | 15:00
| HVDC EvPeak Flow |  | 553 | 18:00
| Load factor L.F |  | 78.24%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-11-14
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-11-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7006.4 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5459 | MW
Evening Peak Generation : |  | 8806 | MW Hour : | 18:00 | Available Max Generation : |  | 10320 | MW
E.P. Demand (at gen end) : |  | 8806 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 8806 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1220 | MW
Total Gen. (MKWH) : |  | 165.3463 | System Load Factor : | 78.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -780 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-11-14
Actual : | 101.55 | Ft.(MSL) , | Rule curve : | 107.7 | Ft.( MSL )
Gas Consumed : | Total = | 853.15 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 72347330.694
|  | Coal : | 14089000 | Oil : | 356145956.52 | Total : | 442582287.214
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3233.8263 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1094.5026 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 979.7155 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 884.928 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 799.8773 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 645.4596 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 367.5717 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 166.3648 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 497.7786 |  |  | 0 | 0%
Total | 0 |  | 8670.0244 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Sirajganj Unit-1
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Ghorasal Regent 108 MW
|  |  |  | 3) Ghorasal Unit-2,3,5 |  | 12) Haripur 412 MW
|  |  |  | 4) Chattogram ST-1,2 |  | 13) Ashuganj-4
|  |  |  | 5) Tongi GT |  | 14) Ghorasal Max 78 MW
|  |  |  | 6) Baghabari-71 MW |  | 15) Shajibazar 330 MW
|  |  |  | 7) Haripur GT-1 |  | 16) Bheramara 360 MW
8) Siddhirganj 210 MW ST
9) Kaptai #2,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Haripur-Bhulta 230 kV Ckt-2 was under shut down from 08:35 to 16:23 for A/M.
b) Jamalpur-United Mymensingh-Sherpur 132 kV Ckt-2 was under shut down from 08:35 to 16:07 for A/M.
c) Natore-Rajshahi 132 kV Ckt-2 was under shut down from 08:06 to 20:08 for A/M.
d) Bogura-Barapukuria 230 kV Ckt-2 was under shut down from 08:10 to 15:34 for A/M.
e) Lalmonirhat 132/33 kV T3 transformer was under shut down from 08:40 to 13:45 for A/M.
f) Faridpur 132/33 kV T2 transformer was under shut down from 08:13 to 15:20 for A/M.
g) Goalpara-Khulna 225 MW 132 kV Ckt was under shut down from 07:48 to 13:19 for A/M.
h) Bakulia-Modern 132 kV Ckt was under shut down from 08:50 to 13:52 for A/M.
i) Bibiyana 400/230 kV ICT-2 was under shut down from 08:50 to 13:52 for A/M.
j) Aminbazar-Hasnabad 230 kV Ckt-1 was under shut down from 09:45 to 15:30 for A/M.
k) Dhamrai-Kaliakoir 132 kV Ckt-2 was under shut down from 09:12 to 17:12 for A/M.
l) Fenchuganj 132/33 kV T1 transformer was under shut down from 10:24 to 15:32 for A/M.
m) Chandragona 132/33 kV T1 transformer was under shut down from 09:36 to 16:52 for D/W.
n) Ishurdi-HVDC 230 kV Ckt-1 & 4 were shut down at 10:00 for D/W.
o) Gopalganj 132/33 kV T1 transformer was under shut down from 08:42 to 16:30 for A/M.
p) Madaripur 132/33 kV T1 transformer was under shut down from 09:08 to 16:56 for A/M.
q) Goalpara 132/33 kV T6 transformer was under shut down from 09:02 to 15:48 for A/M.
r) Bheramara HVDC-Bheramara 230 kV Ckt-1 was under shut down from 08:36 to 17:32 for C/M.
s) Bagerhat 132/33 kV T1 & T3 transformers tripped at 10:46 from both sides due to 33 kV Rampal feeder |  |  |  | About 28 MW Power interruption occurred under Bagerhat S/S
fault and were switched on at 10:56. |  |  |  | area from 10:46 to 10:56.
t) Comilla(S) 132/33 kV T3 transformer was shut down at 08:38 for C/M.
u) After maintenance Shahmirpur-Sikalbaha 132 kV Ckt-1 was switched on at 12:43.
v) After maintenance Sylhet 150 MW GT was synchronized at 15:28.
w) After maintenance Baroaulia( SSM) 132/33 kV Tr transformer was switched on at 14:01.
x) After maintenance Natore 132/33 kV T4 transformer was switched on at 17:04.
y) Fenchuganj 132/33 kV T2 transformer was under shut down from 15:39 to 20:18 for A/M.
z) Baghabari 71 MW was synchronized at 18:05.
aa) Meghnaghat-APR Energy 230 kV Ckt was shut down at 06:20 (14/11/2018) for D/W.
ab) Meghnaghat-Hasnabad 230 kV Ckt-1 was shut down at 06:20(14/11/2018) for D/W.
ac) Sikalbaha-Madunaghat 132 kV Ckt was shut down at 07:08 (14/11/2018) for D/W.
ad) Tongi-Basundhara 132 kV Ckt was shut down at 07:37 (14/11/2018) for A/M.
ae) Barisal 132/33 kV T1 transformer was shut down at 07:08(14/11/2018) for A/M.
af) Shahjibazar GT-9 was shut down at 06:35(14/11/2018) due to air filter change.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-11-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 884000 | #2 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 247 | 6031000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 5505181 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 418900
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 351 | 8052000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 225 | 5213125 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 35 | 774720 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 1594560 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1186333
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 44 | 300387 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 355140 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 87 | 1989000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 75 | 649260 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 46 | 333380
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1665648
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 936192 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1216440
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 845280 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1012553
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 756000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 46 | 876480 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1109960 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 602300 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 721200 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 710424 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 268 | 3512726 | Engine problem
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 53 | 30651 | Low demand
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 50 | 27411 | Low demand
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 51 | 27645 | Low demand
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 105 | 1594080 | Low demand
| Dhaka area Total |  |  |  | 5848 | 2781 | 48931976
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 417600
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 94230
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 876480
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1634400 | Unit-2,5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4803704 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 995040 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 84 | 306348
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 51 | 377257
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 76 | 1181520 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 0 | 100 | 2236800 | On test
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 510960
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 6 | 527040
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 105 | 1086720
| Chattogram area Total |  |  |  | 1581 | 831 | 15048099
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 90 | 2511044 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2414338 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 192 | 4734000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 350 | 6205800
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 301 | 7542500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 30 | 859248 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 152640 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 16 | 434909 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 1244524
| Midland 150MW |  | IPP | 23*7.015 | 0 | 5 | 36800 | On test
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1594560
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 50 | 116040
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2151580 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 0 | 201 | 3129000 | On Test
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507276
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 200880 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 124 | 2232960
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 783200
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 1023259
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 13 | 343260 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 20 | 11520 | Low demand
| Cumilla Area Total |  |  |  | 2541 | 1843 | 38349338
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 49 | 1198730 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 447696
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 79 | 1855680 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12650
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 185 | 2412000 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 333 | 5926756
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 57 | 1292000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 77 | 1600080
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3420581
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 38 | 1091400 | Engine problem
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 42 | 1081000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 219936
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 57 | 1489000
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1873920
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 40 | 827640 | Engine problem
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 90 | 1154820 | Frequency control
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 48 | 1031800
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 571056
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 260 | 7476300 | FGMO
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 252180
| Sylhet Area Total |  |  |  | 1549 | 1004 | 23381713
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 553 | 12441454
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 100 | 592250 | Engine problem
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 25 | 105120
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 35 | 130560
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 948750
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 96 | 100800
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1585440
| Khulna Area Total |  |  |  | 2209 | 954 | 15904374
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 54 | 839040 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 20 | 442520 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 65 | 1298000
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 2161106
| Barisal Area Total |  |  |  | 462 | 234 | 4740666
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 310000 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 121560
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 48 | 90611
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1038000
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 207985 | Engine problem
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 37 | 62797
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 4720909 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 6 | 197900 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 47 | 221058
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 463680
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 109152 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 190782
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 44 | 1226400
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 93 | 452508
| Rajshahi Area Total |  |  |  | 1546 | 676 | 9413342
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 150 | 3650000
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 150 | 3650000
| Total |  |  |  | 16742 | 8806 | 165346264
| Eastern Grid Total |  |  |  | 12041 | 6792 | 131637882
| Western Grid Total |  |  |  | 4701 | 2014 | 33708382
| National Grid Total |  |  |  | 16742 | 8806 | 165346264
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-11-13 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5912 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2467 | MW
i) Dhaka area |  |  | 3351 | MW | i) Khulna area |  |  | 950 | MW
ii) Chittagong area |  |  | 1003 | MW | ii) Rajshahi area |  |  | 818 | MW
iii) Comilla area |  |  | 669 | MW | iii) Barisal area |  |  | 201 | MW
iv) Mymensingh area |  |  | 558 | MW | iv) Rangpur area |  |  | 498 | MW
v) Sylhet area |  |  | 331 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8379 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 1100 | Netrokona | 60 | 1800 | Goalpara | 20 | 1300
Munsiganj | 76 | 1400 | Jamalpur | 88 | 1900 | Central s/s | 66 | 1800
Sonargaon | 37 | 1000 | Sherpur | 60 | 1800 | Noapara | 71 | 1800
Shyampur | 158 | 1400 | Srimongal | 27 | 1830 | Jessore | 106 | 1800
Bhulta | 149 | 1930 | Shahjibazar | 82 | 1800 | Jhenida | 73 | 1800
Madanganj | 49 | 1900 | Fenchuganj | 28 | 1800 | Bottail | 92 | 1800
Shitalakhya | 141 | 1800 | Kulawara | 27 | 1800 | G.K Project | 36 | 1830
Rahim steel | 11 | 1100 | Sylhet | 97 | 1800 | Faridpur | 118 | 1830
Matuail | 96 | 1200 | Chatak | 19 | 1800 | Madaripur | 86 | 1830
Ghorasal | 63 | 1830 | Sunamganj | 24 | 1800 | Gopalganj | 56 | 1900
Narsingdi | 88 | 1900 | Biani Bazar | 28 | 1800 | Bagerhat | 57 | 1930
Haripur (SBU) | 96 | 1200 | Comilla (S) | 124 | 1800 | Mongla | 36 | 1100
Ullon | 46 | 1800 | Comilla(N) | 69 | 1900 | Satkhira | 63 | 1830
Hasnabad | 160 | 2000 | Chandpur | 80 | 1930 | Gallamari | 32 | 1800
Magbazar | 105 | 1200 | Feni | 88 | 1800 | Magura | 36 | 1800
Maniknagar | 78 | 1800 | Chowmuhani | 126 | 1930 | Chuadanga | 55 | 1800
Bangabhaban | 28 | 1000 | Ashuganj | 45 | 1800 | Barisal | 88 | 1800
Narinda | 76 | 1600 | Daudkandi | 84 | 1830 | Patuakhali | 62 | 1930
Dhanmondi | 103 | 1500 | B.Baria | 86 | 1830 | Bhandaria | 40 | 1800
Lalbag | 85 | 1300 | Ramganj | 24 | 1830 | Ishurdi | 39 | 1800
Madartek | 46 | 1830 | Madunaghat | 51 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 87 | 1930 | Hathazari | 73 | 1900 | Natore | 82 | 1800
Kalyanpur | 87 | 1830 | Khulshi | 176 | 1700 | Bogra | 172 | 1900
Gulshan | 96 | 1300 | Halishahar | 114 | 1900 | Noagaon | 80 | 1830
Uttara | 69 | 1800 | Baraulia | 127 | 200 | Rajshahi | 102 | 1900
Uttara(New) | 4 | 2000 | Sikalbaha | 30 | 1830 | C.Nawabganj | 49 | 1830
Kamrangirchar | 70 | 1800 | Dohazari | 66 | 1800 | Amnura | 30 | 1830
Savar | 116 | 1800 | Cox'sbazar | 72 | 1900 | Pabna | 74 | 1830
Bhasantec | 137 | 1800 | Chandraghona | 19 | 1900 | Shahjadpur | 67 | 1830
Agargaon | 43 | 1800 | Kaptai | 4 | 1800 | Serajganj | 69 | 1900
Satmosjid | 75 | 1800 | A. Khaer Stl. | 10 | 1200 | Niyamatpur | 38 | 1800
Tongi | 98 | 1800 | Bakulia | 86 | 1800 | Joypurhat | 37 | 1930
Kabirpur | 151 | 1800 | Julda | 23 | 1200 | Rangpur | 95 | 1830
Basundhara | 93 | 1830 | TK chemical | 4 | 1100 | Lalmonirhat | 71 | 1900
Manikganj | 64 | 1800 | Modern Steel | 14 | 200 | Saidpur | 92 | 1800
Joydevpur | 192 | 1900 | Shahmirpur | 22 | 1800 | Purbasadipur | 69 | 2000
New Tongi | 96 | 1800 | Khagrachhari | 15 | 1800 | Thakurgaon | 50 | 1800
Korda | 219 | 2100 | Matarbari | 19 | 1800 | Palashbari | 72 | 1800
Dhamrai | 42 | 1800 | Baroiar Hat | 16 | 1930 | Barapukuria | 37 | 1900
Tangail | 122 | 1800 | Rangamati | 10 | 1800 | Panchagar | 34 | 1830
Mymensing | 180 | 1830 | Abul Khair 230 | 169 | 1500
Kishorganj | 66 | 2000 | BSRM | 83 | 500
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-11-13
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 398 | 18:00 | 388 | 10:00 | Kaliakoir | 382 | 22:00 | 372 | 10:00
Bheramara | 409 | 4:00 | 400 | 18:30 | Bhulta | 402 | 17:00 | 388 | 23:00
Ashuganj(N) | 401 | 17:00 | 92 | 3:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 232 | 10:00 | 230 | 1:00 | Hathazari | 226 | 19:30 | 216 | 8:00
Ishurdi | 235 | 4:00 | 226 | 7:00 | Megnaghat | 232 | 18:00 | 228 | 1:00
Ashuganj | 239 | 17:00 | 235 | 1:00 | Fenchuganj | 242 | 10:00 | 236 | 1:00
Serajganj | 230 | 4:00 | 220 | 19:00 | Siddhirganj | 229 | 18:00 | 223 | 10:00
Baghabari | 232 | 8:00 | 220 | 19:00 | Maniknagar | 226 | 8:00 | 221 | 15:00
Barapukuria | 234 | 5:00 | 226 | 18:00 | Old Airport | 228 | 8:00 | 222 | 11:00
Bogra | 228 | 5:00 | 218 | 18:00 | Barisal | 238 | 4:00 | 227 | 18:00
Khulna South | 239 | 17:00 | 228 | 1:00 | AKSML | 224 | 20:00 | 212 | 11:00
Rampura | 226 | 20:00 | 221 | 10:00 | BSRM | 227 | 21:00 | 213 | 13:00
Haripur | 227 | 18:00 | 221 | 10:00 | Bibiyana | 238 | 10:00 | 231 | 15:00
Hasnabad | 230 | 5:00 | 222 | 16:00 | Bhulta | 228 | 17:00 | 224 | 1:00
Aminbazar | 229 | 18:00 | 225 | 9:00 | Ashuganj (S) | 238 | 17:00 | 234 | 12:00
Tongi | 226 | 17:00 | 221 | 16:00 | Kaliakoir | 233 | 20:00 | 227 | 16:00
Comilla (N) | 236 | 20:00 | 230 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1800 | 129 | 900 | Ramganj | 135 | 1000 | 132 | 2000
Munsiganj | 137 | 1800 | 132 | 100 | Madanhat | 135 | 800 | 129 | 1300
Megnaghat | 135 | 1700 | 128 | 700 | Hathazari | 135 | 1930 | 130 | 1400
Shyampur | 132 | 1800 | 124 | 900 | Khulshi | 132 | 2000 | 125 | 1300
Bhulta | 134 | 2000 | 131 | 1100 | Halishahar | 136 | 1930 | 129 | 300
Madanganj | 138 | 800 | 130 | 1100 | Baraulia | 134 | 1830 | 125 | 1100
Shitalakhya | 141 | 1800 | 133 | 1600 | Sikalbaha | 134 | 1830 | 127 | 1100
Rahim steal | 135 | 800 | 129 | 1100 | Dohazari | 132 | 700 | 127 | 1100
Matuail | 140 | 800 | 128 | 1600 | Cox'sbazar | 127 | 1700 | 121 | 300
Ghorasal | 140 | 2100 | 138 | 100 | Chandraghona | 135 | 1930 | 128 | 1100
Narsinghdi | 138 | 100 | 136 | 400 | Kaptai | 135 | 1800 | 128 | 1000
Haripur (SBU) | 138 | 1800 | 130 | 100 | A. Khaer Stl. | 132 | 1600 | 127 | 900
Ullon | 137 | 2000 | 132 | 700 | Bakulia | 133 | 2000 | 127 | 1100
Hasnabad | 138 | 800 | 133 | 1600 | Julda | 135 | 1830 | 128 | 300
Magbazar | 138 | 500 | 133 | 1100 | TK Chemical | 136 | 1800 | 131 | 1000
Maniknagar | 136 | 400 | 133 | 1000 | Modern Steel | 134 | 2000 | 126 | 1300
Bangabhaban | 136 | 600 | 128 | 1600 | Shahmirpur | 135 | 2000 | 128 | 1300
Narinda | 138 | 600 | 133 | 1100 | Khagrachhari | 134 | 800 | 128 | 500
Dhanmondi | 137 | 2000 | 132 | 700 | Matarbari | 129 | 800 | 122 | 1800
Lalbag | 136 | 600 | 128 | 1600 | Baroiar Hat | 132 | 100 | 130 | 1000
Madartek | 138 | 600 | 133 | 1100 | Rangamati | 134 | 2000 | 128 | 400
Mirpur | 137 | 600 | 134 | 1200 | Goalpara | 138 | 1700 | 129 | 700
Kalyanpur | 139 | 300 | 136 | 1200 | Central s/s | 139 | 1700 | 130 | 100
Gulshan | 136 | 500 | 131 | 1200 | Noapara | 136 | 500 | 129 | 700
Uttara | 136 | 600 | 131 | 1100 | Jessore | 130 | 600 | 123 | 1900
Uttara(New) | 136 | 500 | 132 | 1100 | Jhenida | 135 | 300 | 124 | 2000
Kamrangirchar | 135 | 400 | 131 | 1200 | Bottail | 138 | 600 | 130 | 1800
Savar | 135 | 300 | 133 | 1200 | G.K.Project | 140 | 300 | 134 | 1800
Bhasantec | 138 | 600 | 134 | 1200 | Faridpur | 138 | 400 | 128 | 1930
Agargaon | 139 | 400 | 136 | 1200 | Madaripur | 137 | 500 | 129 | 1900
Satmosjid | 136 | 600 | 135 | 1100 | Gopalganj | 138 | 600 | 126 | 1930
Tongi | 138 | 800 | 132 | 1600 | Bagerhat | 140 | 1700 | 130 | 100
Kabirpur | 137 | 2000 | 134 | 1600 | Mongla | 135 | 1700 | 129 | 1900
Basundhara | 133 | 1930 | 129 | 1000 | Satkhira | 138 | 1700 | 129 | 700
Manikganj | 140 | 600 | 133 | 1600 | Gallamari | 139 | 1700 | 131 | 100
Joydevpur | 144 | 700 | 137 | 1100 | Magura | 135 | 600 | 120 | 1900
New Tongi | 137 | 2000 | 133 | 1500 | Chuadanga | 132 | 300 | 119 | 2000
Kodda | 141 | 700 | 133 | 1100 | Barisal | 141 | 600 | 136 | 100
Dhamrai | 137 | 800 | 132 | 1100 | Patuakhali | 139 | 600 | 130 | 1800
Tangail | 140 | 500 | 134 | 1200 | Bhandaria | 140 | 1700 | 132 | 1930
Mymensing | 137 | 100 | 133 | 1400 | Ishurdi | 141 | 500 | 133 | 2000
Kishorganj | 138 | 400 | 134 | 1800 | Ruppur Paromanobik | 140 | 600 | 133 | 1930
Netrokona | 136 | 2300 | 133 | 1800 | Natore | 140 | 400 | 132 | 1900
Jamalpur | 139 | 1300 | 135 | 500 | Bogra | 137 | 300 | 127 | 1800
Sherpur | 139 | 2200 | 135 | 1300 | Noagaon | 134 | 600 | 125 | 1800
Srimongal | 143 | 500 | 139 | 1400 | Rajshahi | 136 | 500 | 130 | 2000
Shahjibazar | 141 | 300 | 138 | 1930 | C.Nawabganj | 136 | 1700 | 126 | 1200
Fenchuganj | 140 | 600 | 137 | 1100 | Amnura | 140 | 1700 | 130 | 700
Khulawara | 139 | 300 | 137 | 1300 | Pabna | 136 | 600 | 130 | 1300
Sylhet | 138 | 100 | 135 | 1500 | Shahjadpur | 141 | 500 | 136 | 1100
Chatak | 138 | 100 | 134 | 1400 | Serajganj | 137 | 600 | 130 | 1000
Sunamganj | 138 | 600 | 134 | 1200 | Niyamatpur | 133 | 600 | 123 | 1800
Biani Bazar | 138 | 700 | 135 | 1400 | Joypurhat | 135 | 300 | 125 | 1800
Cumilla(s) | 131 | 2300 | 126 | 1000 | Rangpur | 131 | 600 | 116 | 1800
Cumilla(n) | 141 | 800 | 138 | 1100 | Lalmonirhat | 129 | 500 | 113 | 1900
Chandpur | 142 | 700 | 135 | 1200 | Saidpur | 130 | 600 | 118 | 1800
Feni | 135 | 800 | 130 | 1200 | Purbasadipur | 132 | 100 | 122 | 1800
Chowmuhani | 131 | 600 | 127 | 1200 | Thakurgaon | 128 | 300 | 115 | 1830
Ashuganj | 142 | 500 | 140 | 1100 | Palashbari | 133 | 600 | 117 | 1800
Daudkandi | 138 | 1800 | 132 | 1100 | Barapukuria | 134 | 500 | 126 | 1800
B.Baria | 141 | 400 | 138 | 1400 | Panchagar | 127 | 500 | 112 | 1800

## L-Curve
Date | 2018-11-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 510 | 5311 | 1346 | 6657 |  |  |  | QF-LDC-12
0:30 | 520 | 5121.5 | 1265.5 | 6387 | Date: | 2018-11-13
1:00 | 530 | 4932 | 1185 | 6117
1:30 | 530 | 4831 | 1178.5 | 6009.5
2:00 | 530 | 4730 | 1172 | 5902
2:30 | 530 | 4713.5 | 1101 | 5814.5 | [5 empty] | Gen. at Eve. Peak | 8806 | 8806 MW (18:00 )
3:00 | 530 | 4697 | 1030 | 5727 | [6 empty] | 18:00
3:30 | 525 | 4646 | 1025 | 5671 | [5 empty] | Gen. at Day Peak | 7006.4 | 7006.4 MW (12:00 )
4:00 | 520 | 4595 | 1020 | 5615 | [6 empty] | 12:00
4:30 | 520 | 4524.5 | 1029 | 5553.5 | [5 empty] | Highest Generation | 8806
5:00 | 520 | 4454 | 1038 | 5492 | [6 empty] | 18:00
5:30 | 520 | 4490.5 | 1047 | 5537.5
6:00 | 520 | 4527 | 1056 | 5583
6:30 | 615 | 4655.1 | 1077 | 5732.1
7:00 | 710 | 4783.2 | 1098 | 5881.2
7:30 | 715 | 4814 | 1147 | 5961
8:00 | 720 | 4844.8 | 1196 | 6040.8
8:30 | 550 | 4952.15 | 1261.5 | 6213.65
9:00 | 380 | 5059.5 | 1327 | 6386.5
9:30 | 370 | 5162.7 | 1321.5 | 6484.2
10:00 | 360 | 5265.9 | 1316 | 6581.9
10:30 | 360 | 5317 | 1349.5 | 6666.5
11:00 | 360 | 5368.1 | 1383 | 6751.1
11:30 | 380 | 5479.25 | 1399.5 | 6878.75
12:00 | 400 | 5590.4 | 1416 | 7006.4
12:30 | 415 | 5629 | 1426.5 | 7055.5
13:00 | 430 | 5667.6 | 1437 | 7104.6
13:30 | 420 | 5488.8 | 1401.5 | 6890.3
14:00 | 410 | 5310 | 1366 | 6676
14:30 | 385 | 5422.15 | 1346.5 | 6768.65
15:00 | 360 | 5534.3 | 1327 | 6861.3
15:30 | 340 | 5507.7 | 1328.5 | 6836.2
16:00 | 320 | 5481.1 | 1330 | 6811.1
16:30 | 320 | 5548.65 | 1404.5 | 6953.15
17:00 | 320 | 5616.2 | 1479 | 7095.2
17:30 | 520 | 6204.1 | 1746.5 | 7950.6
18:00 | 720 | 6792 | 2014 | 8806
18:30 | 720 | 6760 | 2018.5 | 8778.5
19:00 | 720 | 6728 | 2023 | 8751
19:30 | 780 | 6664 | 1943 | 8607
20:00 | 770 | 6693 | 1886 | 8579 |  |  |  | Executive Engineer
20:30 | 740 | 6521.5 | 1858 | 8379.5 |  |  |  | Network Operation Division
21:00 | 710 | 6350 | 1830 | 8180
21:30 | 685 | 6169 | 1695.5 | 7864.5
22:00 | 660 | 5988 | 1561 | 7549 |  |  |  |  | Page 6 of 7
22:30 | 610 | 5779 | 1490.5 | 7269.5
23:00 | 560 | 5570 | 1420 | 6990
23:30 | 535 | 5440.5 | 1383 | 6823.5
24:00 | 510 | 5311 | 1346 | 6657
8806 MW (18:00 )
7006.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-11-13 |  | Energy | 165346264
[10 empty] | 2018-11-13 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2691 | 554 | 1575 | 1310 | 149 | 70 | 218 | 0 | 90
0:30 | 2560 | 553 | 1605 | 1138.5 | 149 | 70 | 226.5 | 0 | 85 | Date: | 2018-11-13
1:00 | 2429 | 552 | 1635 | 967 | 149 | 70 | 235 | 0 | 80
1:30 | 2357 | 552.5 | 1623 | 952 | 149 | 70 | 227 | 0 | 79 | [7 empty] | Total Energy | 165.3463 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 2285 | 553 | 1611 | 937 | 149 | 70 | 219 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 2310 | 495 | 1609 | 876.5 | 149 | 70 | 228 | 0 | 77 | [7 empty] | Energy Requirement | 165.3463
3:00 | 2335 | 437 | 1607 | 816 | 149 | 70 | 237 | 0 | 76
3:30 | 2323 | 422.5 | 1639.5 | 772.5 | 149 | 70 | 219.5 | 0 | 75 | [6 empty] | Shortage
4:00 | 2311 | 408 | 1672 | 729 | 149 | 70 | 202 | 0 | 74
4:30 | 2356.5 | 408 | 1651 | 642.5 | 149 | 70 | 202.5 | 0 | 74
5:00 | 2402 | 408 | 1630 | 556 | 149 | 70 | 203 | 0 | 74
5:30 | 2379.5 | 408 | 1642 | 616 | 149 | 69 | 202 | 0 | 72
6:00 | 2357 | 408 | 1654 | 676 | 149 | 68 | 201 | 0 | 70
6:30 | 2370 | 408 | 1660 | 801.5 | 149 | 69 | 203.5 | 0 | 70 |  |  |  |  | Coal
7:00 | 2383 | 408 | 1666 | 927 | 149 | 70 | 206 | 0 | 70
7:30 | 2301.5 | 412.5 | 1557 | 1182.5 | 149 | 70 | 211.5 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 2220 | 417 | 1448 | 1438 | 149 | 70 | 217 | 0 | 72
8:30 | 2271 | 484.5 | 1437 | 1494.5 | 149.5 | 69 | 217.5 | 0 | 77
9:00 | 2322 | 552 | 1426 | 1551 | 150 | 68 | 218 | 0 | 82
9:30 | 2375.5 | 552 | 1456 | 1567.5 | 149.5 | 68 | 218 | 0 | 85
10:00 | 2429 | 552 | 1486 | 1584 | 149 | 68 | 218 | 0 | 88
10:30 | 2468.5 | 552 | 1539 | 1569 | 149 | 69 | 218 | 0 | 87
11:00 | 2508 | 552 | 1592 | 1554 | 149 | 70 | 218 | 0 | 86
11:30 | 2486 | 552 | 1592.5 | 1697.5 | 149 | 70 | 221 | 0 | 89
12:00 | 2464 | 552 | 1593 | 1841 | 149 | 70 | 224 | 0 | 92
12:30 | 2465.5 | 552.5 | 1575.5 | 1902 | 149 | 70 | 224.5 | 0 | 95
13:00 | 2467 | 553 | 1558 | 1963 | 149 | 70 | 225 | 0 | 98
13:30 | 2467 | 553 | 1558 | 1963 | 149 | 70 | 225 | 0 | 98
14:00 | 2467 | 553 | 1558 | 1963 | 149 | 70 | 225 | 0 | 98
14:30 | 2467 | 553.5 | 1467 | 1939 | 149.5 | 70 | 224 | 0 | 99
15:00 | 2467 | 554 | 1376 | 1915 | 150 | 70 | 223 | 0 | 100
15:30 | 2482 | 553.5 | 1387.5 | 1860.5 | 150 | 70 | 232.5 | 0 | 96
16:00 | 2497 | 553 | 1399 | 1806 | 150 | 70 | 242 | 0 | 92
16:30 | 2441.5 | 553 | 1335 | 1924.5 | 150 | 70 | 380 | 0 | 98
17:00 | 2386 | 553 | 1271 | 2043 | 150 | 70 | 518 | 0 | 104
17:30 | 2515 | 553 | 1422 | 2440 | 150 | 70 | 686.5 | 0 | 114
18:00 | 2644 | 553 | 1573 | 2837 | 150 | 70 | 855 | 0 | 124
18:30 | 2697 | 553 | 1602 | 2746.5 | 150 | 70 | 837 | 0 | 123
19:00 | 2750 | 553 | 1631 | 2656 | 150 | 70 | 819 | 0 | 122
19:30 | 2785 | 553 | 1670 | 2570 | 150 | 70 | 687 | 0 | 122
20:00 | 2758 | 553 | 1669 | 2620 | 150 | 70 | 637 | 0 | 122
20:30 | 2764 | 553 | 1638 | 2473 | 150 | 70 | 611.5 | 0 | 120
21:00 | 2770 | 553 | 1607 | 2326 | 150 | 70 | 586 | 0 | 118
21:30 | 2776.5 | 553.5 | 1599 | 2160.5 | 150 | 70 | 442 | 0 | 113
22:00 | 2783 | 554 | 1591 | 1995 | 150 | 70 | 298 | 0 | 108
22:30 | 2753 | 553.5 | 1572.5 | 1801 | 149.5 | 70 | 266 | 0 | 104
23:00 | 2723 | 553 | 1554 | 1607 | 149 | 70 | 234 | 0 | 100
23:30 | 2707 | 553.5 | 1564.5 | 1458.5 | 149 | 70 | 226 | 0 | 95 | Max Temp. in Dhaka |  | 30.2° C
24:00 | 2691 | 554 | 1575 | 1310 | 149 | 70 | 218 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2018-11-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 38 | 40 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 911000
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 723400
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [6 empty] | 8 | 16 | 25 | 16 | 25 | 25 | 16 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 417600
| Teknaf Solartech 20MW | [6 empty] | 2 | 8.9 | 16 | 6 | 20 | 19.2 | 19.6 | 6.4 | 5.4 | 1.7 | 0.2 | 0 | [8 empty] | 94230
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 210 | 202 | 220 | 202 | 203 | 201 | 201 | 201 | 202 | 202 | 202 | 202 | 202 | 201 | 200 | 214 | 201 | 202 |  | 201 | 201 | 201 | 200 | 200 | 200 | 201 | 4803704
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 17 | 17 | 17 | 0 | [12 empty] | 34 | 51 |  | 51 | 51 | 51 | 51 | 34 | 34 | 17 | 377257
12 | Hathazari peaking | [16 empty] | 12 | 84 |  | 75 | 75 | 75 | 25 | 0 |  |  | 306348
| Daudkandi bangla trak | [17 empty] | 20 |  | 0 | 0 | [5 empty] | 11520
14 | Daudkandi Peaking 52MW | [16 empty] | 25 | 50 |  | 50 | 0 | [5 empty] | 116040
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 92 | 92 | 92 | 87 | 87 | 87 | 87 | 83 | 92 | 87 | 62 | 35 | 32 | 35 | 60 | 82 | 27 | 87 |  | 92 | 97 | 97 | 95 | 93 | 87 | 83 | 1989000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [6 empty] | 15 | 90 | 120 | 125 | 112 | 168 | 200 | 200 | 200 | 190 | 195 | 268 |  | 275 | 275 | 274 | 268 | 258 | 255 | 125 | 3512726
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 434909
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 884000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 253 | 257 | 259 | 258 | 257 | 259 | 260 | 260 | 256 | 247 | 243 | 254 | 248 | 243 | 247 | 246 | 245 | 247 |  | 247 | 247 | 247 | 247 | 248 | 245 | 253 | 6031000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5505181
26
28 | Ashuganj ST: Unit- 3 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 95 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 2511044
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 2414338
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 40 | 40 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 859248
33 | Ashuganj CCPP 225 MW | 202 | 190 | 206 | 190 | 191 | 193 | 205 | 182 | 196 | 182 | 201 | 182 | 182 | 193 | 187 | 176 | 188 | 192 |  | 204 | 198 | 211 | 225 | 225 | 200 | 183 | 4734000
34 | Ashuganj CCPP(South) | 334 | 309 | 342 | 309 | 316 | 309 | 338 | 268 | 294 | 287 | 342 | 316 | 316 | 331 | 327 | 345 | 279 | 301 |  | 301 | 301 | 301 | 301 | 320 | 323 | 272 | 7542500
| Ashuganj CCPP(North) | 130 | 20 | 25 | 35 | 75 | 95 | 115 | 120 | 160 | 265 | 325 | 360 | 355 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 6205800
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 152640
36 | Chandpur CCPP | 87 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 155 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 88 | 90 | 2151580
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP
40 | Meghnaghat CCPP 450MW | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5213125
41 | Haripur Power CCPP 360MW | 356 | 335 | 315 | 351 | 351 | 363 | 361 | 284 | 314 | 359 | 358 | 361 | 330 | 282 | 343 | 350 | 312 | 351 |  | 357 | 357 | 356 | 329 | 330 | 330 | 331 | 8052000
42 | Mymensingh RPCL 210MW | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 51 | 50 | 48 | 48 | 48 | 49 | 47 | 47 | 45 | 48 | 49 |  | 49 | 50 | 49 | 50 | 50 | 50 | 50 | 1198730
43 | Haripur NEPC 110MW | [16 empty] | 70 | 110 |  | 110 | 110 | 110 | 30 | 0 |  |  | 418900
44 | Fenchugonj CCPP-1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 55 | 55 | 55 | 55 | 51 | 55 | 57 |  | 57 | 57 | 57 | 57 | 55 | 55 | 55 | 1292000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 51 | 51 | 51 | 51 | 78 | 77 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1600080
46 | Shajibazar 330 MW | [17 empty] | 0
47 | Shahjibazar GT: Unit- 8, 9 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 41 | 64 | 57 | 52 | 63 | 63 | 63 | 40 | 57 |  | 67 | 67 | 64 | 67 | 67 | 67 | 59 | 1489000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 50 | 50 | 84 | 84 | 86 | 50 | 50 | 50 | 50 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1873920
49 | Shahjibazar (EPL) 50MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 34 | 35 | 20 | 20 | 20 | 20 | 40 |  | 40 | 41 | 41 | 41 | 42 | 42 | 42 | 827640
50 | Sylhet GT 150 MW | 80 | 80 | 80 | 80 | 80 | 0 | [9 empty] | 28 | 48 | 90 |  | 98 | 130 | 100 | 100 | 100 | 78 | 78 | 1154820
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 48 | 48 | 48 | 49 | 48 | 48 | 48 | 47 | 45 | 45 | 46 | 44 | 46 | 20 | 22 | 22 | 21 | 48 |  | 48 | 48 | 48 | 48 | 48 | 49 | 48 | 1031800
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252180
54 | Hobiganj 11MW | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219936
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 47 | 47 | 50 | 50 | 22 | 22 | 22 | 22 | 38 |  | 50 | 50 | 50 | 49 | 50 | 50 | 50 | 1091400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 571056
57 | Summit Bibiana- 2 | 300 | 310 | 290 | 320 | 310 | 290 | 295 | 240 | 270 | 300 | 270 | 270 | 290 | 275 | 315 | 295 | 265 | 260 |  | 270 | 305 | 300 | 300 | 275 | 275 | 295 | 7476300
58 | Southern 55MW | [7 empty] | 36 | 36 | 36 | 49 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 17 | 0 |  | 756000
59 | Sikalbaha (Energis) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 45 | 50 | 50 | 50 | 995040
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 12 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510960
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 355140
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 447696
63 | Tripura | 80 | 78 | 76 | 74 | 74 | 70 | 70 | 72 | 82 | 88 | 86 | 92 | 98 | 68 | 100 | 92 | 104 | 124 |  | 122 | 122 | 122 | 118 | 108 | 100 | 90 | 2232960
64 | Malancha, Ctg. EPZ (United) | 34 | 26 | 32 | 32 | 42 | 40 | 37 | 11 | 5 | 3 | 3 | 3 | 3 | 8 | 3 | 4 | 9 | 6 |  | 25 | 26 | 32 | 31 | 37 | 39 | 42 | 527040
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507276
66 | Feni, Mohipal (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 8 | 11 | 11 | 200880
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 783200
68 | Summit Cumilla 25MW | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 9 | 9 | 11 | 8 | 9 | 18 | 13 | 13 | 13 | 13 | 13 |  | 21 | 21 | 21 | 21 | 21 | 16 | 9 | 343260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 21 | 21 | 24 | 20 | 20 | 20 | 20 | 20 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 534960
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 602300
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 721200
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh) | [14 empty] | 0 | 0 | 0 | 0
77 | Siddhirganj (Dutch Bangla) | [7 empty] | 4 | 7 | 7 | 7 | 24 | 40 | 24 | 24 | 24 | 32 | 75 |  | 100 | 100 | 100 | 40 | 0 |  |  | 649260
78 | Gazipur (RPCL) | [5 empty] | 2 | 27 | 34 | 34 | 38 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 26 | 0 | 710424
79 | Kodda 149MW | [6 empty] | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 133 |  | 133 | 133 | 133 | 133 | 64 | 0 |  | 845280
80 | Jamalpur 95MW | 78 | 78 | 78 | 78 | 64 | 70 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 72 | 72 | 72 | 79 | 79 |  | 79 | 79 | 79 | 79 | 78 | 78 | 78 | 1855680
81 | Lakdhanvi 52 MW | 52 | 52 | 25 | 8 | 0 |  | 14 | 39 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 34 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1023259
82 | Madanganj 102MW | 16 | 16 | 0 |  |  |  | 9 | 56 | 95 | 87 | 82 | 81 | 90 | 97 | 97 | 70 | 70 | 80 |  | 100 | 100 | 100 | 100 | 98 | 98 | 85 | 1594560
83 | Pagla (DPA ) | 21 | 21 | 10 | 0 | 0 | 21 | 21 | 21 | 10 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 46 |  | 10 | 0 | 0 |  |  |  |  | 333380
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 50 | 85 | 85 | 85 | 30 | 30 | 30 | 30 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1594560
85 | Keraniganj (Powerpac) 100MW | [15 empty] | 0 | 6 | 44 |  | 80 | 86 | 85 | 50 | 0 |  |  | 300387
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [6 empty] | 2 | 7 | 7 | 7 | 58 | 88 | 100 | 100 | 100 | 82 | 57 | 35 |  | 18 | 16 | 16 | 16 | 10 | 0 |  | 774720
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 15 | 15 | 15 | 15 | 15 | 15 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 76 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1181520
92 | Fenchuganj (EPL) 44MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 51 | 48 | 51 | 25 | 25 | 25 | 25 | 42 |  | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 1081000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1244524
94 | Gagnagar (Orion) | 102 | 102 | 80 | 60 | 7 | 0 | 8 | 50 | 65 | 65 | 75 | 102 | 102 | 102 | 102 | 59 | 60 | 102 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1665648
95 | Patenga 50MW | [6 empty] | 2 | 28 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 876480
96 | Chattogram ECPV 108 MW | [7 empty] | 33 | 33 | 33 | 33 | 52 | 52 | 55 | 71 | 71 | 90 | 105 |  | 106 | 106 | 106 | 106 | 66 | 32 | 0 | 1086720
97 | Katpotti 51 MW | 39 | 39 | 39 | 39 | 39 | 39 | 37 | 32 | 37 | 39 | 39 | 38 | 40 | 39 | 39 | 39 | 39 | 40 |  | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 936192
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 37 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 47 | 47 | 876480
99 | Madanganj-55 MW | 55 | 55 | 55 | 30 | 15 | 0 | 8 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1186333
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 36 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 36 | 18 | 1012553
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 163 | 163 | 130 | 163 | 163 | 100 | 100 | 100 | 163 | 163 | 130 | 100 | 130 | 163 | 100 | 163 |  | 163 | 163 | 163 | 130 | 130 | 100 | 100 | 3420581
102 | Sarishabari (Solar) | [6 empty] | 0.2 | 0.9 | 1.5 | 1.9 | 2.1 | 2.2 | 2 | 1.6 | 0.9 | 0.4 | 0 | 0 | [8 empty] | 12650
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 54 | 36 | 36 | 36 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1216440
104 | APR Energy , Keranigonj | [17 empty] | 53 |  | 0 | 0 | 0 |  |  |  |  | 30651
105 | Bramhangoan 100 MW (Aggreko) | [17 empty] | 50 |  | 0 | 0 | 0 |  |  |  |  | 27411
106 | United Mymensingh PPL | 50 | 30 | 7 | 7 | 7 | 24 | 24 | 80 | 80 | 80 | 120 | 150 | 150 | 100 | 100 | 108 | 120 | 185 |  | 200 | 200 | 200 | 170 | 140 | 100 | 100 | 2412000
112 | Aggreko Aurahati 100MW | [17 empty] | 51 |  | 0 | 0 | 0 |  |  |  |  | 27645
114 | Summit Gazipur-1 150MW | 17 | 17 | 15 | 15 | 15 | 17 | 33 | 40 | 56 | 64 | 48 | 87 | 87 | 85 | 85 | 83 | 87 | 105 |  | 129 | 66 | 131 | 131 | 132 | 15 | 15 | 1594080
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 80 | 89 | 91 | 91 | 92 | 82 | 92 | 100 | 72 | 73 | 100 | 92 | 92 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2236800
116 | Chandpur Desh 200MW | 160 | 150 | 150 | 135 | 90 | 128 | 166 | 166 | 145 | 184 | 0 |  | 106 | 110 | 110 | 110 | 195 | 201 |  | 202 | 177 | 172 | 142 | 145 | 140 | 140 | 3129000
117 | Midland 150MW | [9 empty] | 2 | 5 | 7 | 7 | 0 | 0 |  |  | 5 |  | 5 | 13 | 5 | 0 |  |  |  | 36800
118
120 | Eastern Zone Total | 4932 | 4730 | 4697 | 4595 | 4454 | 4527 | 4783.2 | 4844.8 | 5059.5 | 5265.9 | 5368.1 | 5590.4 | 5667.6 | 5310 | 5534.3 | 5481.1 | 5616.2 | 6792 |  | 6728 | 6664 | 6693 | 6350 | 5988 | 5570 | 5311 | 131637882
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 100 |  | 99 | 99 | 99 | 90 | 3 | 0 |  | 592250
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 12 | 25 |  | 29 | 29 | 29 | 28 | 0 |  |  | 105120
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [5 empty] | 0 | 17 | 53 | 53 | 53 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 107 | 67 | 5 | 1585440
130
131
132
133
| Summit Barisal 110 MW | [7 empty] | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 16 | 16 | 16 | 54 |  | 110 | 110 | 110 | 110 | 110 | 16 | 0 | 839040
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 96 | 96 | 95 | 94 | 95 | 94 | 95 | 95 | 96 | 96 | 61 | 60 | 62 | 62 | 95 |  | 95 | 96 | 96 | 96 | 96 | 96 | 95 | 2161106
| Bhola CCPP 194MW |  |  |  | 15 | 66 | 66 | 67 | 67 | 68 | 56 | 65 | 62 | 61 | 62 | 64 | 64 | 48 | 65 |  | 67 | 67 | 61 | 67 | 67 | 67 | 67 | 1298000
140 | Bhola (Venture) 33MW | 19 | 16 | 17 | 17 | 14 | 16 | 17 | 17 | 15 | 15 | 16 | 16 | 17 | 18 | 17 | 17 | 17 | 20 |  | 25 | 26 | 25 | 25 | 25 | 22 | 21 | 442520
141 | Bangla Trak Noapara | [17 empty] | 96 |  | 0 | [6 empty] | 100800
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 32 | 40 | 40 | 948750
143 | Gopalganj Peaking | 8 | [10 empty] | 6 | 7 | 7 | 7 | 12 | 12 | 35 |  | 50 | 8 | 9 | 9 | 0 |  |  | 130560
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 552 | 553 | 437 | 408 | 408 | 408 | 408 | 417 | 552 | 552 | 552 | 552 | 553 | 552 | 554 | 553 | 553 | 553 |  | 553 | 553 | 553 | 553 | 554 | 553 | 554 | 12441454
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3650000
153 | Baghabari GT 71MW | [17 empty] | 0 |  | 60 | 60 | 60 | 50 | 50 | 50 | 50 | 310000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 50 |  | 50 | 50 | 0 | 0 |  |  |  | 121560
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 189 | 188 | 185 | 191 | 184 | 201 | 190 | 181 | 178 | 179 | 189 | 178 | 188 | 152 | 146 | 143 | 136 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4720909
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | [11 empty] | 3 | 12 | 11 | 7 | 7 | 7 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 197900
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [16 empty] | 24 | 48 |  | 0 | 0 | 0 |  |  |  |  | 90611
162 | Bogra (GBB) | 20 | 18 | 14 | 12 | 12 | 12 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 463680
163 | Bogra (EPL) | 5 | 5 | 5 | 5 | 0 | 0 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 109152
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 190782
165 | Amnura 50MW | 50 | 50 | 30 | 30 | 12 | 12 | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1038000
166 | Katakhali (Northern) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 43 |  | 43 | 43 | 43 | 0 |  |  |  | 207985
167 | Katakhali Peaking | [16 empty] | 15 | 37 |  | 40 | 0 | 0 |  |  |  |  | 62797
168 | Santahar Peaking | [16 empty] | 23 | 47 |  | 47 | 47 | 46 | 47 | 0 |  |  | 221058
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 44 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1226400
170 | Chapainawabganj-100 MW | [16 empty] | 60 | 93 |  | 93 | 93 | 93 | 93 | 0 |  |  | 452508
171
172
173 | Rangpur GT
175 | Saidpur GT
176
177
178
178 | Western Zone Total | 1185 | 1172 | 1030 | 1020 | 1038 | 1056 | 1098 | 1196 | 1327 | 1316 | 1383 | 1416 | 1437 | 1366 | 1327 | 1330 | 1479 | 2014 |  | 2023 | 1943 | 1886 | 1830 | 1561 | 1420 | 1346 | 33708382