## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-11-11 | Sunday
|  | Date (day): | 2018-11-11 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9578 | MW |  |  | (b) At Evening Peak Hour : |  | 10528 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-11-10 | 2018-11-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 65 | 65 | 65 | 65 | 20
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 252 | 252 | 260 | 260 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 380 | 365 | 365 | 0
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 2018-01-12
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 321 | 361 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 0
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 10 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 98 | 20 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 48 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 80 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 87 | 180 | 193 | 193 | 17
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 30 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Gas shortage
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 46 | 46 | 46
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 82 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 4 | 6 | 0 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 133 | 133 |  | 16 | Engine problem
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 54 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 46 | 47 | 46 | 46 |  | 62 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 50 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 107 | 273 | 200 | 300
35 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 54 | 150 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 51 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 108 | 38 | 100 | 149
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 2300 | 3101 | 3576 | 4015 | 585 | 1016
39 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint. |  | 2018-04-11
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
41 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.9 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 45 | 45 | 45
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 70 | 110 | 110 |  | 120 | #2,5 Under maint.
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 200 | 201 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 29 | 40 | 50 | 50
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 29 | 70 | 70
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 90 | 100 | 100
| Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 0 | 0 | 52 | 71 | 100 | 100 |  |  | On test
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 20 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 16 | 99 | 105 | 105
| Chattogram area Total |  |  |  |  | 1661 | 1581 | 482.9 | 757 | 943 | 923 | 510 | 160
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 134 | 134
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 182 | 221 | 221
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 100 | 100 |  | 260 | ST under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 305 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 140 | 45 | 45 | 55 |  | Gas shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| Midland 150MW |  | HFO | IPP | 23*7.015 | 0 | 0 | 0 | 2 | 0 | 0 |  |  | On test
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 100 | 100 | 100 |  | 63 | ST Under maint.
| Chandpur Desh 200MW |  | HFO | IPP | 0 | 0 | 0 | 218 | 205 | 200 | 200 |  |  | On test
65 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
66 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 94 | 122 | 103 | 137
67 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
68 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 14 | 52 | 52
69 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 22 | 22
70 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2601 | 2541 | 1407 | 1628 | 1809 | 1993 | 297 | 323
71 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 122 | 108 | 107 | 107 | 95 |  | Gas shortage
72 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
73 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 75 | 78 | 78 |  | 17 | Engine problem.
74 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
75 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 17 | 190 | 150 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 185.1 | 393 | 357 | 405 | 95 | 17
76 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 54 | 55 | 55
77 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 52 | 78 | 63 | 63
78 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
79 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Uner maint. |  | 24/12/2018
80 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
81 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 48 | 44 | 44
82 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
83 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 67 | 66 | 66
84 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
85 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 38 | 40 | 45 | 45
86 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 98 | 130 | 130
87 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 19 | 19
88 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 45 | 47 | 48 | 48
89 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 24 | 25 | 25
90 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 125 | 0 | 0 | 0 |  | 341 | Under maint.
91 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 790 | 792 | 816 | 816 | 0 | 671
92 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 560 | 551 | 565 | 565
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 72 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 18 | 0 | 23
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 4 | 50 | 75 | 75
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
99 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 96 | 96
101 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2278 | 2209 | 723 | 836 | 996 | 1049 | 0 | 410
102 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
103 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
104 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 22 | 22 |  | 11 | Engine problem
105 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 161 | 185 | 182 | 182
106 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 70 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 249 | 415 | 409 | 439 | 0 | 11
107 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 80 | 80 | 80
108 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 |  | 52 | Under maint.
109 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 53 | 0 | 53
110 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
111 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 43 | 43 |  | 7 | Engine problem
112 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40
113 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
114 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 151 | 220 | 220
115 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 | 141 |  | Gas shortage
116 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | On test.
117 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 0 | 37
118 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
119 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
120 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
121 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
122 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 328 | 633 | 523 | 703 | 422 | 78
123 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
124 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 215 | 149 | 149 | 149 | 125
125 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
126 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 19 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 215 | 168 | 149 | 185 | 210 | 85
| Total |  |  |  |  | 17340 | 16742 | 6680 | 8723 | 9578 | 10528 | 2119 | 2771
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6368.3228 | 8316 | 9131.1072 | 10036.7818
A. |  | 2018-11-10 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8723 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 5012 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8723 | MW
3 | Day peak Generation : |  |  | 6680 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8316 | MW
4 | Evening peak Generation : |  |  | 8723 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 154.8591 | MKWHr | By Solar | 0.14695 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 101.3451 | MKWHr |  | By Oil: | 34.1008 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.9475 | MKWHr |  | By Hydro: | 1.3361 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2119 | MW | Dhaka | 3188 | 3188 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2771 | MW | Chittagong | 1094 | 1094 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4890 | MW | Khulna | 931 | 931 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 915.93 |  | MMCFD |  |  | Rajshahi | 812 | 812 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 75970465.701 | ii) Oil : | Taka | 280620585.56 | Comilla | 689 | 689 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15237350 | Total | Taka | 371828401.261 | Mymensingh | 565 | 565 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 4.646 | MKWHr. | Sylhet | 339 | 339 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -580 | MW at | 18:00 | hrs | Barisal | 180 | 180 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -760 | MW at | 20:00 | hrs | Rangpur | 518 | 518 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.4° C |  |  | Total | 8316 | 8316 |  | 0
B. |  | 2018-11-11 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 28.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10528 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 1028 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 168.6532 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5425 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8131 | MKWHr. | ii) HVDC Flow at Peak Time |  | 551 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1696 | MKWHr. | iii) Maximum HVDC Flow : |  | 560 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.85 |  | (b) Today: | 101.78 |  | (c) Rule Curve: |  | 108
.

## YesterdayGen
2018-11-10
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 65 | 0 | 254 | 0 | 310 | 0 | 0 | 0 | 364 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 34 | 20 | 0 | 0 | 22 | 42 | 80 | 0 | 100 | 360 | 305 | 182 | 16 | 90 | 38 | 5 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 8 | 12 | 76 | 104 | 0 | 20 | 0 | 55 | 63 | 5 | 50 | 130 | 0 | 65 | 10 | 40 | 78 | 0 | 47 | 0 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 0 | 18 | 0 |  | 513 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 19 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 130 | 97 | 0 | 0 | 0 | 0 | 0 |  | 4253 | 1438 | 5691 | 3006 | 513 | 1412 | 84 | 150 | 70 | 380 | 76 | 0 | 0 | 101.86
2:00 | 65 | 0 | 255 | 0 | 310 | 0 | 0 | 0 | 363 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 42 | 80 | 0 | 100 | 360 | 327 | 195 | 16 | 90 | 38 | 5 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 8 | 12 | 74 | 105 | 0 | 20 | 0 | 55 | 63 | 5 | 5 | 130 | 0 | 64 | 10 | 40 | 77 | 0 | 48 | 0 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 0 | 18 | 0 |  | 366 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 132 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4184 | 1198 | 5382 | 3049 | 366 | 1264 | 75 | 150 | 70 | 334 | 74 | 0 | 0 | 101.86
3:00 | 65 | 0 | 255 | 0 | 310 | 0 | 0 | 0 | 363 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 11 | 80 | 0 | 100 | 360 | 316 | 190 | 16 | 90 | 20 | 5 | 5 | 51 | 10 | 0 | 0 | 0 | 0 | 8 | 12 | 74 | 106 | 0 | 0 | 0 | 55 | 63 | 5 | 5 | 100 | 0 | 65 | 10 | 5 | 78 | 0 | 7 | 0 | 280 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 0 | 18 | 0 |  | 367 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 18 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 135 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3966 | 1201 | 5167 | 2965 | 367 | 1137 | 69 | 150 | 70 | 335 | 74 | 0 | 0 | 101.86
4:00 | 65 | 0 | 255 | 0 | 310 | 0 | 0 | 0 | 364 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 11 | 80 | 0 | 80 | 360 | 305 | 180 | 16 | 90 | 10 | 5 | 5 | 51 | 10 | 0 | 0 | 0 | 0 | 8 | 12 | 72 | 106 | 0 | 0 | 0 | 55 | 63 | 5 | 5 | 100 | 0 | 63 | 10 | 5 | 77 | 0 | 7 | 0 | 270 | 25 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 0 | 18 | 0 |  | 366 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 18 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 135 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3861 | 1199 | 5060 | 2871 | 366 | 1128 | 69 | 149 | 70 | 335 | 72 | 0 | 0 | 101.85
5:00 | 65 | 0 | 256 | 0 | 310 | 0 | 0 | 0 | 366 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 11 | 80 | 0 | 80 | 360 | 309 | 150 | 16 | 90 | 10 | 5 | 5 | 51 | 10 | 0 | 0 | 0 | 0 | 8 | 12 | 72 | 89 | 0 | 0 | 0 | 55 | 63 | 5 | 5 | 100 | 0 | 66 | 10 | 5 | 78 | 0 | 7 | 0 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 0 | 18 | 0 |  | 366 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 138 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3849 | 1163 | 5012 | 2793 | 366 | 1140 | 70 | 149 | 70 | 352 | 72 | 0 | 0 | 101.85
6:00 | 65 | 0 | 262 | 0 | 310 | 0 | 0 | 0 | 366 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 20 | 80 | 0 | 80 | 360 | 272 | 183 | 16 | 90 | 10 | 5 | 5 | 51 | 10 | 0 | 0 | 0 | 0 | 8 | 12 | 70 | 104 | 0 | 0 | 0 | 55 | 63 | 5 | 9 | 163 | 0 | 60 | 10 | 5 | 129 | 0 | 46 | 0 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0.1 | 0 | 18 | 0 |  | 366 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 19 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 152 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4055.1 | 1189 | 5244.1 | 2905 | 366 | 1261 | 69 | 150 | 70 | 353 | 70 | 0.1 | 0 | 101.85
7:00 | 65 | 0 | 262 | 0 | 310 | 0 | 0 | 0 | 366 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 20 | 80 | 0 | 80 | 360 | 272 | 183 | 16 | 90 | 37 | 5 | 5 | 51 | 80 | 0 | 0 | 0 | 0 | 20 | 12 | 70 | 104 | 0 | 0 | 0.2 | 55 | 63 | 47 | 47 | 163 | 0 | 68 | 89 | 40 | 127 | 0 | 47 | 0 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 3.357 | 0 | 221 | 0 |  | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 18 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 134 | 42 | 0 | 0 | 0 | 0 | 0 |  | 4553.557 | 951 | 5504.557 | 2688 | 366 | 1551 | 272 | 149 | 70 | 335 | 70 | 3.557 | 0 | 101.85
8:00 | 65 | 0 | 259 | 0 | 310 | 0 | 0 | 0 | 362 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 36 | 10 | 0 | 18 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 6 | 0 | 40 | 30 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 22 | 20 | 120 | 0 | 135 | 0 | 360 | 210 | 16 | 90 | 38 | 5 | 5 | 51 | 85 | 0 | 0 | 0 | 0 | 33 | 12 | 73 | 105 | 7 | 0 | 0.7 | 55 | 63 | 47 | 47 | 130 | 0 | 64 | 89 | 40 | 127 | 0 | 47 | 0 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 9.6 | 15 | 221 | 0 |  | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 186 | 11 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 21 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 220 | 0 | 95 | 0 | 0 | 0 | 0 | 17 |  | 4471.3 | 1195 | 5666.3 | 2754 | 366 | 1576 | 455 | 149 | 70 | 213 | 73 | 10.3 | 0 | 101.84
9:00 | 65 | 0 | 100 | 0 | 310 | 0 | 0 | 0 | 306 | 0 | 0 | 255 | 0 | 0 | 14 | 5 | 0 | 0 | 103 | 0 | 0 | 24 | 0 | 0 | 47 | 21 | 0 | 54 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 29 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 4 | 0 | 0 | 24 | 16 | 2 | 22 | 10 | 120 | 0 | 135 | 0 | 305 | 183 | 102 | 90 | 38 | 5 | 53 | 51 | 85 | 0 | 0 | 16 | 0 | 33 | 12 | 78 | 114 | 48 | 20 | 1.4 | 55 | 63 | 44 | 47 | 100 | 0 | 50 | 86 | 40 | 78 | 0 | 47 | 10 | 270 | 16 | 8 | 0 | 22 | 0 | 0 | 60 | 0 | 14 | 14 | 52 | 221 | 0 |  | 560 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 185 | 10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 52 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 4571.4 | 1520 | 6091.4 | 2475 | 560 | 1643 | 929 | 150 | 40 | 201 | 78 | 15.4 | 0 | 101.84
10:00 | 65 | 0 | 115 | 0 | 380 | 0 | 0 | 0 | 359 | 0 | 0 | 270 | 0 | 0 | 40 | 33 | 0 | 0 | 102 | 0 | 0 | 42 | 0 | 0 | 47 | 21 | 0 | 54 | 0 | 0 | 19 | 25 | 25 | 33 | 25 | 26 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 233 | 0 | 0 | 0 | 16 | 0 | 0 | 30 | 13 | 6 | 22 | 10 | 120 | 0 | 135 | 0 | 323 | 198 | 102 | 50 | 38 | 5 | 53 | 43 | 85 | 0 | 0 | 22 | 11 | 8 | 12 | 84 | 152 | 24 | 20 | 1.8 | 55 | 63 | 47 | 50 | 100 | 0 | 64 | 50 | 40 | 78 | 0 | 46 | 10 | 150 | 16 | 8 | 0 | 56 | 0 | 0 | 17 | 0 | 40 | 18.4 | 52 | 202 | 0 |  | 560 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 21 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 51 | 0 | 0 | 0 | 0 | 53 |  | 4725.2 | 1420 | 6145.2 | 2582 | 560 | 1513 | 963 | 150 | 40 | 233 | 84 | 20.2 | 0 | 101.83
11:00 | 65 | 0 | 100 | 0 | 380 | 0 | 0 | 0 | 359 | 0 | 0 | 290 | 0 | 2 | 60 | 55 | 0 | 0 | 102 | 0 | 0 | 74 | 16 | 0 | 47 | 21 | 0 | 54 | 0 | 17 | 19 | 25 | 25 | 33 | 25 | 40 | 0 | 40 | 0 | 0 | 0 | 26 | 0 | 201 | 0 | 0 | 0 | 16 | 0 | 0 | 30 | 12 | 6 | 23 | 3 | 120 | 0 | 135 | 0 | 323 | 195 | 110 | 50 | 40 | 5 | 5 | 45 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 88 | 137 | 24 | 20 | 2 | 55 | 52 | 50 | 47 | 130 | 0 | 63 | 50 | 38 | 100 | 0 | 44 | 10 | 140 | 16 | 8 | 0 | 68 | 0 | 0 | 17 | 0 | 70 | 19.8 | 0 | 219 | 0 |  | 560 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 3 | 40 | 184 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 192 | 0 | 51 | 0 | 0 | 0 | 0 | 53 |  | 4758.8 | 1536 | 6294.8 | 2567 | 560 | 1505 | 1093 | 200 | 40 | 220 | 88 | 21.8 | 0 | 101.83
12:00 | 65 | 0 | 252 | 0 | 340 | 0 | 0 | 0 | 321 | 0 | 0 | 450 | 0 | 7 | 98 | 55 | 0 | 0 | 87 | 0 | 0 | 82 | 16 | 0 | 46 | 21 | 4 | 54 | 0 | 17 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 36 | 0 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 29 | 0 | 0 | 68 | 16 | 13 | 22 | 2 | 120 | 0 | 135 | 0 | 305 | 185 | 102 | 50 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 122 | 24 | 20 | 2.1 | 55 | 52 | 47 | 47 | 130 | 0 | 54 | 84 | 38 | 78 | 0 | 45 | 10 | 125 | 17 | 8 | 0 | 107 | 0 | 0 | 17 | 0 | 108 | 19.9 | 52 | 218 | 0 |  | 560 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 4 | 40 | 161 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 183 | 0 | 70 | 0 | 0 | 0 | 0 | 70 |  | 5165 | 1515 | 6680 | 2498 | 560 | 1662 | 1373 | 215 | 36 | 220 | 94 | 22 | 0 | 101.82
13:00 | 65 | 0 | 243 | 0 | 300 | 0 | 0 | 0 | 355 | 0 | 0 | 450 | 0 | 7 | 98 | 55 | 0 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 47 | 21 | 6 | 54 | 0 | 36 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 0 | 0 | 0 | 26 | 0 | 200 | 0 | 0 | 0 | 32 | 0 | 17 | 90 | 52 | 36 | 22 | 9 | 120 | 0 | 135 | 0 | 305 | 185 | 102 | 50 | 40 | 30 | 5 | 45 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 92 | 103 | 24 | 20 | 1.8 | 55 | 52 | 50 | 47 | 163 | 0 | 51 | 84 | 40 | 78 | 0 | 47 | 10 | 0 | 16 | 8 | 0 | 105 | 0 | 0 | 17 | 0 | 131 | 18.3 | 52 | 219 | 0 |  | 560 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 4 | 40 | 150 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 195 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 5147.1 | 1590 | 6737.1 | 2340 | 560 | 1661 | 1573 | 214 | 40 | 237 | 92 | 20.1 | 0 | 101.82
14:00 | 65 | 0 | 248 | 0 | 200 | 0 | 0 | 0 | 281 | 0 | 0 | 450 | 0 | 35 | 97 | 55 | 0 | 0 | 38 | 0 | 7 | 102 | 16 | 0 | 47 | 11 | 6 | 54 | 0 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 214 | 0 | 0 | 0 | 32 | 0 | 17 | 90 | 52 | 38 | 22 | 7 | 120 | 0 | 135 | 0 | 253 | 190 | 73 | 50 | 40 | 5 | 5 | 51 | 40 | 0 | 0 | 0 | 0 | 0 | 12 | 96 | 107 | 28 | 20 | 1.6 | 55 | 56 | 11 | 47 | 100 | 0 | 64 | 40 | 40 | 80 | 0 | 45 | 10 | 0 | 16 | 8 | 0 | 140 | 0 | 0 | 17 | 0 | 129 | 15.1 | 0 | 218 | 0 |  | 551 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 170 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 4791.7 | 1588 | 6379.7 | 2267 | 551 | 1345 | 1603 | 214 | 40 | 247 | 96 | 16.7 | 0 | 101.82
15:00 | 65 | 0 | 249 | 0 | 358 | 0 | 0 | 0 | 357 | 0 | 0 | 450 | 0 | 21 | 70 | 55 | 0 | 0 | 93 | 0 | 4 | 50 | 16 | 0 | 47 | 10 | 6 | 54 | 0 | 55 | 19 | 25 | 25 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 36 | 0 | 17 | 90 | 43 | 39 | 22 | 2 | 120 | 0 | 135 | 0 | 305 | 183 | 92 | 50 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 98 | 105 | 28 | 20 | 1 | 54 | 76 | 38 | 48 | 163 | 0 | 63 | 40 | 40 | 78 | 0 | 44 | 10 | 0 | 8 | 8 | 0 | 114 | 0 | 0 | 17 | 0 | 74 | 10.7 | 0 | 218 | 0 |  | 551 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 7 | 40 | 163 | 17 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 135 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 5033.7 | 1541 | 6574.7 | 2539 | 551 | 1570 | 1343 | 180 | 40 | 242 | 98 | 11.7 | 0 | 101.82
16:00 | 65 | 0 | 250 | 0 | 380 | 0 | 0 | 0 | 359 | 0 | 0 | 450 | 0 | 7 | 15 | 15 | 0 | 0 | 95 | 0 | 7 | 16 | 16 | 0 | 47 | 21 | 6 | 54 | 0 | 17 | 19 | 25 | 25 | 33 | 25 | 23 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 202 | 0 | 0 | 0 | 40 | 0 | 17 | 90 | 18 | 45 | 22 | 2 | 120 | 0 | 135 | 0 | 305 | 184 | 130 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 15 | 8 | 30 | 12 | 92 | 109 | 50 | 20 | 0.5 | 54 | 76 | 44 | 48 | 163 | 0 | 51 | 86 | 40 | 98 | 0 | 44 | 10 | 0 | 8 | 8 | 0 | 42 | 0 | 0 | 110 | 0 | 15 | 3.9 | 10 | 218 | 0 |  | 551 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 14 | 40 | 154 | 17 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 24 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 132 | 0 | 96 | 0 | 0 | 0 | 0 | 17 |  | 5096.4 | 1392 | 6488.4 | 2676 | 551 | 1662 | 1064 | 150 | 40 | 249 | 92 | 4.4 | 0 | 101.82
17:00 | 65 | 0 | 251 | 0 | 380 | 0 | 0 | 0 | 358 | 40 | 0 | 450 | 0 | 7 | 15 | 15 | 0 | 0 | 150 | 0 | 7 | 24 | 16 | 0 | 47 | 0 | 6 | 54 | 18 | 40 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 17 | 90 | 40 | 48 | 22 | 8 | 120 | 0 | 135 | 0 | 305 | 184 | 130 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 12 | 100 | 108 | 57 | 20 | 0 | 54 | 78 | 47 | 48 | 130 | 0 | 64 | 86 | 40 | 128 | 19 | 44 | 10 | 0 | 13 | 8 | 0 | 42 | 0 | 0 | 110 | 0 | 15 | 0.2 | 27 | 150 | 0 |  | 552 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 7 | 40 | 40 | 165 | 17 | 20 | 0 | 80 | 0 | 0 | 10 | 0 | 12 | 8 | 0 | 40 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 132 | 0 | 96 | 0 | 0 | 0 | 0 | 35 |  | 5307.2 | 1465 | 6772.2 | 2828 | 552 | 1637 | 1145 | 149 | 70 | 291 | 100 | 0.2 | 0 | 101.81
18:00 | 65 | 0 | 252 | 0 | 380 | 0 | 0 | 0 | 361 | 110 | 0 | 450 | 0 | 10 | 20 | 48 | 0 | 0 | 180 | 0 | 30 | 102 | 115 | 80 | 47 | 46 | 6 | 54 | 54 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 29 | 51 | 90 | 99 | 45 | 22 | 14 | 120 | 0 | 135 | 0 | 305 | 182 | 140 | 100 | 40 | 5 | 5 | 51 | 85 | 31 | 14 | 22 | 11 | 33 | 20 | 122 | 108 | 75 | 20 | 0 | 54 | 78 | 50 | 48 | 163 | 0 | 67 | 86 | 40 | 98 | 19 | 47 | 10 | 0 | 24 | 8 | 0 | 273 | 54 | 50 | 190 | 51 | 38 | 0 | 71 | 205 | 2 |  | 551 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 18 | 50 | 40 | 185 | 25 | 110 | 0 | 80 | 0 | 0 | 53 | 90 | 50 | 43 | 30 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 151 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 6671 | 2052 | 8723 | 2897 | 551 | 1702 | 2499 | 149 | 70 | 733 | 122 | 0 | 0 | 101.81
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 560 | 560 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 65 | 0 | 252 | 0 | 380 | 0 | 0 | 0 | 322 | 55 | 0 | 450 | 0 | 57 | 84 | 55 | 0 | 0 | 188 | 0 | 60 | 102 | 100 | 50 | 47 | 25 | 29 | 54 | 54 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 194 | 0 | 0 | 0 | 40 | 0 | 34 | 100 | 99 | 50 | 22 | 25 | 120 | 0 | 135 | 55 | 305 | 182 | 157 | 96 | 40 | 5 | 5 | 51 | 41 | 0 | 52 | 22 | 11 | 33 | 20 | 118 | 114 | 78 | 20 | 0 | 54 | 78 | 50 | 48 | 100 | 0 | 67 | 86 | 40 | 77 | 19 | 48 | 10 | 0 | 24 | 8 | 0 | 252 | 0 | 0 | 180 | 0 | 118 | 0 | 100 | 205 | 5 |  | 551 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 18 | 55 | 40 | 185 | 22 | 110 | 0 | 80 | 0 | 0 | 0 | 93 | 50 | 8 | 0 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 179 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 6542 | 2010 | 8552 | 2969 | 551 | 1582 | 2554 | 149 | 70 | 559 | 118 | 0 | 0 | 101.8
19:30 | 65 | 0 | 252 | 0 | 380 | 0 | 0 | 0 | 322 | 13 | 0 | 450 | 0 | 57 | 100 | 55 | 0 | 0 | 205 | 0 | 40 | 102 | 100 | 10 | 47 | 25 | 40 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 40 | 0 | 34 | 100 | 99 | 50 | 22 | 31 | 120 | 0 | 135 | 100 | 305 | 181 | 157 | 100 | 40 | 5 | 5 | 51 | 40 | 0 | 52 | 22 | 11 | 33 | 20 | 118 | 114 | 79 | 20 | 0 | 54 | 78 | 53 | 50 | 100 | 0 | 66 | 86 | 40 | 78 | 19 | 48 | 10 | 0 | 24 | 11 | 0 | 275 | 0 | 0 | 180 | 0 | 118 | 0 | 100 | 220 | 5 |  | 551 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 18 | 58 | 40 | 184 | 25 | 110 | 0 | 80 | 0 | 0 | 0 | 93 | 50 | 0 | 0 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 177 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 6591 | 1971 | 8562 | 3034 | 551 | 1595 | 2477 | 149 | 70 | 568 | 118 | 0 | 0 | 101.8
20:00 | 65 | 0 | 253 | 0 | 380 | 0 | 0 | 0 | 330 | 0 | 0 | 450 | 0 | 47 | 100 | 55 | 0 | 0 | 207 | 0 | 7 | 102 | 50 | 0 | 47 | 10 | 39 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 34 | 100 | 99 | 50 | 22 | 33 | 105 | 0 | 120 | 160 | 338 | 169 | 78 | 100 | 40 | 5 | 5 | 51 | 40 | 0 | 52 | 22 | 11 | 33 | 20 | 118 | 109 | 78 | 20 | 0 | 54 | 78 | 53 | 50 | 100 | 0 | 66 | 86 | 40 | 98 | 19 | 47 | 10 | 0 | 24 | 11 | 0 | 272 | 0 | 0 | 200 | 0 | 126 | 0 | 100 | 220 | 7 |  | 551 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 60 | 40 | 185 | 26 | 110 | 0 | 85 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 6485 | 1894 | 8379 | 3115 | 551 | 1526 | 2391 | 149 | 70 | 459 | 118 | 0 | 0 | 101.8
21:00 | 65 | 0 | 255 | 0 | 380 | 0 | 0 | 0 | 350 | 0 | 0 | 450 | 0 | 0 | 100 | 55 | 0 | 0 | 205 | 0 | 0 | 102 | 0 | 0 | 47 | 10 | 40 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 40 | 0 | 34 | 30 | 45 | 50 | 22 | 39 | 100 | 0 | 80 | 230 | 356 | 178 | 36 | 101 | 10 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 20 | 112 | 104 | 78 | 20 | 0 | 54 | 78 | 53 | 50 | 130 | 0 | 65 | 40 | 40 | 128 | 19 | 10 | 10 | 0 | 24 | 11 | 0 | 272 | 0 | 0 | 100 | 0 | 131 | 0 | 100 | 221 | 6 |  | 551 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 58 | 40 | 184 | 26 | 110 | 0 | 100 | 0 | 0 | 0 | 24 | 50 | 0 | 0 | 52 | 45 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 6179 | 1849 | 8028 | 3180 | 551 | 1503 | 2084 | 149 | 70 | 379 | 112 | 0 | 0 | 101.8
22:00 | 65 | 0 | 253 | 0 | 380 | 0 | 0 | 0 | 298 | 0 | 0 | 450 | 0 | 0 | 100 | 55 | 0 | 0 | 183 | 0 | 0 | 102 | 0 | 0 | 47 | 11 | 39 | 54 | 55 | 17 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 0 | 34 | 30 | 12 | 50 | 22 | 41 | 80 | 0 | 80 | 210 | 305 | 182 | 36 | 100 | 10 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 10 | 106 | 104 | 78 | 20 | 0 | 55 | 78 | 53 | 51 | 100 | 0 | 53 | 40 | 40 | 98 | 19 | 12 | 10 | 0 | 24 | 11 | 0 | 275 | 0 | 0 | 100 | 0 | 126 | 0 | 100 | 221 | 0 |  | 551 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 59 | 40 | 168 | 26 | 64 | 0 | 90 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 0 | 0 | 107 |  | 5855 | 1703 | 7558 | 2984 | 551 | 1425 | 1961 | 149 | 70 | 312 | 106 | 0 | 0 | 101.79
23:00 | 65 | 0 | 250 | 0 | 380 | 0 | 0 | 0 | 303 | 0 | 0 | 450 | 0 | 0 | 100 | 55 | 0 | 0 | 163 | 0 | 0 | 102 | 0 | 0 | 47 | 10 | 39 | 54 | 56 | 17 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 205 | 0 | 0 | 0 | 40 | 0 | 34 | 20 | 13 | 50 | 22 | 42 | 80 | 0 | 80 | 21 | 323 | 196 | 36 | 100 | 30 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 15 | 98 | 107 | 78 | 20 | 0 | 55 | 78 | 53 | 51 | 100 | 0 | 63 | 40 | 40 | 98 | 19 | 12 | 10 | 0 | 25 | 11 | 0 | 130 | 0 | 0 | 15 | 0 | 41 | 0 | 100 | 128 | 0 |  | 551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 186 | 22 | 48 | 0 | 80 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 20 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 95 | 0 | 0 | 0 | 0 | 107 |  | 5299 | 1622 | 6921 | 2846 | 551 | 1425 | 1512 | 150 | 70 | 269 | 98 | 0 | 0 | 101.79
24:00 | 65 | 0 | 254 | 0 | 380 | 0 | 0 | 0 | 335 | 0 | 0 | 450 | 0 | 0 | 74 | 55 | 0 | 0 | 180 | 0 | 0 | 24 | 0 | 0 | 47 | 10 | 39 | 54 | 56 | 17 | 19 | 25 | 25 | 33 | 25 | 8 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 40 | 0 | 17 | 20 | 13 | 18 | 22 | 42 | 80 | 0 | 110 | 10 | 305 | 182 | 36 | 100 | 38 | 5 | 5 | 51 | 85 | 0 | 25 | 22 | 11 | 33 | 12 | 90 | 107 | 57 | 20 | 0 | 55 | 78 | 50 | 51 | 100 | 0 | 57 | 40 | 40 | 98 | 0 | 16 | 10 | 0 | 25 | 11 | 0 | 107 | 0 | 0 | 15 | 0 | 15 | 0 | 91 | 128 | 0 |  | 553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 179 | 21 | 16 | 0 | 80 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 52 | 0 | 18 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 95 | 0 | 0 | 0 | 0 | 35 |  | 5013 | 1460 | 6473 | 2828 | 553 | 1455 | 1106 | 150 | 70 | 221 | 90 | 0 | 0 | 101.79
KWH | 1462000 | 0 | 5698000 | 0 | 8048118 | 0 | 0 | 0 | 8214000 | 179400 | 0 | 8397775 | 0 | 216960 | 1177824 | 745539 | 0 | 0 | 2852000 | 0 | 206150 | 1190304 | 367200 | 182747 | 744960 | 388830 | 269808 | 876960 | 364646 | 516096 | 409464 | 600000 | 560520 | 827000 | 629000 | 630840 | 0 | 860000 | 476100 | 0 | 0 | 395820 | 0 | 4848898 | 0 | 0 | 0 | 542880 | 29216 | 380376 | 1149240 | 695040 | 586560 | 538224 | 512640 | 2530816 | 0 | 2704860 | 3473000 | 7550000 | 4562000 | 1656000 | 1982600 | 757440 | 205440 | 216000 | 1181567 | 1177824 | 16800 | 319886 | 268920 | 130320 | 432900 | 327420 | 2169600 | 2632840 | 864000 | 343548 | 12950 | 1267000 | 1613720 | 864600 | 951000 | 3449749 | 0 | 1451000 | 1344000 | 789480 | 2270130 | 138000 | 835440 | 158220 | 3021136 | 462216 | 216480 | 0 | 2215520 | 36989 | 19633 | 1269600 | 21807 | 1323360 | 134000 | 911040 | 3687000 | 11710 |  | 11813091 | 0 | 0 | 0 | 526080 | 0 | 0 | 0 | 85440 | 356224 | 608250 | 4382000 | 445200 | 642240 | 0 | 1329000 | 0 | 0 | 69941 | 268344 | 682270 | 159878 | 21130 | 816480 | 186467 | 418800 | 120420 | 187023 | 0 | 0 | 3947500 | 0 | 39000 | 0 | 0 | 3060900 | 970436 | 1687323 | 0 | 0 | 0 | 0 | 1285000 |  | 120750696 | 34108437 | 154859133 | 65698459 | 11813091 | 35646614 | 26461347 | 3947500 | 1336100 | 7639472 | 2169600 | 146950 | 0
Fuel Cost | 1257320 | 0 | 4900280 | 0 | 5150795.52 | 0 | 0 | 0 | 5010540 | 1724034 | 0 | 5626509.25 | 0 | 1362508.8 | 7867864.32 | 4555243.29 | 0 | 0 | 3165720 | 0 | 1288437.5 | 7844103.36 | 3550824 | 1164098.39 | 4462310.4 | 6217391.7 | 1799619.36 | 6252724.8 | 2279037.5 | 3235921.92 | 307098 | 450000 | 0 | 0 | 0 | 5967746.4 | 0 | 0 | 0 | 0 | 0 | 3748415.4 | 0 | 66187457.7 | 0 | 0 | 0 | 4771915.2 | 314656.32 | 3701058.48 | 7113795.6 | 4489958.4 | 3836102.4 | 457490.4 | 0 | 2303042.56 | 0 | 2461422.6 | 2153260 | 5209500 | 3193400 | 1142640 | 1903296 | 507484.8 | 176678.4 | 198720 | 968884.94 | 1118932.8 | 182112 | 2373554.12 | 207068.4 | 97740 | 333333 | 245565 | 14840064 | 1974630 | 7940160 | 264531.96 | 0 | 1317680 | 1678268.8 | 830016 | 855900 | 2690804.22 | 0 | 1654140 | 1438080 | 868428 | 2587948.2 | 176640 | 776959.2 | 147144.6 | 1933527.04 | 346662 | 164524.8 | 0 | 16084675.2 | 641019.37 | 334742.65 | 9077640 | 371809.35 | 0 | 0 | 0 | 34436580 | 109371.4 |  | 60246764.1 | 0 | 0 | 0 | 4361203.2 | 0 | 0 | 0 | 962054.4 | 4196318.72 | 4793010 | 3023580 | 440748 | 4752576 | 0 | 1395450 | 0 | 0 | 749767.52 | 2404362.24 | 5901635.5 | 1422914.2 | 225034.5 | 8099481.6 | 2194716.59 | 460680 | 113194.8 | 141576.411 | 0 | 0 | 15237350 | 0 | 1044030 | 0 | 0 | 2142630 | 14226591.76 | 0 | 0 | 0 | 0 | 0 | 0 |  | 308379559.82 | 138535669.541 | 446915229.361 | 51172078.451 | 60246764.1 | 24798387.25 | 180681601.33 | 15237350 | 0 | 99938984.23 | 14840064 | 0 | 0
Yesterday Day Peak | 65 | 0 | 252 | 0 | 340 | 0 | 0 | 0 | 321 | 0 | 0 | 450 | 0 | 7 | 98 | 55 | 0 | 0 | 87 | 0 | 0 | 82 | 16 | 0 | 46 | 21 | 4 | 54 | 0 | 17 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 36 | 0 | 0 | 0 | 25 | 0 | 200 | 0 | 0 | 0 | 29 | 0 | 0 | 68 | 16 | 13 | 22 | 2 | 120 | 0 | 135 | 0 | 305 | 185 | 102 | 50 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 122 | 24 | 20 | 2.1 | 55 | 52 | 47 | 47 | 130 | 0 | 54 | 84 | 38 | 78 | 0 | 45 | 10 | 125 | 17 | 8 | 0 | 107 | 0 | 0 | 17 | 0 | 108 | 19.9 | 52 | 218 | 0 |  | 560 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 4 | 40 | 161 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 52 | 0 | 22 | 5 | 8 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 183 | 0 | 70 | 0 | 0 | 0 | 0 | 70 |  | 6680 | DayPeak
Yesterday Evening Peak | 65 | 0 | 252 | 0 | 380 | 0 | 0 | 0 | 361 | 110 | 0 | 450 | 0 | 10 | 20 | 48 | 0 | 0 | 180 | 0 | 30 | 102 | 115 | 80 | 47 | 46 | 6 | 54 | 54 | 55 | 19 | 25 | 25 | 33 | 25 | 43 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 40 | 29 | 51 | 90 | 99 | 45 | 22 | 14 | 120 | 0 | 135 | 0 | 305 | 182 | 140 | 100 | 40 | 5 | 5 | 51 | 85 | 31 | 14 | 22 | 11 | 33 | 20 | 122 | 108 | 75 | 20 | 0 | 54 | 78 | 50 | 48 | 163 | 0 | 67 | 86 | 40 | 98 | 19 | 47 | 10 | 0 | 24 | 8 | 0 | 273 | 54 | 50 | 190 | 51 | 38 | 0 | 71 | 205 | 2 |  | 551 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 18 | 50 | 40 | 185 | 25 | 110 | 0 | 80 | 0 | 0 | 53 | 90 | 50 | 43 | 30 | 52 | 46 | 22 | 5 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 151 | 0 | 95 | 0 | 0 | 0 | 0 | 105 |  | 8723 | EvPeak
Forecast for Evening | 65 | 0 | 260 | 0 | 365 | 0 | 0 | 0 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 193 | 100 | 100 | 102 | 133 | 100 | 46 | 46 | 40 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 25 | 43 | 0 | 80 | 30 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 0 | 50 | 70 | 51 | 100 | 105 | 45 | 22 | 20 | 120 | 0 | 134 | 100 | 360 | 221 | 45 | 100 | 40 | 5 | 5 | 51 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 137 | 107 | 78 | 20 | 0 | 55 | 63 | 51 | 44 | 163 | 0 | 66 | 86 | 45 | 130 | 19 | 48 | 10 | 0 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 |  |  | 565 | 30 | 0 | 0 | 115 | 0 | 0 | 0 | 23 | 75 | 40 | 182 | 22 | 110 | 30 | 80 | 0 | 0 | 53 | 90 | 50 | 43 | 40 | 52 | 37 | 22 | 5 | 11 | 0 | 0 | 149 | 17 | 19 | 0 | 0 | 220 | 0 | 95 | 96 | 0 | 0 | 0 | 105
Forecast for Day | 65 | 0 | 260 | 0 | 365 | 0 | 0 | 0 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 193 | 100 | 100 | 102 | 133 | 100 | 46 | 46 | 0 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 25 | 43 | 0 | 80 | 30 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 0 | 50 | 70 | 51 | 100 | 105 | 45 | 22 | 20 | 120 | 0 | 134 | 100 | 360 | 221 | 45 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 103 | 107 | 78 | 20 | 2 | 55 | 63 | 51 | 44 | 163 | 0 | 66 | 86 | 45 | 130 | 19 | 48 | 10 | 0 | 25 | 11 | 100 | 200 | 150 | 0 | 150 | 100 | 100 | 20 | 100 | 200 |  |  | 565 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 75 | 40 | 182 | 22 | 110 | 0 | 80 | 0 | 0 | 0 | 0 | 50 | 43 | 40 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 149 |  | 0 | 0 | 0 | 220 | 0 | 95 | 96 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 65 | 0 | 260 | 0 | 300 | 0 | 0 | 0 | 367 | 0 | 0 | 380 | 0 | 7 | 20 | 20 | 0 | 0 | 193 | 0 | 4 | 24 | 0 | 0 | 46 | 31 | 0 | 54 | 54 | 17 | 19 | 25 | 10 | 33 | 8 | 8 | 0 | 38 | 30 | 0 | 0 | 8 | 0 | 199 | 0 | 0 | 0 | 40 | 0 | 0 | 20 | 12 | 6 | 22 | 14 | 100 | 0 | 100 | 150 | 276 | 184 | 16 | 100 | 38 | 5 | 5 | 51 | 20 | 0 | 16 | 22 | 8 | 33 | 12 | 72 | 107 | 78 | 20 | 0.5 | 55 | 63 | 45 | 40 | 100 | 0 | 32 | 20 | 40 | 88 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 70 | 0 | 15 | 3.2 | 51 | 105 | 0 | 0 | 466 | 0 | 11 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 17 | 16 | 0 | 80 | 0 | 0 | 0 | 0 | 24 | 8 | 0 | 44 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 132 | 0 | 95 | 0 | 0 | 0 | 0 | 53 | 0
199
| Minimum Generation |  | 5012 | 5:00
| Highest Generation |  | 8723 | 18:00
| Day Peak Generation |  | 6680 | 12:00
| Evening Peak Generation |  | 8723 | 18:00
| HVDC Max Flow |  | 560 | 9:00
| HVDC EvPeak Flow |  | 551 | 18:00
| Load factor L.F |  | 73.97%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-11-11
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-11-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6680 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5425 | MW
Evening Peak Generation : |  | 8723 | MW Hour : | 18:00 | Available Max Generation : |  | 10528 | MW
E.P. Demand (at gen end) : |  | 8723 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 8723 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1028 | MW
Total Gen. (MKWH) : |  | 154.8591 | System Load Factor : | 73.97% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -760 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-11-11
Actual : | 101.78 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 915.93 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 75970465.701
|  | Coal : | 15237350 | Oil : | 280620585.56 | Total : | 371828401.261
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3379.8842 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1145.2293 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1025.3536 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 926.2329 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 837.167 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 675.5537 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 383.0362 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.0772 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 520.9952 |  |  | 0 | 0%
Total | 0 |  | 9067.5293 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Sirajganj Unit-1 ,3
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Ghorasal Regent 108 MW
|  |  |  | 3) Ghorasal Unit-3,5 |  | 12) Haripur 412 MW
|  |  |  | 4) Chattogram ST-1,2 |  | 13) Ashuganj-3,4
|  |  |  | 5) Tongi GT |  | 14) Ghorasal Max 78 MW
|  |  |  | 6) Baghabari-71 MW |  | 15) Shajibazar 330 MW
|  |  |  | 7) Haripur GT-1 |  | 16) Summit Bibiyana-2
|  |  |  | 8) Siddhirganj 210 MW ST |  | 17) Bheramara 360 MW
|  |  |  | 9) Kaptai #2,5 |  | 18) Ashuganj(N) ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Kaptai-Hathazari 132 kV Ckt-2 was under shut down from 08:48 to 15:50 for A/M.
b) Tongi(old)-Tongi(New) 132 kV Ckt was under shut down from 10:45 to 11:45 for A/M.
c) Haripur-Meghnaghat 230 kV Ckt-1 & Haripur 230 kV bus-2 were under shut down from 08:46 to 14:36 for A/M.
d) Sirajganj 230 kV MTR-1 was under shut down from 09:06 to 12:47 for A/M.
e) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 08:38 to 16:53 for A/M.
f) Jamalpur-United Mymensingh 200 MW P/S 132 kV Ckt-2 was under shut down from 08:20 to 16:17 for A/M.
g) Maniknagar 230/132 kv TR1 along with Maniknagar-Siddhirganj 230 kV Ckt-1 were under shut down
from 08:01 to 16:34 for A/M.
h) Tongi-Bashundhara 132 kV Ckt-2 was under shut down from 08:40 to 16:31 for A/M.
i) Rajshahi-Natore 132 kV Ckt-1 was under shut down from 08:52 to 16:16 for A/M.
j) Bogura-Barapukuria 230 kV Ckt-1 was under shut down from 08:38 to 16:06 for A/M.
k) Joypurhat 132/33 kV T4 transformer was under shut down from 08:10 to 16:13 for A/M.
l) Goalpara 132/33 kV T5 transformer was under shut down from 09:03 to 16:16 for A/M.
m) After maintenance Meghnaghat 450 MW CCPP GT-2 was synchronized at 08:10.
n) Pabna-Shahjadpur 132 kV Ckt was under shut down from 10:10 to 10:32 due to isolator problem.
o) Hasnabad-Kamrangirchar 132 kV Ckt tripped at 10:37 from Hasnabad end showing Dist C-phase and |  |  |  | About 58 MW power interruption occurred under Kamrangirchar S/S area
was switched on at 10:43. |  |  |  | from 10:37 to 10:43.
p) Summit Bibiyana 341 MW CCPP was shut down at 12:32 due to problem at GT controller.
q) Baghabari 100 MW tripped at 11:52 due to air intake atom differential pressure low and
was synchronized at 14:03.
r) Aminbazar-Meghnaghat 230 kV Ckt-1 was switched on at 13:20.
s) Ishurdi 230 kV bus-1 was under shut down from 10:23 to 15:48 for test by protection department.
t) Siddhirganj-Haripur 230 kV Ckt-1 was under shut down from 14:45 to 18:20 for C/M.
u) Siddhirganj GT-1 was synchronized at 16:47.
v) Siddhirganj GT-2 was shut down at 12:52 and was synchronized at 13:35 for test run FGMO.
w) Shyampur 230 kV (New)-Shyampur (old) 132 kV Ckt-1 tripped at 16:57 from Shyampur (Old) end
showing busbar protection fail due to 33 kV Ranisteel feeder fault and was switched on at 17:05.Again |  |  |  | About 82 MW power interruption occurred under Shyampur(Old) S/S area
tripped at 17:12 due to same reason showing same relay and was switched on at 17:18. |  |  |  | from 16:57 to 17:05 & 17:12 to 17:18 respectively.
x) Ashuganj(N )360 MW CCPP GT was synchronized at 18:24.
y) After maintenance Madaripur 132 kV bus-2 was switched on at 17:02.
z) After maintenance Madaripur 132/33 kV T3 transformer was switched on at 17:10.
aa) Madaripur 132 kV bus-B was shut down at 07:16 (11/11/2018) for A/M.
ab) Sylhet 132/33 kV T4 transformer was shut down at 07:19(11/11/2018) for A/M.
ac) Bheramara 360 MW CCPP GT was synchronized at 04:41(11/11/2018) and was shut down at 09:29 for
maintenance.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-11-10 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 65 | 1462000
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 252 | 5698000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 8048118
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 179400
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 361 | 8214000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8397775
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 10 | 216960 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 20 | 1177824 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 48 | 745539 | Engine problem
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 80 | 182747 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 409464 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 180 | 2852000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 30 | 206150 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 46 | 388830 | Engine problem
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1190304
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 6 | 269808 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 876960
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 367200 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 54 | 364646
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 516096
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 47 | 744960 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1160520 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 827000
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 629000 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 630840 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 273 | 2215520 | Engine problem
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 54 | 36989 | Low demand
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 50 | 19633 | Low demand
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 51 | 21807 | Low demand
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 38 | 1323360 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3101 | 49373450
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 395820
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134000
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 45 | 586560 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1336100 | Unit-2,5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 201 | 4848898 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 542880 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 29 | 29216 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 51 | 380376
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1149240 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 0 | 71 | 911040 | On test
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 538224
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 512640
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 695040 | Engine problem
| Chattogram area Total |  |  |  | 1581 | 757 | 12060034
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2530816 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 2704860
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 182 | 4562000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 3473000 | Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7550000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 757440 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 205440 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 216000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 140 | 1656000 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 1181567
| Midland 150MW |  | IPP | 23*7.015 | 0 | 2 | 11710 | On test
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1177824
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 31 | 16800 | Low demand
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 1982600 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 0 | 205 | 3687000 | On Test
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 268920
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 130320
** | Tripura |  | Imported power | 0 | 160 | 122 | 2169600
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 432900
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 14 | 319886 | Engine problem
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 327420 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Low demand
| Cumilla Area Total |  |  |  | 2541 | 1628 | 35362103
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 108 | 2632840 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 343548
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 75 | 864000 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12950
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 190 | 1269600 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 393 | 5122938
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1267000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 78 | 1613720
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3449749
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 864600
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 48 | 951000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 8 | 216480 | Engine problem
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 67 | 1451000
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1344000
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 40 | 789480 | Engine problem
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 98 | 2270130 | Frequency control
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 138000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 835440
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 462216
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 3021136 | Under maint.
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 158220
| Sylhet Area Total |  |  |  | 1549 | 792 | 18832171
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 551 | 11813091
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 72 | 526080 | Engine problem
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 18 | 85440
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 50 | 356224
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 608250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1285000
| Khulna Area Total |  |  |  | 2209 | 836 | 14674085
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 642240
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 25 | 445200 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 185 | 4382000
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 1687323
| Barisal Area Total |  |  |  | 462 | 415 | 7156763
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 80 | 1329000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0 | Under maint.
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 53 | 69941
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 682270
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 159878
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 30 | 21130 | Engine problem
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 151 | 3060900 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 46 | 186467
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 418800
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 120420 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 187023
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 816480
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 268344
| Rajshahi Area Total |  |  |  | 1546 | 633 | 7320653
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3947500
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 19 | 39000
| Rangpur Area Total |  |  |  | 484 | 168 | 3986500
| Total |  |  |  | 16742 | 8723 | 153888697
| Eastern Grid Total |  |  |  | 12041 | 6671 | 120750696
| Western Grid Total |  |  |  | 4701 | 2052 | 33138001
| National Grid Total |  |  |  | 16742 | 8723 | 153888697
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-11-10 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5875 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2441 | MW
i) Dhaka area |  |  | 3188 | MW | i) Khulna area |  |  | 931 | MW
ii) Chittagong area |  |  | 1094 | MW | ii) Rajshahi area |  |  | 812 | MW
iii) Comilla area |  |  | 689 | MW | iii) Barisal area |  |  | 180 | MW
iv) Mymensingh area |  |  | 565 | MW | iv) Rangpur area |  |  | 518 | MW
v) Sylhet area |  |  | 339 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8316 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 1200 | Netrokona | 59 | 1830 | Goalpara | 20 | 1900
Munsiganj | 73 | 1930 | Jamalpur | 88 | 1830 | Central s/s | 66 | 1830
Sonargaon | 36 | 1830 | Sherpur | 58 | 1800 | Noapara | 66 | 1930
Shyampur | 154 | 2400 | Srimongal | 24 | 1800 | Jessore | 104 | 1800
Bhulta | 148 | 1830 | Shahjibazar | 85 | 1800 | Jhenida | 72 | 1800
Madanganj | 56 | 2100 | Fenchuganj | 30 | 1800 | Bottail | 80 | 1800
Shitalakhya | 94 | 1200 | Kulawara | 30 | 1830 | G.K Project | 42 | 1800
Rahim steel | 7 | 1100 | Sylhet | 99 | 1900 | Faridpur | 114 | 1830
Matuail | 84 | 1200 | Chatak | 19 | 1830 | Madaripur | 87 | 2000
Ghorasal | 57 | 1900 | Sunamganj | 23 | 1800 | Gopalganj | 58 | 1800
Narsingdi | 88 | 2000 | Biani Bazar | 29 | 1800 | Bagerhat | 62 | 1830
Haripur (SBU) | 95 | 1930 | Comilla (S) | 122 | 1800 | Mongla | 34 | 1200
Ullon | 51 | 1930 | Comilla(N) | 69 | 2000 | Satkhira | 68 | 1830
Hasnabad | 157 | 1800 | Chandpur | 79 | 2000 | Gallamari | 30 | 1900
Magbazar | 91 | 1800 | Feni | 86 | 2000 | Magura | 34 | 1800
Maniknagar | 82 | 1300 | Chowmuhani | 124 | 2000 | Chuadanga | 57 | 1800
Bangabhaban | 16 | 1200 | Ashuganj | 37 | 2000 | Barisal | 86 | 1800
Narinda | 66 | 1300 | Daudkandi | 84 | 2000 | Patuakhali | 64 | 2000
Dhanmondi | 101 | 1700 | B.Baria | 84 | 1900 | Bhandaria | 38 | 1930
Lalbag | 79 | 1800 | Ramganj | 24 | 2000 | Ishurdi | 38 | 1800
Madartek | 44 | 2100 | Madunaghat | 50 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 86 | 1800 | Hathazari | 72 | 2000 | Natore | 82 | 1800
Kalyanpur | 81 | 1800 | Khulshi | 175 | 1500 | Bogra | 171 | 1830
Gulshan | 72 | 1800 | Halishahar | 106 | 1930 | Noagaon | 78 | 1900
Uttara | 60 | 1800 | Baraulia | 141 | 1000 | Rajshahi | 101 | 1900
Uttara(New) | 6 | 1000 | Sikalbaha | 28 | 1900 | C.Nawabganj | 53 | 1800
Kamrangirchar | 65 | 1830 | Dohazari | 70 | 1800 | Amnura | 33 | 1930
Savar | 113 | 1830 | Cox'sbazar | 69 | 1800 | Pabna | 76 | 1800
Bhasantec | 126 | 1800 | Chandraghona | 19 | 1830 | Shahjadpur | 65 | 1800
Agargaon | 41 | 1800 | Kaptai | 4 | 1800 | Serajganj | 59 | 1930
Satmosjid | 74 | 1800 | A. Khaer Stl. | 15 | 1700 | Niyamatpur | 40 | 1830
Tongi | 102 | 1500 | Bakulia | 80 | 1800 | Joypurhat | 36 | 1800
Kabirpur | 147 | 1000 | Julda | 21 | 1000 | Rangpur | 94 | 1800
Basundhara | 100 | 1800 | TK chemical | 4 | 1000 | Lalmonirhat | 69 | 1830
Manikganj | 57 | 1900 | Modern Steel | 15 | 1200 | Saidpur | 99 | 1800
Joydevpur | 180 | 1900 | Shahmirpur | 22 | 1800 | Purbasadipur | 68 | 1900
New Tongi | 99 | 1600 | Khagrachhari | 15 | 1800 | Thakurgaon | 53 | 1900
Korda | 219 | 1800 | Matarbari | 20 | 1800 | Palashbari | 78 | 1800
Dhamrai | 40 | 1800 | Baroiar Hat | 18 | 1800 | Barapukuria | 35 | 1800
Tangail | 123 | 1930 | Rangamati | 8 | 1800 | Panchagar | 34 | 1830
Mymensing | 181 | 1900 | Abul Khair 230 | 115 | 1800
Kishorganj | 68 | 2100 | BSRM | 101 | 1100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-11-10
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 394 | 1:00 | 377 | 15:00 | Kaliakoir | 376 | 4:00 | 362 | 16:00
Bheramara | 410 | 3:00 | 400 | 18:30 | Bhulta | 394 | 6:00 | 380 | 16:00
Ashuganj(N) | 400 | 4:00 | 382 | 8:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 232 | 1:00 | 230 | 7:00 | Hathazari | 222 | 9:00 | 207 | 11:00
Ishurdi | 235 | 1:00 | 224 | 20:00 | Megnaghat | 232 | 22:00 | 220 | 15:00
Ashuganj | 238 | 6:00 | 232 | 11:00 | Fenchuganj | 240 | 6:00 | 232 | 15:00
Serajganj | 230 | 3:00 | 220 | 18:00 | Siddhirganj | 225 | 3:00 | 217 | 16:00
Baghabari | 229 | 6:00 | 222 | 19:00 | Maniknagar | 224 | 6:00 | 216 | 15:00
Barapukuria | 235 | 6:00 | 226 | 18:00 | Old Airport | 225 | 18:00 | 219 | 16:00
Bogra | 229 | 6:00 | 215 | 18:00 | Barisal | 230 | 9:00 | 224 | 7:00
Khulna South | 239 | 3:00 | 224 | 7:00 | AKSML | 224 | 21:00 | 205 | 11:00
Rampura | 223 | 3:00 | 218 | 11:00 | BSRM | 226 | 19:30 | 212 | 11:00
Haripur | 223 | 22:00 | 218 | 10:00 | Bibiyana | 236 | 6:00 | 225 | 15:00
Hasnabad | 226 | 18:00 | 220 | 11:00 | Bhulta | 226 | 4:00 | 219 | 15:00
Aminbazar | 227 | 22:00 | 221 | 10:00 | Ashuganj (S) | 237 | 4:00 | 231 | 11:00
Tongi | 224 | 21:00 | 217 | 16:00 | Kaliakoir | 230 | 22:00 | 222 | 16:00
Comilla (N) | 235 | 4:00 | 228 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 1800 | 131 | 1000 | Ramganj | 133 | 700 | 132 | 1100
Munsiganj | 139 | 1800 | 131 | 1600 | Madanhat | 134 | 1900 | 130 | 1100
Megnaghat | 138 | 1800 | 130 | 1000 | Hathazari | 133 | 900 | 126 | 1100
Shyampur | 135 | 1800 | 125 | 1600 | Khulshi | 131 | 1900 | 125 | 900
Bhulta | 133 | 100 | 129 | 1500 | Halishahar | 135 | 1900 | 125 | 1100
Madanganj | 138 | 1800 | 132 | 1500 | Baraulia | 132 | 1900 | 123 | 1100
Shitalakhya | 140 | 1800 | 131 | 1600 | Sikalbaha | 134 | 2100 | 125 | 1100
Rahim steal | 137 | 1800 | 131 | 1000 | Dohazari | 131 | 1300 | 1223 | 1100
Matuail | 136 | 1800 | 129 | 1600 | Cox'sbazar | 127 | 900 | 120 | 1100
Ghorasal | 138 | 100 | 135 | 1400 | Chandraghona | 133 | 1830 | 126 | 1100
Narsinghdi | 139 | 900 | 134 | 1900 | Kaptai | 134 | 1830 | 127 | 1100
Haripur (SBU) | 138 | 100 | 131 | 900 | A. Khaer Stl. | 131 | 2100 | 125 | 1000
Ullon | 136 | 600 | 131 | 1200 | Bakulia | 131 | 1830 | 124 | 1100
Hasnabad | 136 | 2100 | 129 | 1700 | Julda | 134 | 1900 | 123 | 1100
Magbazar | 137 | 600 | 131 | 1100 | TK Chemical | 137 | 2000 | 127 | 1000
Maniknagar | 134 | 600 | 125 | 1200 | Modern Steel | 133 | 200 | 125 | 1100
Bangabhaban | 136 | 600 | 129 | 1700 | Shahmirpur | 133 | 1900 | 124 | 1100
Narinda | 137 | 600 | 131 | 1600 | Khagrachhari | 133 | 2000 | 123 | 300
Dhanmondi | 134 | 600 | 125 | 1200 | Matarbari | 130 | 900 | 121 | 1100
Lalbag | 136 | 600 | 129 | 1700 | Baroiar Hat | 134 | 1800 | 127 | 1000
Madartek | 137 | 600 | 131 | 1600 | Rangamati | 132 | 1830 | 126 | 1000
Mirpur | 136 | 400 | 131 | 1200 | Goalpara | 137 | 2200 | 129 | 700
Kalyanpur | 137 | 300 | 134 | 1600 | Central s/s | 136 | 600 | 128 | 700
Gulshan | 136 | 500 | 131 | 1000 | Noapara | 137 | 900 | 126 | 1800
Uttara | 136 | 500 | 130 | 1100 | Jessore | 131 | 500 | 120 | 1830
Uttara(New) | 134 | 100 | 132 | 900 | Jhenida | 135 | 400 | 121 | 1830
Kamrangirchar | 134 | 400 | 130 | 1100 | Bottail | 139 | 400 | 129 | 1800
Savar | 134 | 100 | 132 | 1600 | G.K.Project | 143 | 500 | 133 | 2000
Bhasantec | 137 | 300 | 133 | 1600 | Faridpur | 134 | 400 | 126 | 1800
Agargaon | 138 | 400 | 131 | 1600 | Madaripur | 135 | 900 | 129 | 1800
Satmosjid | 138 | 400 | 133 | 1500 | Gopalganj | 130 | 700 | 137 | 2200
Tongi | 136 | 2300 | 132 | 1500 | Bagerhat | 138 | 900 | 128 | 1830
Kabirpur | 138 | 2200 | 133 | 1300 | Mongla | 135 | 2200 | 126 | 1800
Basundhara | 134 | 600 | 126 | 1300 | Satkhira | 136 | 400 | 128 | 1800
Manikganj | 140 | 600 | 114 | 1200 | Gallamari | 137 | 600 | 130 | 1800
Joydevpur | 143 | 1100 | 135 | 1500 | Magura | 136 | 600 | 121 | 1800
New Tongi | 137 | 2200 | 132 | 1500 | Chuadanga | 133 | 300 | 117 | 1830
Kodda | 143 | 1300 | 131 | 1500 | Barisal | 139 | 2200 | 134 | 1800
Dhamrai | 138 | 2200 | 133 | 1500 | Patuakhali | 137 | 800 | 130 | 1800
Tangail | 140 | 2200 | 134 | 1500 | Bhandaria | 137 | 800 | 130 | 600
Mymensing | 138 | 2200 | 133 | 100 | Ishurdi | 141 | 300 | 133 | 1830
Kishorganj | 138 | 900 | 135 | 100 | Ruppur Paromanobik | 142 | 100 | 133 | 1800
Netrokona | 137 | 2200 | 130 | 1000 | Natore | 138 | 900 | 130 | 700
Jamalpur | 140 | 2200 | 131 | 100 | Bogra | 136 | 600 | 128 | 1830
Sherpur | 138 | 1600 | 129 | 100 | Noagaon | 133 | 600 | 125 | 1800
Srimongal | 141 | 700 | 140 | 100 | Rajshahi | 134 | 1700 | 126 | 700
Shahjibazar | 140 | 900 | 134 | 1830 | C.Nawabganj | 132 | 1800 | 124 | 800
Fenchuganj | 138 | 400 | 135 | 1500 | Amnura | 135 | 1800 | 125 | 1100
Khulawara | 138 | 500 | 135 | 1600 | Pabna | 137 | 500 | 130 | 700
Sylhet | 137 | 100 | 135 | 1400 | Shahjadpur | 143 | 400 | 137 | 1830
Chatak | 137 | 100 | 135 | 1400 | Serajganj | 136 | 100 | 130 | 1830
Sunamganj | 137 | 100 | 134 | 2100 | Niyamatpur | 133 | 600 | 123 | 1800
Biani Bazar | 137 | 700 | 135 | 1300 | Joypurhat | 135 | 100 | 125 | 1800
Cumilla(s) | 131 | 800 | 126 | 1200 | Rangpur | 131 | 600 | 117 | 1800
Cumilla(n) | 140 | 700 | 138 | 1100 | Lalmonirhat | 128 | 600 | 110 | 1830
Chandpur | 145 | 2100 | 140 | 1600 | Saidpur | 132 | 600 | 116 | 1800
Feni | 135 | 2100 | 130 | 1100 | Purbasadipur | 132 | 100 | 125 | 1800
Chowmuhani | 134 | 1000 | 130 | 2100 | Thakurgaon | 130 | 600 | 114 | 1800
Ashuganj | 140 | 2100 | 139 | 1500 | Palashbari | 130 | 400 | 118 | 1800
Daudkandi | 135 | 1930 | 131 | 1100 | Barapukuria | 135 | 600 | 126 | 1800
B.Baria | 141 | 1300 | 137 | 1900 | Panchagar | 128 | 300 | 111 | 1800

## L-Curve
Date | 2018-11-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 360 | 5013 | 1460 | 6473 |  |  |  | QF-LDC-12
0:30 | 296 | 4633 | 1449 | 6082 | Date: | 2018-11-10
1:00 | 232 | 4253 | 1438 | 5691
1:30 | 281 | 4218.5 | 1318 | 5536.5
2:00 | 330 | 4184 | 1198 | 5382
2:30 | 315 | 4075 | 1199.5 | 5274.5 |  |  |  |  | Gen. at Eve. Peak | 8723 | 8723 MW (18:00 )
3:00 | 300 | 3966 | 1201 | 5167 | [5 empty] | 18:00
3:30 | 295 | 3913.5 | 1200 | 5113.5 |  |  |  |  | Gen. at Day Peak | 6680 | 6680 MW (12:00 )
4:00 | 290 | 3861 | 1199 | 5060 | [5 empty] | 12:00
4:30 | 280 | 3855 | 1181 | 5036 |  |  |  |  | Highest Generation | 8723
5:00 | 270 | 3849 | 1163 | 5012 | [5 empty] | 18:00
5:30 | 320 | 3952.05 | 1176 | 5128.05
6:00 | 370 | 4055.1 | 1189 | 5244.1
6:30 | 495 | 4304.3285 | 1070 | 5374.3285
7:00 | 620 | 4553.557 | 951 | 5504.557
7:30 | 585 | 4512.4285 | 1073 | 5585.4285
8:00 | 550 | 4471.3 | 1195 | 5666.3
8:30 | 400 | 4521.35 | 1357.5 | 5878.85
9:00 | 250 | 4571.4 | 1520 | 6091.4
9:30 | 215 | 4648.3 | 1470 | 6118.3
10:00 | 180 | 4725.2 | 1420 | 6145.2
10:30 | 170 | 4742 | 1478 | 6220
11:00 | 160 | 4758.8 | 1536 | 6294.8
11:30 | 230 | 4961.9 | 1525.5 | 6487.4
12:00 | 300 | 5165 | 1515 | 6680
12:30 | 298 | 5156.05 | 1552.5 | 6708.55
13:00 | 296 | 5147.1 | 1590 | 6737.1
13:30 | 273 | 4969.4 | 1589 | 6558.4
14:00 | 250 | 4791.7 | 1588 | 6379.7
14:30 | 195 | 4912.7 | 1564.5 | 6477.2
15:00 | 140 | 5033.7 | 1541 | 6574.7
15:30 | 190 | 5065.05 | 1466.5 | 6531.55
16:00 | 240 | 5096.4 | 1392 | 6488.4
16:30 | 255 | 5201.8 | 1428.5 | 6630.3
17:00 | 270 | 5307.2 | 1465 | 6772.2
17:30 | 425 | 5989.1 | 1758.5 | 7747.6
18:00 | 580 | 6671 | 2052 | 8723
18:30 | 655 | 6606.5 | 2031 | 8637.5
19:00 | 730 | 6542 | 2010 | 8552
19:30 | 740 | 6591 | 1971 | 8562
20:00 | 760 | 6485 | 1894 | 8379
20:30 | 720 | 6332 | 1871.5 | 8203.5
21:00 | 680 | 6179 | 1849 | 8028
21:30 | 625 | 6017 | 1776 | 7793
22:00 | 570 | 5855 | 1703 | 7558
22:30 | 475 | 5577 | 1662.5 | 7239.5
23:00 | 380 | 5299 | 1622 | 6921
23:30 | 370 | 5156 | 1541 | 6697
24:00 | 360 | 5013 | 1460 | 6473
8723 MW (18:00 )
6680 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-11-10 |  | Energy | 154859133
[10 empty] | 2018-11-10 |  |  |  |  | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2828 | 553 | 1455 | 1106 | 150 | 70 | 221 | 0 | 90
0:30 | 2917 | 533 | 1433.5 | 595 | 150 | 70 | 300.5 | 0 | 83 | Date: | 2018-11-10
1:00 | 3006 | 513 | 1412 | 84 | 150 | 70 | 380 | 0 | 76
1:30 | 3027.5 | 439.5 | 1338 | 79.5 | 150 | 70 | 357 | 0 | 75 | [6 empty] | Total Energy | 154.8591 | Total Energy Gen 154.859 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 154.859 MKWHr
2:00 | 3049 | 366 | 1264 | 75 | 150 | 70 | 334 | 0 | 74 | [6 empty] | Energy not Served | 0
2:30 | 3007 | 366.5 | 1200.5 | 72 | 150 | 70 | 334.5 | 0 | 74 | [6 empty] | Energy Requirement | 154.8591
3:00 | 2965 | 367 | 1137 | 69 | 150 | 70 | 335 | 0 | 74
3:30 | 2918 | 366.5 | 1132.5 | 69 | 149.5 | 70 | 335 | 0 | 73 | [5 empty] | Shortage
4:00 | 2871 | 366 | 1128 | 69 | 149 | 70 | 335 | 0 | 72
4:30 | 2832 | 366 | 1134 | 69.5 | 149 | 70 | 343.5 | 0 | 72
5:00 | 2793 | 366 | 1140 | 70 | 149 | 70 | 352 | 0 | 72
5:30 | 2849 | 366 | 1200.5 | 69.5 | 149.5 | 70 | 352.5 | 0 | 71
6:00 | 2905 | 366 | 1261 | 69 | 150 | 70 | 353 | 0 | 70
6:30 | 2796.5 | 366 | 1406 | 170.5 | 149.5 | 70 | 344 | 0 | 70 |  |  |  |  | Coal
7:00 | 2688 | 366 | 1551 | 272 | 149 | 70 | 335 | 0 | 70
7:30 | 2721 | 366 | 1563.5 | 363.5 | 149 | 70 | 274 | 0 | 71.5 |  |  |  | Oil |  |  | ,
8:00 | 2754 | 366 | 1576 | 455 | 149 | 70 | 213 | 0 | 73
8:30 | 2614.5 | 463 | 1609.5 | 692 | 149.5 | 55 | 207 | 0 | 75.5
9:00 | 2475 | 560 | 1643 | 929 | 150 | 40 | 201 | 0 | 78
9:30 | 2528.5 | 560 | 1578 | 946 | 150 | 40 | 217 | 0 | 81
10:00 | 2582 | 560 | 1513 | 963 | 150 | 40 | 233 | 0 | 84
10:30 | 2574.5 | 560 | 1509 | 1028 | 175 | 40 | 226.5 | 0 | 86
11:00 | 2567 | 560 | 1505 | 1093 | 200 | 40 | 220 | 0 | 88
11:30 | 2532.5 | 560 | 1583.5 | 1233 | 207.5 | 38 | 220 | 0 | 91
12:00 | 2498 | 560 | 1662 | 1373 | 215 | 36 | 220 | 0 | 94
12:30 | 2419 | 560 | 1661.5 | 1473 | 214.5 | 38 | 228.5 | 0 | 93
13:00 | 2340 | 560 | 1661 | 1573 | 214 | 40 | 237 | 0 | 92
13:30 | 2340 | 560 | 1661 | 1573 | 214 | 40 | 237 | 0 | 92
14:00 | 2340 | 560 | 1661 | 1573 | 214 | 40 | 237 | 0 | 92
14:30 | 2439.5 | 555.5 | 1615.5 | 1458 | 197 | 40 | 239.5 | 0 | 95
15:00 | 2539 | 551 | 1570 | 1343 | 180 | 40 | 242 | 0 | 98
15:30 | 2607.5 | 551 | 1616 | 1203.5 | 165 | 40 | 245.5 | 0 | 95
16:00 | 2676 | 551 | 1662 | 1064 | 150 | 40 | 249 | 0 | 92
16:30 | 2752 | 551.5 | 1649.5 | 1104.5 | 149.5 | 55 | 270 | 0 | 96
17:00 | 2828 | 552 | 1637 | 1145 | 149 | 70 | 291 | 0 | 100
17:30 | 2862.5 | 551.5 | 1669.5 | 1822 | 149 | 70 | 512 | 0 | 111
18:00 | 2897 | 551 | 1702 | 2499 | 149 | 70 | 733 | 0 | 122
18:30 | 2933 | 551 | 1642 | 2526.5 | 149 | 70 | 646 | 0 | 120
19:00 | 2969 | 551 | 1582 | 2554 | 149 | 70 | 559 | 0 | 118
19:30 | 3034 | 551 | 1595 | 2477 | 149 | 70 | 568 | 0 | 118
20:00 | 3115 | 551 | 1526 | 2391 | 149 | 70 | 459 | 0 | 118
20:30 | 3147.5 | 551 | 1514.5 | 2237.5 | 149 | 70 | 419 | 0 | 115
21:00 | 3180 | 551 | 1503 | 2084 | 149 | 70 | 379 | 0 | 112
21:30 | 3082 | 551 | 1464 | 2022.5 | 149 | 70 | 345.5 | 0 | 109
22:00 | 2984 | 551 | 1425 | 1961 | 149 | 70 | 312 | 0 | 106
22:30 | 2915 | 551 | 1425 | 1736.5 | 149.5 | 70 | 290.5 | 0 | 102
23:00 | 2846 | 551 | 1425 | 1512 | 150 | 70 | 269 | 0 | 98
23:30 | 2837 | 552 | 1440 | 1309 | 150 | 70 | 245 | 0 | 94 | Max Temp. in Dhaka |  | 29.4° C
24:00 | 2828 | 553 | 1455 | 1106 | 150 | 70 | 221 | 0 | 90
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 154.859 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 154.859 MKWHr
Note on W13: Author:

## Generation
2018-11-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 36 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 860000
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | [5 empty] | 0 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 476100
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [7 empty] | 0 | 25 | 25 | 26 | 25 | 26 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 395820
| Teknaf Solartech 20MW | [5 empty] | 0.1 | 3.357 | 9.6 | 14 | 18.4 | 19.8 | 19.9 | 18.3 | 15.1 | 10.7 | 3.9 | 0.2 | 0 | [8 empty] | 134000
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 200 | 202 | 200 | 200 | 214 | 201 | 201 | 213 | 201 | 233 | 201 | 200 | 200 | 214 | 202 | 202 | 201 | 201 |  | 194 | 200 | 201 | 200 | 201 | 205 | 200 | 4848898
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 34 | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 51 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 380376
12 | Hathazari peaking | [16 empty] | 0 | 29 | [8 empty] | 29216
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 31 |  | 0 | [6 empty] | 16800
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 97 | 97 | 97 | 60 | 60 | 100 | 95 | 100 | 103 | 102 | 102 | 87 | 0 | 38 | 93 | 95 | 150 | 180 |  | 188 | 205 | 207 | 205 | 183 | 163 | 180 | 2852000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [8 empty] | 22 | 56 | 68 | 107 | 105 | 140 | 114 | 42 | 42 | 273 |  | 252 | 275 | 272 | 272 | 275 | 130 | 107 | 2215520
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 102 | 102 | 110 | 102 | 102 | 73 | 92 | 130 | 130 | 140 |  | 157 | 157 | 78 | 36 | 36 | 36 | 36 | 1656000
20 | Ghorasal ST: Unit-1,2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1462000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 254 | 255 | 255 | 255 | 256 | 262 | 262 | 259 | 100 | 115 | 100 | 252 | 243 | 248 | 249 | 250 | 251 | 252 |  | 252 | 252 | 253 | 255 | 253 | 250 | 254 | 5698000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 380 | 380 | 340 | 300 | 200 | 358 | 380 | 380 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8048118
26
28 | Ashuganj ST: Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 105 | 100 | 80 | 80 | 80 | 2530816
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 120 | 80 | 80 | 80 | 110 | 2704860
32 | Ashuganj Engines TSK | 38 | 38 | 20 | 10 | 10 | 10 | 37 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 10 | 10 | 30 | 38 | 757440
33 | Ashuganj CCPP 225 MW | 182 | 195 | 190 | 180 | 150 | 183 | 183 | 210 | 183 | 198 | 195 | 185 | 185 | 190 | 183 | 184 | 184 | 182 |  | 182 | 181 | 169 | 178 | 182 | 196 | 182 | 4562000
34 | Ashuganj CCPP(South) | 305 | 327 | 316 | 305 | 309 | 272 | 272 | 360 | 305 | 323 | 323 | 305 | 305 | 253 | 305 | 305 | 305 | 305 |  | 305 | 305 | 338 | 356 | 305 | 323 | 305 | 7550000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | [12 empty] | 55 | 100 | 160 | 230 | 210 | 21 | 10 | 3473000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 205440
36 | Chandpur CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 100 |  | 96 | 100 | 100 | 101 | 100 | 100 | 100 | 1982600
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP
40 | Meghnaghat CCPP 450MW | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 255 | 270 | 290 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8397775
41 | Haripur Power CCPP 360MW | 364 | 363 | 363 | 364 | 366 | 366 | 366 | 362 | 306 | 359 | 359 | 321 | 355 | 281 | 357 | 359 | 358 | 361 |  | 322 | 322 | 330 | 350 | 298 | 303 | 335 | 8214000
42 | Mymensingh RPCL 210MW | 104 | 105 | 106 | 106 | 89 | 104 | 104 | 105 | 114 | 152 | 137 | 122 | 103 | 107 | 105 | 109 | 108 | 108 |  | 114 | 114 | 109 | 104 | 104 | 107 | 107 | 2632840
43 | Haripur NEPC 110MW | [15 empty] | 0 | 40 | 110 |  | 55 | 13 | 0 | 0 |  |  |  | 179400
44 | Fenchugonj CCPP-1 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 1267000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 52 | 52 | 52 | 56 | 76 | 76 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1613720
46 | Shajibazar 330 MW | [7 empty] | 0
47 | Shahjibazar GT: Unit- 8, 9 | 65 | 64 | 65 | 63 | 66 | 60 | 68 | 64 | 50 | 64 | 63 | 54 | 51 | 64 | 63 | 51 | 64 | 67 |  | 67 | 66 | 66 | 65 | 53 | 63 | 57 | 1451000
48 | Shahjibazar 86MW | 10 | 10 | 10 | 10 | 10 | 10 | 89 | 89 | 86 | 50 | 50 | 84 | 84 | 40 | 40 | 86 | 86 | 86 |  | 86 | 86 | 86 | 40 | 40 | 40 | 40 | 1344000
49 | Shahjibazar (EPL) 50MW | 40 | 40 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 789480
50 | Sylhet GT 150 MW | 78 | 77 | 78 | 77 | 78 | 129 | 127 | 127 | 78 | 78 | 100 | 78 | 78 | 80 | 78 | 98 | 128 | 98 |  | 77 | 78 | 98 | 128 | 98 | 98 | 98 | 2270130
51 | Sylhet GT 20 MW | [15 empty] | 0 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 138000
52 | Sylhet (EPL) 50MW | 47 | 48 | 7 | 7 | 7 | 46 | 47 | 47 | 47 | 46 | 44 | 45 | 47 | 45 | 44 | 44 | 44 | 47 |  | 48 | 48 | 47 | 10 | 12 | 12 | 16 | 835440
53 | Sylhet (Desh) 10MW | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 158220
54 | Hobiganj 11MW | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 216480
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 47 | 47 | 44 | 47 | 50 | 47 | 50 | 11 | 38 | 44 | 47 | 50 |  | 50 | 53 | 53 | 53 | 53 | 53 | 50 | 864600
56 | Shahjahanulla 25 MW | 24 | 24 | 25 | 25 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 8 | 8 | 13 | 24 |  | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 462216
57 | Summit Bibiana- 2 | 270 | 270 | 280 | 270 | 280 | 285 | 280 | 275 | 270 | 150 | 140 | 125 | 0 | 0 | [12 empty] | 3021136
58 | Southern 55MW | [10 empty] | 17 | 17 | 36 | 55 | 55 | 17 | 40 | 55 |  | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 516096
59 | Sikalbaha (Energis) | [8 empty] | 4 | 16 | 16 | 29 | 32 | 32 | 36 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 542880
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 538224
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 409464
62 | Tangail (Doreen) 22MW | 20 | 20 | 0 | [5 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 343548
63 | Tripura | 76 | 74 | 74 | 72 | 72 | 70 | 70 | 73 | 78 | 84 | 88 | 94 | 92 | 96 | 98 | 92 | 100 | 122 |  | 118 | 118 | 118 | 112 | 106 | 98 | 90 | 2169600
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 11 | 11 | 11 | 20 | 20 | 20 | 10 | 10 | 3 | 2 | 9 | 7 | 2 | 2 | 8 | 14 |  | 25 | 31 | 33 | 39 | 41 | 42 | 42 | 512640
65 | Feni (Doreen) 22MW | 22 | 22 | 0 | [5 empty] | 16 | 22 | 0 |  |  |  | 0 | 15 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 268920
66 | Feni, Mohipal (Doreen) | 11 | 11 | 0 | [6 empty] | 11 | 0 |  |  |  | 0 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 130320
67 | Jangalia (Summit) 33MW | 8 | 8 | 8 | 8 | 8 | 8 | 20 | 33 | 33 | 8 | 0 |  |  |  | 0 | 30 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 432900
68 | Summit Cumilla 25MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 |  | 20 | 20 | 20 | 20 | 10 | 15 | 12 | 327420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 560520
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 827000
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 629000
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [13 empty] | 7 | 4 | 7 | 7 | 30 |  | 60 | 40 | 7 | 0 | 0 |  |  | 206150
78 | Gazipur (RPCL) | [7 empty] | 6 | 29 | 26 | 40 | 43 | 43 | 43 | 0 | 23 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 630840
79 | Kodda 149MW | 16 | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 115 |  | 100 | 100 | 50 |  |  |  |  | 367200
80 | Jamalpur 95MW | [7 empty] | 7 | 48 | 24 | 24 | 24 | 24 | 28 | 28 | 50 | 57 | 75 |  | 78 | 79 | 78 | 78 | 78 | 78 | 57 | 864000
81 | Lakdhanvi 52 MW | [16 empty] | 0 | 14 |  | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 319886
82 | Madanganj 102MW | [7 empty] | 0 | 14 | 40 | 60 | 98 | 98 | 97 | 70 | 15 | 15 | 20 |  | 84 | 100 | 100 | 100 | 100 | 100 | 74 | 1177824
83 | Pagla (DPA ) | 25 | 16 | 10 | 10 | 11 | 10 | 10 | 10 | 21 | 21 | 21 | 21 | 21 | 11 | 10 | 21 | 0 | 46 |  | 25 | 25 | 10 | 10 | 11 | 10 | 10 | 388830
84 | B.Baria (Aggreko) 85MW | 10 | 10 | 10 | 10 | 10 | 10 | 80 | 85 | 85 | 85 | 85 | 85 | 85 | 40 | 85 | 85 | 85 | 85 |  | 41 | 40 | 40 | 85 | 85 | 85 | 85 | 1177824
85 | Keraniganj (Powerpac) 100MW | [16 empty] | 0 | 80 |  | 50 | 10 | 0 | 0 | 0 |  |  | 182747
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [10 empty] | 2 | 7 | 7 | 35 | 21 | 7 | 7 | 10 |  | 57 | 57 | 47 | 0 | 0 |  |  | 216960
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 216000
91 | Juldah (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 24 | 30 | 30 | 68 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 30 | 30 | 20 | 20 | 1149240
92 | Fenchuganj (EPL) 44MW | 50 | 5 | 5 | 5 | 5 | 9 | 47 | 47 | 47 | 50 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 |  | 48 | 50 | 50 | 50 | 51 | 51 | 51 | 951000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 45 | 51 | 45 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1181567
94 | Gagnagar (Orion) | [7 empty] | 7 | 24 | 42 | 74 | 82 | 102 | 102 | 50 | 16 | 24 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 24 | 1190304
95 | Patenga 50MW | [8 empty] | 2 | 6 | 6 | 13 | 36 | 38 | 39 | 45 | 48 | 45 |  | 50 | 50 | 50 | 50 | 50 | 50 | 18 | 586560
96 | Chattogram ECPV 108 MW | [8 empty] | 16 | 13 | 12 | 16 | 52 | 52 | 43 | 18 | 40 | 99 |  | 99 | 99 | 99 | 45 | 12 | 13 | 13 | 695040
97 | Katpotti 51 MW | [11 empty] | 4 | 6 | 6 | 6 | 6 | 6 | 6 |  | 29 | 40 | 39 | 40 | 39 | 39 | 39 | 269808
98 | Bosila 108MW | [7 empty] | 36 | 47 | 47 | 47 | 46 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 744960
99 | Madanganj-55 MW | [8 empty] | 5 | 33 | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 48 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 745539
100 | Northern 55 MW | [15 empty] | 0 | 18 | 54 |  | 54 | 55 | 55 | 55 | 55 | 56 | 56 | 364646
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 100 | 100 | 100 | 163 | 163 | 130 | 100 | 100 | 130 | 130 | 163 | 100 | 163 | 163 | 130 | 163 |  | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 3449749
102 | Sarishabari (Solar) | [6 empty] | 0.2 | 0.7 | 1.4 | 1.8 | 2 | 2.1 | 1.8 | 1.6 | 1 | 0.5 | 0 | [9 empty] | 12950
103 | Banco Energy 54MW | [7 empty] | 18 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 876960
104 | APR Energy , Keranigonj | [16 empty] | 0 | 54 | [8 empty] | 36989
105 | Bramhangoan 100 MW (Aggreko) | [16 empty] | 0 | 50 | [8 empty] | 19633
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 60 | 17 | 17 | 17 | 17 | 17 | 17 | 110 | 110 | 190 |  | 180 | 180 | 200 | 100 | 100 | 15 | 15 | 1269600
112 | Aggreko Aurahati 100MW | [16 empty] | 0 | 51 | [8 empty] | 21807
114 | Summit Gazipur-1 150MW | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 40 | 70 | 108 | 131 | 129 | 74 | 15 | 15 | 38 |  | 118 | 118 | 126 | 131 | 126 | 41 | 15 | 1323360
115 | Juldah 100 MW Unit-3 | [7 empty] | 15 | 52 | 52 | 0 | 52 | 52 | 0 | 0 | 10 | 27 | 71 |  | 100 | 100 | 100 | 100 | 100 | 100 | 91 | 911040
116 | Chandpur Desh 200MW | 18 | 18 | 18 | 18 | 18 | 18 | 221 | 221 | 221 | 202 | 219 | 218 | 219 | 218 | 218 | 218 | 150 | 205 |  | 205 | 220 | 220 | 221 | 221 | 128 | 128 | 3687000
117 | Midland 150MW | [16 empty] | 0 | 2 |  | 5 | 5 | 7 | 6 | 0 | 0 | 0 | 11710
118
120 | Eastern Zone Total | 4253 | 4184 | 3966 | 3861 | 3849 | 4055.1 | 4553.557 | 4471.3 | 4571.4 | 4725.2 | 4758.8 | 5165 | 5147.1 | 4791.7 | 5033.7 | 5096.4 | 5307.2 | 6671 | 0 | 6542 | 6591 | 6485 | 6179 | 5855 | 5299 | 5013 | 120750696
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [7 empty] | 0 | 16 | 16 | 32 | 49 | 49 | 16 | 16 | 16 | 30 | 72 |  | 115 | 81 | 51 | 16 | 16 | 0 |  | 526080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 7 | 18 |  | 18 | 18 | 18 | 18 | 18 | 0 |  | 85440
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [7 empty] | 17 | 105 | 53 | 53 | 70 | 105 | 105 | 105 | 17 | 35 | 105 |  | 105 | 105 | 105 | 105 | 107 | 107 | 35 | 1285000
130
131
132
133
| Summit Barisal 110 MW | [12 empty] | 16 | 16 | 16 | 16 | 20 | 110 |  | 110 | 110 | 110 | 110 | 64 | 48 | 16 | 642240
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 97 | 11 | 11 | 11 | 11 | 11 | 42 | 95 | 96 | 51 | 51 | 70 | 95 | 96 | 96 | 96 | 96 | 95 |  | 95 | 95 | 95 | 96 | 95 | 95 | 95 | 1687323
| Bhola CCPP 194MW | 178 | 186 | 185 | 185 | 186 | 186 | 187 | 186 | 185 | 183 | 184 | 161 | 150 | 183 | 163 | 154 | 165 | 185 |  | 185 | 184 | 185 | 184 | 168 | 186 | 179 | 4382000
140 | Bhola (Venture) 33MW | 19 | 18 | 18 | 18 | 18 | 19 | 18 | 11 | 10 | 16 | 16 | 18 | 17 | 17 | 17 | 17 | 17 | 25 |  | 22 | 25 | 26 | 26 | 26 | 22 | 21 | 445200
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [7 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 608250
143 | Gopalganj Peaking | [10 empty] | 3 | 4 | 4 | 0 | 7 | 14 | 40 | 50 |  | 55 | 58 | 60 | 58 | 59 | 30 | 4 | 356224
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 513 | 366 | 367 | 366 | 366 | 366 | 366 | 366 | 560 | 560 | 560 | 560 | 560 | 551 | 551 | 551 | 552 | 551 | 560 | 551 | 551 | 551 | 551 | 551 | 551 | 553 | 11813091
147 | Bheramara 360 MW | 280 | 280 | 280 | 280 | 250 | 250 | 0
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 150 | 150 | 149 | 149 | 150 | 149 | 149 | 150 | 150 | 200 | 215 | 214 | 214 | 180 | 150 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 3947500
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW | 40 | 40 | 40 | 40 | 30 | 40 | 40 | 40 | 50 | 60 | 60 | 0 |  | 0 | 70 | 70 | 80 | 80 |  | 80 | 80 | 85 | 100 | 90 | 80 | 80 | 1329000
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | [7 empty] | 220 | 188 | 147 | 192 | 183 | 195 | 170 | 135 | 132 | 132 | 151 |  | 179 | 177 | 183 | 187 | 180 | 178 | 182 | 3060900
| Sirajgonj Unit-2 225MW (Oil) | 130 | 132 | 135 | 135 | 138 | 152 | 134 | 0 | [18 empty] | 970436
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [15 empty] | 0 | 10 | 53 |  | 0 | [6 empty] | 69941
162 | Bogra (GBB) | 21 | 5 | 5 | 5 | 5 | 5 | 5 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 418800
163 | Bogra (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120420
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 187023
165 | Amnura 50MW | [8 empty] | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 24 | 12 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 682270
166 | Katakhali (Northern) | [9 empty] | 8 | 8 | 8 | 8 | 43 | 8 | 8 | 8 | 43 |  | 8 | 0 | 0 |  |  |  |  | 159878
167 | Katakhali Peaking | [16 empty] | 0 | 30 | [8 empty] | 21130
168 | Santahar Peaking | [16 empty] | 0 | 46 |  | 46 | 46 | 46 | 45 | 0 |  |  | 186467
169 | Rajlanka 52 MW | [7 empty] | 37 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 40 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 816480
170 | Chapainawabganj-100 MW | [16 empty] | 0 | 90 |  | 93 | 93 | 50 | 24 | 0 |  |  | 268344
171
172
173 | Rangpur GT
175 | Saidpur GT | [16 empty] | 0 | 19 |  | 19 | 19 | 0 |  |  |  |  | 39000
176
177
178
178 | Western Zone Total | 1438 | 1198 | 1201 | 1199 | 1163 | 1189 | 951 | 1195 | 1520 | 1420 | 1536 | 1515 | 1590 | 1588 | 1541 | 1392 | 1465 | 2052 |  | 2010 | 1971 | 1894 | 1849 | 1703 | 1622 | 1460 | 34108437