## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-10-17 | Wednesday
|  | Date (day): | 2018-10-17 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11419 | MW |  |  | (b) At Evening Peak Hour : |  | 12908 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-10-16 | 2018-10-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 68 | 68 | 68 | 68 | 17 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 255 | 201 | 262 | 262 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint. |  | 20/10/2018
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 380 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 80 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 94 | 94 | 94 |  | 14 | Engine problem
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 349 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 352 | 322 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 27 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 15 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 92 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 30 | 90 | 90 |  | 10 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint. |  | 21/10/18
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 11 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 32 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 39 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 50 | 50 | 50 |  | 58 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 26 | 26 | 26 |  | 8 | Engine problem
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 40 | 43 | 43 |  | 9 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 32 | 170 | 270 | 270 |  | 30 | Engine problem
35 | APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 0 | 100 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 98 | 113 | 110 | 115 |  | 34 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 2295 | 2993 | 3995 | 4400 | 352 | 889
39 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 150 | 150 | 150 | 30 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 18 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 136 | 132 | 135 | 135 |  | 95 | #2,3,5 Under maint.
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 202 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 |  | Gas shortage
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 32 | 40 | 40 |  | 11 | Engine problem
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 0 | 80
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 46
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 7 | 10 | 15
51 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 13 | 93 | 100 | 100
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 855 | 1052 | 1027 | 1138 | 210 | 146
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint. |  | 18/10/2018
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 223 | 228 | 225 | 225
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 305 | 360 | 360 |  |  | FGMO
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 41 | 41 | 41
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint. |  | 17/10/2018
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage.
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 78 | 90 | 195
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Devolopment work.
61 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 10 | 85 | 85 | 85
62 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
63 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST Under maint.
64 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
65 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 104 | 144 | 115 | 148
66 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
67 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
68 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20 |  | 5 | Engine problem
69 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1445 | 1606 | 1716 | 2094 | 112 | 308
70 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 78 | 69 | 150 | 150 | 52 |  | Gas shortage
71 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
72 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 73 | 72 | 72 |  | 23 | Engine problem.
73 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
74 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 17 | 168 | 150 | 160 |  | 40 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 117.1 | 332 | 396 | 404 | 52 | 23
75 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 55 | 60 | 60
76 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
77 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
78 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 309 | 306 | 330 | 330
79 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 44 | 50 | 50
80 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 46 | 44 | 44
81 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
82 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 62 | 66 | 66
83 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 89 | 86 | 86
84 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 5 | 46 | 46 | 46
85 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 98 | 130 | 130
86 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
87 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 43 | 46 | 46
88 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 25 | 25 | 25 | 25
89 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 0 | 341 | 341 |  |  | FGMO
90 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1035 | 1011 | 1488 | 1488 | 0 | 0
91 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 762 | 762 | 770 | 770
92 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 49 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 42
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 75 | 0 | 80
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 426 | 410 | 410
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| Labon Chora 105 MW |  | HFO | IPP | 105 | 0 | 0 | 0 | 54 | 50 | 105
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 1228 | 1563 | 1610 | 1917 | 0 | 0
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 80 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 27 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 168 | 147 | 188 | 188
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 82 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 283 | 381 | 396 | 456 | 0 | 0
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 48 | 0 | 54
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 40
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 183 | 219 | 210 | 210
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint.
113 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 101 | 150 | 141 | 141
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
114 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 42
115 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
116 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 4 | 4 | 5 | 5 |  | 5 | Engine problem
117 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
118 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 35 | 52 | 52
119 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 338 | 799 | 641 | 827 | 71 | 325
120 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
121 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal shortage
122 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
123 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 149 | 150 | 184 | 209 | 85
| Total |  |  |  |  | 17043 | 16445 | 7746.1 | 9886 | 11419 | 12908 | 1006 | 1776
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7253.2518 | 9257 | 10692.4624 | 12086.7243
A. |  | 2018-10-16 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9886 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6311 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9886 | MW
3 | Day peak Generation : |  |  | 7746.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9257 | MW
4 | Evening peak Generation : |  |  | 9886 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 187.1031 | MKWHr | By Solar | 0.1482 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 138.3773 | MKWHr |  | By Oil: | 21.243 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6532 | MKWHr |  | By Hydro: | 3.1076 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1006 | MW | Dhaka | 3604 | 3604 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1776 | MW | Chittagong | 1025 | 1025 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2782 | MW | Khulna | 1121 | 1121 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1157.94 |  | MMCFD |  |  | Rajshahi | 910 | 910 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 99194092.874 | ii) Oil : | Taka | 171438724.86 | Comilla | 878 | 878 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14101352 | Total | Taka | 284734169.734 | Mymensingh | 616 | 616 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 0.9815 | MKWHr. | Sylhet | 344 | 344 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -220 | MW at | 19:00 | hrs | Barisal | 218 | 218 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -290 | MW at | 20:00 | hrs | Rangpur | 541 | 541 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 9257 | 9257 |  | 0
B. |  | 2018-10-17 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12908 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 2308 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 200.6163 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6163.8 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.8407 | MKWHr. | ii) HVDC Flow at Peak Time |  | 762 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7331 | MKWHr. | iii) Maximum HVDC Flow : |  | 762 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.56 |  | (b) Today: | 102.56 |  | (c) Rule Curve: |  | 0
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-10-16
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 68 | 0 | 258 | 0 | 320 | 12 | 35 | 345 | 303 | 0 | 20 | 360 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 55 | 22 | 25 | 32 | 25 | 33 | 25 | 0 | 82 | 50 | 150 | 140 | 8 | 228 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 50 | 12 | 26 | 22 | 40 | 100 | 100 | 0 | 360 | 301 | 51 | 68 | 100 | 34 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 8 | 21 | 112 | 117 | 7 | 0 | 0 | 56 | 60 | 11 | 10 | 100 | 310 | 48 | 50 | 47 | 78 | 0 | 45 | 9 | 260 | 24 | 11 | 0 | 17 | 0 | 0 | 36 | 0 | 15 | 0 |  | 762 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 153 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 175 | 0 | 0 | 0 | 82 | 0 | 137 | 0 | 0 | 0 |  | 5500 | 2009 | 7509 | 4327 | 762 | 1572 | 334 | 150 | 132 | 120 | 112 | 0 | 0 | 102.61
2:00 | 68 | 0 | 258 | 0 | 270 | 12 | 35 | 345 | 302 | 0 | 20 | 330 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 36 | 0 | 25 | 32 | 25 | 33 | 8 | 0 | 82 | 50 | 150 | 150 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 22 | 40 | 100 | 100 | 0 | 360 | 301 | 110 | 68 | 100 | 34 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 0 | 21 | 110 | 108 | 0 | 0 | 0 | 56 | 60 | 11 | 10 | 100 | 307 | 40 | 50 | 47 | 79 | 0 | 45 | 0 | 265 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 15 | 0 |  | 762 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 151 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 177 | 0 | 0 | 0 | 44 | 0 | 103 | 0 | 0 | 0 |  | 5247 | 1930 | 7177 | 4260 | 762 | 1460 | 183 | 150 | 132 | 120 | 110 | 0 | 0 | 102.6
3:00 | 68 | 0 | 257 | 0 | 250 | 12 | 20 | 320 | 262 | 0 | 20 | 330 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 17 | 10 | 25 | 32 | 25 | 33 | 8 | 0 | 82 | 50 | 150 | 150 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 22 | 40 | 100 | 100 | 0 | 360 | 301 | 186 | 15 | 100 | 34 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 0 | 21 | 106 | 106 | 0 | 0 | 0 | 56 | 60 | 11 | 10 | 100 | 304 | 40 | 10 | 20 | 77 | 0 | 22 | 0 | 270 | 24 | 6 | 0 | 17 | 0 | 0 | 17 | 0 | 15 | 0 |  | 762 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 165 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 0 | 0 | 22 | 0 | 91 | 0 | 0 | 0 |  | 5062 | 1819 | 6881 | 4214 | 762 | 1231 | 166 | 150 | 132 | 120 | 106 | 0 | 0 | 102.59
4:00 | 68 | 0 | 258 | 0 | 230 | 12 | 20 | 300 | 232 | 0 | 20 | 300 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 82 | 50 | 150 | 150 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 22 | 40 | 100 | 100 | 0 | 360 | 301 | 211 | 12 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 0 | 21 | 104 | 107 | 0 | 0 | 0 | 40 | 30 | 11 | 10 | 100 | 307 | 40 | 10 | 5 | 77 | 0 | 5 | 0 | 270 | 24 | 3 | 0 | 15 | 0 | 0 | 17 | 0 | 15 | 0 |  | 762 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 176 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 151 | 0 | 0 | 0 | 22 | 0 | 66 | 0 | 0 | 0 |  | 4840 | 1775 | 6615 | 4122 | 762 | 1095 | 130 | 150 | 132 | 120 | 104 | 0 | 0 | 102.58
5:00 | 68 | 0 | 257 | 0 | 230 | 6 | 20 | 305 | 232 | 0 | 20 | 300 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 85 | 50 | 150 | 150 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 22 | 40 | 80 | 100 | 0 | 360 | 316 | 189 | 12 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 0 | 21 | 102 | 107 | 0 | 0 | 0 | 40 | 30 | 11 | 10 | 100 | 240 | 67 | 10 | 5 | 77 | 0 | 5 | 0 | 290 | 24 | 3 | 0 | 15 | 0 | 0 | 17 | 0 | 15 | 0 |  | 762 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 185 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 152 | 0 | 0 | 0 | 7 | 0 | 51 | 0 | 0 | 0 |  | 4770 | 1755 | 6525 | 4032 | 762 | 1094 | 130 | 150 | 135 | 120 | 102 | 0 | 0 | 102.57
6:00 | 68 | 0 | 264 | 0 | 200 | 6 | 20 | 309 | 212 | 0 | 20 | 300 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 85 | 50 | 140 | 150 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 22 | 40 | 80 | 100 | 0 | 330 | 301 | 182 | 8 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 0 | 21 | 92 | 109 | 0 | 0 | 0 | 40 | 30 | 11 | 10 | 100 | 240 | 65 | 10 | 5 | 78 | 0 | 5 | 0 | 270 | 24 | 3 | 0 | 17 | 0 | 0 | 19 | 0 | 15 | 2 |  | 762 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 152 | 0 | 0 | 0 | 11 | 0 | 51 | 0 | 0 | 0 |  | 4639 | 1695 | 6334 | 3887 | 762 | 1052 | 134 | 150 | 135 | 120 | 92 | 2 | 0 | 102.56
7:00 | 68 | 0 | 265 | 0 | 220 | 6 | 20 | 309 | 242 | 0 | 20 | 300 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 3 | 0 | 6 | 0 | 0 | 17 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 85 | 50 | 150 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 6 | 22 | 38 | 80 | 100 | 0 | 360 | 320 | 191 | 8 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 0 | 21 | 84 | 108 | 0 | 0 | 0 | 40 | 30 | 11 | 10 | 100 | 240 | 62 | 10 | 5 | 78 | 0 | 6 | 0 | 280 | 24 | 5 | 0 | 15 | 0 | 0 | 17 | 0 | 15 | 4 |  | 541 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 185 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 152 | 0 | 0 | 0 | 50 | 0 | 51 | 0 | 0 | 0 |  | 4767 | 1544 | 6311 | 4007 | 541 | 1129 | 141 | 150 | 135 | 120 | 84 | 4 | 0 | 102.55
8:00 | 68 | 0 | 262 | 0 | 220 | 42 | 20 | 320 | 223 | 0 | 20 | 300 | 0 | 6 | 0 | 15 | 0 | 0 | 0 | 0 | 6 | 7 | 0 | 10 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 25 | 33 | 8 | 0 | 85 | 50 | 150 | 150 | 0 | 202 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 15 | 13 | 6 | 22 | 5 | 80 | 100 | 0 | 360 | 268 | 160 | 73 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 6 | 12 | 86 | 106 | 0 | 22 | 0.4 | 40 | 30 | 11 | 10 | 100 | 303 | 67 | 10 | 5 | 79 | 0 | 7 | 0 | 290 | 23 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 15 | 11 |  | 540 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 182 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 5 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 0 | 0 | 51 | 0 | 66 | 0 | 0 | 0 |  | 4915.4 | 1597 | 6512.4 | 4024 | 540 | 1183 | 264 | 149 | 135 | 120 | 86 | 11.4 | 0 | 102.54
9:00 | 68 | 0 | 264 | 0 | 250 | 42 | 20 | 364 | 291 | 0 | 20 | 370 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 11 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 25 | 33 | 8 | 0 | 85 | 50 | 150 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 22 | 13 | 6 | 22 | 5 | 80 | 100 | 0 | 360 | 290 | 197 | 73 | 100 | 34 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 5 | 8 | 12 | 94 | 105 | 0 | 22 | 0.8 | 56 | 30 | 11 | 10 | 130 | 317 | 65 | 10 | 5 | 79 | 0 | 7 | 0 | 300 | 25 | 5 | 0 | 17 | 0 | 0 | 17 | 0 | 70 | 16.7 |  | 541 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 183 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 11 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 157 | 0 | 0 | 0 | 60 | 0 | 50 | 0 | 0 | 0 |  | 5358.5 | 1596 | 6954.5 | 4186 | 541 | 1366 | 345 | 150 | 135 | 120 | 94 | 17.5 | 0 | 102.53
10:00 | 68 | 0 | 257 | 0 | 250 | 42 | 20 | 358 | 291 | 0 | 20 | 340 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 85 | 50 | 150 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 80 | 13 | 10 | 22 | 2 | 80 | 100 | 0 | 360 | 290 | 198 | 73 | 100 | 38 | 0 | 5 | 0 | 10 | 0 | 0 | 16 | 5 | 8 | 12 | 102 | 88 | 0 | 22 | 1.4 | 56 | 30 | 11 | 10 | 130 | 315 | 65 | 10 | 5 | 78 | 0 | 7 | 0 | 310 | 25 | 5 | 0 | 17 | 0 | 0 | 17 | 0 | 95 | 19.7 |  | 762 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 182 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 21 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 189 | 0 | 0 | 0 | 81 | 0 | 50 | 0 | 0 | 0 |  | 5418.1 | 1883 | 7301.1 | 4164 | 762 | 1389 | 458 | 150 | 135 | 120 | 102 | 21.1 | 0 | 102.52
11:00 | 68 | 0 | 257 | 0 | 300 | 42 | 20 | 356 | 356 | 0 | 20 | 340 | 0 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 85 | 50 | 150 | 150 | 0 | 216 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 80 | 13 | 41 | 22 | 2 | 80 | 100 | 0 | 360 | 294 | 199 | 73 | 100 | 38 | 0 | 5 | 0 | 10 | 0 | 0 | 16 | 0 | 8 | 12 | 104 | 87 | 0 | 20 | 2.1 | 56 | 60 | 11 | 10 | 100 | 315 | 64 | 10 | 5 | 78 | 0 | 7 | 0 | 320 | 25 | 8 | 0 | 17 | 0 | 0 | 17 | 0 | 98 | 19.8 |  | 762 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 182 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 188 | 0 | 0 | 0 | 81 | 0 | 50 | 0 | 0 | 0 |  | 5623.9 | 1933 | 7556.9 | 4302 | 762 | 1435 | 527 | 150 | 135 | 120 | 104 | 21.9 | 0 | 102.51
12:00 | 68 | 0 | 255 | 0 | 380 | 42 | 20 | 355 | 352 | 0 | 20 | 370 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 11 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 86 | 50 | 150 | 140 | 0 | 204 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 80 | 13 | 50 | 22 | 2 | 80 | 100 | 0 | 360 | 305 | 223 | 73 | 100 | 38 | 0 | 5 | 0 | 10 | 0 | 0 | 16 | 8 | 8 | 15 | 104 | 78 | 0 | 20 | 2.1 | 56 | 60 | 11 | 10 | 100 | 309 | 56 | 10 | 5 | 78 | 0 | 7 | 0 | 300 | 25 | 8 | 0 | 32 | 0 | 0 | 17 | 0 | 98 | 18 |  | 762 | 0 | 330 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 168 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 183 | 0 | 0 | 0 | 82 | 0 | 101 | 0 | 0 | 0 |  | 5747.1 | 1999 | 7746.1 | 4445 | 762 | 1442 | 567 | 150 | 136 | 120 | 104 | 20.1 | 0 | 102.5
13:00 | 68 | 0 | 254 | 0 | 380 | 42 | 20 | 350 | 316 | 0 | 20 | 370 | 0 | 7 | 15 | 23 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 86 | 50 | 150 | 140 | 8 | 204 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 80 | 51 | 50 | 22 | 6 | 80 | 100 | 0 | 360 | 305 | 184 | 73 | 100 | 38 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 8 | 8 | 15 | 112 | 65 | 0 | 22 | 1.9 | 56 | 50 | 14 | 10 | 100 | 313 | 55 | 10 | 5 | 78 | 0 | 7 | 0 | 300 | 24 | 8 | 0 | 47 | 0 | 0 | 46 | 0 | 98 | 19 |  | 762 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 155 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 189 | 0 | 0 | 0 | 82 | 0 | 123 | 0 | 0 | 0 |  | 5757.9 | 2000 | 7757.9 | 4369 | 762 | 1410 | 678 | 150 | 136 | 120 | 112 | 20.9 | 0 | 102.49
14:00 | 68 | 0 | 254 | 0 | 300 | 12 | 20 | 354 | 316 | 0 | 20 | 370 | 0 | 7 | 7 | 41 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 11 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 26 | 17 | 8 | 0 | 86 | 50 | 150 | 140 | 8 | 205 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 51 | 50 | 22 | 4 | 80 | 100 | 0 | 360 | 316 | 197 | 73 | 100 | 38 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 8 | 8 | 17 | 114 | 65 | 0 | 22 | 1.7 | 56 | 50 | 14 | 10 | 100 | 315 | 63 | 5 | 5 | 78 | 0 | 7 | 0 | 290 | 25 | 0 | 0 | 45 | 0 | 0 | 46 | 0 | 98 | 16.5 |  | 762 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 176 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 184 | 0 | 0 | 0 | 94 | 0 | 123 | 0 | 0 | 0 |  | 5684.2 | 2036 | 7720.2 | 4340 | 762 | 1376 | 704 | 150 | 136 | 120 | 114 | 18.2 | 0 | 102.48
15:00 | 68 | 0 | 253 | 0 | 380 | 12 | 20 | 377 | 351 | 0 | 20 | 420 | 0 | 7 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 26 | 17 | 8 | 0 | 82 | 50 | 150 | 140 | 8 | 218 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 52 | 50 | 22 | 2 | 80 | 100 | 0 | 360 | 331 | 205 | 77 | 100 | 38 | 0 | 5 | 0 | 6 | 0 | 0 | 19 | 5 | 8 | 17 | 116 | 66 | 0 | 22 | 0 | 55 | 50 | 14 | 10 | 130 | 317 | 62 | 5 | 5 | 78 | 0 | 6 | 0 | 130 | 25 | 0 | 0 | 45 | 0 | 0 | 45 | 0 | 98 | 9.8 |  | 762 | 0 | 412 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 180 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 194 | 0 | 0 | 0 | 94 | 0 | 138 | 0 | 0 | 0 |  | 5787.8 | 2175 | 7962.8 | 4617 | 762 | 1332 | 725 | 149 | 132 | 120 | 116 | 9.8 | 0 | 102.47
16:00 | 68 | 0 | 253 | 0 | 380 | 12 | 20 | 359 | 322 | 0 | 20 | 420 | 0 | 7 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 26 | 17 | 10 | 0 | 82 | 50 | 150 | 150 | 8 | 202 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 52 | 50 | 22 | 2 | 80 | 100 | 0 | 360 | 305 | 183 | 78 | 95 | 38 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 5 | 8 | 17 | 108 | 68 | 0 | 22 | 0 | 55 | 50 | 13 | 10 | 163 | 310 | 62 | 5 | 5 | 98 | 0 | 42 | 0 | 90 | 25 | 8 | 0 | 45 | 0 | 0 | 45 | 0 | 97 | 5.8 |  | 762 | 0 | 416 | 0 | 16 | 120 | 0 | 0 | 0 | 5 | 0 | 180 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 185 | 0 | 0 | 0 | 94 | 0 | 124 | 0 | 0 | 0 |  | 5721.8 | 2162 | 7883.8 | 4544 | 762 | 1332 | 726 | 149 | 132 | 125 | 108 | 5.8 | 0 | 102.47
17:00 | 68 | 0 | 253 | 0 | 300 | 12 | 20 | 349 | 272 | 0 | 20 | 400 | 0 | 7 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 7 | 6 | 10 | 8 | 10 | 6 | 18 | 18 | 55 | 19 | 25 | 24 | 26 | 17 | 25 | 0 | 82 | 50 | 150 | 150 | 8 | 203 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 65 | 50 | 22 | 3 | 80 | 100 | 0 | 360 | 305 | 183 | 78 | 100 | 38 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 8 | 8 | 17 | 112 | 69 | 0 | 22 | 0 | 55 | 50 | 14 | 10 | 130 | 307 | 62 | 5 | 5 | 78 | 0 | 42 | 0 | 80 | 25 | 11 | 0 | 62 | 0 | 0 | 48 | 0 | 99 | 0.7 |  | 762 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 8 | 25 | 0 | 182 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 176 | 0 | 0 | 0 | 97 | 0 | 120 | 0 | 0 | 18 |  | 5557.7 | 2159 | 7716.7 | 4359 | 762 | 1224 | 819 | 149 | 132 | 159 | 112 | 0.7 | 0 | 102.46
18:00 | 68 | 0 | 253 | 0 | 305 | 94 | 40 | 352 | 307 | 0 | 20 | 380 | 0 | 7 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 10 | 64 | 26 | 8 | 10 | 28 | 45 | 18 | 55 | 22 | 25 | 32 | 26 | 33 | 38 | 0 | 82 | 50 | 150 | 150 | 25 | 211 | 0 | 0 | 0 | 0 | 32 | 48 | 47 | 90 | 93 | 50 | 22 | 8 | 80 | 100 | 0 | 360 | 323 | 195 | 78 | 100 | 38 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 148 | 69 | 56 | 22 | 0 | 55 | 60 | 44 | 32 | 163 | 312 | 63 | 89 | 46 | 126 | 19 | 44 | 7 | 80 | 25 | 11 | 0 | 172 | 0 | 0 | 144 | 0 | 102 | 0 |  | 762 | 0 | 419 | 0 | 32 | 120 | 0 | 0 | 43 | 41 | 40 | 185 | 26 | 110 | 0 | 0 | 0 | 50 | 31 | 60 | 50 | 50 | 38 | 0 | 33 | 22 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 123 | 0 | 0 | 18 |  | 6734 | 2688 | 9422 | 4619 | 762 | 1650 | 1386 | 150 | 132 | 575 | 148 | 0 | 0 | 102.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 68 | 0 | 201 | 0 | 380 | 94 | 80 | 349 | 322 | 0 | 20 | 450 | 0 | 27 | 15 | 55 | 0 | 0 | 0 | 0 | 30 | 32 | 64 | 92 | 50 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 40 | 0 | 82 | 50 | 150 | 150 | 25 | 202 | 0 | 0 | 0 | 0 | 32 | 40 | 49 | 100 | 93 | 50 | 22 | 7 | 80 | 100 | 0 | 360 | 305 | 228 | 78 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 144 | 69 | 73 | 22 | 0 | 55 | 60 | 44 | 46 | 100 | 306 | 62 | 89 | 46 | 98 | 19 | 43 | 7 | 0 | 25 | 11 | 0 | 170 | 0 | 0 | 168 | 0 | 113 | 0 |  | 762 | 0 | 426 | 0 | 49 | 120 | 0 | 0 | 37 | 75 | 40 | 147 | 27 | 110 | 0 | 0 | 0 | 50 | 48 | 90 | 50 | 50 | 38 | 35 | 35 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 219 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 54 |  | 6994 | 2892 | 9886 | 4651 | 762 | 1646 | 1756 | 149 | 132 | 646 | 144 | 0 | 0 | 102.45
19:30 | 68 | 0 | 200 | 0 | 300 | 94 | 80 | 347 | 306 | 0 | 20 | 380 | 0 | 49 | 15 | 55 | 0 | 0 | 0 | 0 | 50 | 50 | 64 | 100 | 50 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 42 | 0 | 82 | 50 | 150 | 150 | 25 | 202 | 0 | 0 | 0 | 0 | 40 | 40 | 31 | 100 | 93 | 50 | 22 | 8 | 80 | 100 | 0 | 360 | 305 | 214 | 78 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 144 | 70 | 73 | 22 | 0 | 55 | 60 | 44 | 44 | 100 | 310 | 67 | 89 | 47 | 98 | 19 | 43 | 7 | 0 | 25 | 11 | 0 | 172 | 0 | 0 | 180 | 0 | 104 | 0 |  | 762 | 0 | 300 | 0 | 49 | 120 | 0 | 0 | 37 | 68 | 40 | 180 | 29 | 110 | 0 | 0 | 0 | 40 | 48 | 100 | 50 | 50 | 38 | 35 | 35 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 219 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 54 |  | 6886 | 2794 | 9680 | 4471 | 762 | 1562 | 1839 | 149 | 132 | 621 | 144 | 0 | 0 | 0
20:00 | 68 | 0 | 200 | 0 | 300 | 94 | 79 | 352 | 326 | 0 | 20 | 350 | 0 | 48 | 15 | 55 | 0 | 0 | 0 | 0 | 50 | 16 | 48 | 100 | 50 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 42 | 0 | 82 | 50 | 150 | 150 | 25 | 214 | 0 | 0 | 0 | 0 | 40 | 8 | 16 | 100 | 93 | 50 | 22 | 26 | 80 | 100 | 0 | 360 | 331 | 193 | 78 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 142 | 69 | 73 | 22 | 0 | 55 | 60 | 44 | 44 | 100 | 320 | 67 | 89 | 47 | 98 | 19 | 45 | 7 | 0 | 25 | 11 | 0 | 171 | 0 | 0 | 182 | 0 | 115 | 0 |  | 761 | 0 | 300 | 0 | 49 | 120 | 0 | 0 | 37 | 48 | 40 | 184 | 31 | 110 | 0 | 0 | 0 | 0 | 48 | 50 | 50 | 50 | 40 | 35 | 0 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 219 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 54 |  | 6838 | 2656 | 9494 | 4506 | 761 | 1573 | 1816 | 149 | 132 | 415 | 142 | 0 | 0 | 102.45
21:00 | 68 | 0 | 196 | 0 | 380 | 94 | 80 | 365 | 353 | 0 | 20 | 430 | 0 | 20 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 39 | 18 | 55 | 55 | 0 | 25 | 32 | 26 | 33 | 42 | 0 | 82 | 50 | 150 | 150 | 25 | 202 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 93 | 44 | 22 | 35 | 80 | 100 | 0 | 360 | 327 | 175 | 78 | 101 | 25 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 138 | 69 | 72 | 22 | 0 | 55 | 60 | 44 | 47 | 100 | 306 | 67 | 89 | 47 | 98 | 19 | 45 | 7 | 0 | 25 | 11 | 0 | 172 | 0 | 0 | 173 | 0 | 113 | 0 |  | 762 | 0 | 420 | 0 | 32 | 120 | 0 | 0 | 37 | 48 | 40 | 185 | 27 | 110 | 0 | 0 | 0 | 0 | 48 | 8 | 50 | 50 | 38 | 43 | 0 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 220 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 54 |  | 6571 | 2722 | 9293 | 4632 | 762 | 1689 | 1492 | 149 | 132 | 299 | 138 | 0 | 0 | 102.44
22:00 | 68 | 0 | 204 | 0 | 380 | 94 | 81 | 347 | 355 | 0 | 20 | 430 | 0 | 7 | 16 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 18 | 18 | 55 | 55 | 0 | 25 | 32 | 26 | 33 | 25 | 0 | 82 | 50 | 150 | 150 | 25 | 209 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 95 | 45 | 22 | 37 | 80 | 100 | 0 | 360 | 323 | 176 | 78 | 100 | 25 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 33 | 20 | 130 | 71 | 36 | 22 | 0 | 55 | 60 | 5 | 5 | 100 | 308 | 66 | 50 | 5 | 77 | 19 | 6 | 7 | 0 | 25 | 11 | 0 | 117 | 0 | 0 | 163 | 0 | 112 | 0 |  | 762 | 0 | 427 | 0 | 32 | 120 | 0 | 0 | 5 | 7 | 40 | 185 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 50 | 37 | 25 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 219 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 45 |  | 6158 | 2511 | 8669 | 4613 | 762 | 1457 | 1248 | 150 | 132 | 177 | 130 | 0 | 0 | 102.44
23:00 | 68 | 0 | 262 | 0 | 380 | 94 | 80 | 344 | 358 | 0 | 20 | 430 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 18 | 55 | 19 | 25 | 32 | 26 | 33 | 0 | 0 | 80 | 50 | 150 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 90 | 35 | 45 | 22 | 40 | 80 | 100 | 0 | 360 | 309 | 171 | 78 | 100 | 25 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 33 | 18 | 124 | 69 | 0 | 22 | 0 | 55 | 60 | 5 | 5 | 100 | 323 | 66 | 50 | 5 | 78 | 20 | 6 | 7 | 0 | 25 | 11 | 0 | 60 | 0 | 0 | 173 | 0 | 70 | 0 |  | 757 | 0 | 425 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 185 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 50 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 221 | 0 | 0 | 0 | 96 | 0 | 150 | 0 | 0 | 0 |  | 5912 | 2251 | 8163 | 4675 | 757 | 1462 | 737 | 150 | 130 | 128 | 124 | 0 | 0 | 102.43
24:00 | 68 | 0 | 256 | 0 | 380 | 94 | 80 | 334 | 357 | 0 | 20 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 0 | 19 | 25 | 32 | 26 | 33 | 0 | 0 | 84 | 50 | 150 | 150 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 90 | 12 | 0 | 22 | 38 | 80 | 100 | 0 | 360 | 301 | 180 | 78 | 100 | 25 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 5 | 33 | 20 | 120 | 71 | 0 | 22 | 0 | 56 | 60 | 5 | 5 | 163 | 311 | 66 | 50 | 5 | 80 | 20 | 30 | 7 | 0 | 24 | 11 | 0 | 55 | 0 | 0 | 65 | 0 | 54 | 0 |  | 758 | 0 | 425 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 169 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 24 | 0 | 0 | 0 | 22 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 188 | 0 | 0 | 0 | 96 | 0 | 124 | 0 | 0 | 0 |  | 5632 | 2130 | 7762 | 4572 | 758 | 1544 | 356 | 150 | 134 | 128 | 120 | 0 | 0 | 102.43
KWH | 1542000 | 0 | 6050000 | 0 | 6228936 | 973841 | 1077216 | 8299520 | 7200000 | 0 | 511000 | 8818150 | 0 | 219840 | 246000 | 657619 | 0 | 0 | 0 | 0 | 258240 | 211248 | 183840 | 456335 | 243840 | 95940 | 337056 | 441360 | 487522 | 1006000 | 380052 | 600000 | 732280 | 621100 | 681100 | 365736 | 0 | 1928571 | 1179000 | 3600000 | 3600000 | 193680 | 4867856 | 0 | 0 | 0 | 0 | 628800 | 96348 | 110844 | 1491480 | 987840 | 756960 | 527768 | 512160 | 2066174 | 2384695 | 0 | 8967300 | 7414000 | 4321200 | 1555636 | 2359700 | 802224 | 0 | 120000 | 0 | 246000 | 0 | 0 | 441000 | 173160 | 311900 | 435000 | 2733120 | 2068360 | 344640 | 372564 | 10100 | 1222000 | 1886600 | 393000 | 354000 | 3114221 | 6902391 | 1401000 | 842880 | 415800 | 2061700 | 123000 | 517840 | 56880 | 4805700 | 581520 | 170640 | 0 | 1310000 | 0 | 0 | 1555200 | 0 | 1673280 | 138100 |  | 17840727 | 0 | 8285472 | 0 | 324480 | 3043200 | 0 | 0 | 162720 | 240384 | 200250 | 4267000 | 500029 | 769920 | 0 | 0 | 0 | 111784 | 180540 | 202086 | 555670 | 457728 | 176544 | 152640 | 67798 | 408720 | 85824 | 180792 | 0 | 0 | 3653200 | 0 | 0 | 4655155 | 0 | 0 | 0 | 1757389 | 0 | 2525818 | 0 | 0 | 237600 |  | 136059603 | 51043470 | 187103073 | 104621977 | 17840727 | 33755286 | 16666904 | 3653200 | 3107571 | 4576088 | 2733120 | 148200 | 0
Fuel Cost | 1326120 | 0 | 5203000 | 0 | 3986519.04 | 788811.21 | 1012583.04 | 5062707.2 | 4392000 | 0 | 700070 | 5908160.5 | 0 | 1380595.2 | 1643280 | 4018052.09 | 0 | 0 | 0 | 0 | 1614000 | 1392124.32 | 1777732.8 | 2906853.95 | 1460601.6 | 1534080.6 | 2248163.52 | 3146896.8 | 3047012.5 | 6307620 | 285039 | 450000 | 0 | 0 | 0 | 3459862.56 | 0 | 0 | 0 | 3960000 | 3960000 | 1834149.6 | 3212784.96 | 0 | 0 | 0 | 0 | 5527152 | 1037667.96 | 1078512.12 | 9232261.2 | 6381446.4 | 4950518.4 | 448602.8 | 0 | 1880218.34 | 2170072.45 | 0 | 5559726 | 5115660 | 3024840 | 1073388.84 | 2265312 | 537490.08 | 0 | 110400 | 0 | 233700 | 0 | 0 | 339570 | 129870 | 240163 | 326250 | 18694540.8 | 1551270 | 3167241.6 | 286874.28 | 0 | 1270880 | 1962064 | 377280 | 318600 | 2429092.38 | 4831673.7 | 1597140 | 901881.6 | 457380 | 2350338 | 157440 | 481591.2 | 52898.4 | 3075648 | 436140 | 129686.4 | 0 | 9510600 | 0 | 0 | 11119680 | 0 | 0 | 0 |  | 90987707.7 | 0 | 5551266.24 | 0 | 2689939.2 | 48934656 | 0 | 0 | 1832227.2 | 2831723.52 | 1577970 | 2944230 | 495028.71 | 5697408 | 0 | 0 | 0 | 1279926.8 | 1935388.8 | 1810690.56 | 4806545.5 | 4073779.2 | 1880193.6 | 1514188.8 | 797982.46 | 449592 | 80674.56 | 136859.544 | 0 | 0 | 14101352 | 0 | 0 | 3165505.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 194841582.44 | 199574835.794 | 394416418.234 | 76555382.434 | 90987707.7 | 22638710.44 | 106242023.04 | 14101352 | 0 | 65196701.82 | 18694540.8 | 0 | 0
Yesterday Day Peak | 68 | 0 | 255 | 0 | 380 | 42 | 20 | 355 | 352 | 0 | 20 | 370 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 11 | 6 | 18 | 18 | 55 | 19 | 25 | 32 | 25 | 17 | 8 | 0 | 86 | 50 | 150 | 140 | 0 | 204 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 80 | 13 | 50 | 22 | 2 | 80 | 100 | 0 | 360 | 305 | 223 | 73 | 100 | 38 | 0 | 5 | 0 | 10 | 0 | 0 | 16 | 8 | 8 | 15 | 104 | 78 | 0 | 20 | 2.1 | 56 | 60 | 11 | 10 | 100 | 309 | 56 | 10 | 5 | 78 | 0 | 7 | 0 | 300 | 25 | 8 | 0 | 32 | 0 | 0 | 17 | 0 | 98 | 18 |  | 762 | 0 | 330 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 168 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 22 | 4 | 8 | 0 | 0 | 150 | 0 | 0 | 183 | 0 | 0 | 0 | 82 | 0 | 101 | 0 | 0 | 0 |  | 7746.1 | DayPeak
Yesterday Evening Peak | 68 | 0 | 201 | 0 | 380 | 94 | 80 | 349 | 322 | 0 | 20 | 450 | 0 | 27 | 15 | 55 | 0 | 0 | 0 | 0 | 30 | 32 | 64 | 92 | 50 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 40 | 0 | 82 | 50 | 150 | 150 | 25 | 202 | 0 | 0 | 0 | 0 | 32 | 40 | 49 | 100 | 93 | 50 | 22 | 7 | 80 | 100 | 0 | 360 | 305 | 228 | 78 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 20 | 144 | 69 | 73 | 22 | 0 | 55 | 60 | 44 | 46 | 100 | 306 | 62 | 89 | 46 | 98 | 19 | 43 | 7 | 0 | 25 | 11 | 0 | 170 | 0 | 0 | 168 | 0 | 113 | 0 |  | 762 | 0 | 426 | 0 | 49 | 120 | 0 | 0 | 37 | 75 | 40 | 147 | 27 | 110 | 0 | 0 | 0 | 50 | 48 | 90 | 50 | 50 | 38 | 35 | 35 | 22 | 4 | 8 | 0 | 0 | 149 | 0 | 0 | 219 | 0 | 0 | 0 | 97 | 0 | 150 | 0 | 0 | 54 |  | 9886 | EvPeak
Forecast for Evening | 68 | 0 | 262 | 0 | 380 | 94 | 78 | 412 | 360 | 110 | 20 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 90 | 102 | 149 | 100 | 50 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 43 | 0 | 85 | 50 | 150 | 150 | 25 | 225 |  | 0 | 0 | 0 | 40 | 80 | 46 | 100 | 100 | 50 | 22 | 15 | 100 | 100 | 0 | 360 | 360 | 225 | 195 | 100 | 41 | 0 | 5 | 0 | 85 | 40 | 52 | 19 | 11 | 33 | 20 | 148 | 150 | 72 | 22 | 0 | 60 | 60 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 20 | 46 | 10 | 341 | 25 | 11 | 200 | 270 | 300 | 100 | 160 | 100 | 115 | 0 |  | 770 | 30 | 410 | 0 | 115 | 225 | 0 | 0 | 42 | 80 | 40 | 188 | 33 | 110 | 30 | 0 | 0 | 50 | 54 | 100 | 50 | 50 | 40 | 52 | 42 | 22 | 5 | 11 | 0 | 0 | 150 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 141 | 0 | 0 | 105
Forecast for Day | 68 | 0 | 262 | 0 | 380 | 94 | 78 | 412 | 360 | 110 | 20 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 90 | 102 | 149 | 100 | 50 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 26 | 33 | 43 | 0 | 85 | 50 | 150 | 150 | 25 | 225 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 100 | 100 | 50 | 22 | 10 | 100 | 100 | 0 | 360 | 360 | 225 | 90 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 52 | 19 | 11 | 33 | 20 | 115 | 150 | 72 | 22 | 2 | 60 | 60 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 20 | 46 | 10 | 341 | 25 | 11 | 0 | 270 | 100 | 0 | 150 | 0 | 110 | 20 |  | 770 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 188 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 |  | 0 | 210 | 0 | 0 | 0 | 95 | 0 | 141 | 0 | 0 | 50
Generation at 08:00(Today) | 68 | 0 | 259 | 0 | 330 | 6 | 20 | 360 | 354 | 0 | 10 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 10 | 6 | 0 | 18 | 0 | 0 | 25 | 32 | 26 | 33 | 2 | 0 | 40 | 50 | 150 | 150 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 0 | 0 | 8 | 80 | 100 | 0 | 250 | 327 | 200 | 8 | 100 | 41 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 5 | 8 | 15 | 84 | 90 | 0 | 0 | 0 | 56 | 60 | 5 | 30 | 130 | 314 | 61 | 5 | 5 | 68 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 18 | 11 | 0 | 761 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 188 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 5 | 0 | 0 | 150 | 0 | 0 | 189 | 0 | 0 | 0 | 50 | 0 | 51 | 0 | 0 | 0 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [66 empty] | 199
| Minimum Generation |  | 6311 | 7:00
| Highest Generation |  | 9886 | 19:00
| Day Peak Generation |  | 7746.1 | 12:00
| Evening Peak Generation |  | 9886 | 19:00
| HVDC Max Flow |  | 762 | 1:00
| HVDC EvPeak Flow |  | 762 | 19:00
| Load factor L.F |  | 78.86%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-10-17
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-10-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7746.1 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6163.8 | MW
Evening Peak Generation : |  | 9886 | MW Hour : | 19:00 | Available Max Generation : |  | 12908 | MW
E.P. Demand (at gen end) : |  | 9886 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10600 | MW
Maximum Generation : |  | 9886 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2308 | MW
Total Gen. (MKWH) : |  | 187.1031 | System Load Factor : | 78.86% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -290 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-10-17
Actual : | 102.56 | Ft.(MSL) , | Rule curve : | 0 | Ft.( MSL )
Gas Consumed : | Total = | 1157.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 99194092.874
|  | Coal : | 14101352 | Oil : | 171438724.86 | Total : | 284734169.734
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3700.649 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1256.6326 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1125.5817 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1016.9445 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 919.0606 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 741.6449 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 416.9985 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 191.0147 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 571.9823 |  |  | 0 | 0%
Total | 0 |  | 9940.5087 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Kaptai #2,3,5
|  |  |  | 3) Ghorasal Unit-3,5 |  | 11) Siddhirganj CCPP-335 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Sirajganj unit-2 255 MW
|  |  |  | 5) Tongi GT |  | 13) Ashuganj (Precision) 55 MW
|  |  |  | 6) Ashuganj Midland 51 MW |  | 14) Sikalbaha-150 MW
7) Baghabari-71 MW
8) Haripur GT-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Khulna( C)-North West 225 MW power station 132 kv Ckt-2 was under shut down from 08:26 to 13:33 for corrective maintenance.
b) Noapara 132/33 kV T4 transformer was under shut down from 09:38 to 11:52 due to red hot at B phase of 33 kV CT.
c) Amnura 132/33 kV T2 transformer was under shut down from 08:31 to 15:54 for A/M.
d) Khulna(S)-Satkhira 132 kV Ckt-2 was under shut down from 09:16 to 17:25 for corrective maintenance.
e) Baghabari-Ishurdi 132 kV Ckt was under shut down from 08:35 to 16:26 for A/M.
f) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 10:06 to 16:51 for A/M.
g) Bogura-Confidence power station 132 kV Ckt(New) was switched on and off at 11:51 to 13:21 respectively for on test.
h) Summit Bibiyana unit-2 CCPP ST & GT were shut down at 18:10 & 18:14 respectively due to Boiler maintenance.
i) Ashuganj (N) CCPP ST tripped at 03:34(17/101/2018) showing drain tank level high and GT also shut down at 09:22 for cooling
water pump maintenance.
j) Sirajgonj-Bogura 132 kV Ckt-1 was shut down at 07:26(17/10/2018) due to development work.
k) Barapukuria 230/132 kV T2 transformer was shut down at 06:29 due to corrective maintenance.
l) Faridpur-Bheramara 132 kV Ckt-1 was shut down at 07:17 due to corrective maintenance.
m) Khulna(C ) 132/33 kV T2 transformer tripped at 07:34 from both end showing no relay at 132 kV side and E/F at 33 kV
side due to 33 kV Paikgacha feeder fault.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-10-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 68 | 1542000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 201 | 6050000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 6228936
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 80 | 1077216
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 94 | 973841 | Engine problem
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 511000 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8299520 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 322 | 7200000 | Frequency control.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8818150
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 27 | 219840 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 15 | 246000 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 657619
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 92 | 456335 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 380052
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 30 | 258240 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 95940 | Reserve
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 32 | 211248 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 39 | 337056 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 441360
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 183840 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 487522
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1006000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 50 | 243840 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1332280 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 26 | 621100 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 681100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 40 | 365736 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 170 | 1310000 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 0 | 0 | Rererve.
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 113 | 1673280 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 2993 | 51909051
39 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3600000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3600000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 193680
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 138100
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 756960
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 132 | 3107571 | Unit-2,4 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4867856
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 628800 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 40 | 96348 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 49 | 110844 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1491480
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 527768
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 512160
51 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 93 | 987840 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 1052 | 20619407
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2066174 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2384695 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 228 | 4321200
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8967300
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7414000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 41 | 802224
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 1555636 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Under maint.
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 246000
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2359700 | ST Under maint.
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 441000
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173160 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 144 | 2733120
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 311900
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 435000 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Comilla Area Total |  |  |  | 2541 | 1606 | 34331109
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 69 | 2068360 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 372564
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 73 | 344640 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 10100
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 168 | 1555200 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 332 | 4350864
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 55 | 1222000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1886600
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3114221 | Frequency control.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 306 | 6902391 | FGMO.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 44 | 393000 | Engine problem
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 46 | 354000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 170640
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 1401000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 89 | 842880
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 415800
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 98 | 2061700
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 123000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 517840 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 581520
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 4805700 | Under shut down.
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 7 | 56880 | Engine problem
| Sylhet Area Total |  |  |  | 1549 | 1011 | 24849172
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 762 | 17840727
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 324480 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 37 | 162720
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3043200 | Low demand
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 75 | 240384
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 426 | 8285472
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 200250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 105 | 0 | 54 | 237600 | Low demand
| Khulna Area Total |  |  |  | 2214 | 1563 | 30334833
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 769920
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 27 | 500029 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 147 | 4267000
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1757389
| Barisal Area Total |  |  |  | 462 | 381 | 7294338
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 111784
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 48 | 180540
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 555670
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 457728
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 38 | 176544
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 219 | 4655155 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 150 | 2525818 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 | 0 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 35 | 67798
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 408720
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 4 | 85824 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 180792 | Engine problem
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 35 | 152640 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 202086
| Rajshahi Area Total |  |  |  | 1264 | 799 | 9761099
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3653200
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 149 | 3653200
| Total |  |  |  | 16445 | 9886 | 187103073
| Eastern Grid Total |  |  |  | 12021 | 6994 | 136059603
| Western Grid Total |  |  |  | 4424 | 2892 | 51043470
| National Grid Total |  |  |  | 16445 | 9886 | 187103073
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-10-16 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6467 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2790 | MW
i) Dhaka area |  |  | 3604 | MW | i) Khulna area |  |  | 1121 | MW
ii) Chittagong area |  |  | 1025 | MW | ii) Rajshahi area |  |  | 910 | MW
iii) Comilla area |  |  | 878 | MW | iii) Barisal area |  |  | 218 | MW
iv) Mymensingh area |  |  | 616 | MW | iv) Rangpur area |  |  | 541 | MW
v) Sylhet area |  |  | 344 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9257 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1500 | Netrokona | 67 | 1830 | Goalpara | 32 | 1900
Munsiganj | 197 | 2000 | Jamalpur | 90 | 1930 | Central s/s | 75 | 1930
Sonargaon | 46 | 1000 | Sherpur | 62 | 1830 | Noapara | 72 | 1830
Shyampur | 165 | 1200 | Srimongal | 24 | 1800 | Jessore | 120 | 1830
Bhulta | 171 | 1930 | Shahjibazar | 87 | 1800 | Jhenida | 0 | 1830
Madanganj | 57 | 1930 | Fenchuganj | 32 | 1900 | Bottail | 102 | 1900
Shitalakhya | 96 | 1100 | Kulawara | 31 | 1800 | G.K Project | 43 | 1830
Rahim steel | 15 | 1600 | Sylhet | 104 | 1900 | Faridpur | 132 | 1900
Matuail | 93 | 1200 | Chatak | 20 | 1800 | Madaripur | 113 | 1930
Ghorasal | 67 | 1900 | Sunamganj | 25 | 1800 | Gopalganj | 69 | 1900
Narsingdi | 115 | 1900 | Biani Bazar | 32 | 1800 | Bagerhat | 67 | 1830
Haripur (SBU) | 108 | 1930 | Comilla (S) | 148 | 1800 | Mongla | 32 | 100
Ullon | 75 | 1800 | Comilla(N) | 93 | 1900 | Satkhira | 73 | 1830
Hasnabad | 177 | 1900 | Chandpur | 99 | 1800 | Gallamari | 34 | 1800
Magbazar | 113 | 1200 | Feni | 107 | 1800 | Magura | 38 | 1930
Maniknagar | 88 | 1200 | Chowmuhani | 162 | 1900 | Chuadanga | 66 | 1830
Bangabhaban | 34 | 1000 | Ashuganj | 47 | 2000 | Barisal | 96 | 1830
Narinda | 72 | 1400 | Daudkandi | 104 | 1930 | Patuakhali | 70 | 2000
Dhanmondi | 107 | 1300 | B.Baria | 104 | 2000 | Bhandaria | 40 | 2000
Lalbag | 88 | 1300 | Ramganj | 33 | 2100 | Ishurdi | 46 | 1830
Madartek | 42 | 1900 | Madunaghat | 54.6 | 1800 | Ruppur Paromanobik | 2 | 1200
Mirpur | 94 | 1830 | Hathazari | 86 | 1900 | Natore | 90 | 1830
Kalyanpur | 105 | 1900 | Khulshi | 172 | 1600 | Bogra | 188 | 1900
Gulshan | 118 | 1200 | Halishahar | 122 | 1500 | Noagaon | 84 | 1830
Uttara | 75 | 1800 | Baraulia | 141 | 1100 | Rajshahi | 108 | 1900
Uttara(New) | 6 | 1200 | Sikalbaha | 34 | 1800 | C.Nawabganj | 52 | 1830
Kamrangirchar | 68 | 1800 | Dohazari | 78 | 1930 | Amnura | 32 | 1900
Savar | 115 | 1200 | Cox'sbazar | 68 | 1800 | Pabna | 86 | 1930
Bhasantec | 136 | 1800 | Chandraghona | 22 | 1800 | Shahjadpur | 76 | 1900
Agargaon | 38 | 1800 | Kaptai | 4 | 1800 | Serajganj | 78 | 1900
Satmosjid | 80 | 1900 | A. Khaer Stl. | 13 | 1200 | Niyamatpur | 40 | 1930
Tongi | 116 | 1800 | Bakulia | 94 | 1900 | Joypurhat | 37 | 1830
Kabirpur | 181 | 1800 | Julda | 19 | 900 | Rangpur | 100 | 1830
Basundhara | 115 | 1800 | TK chemical | 8 | 1200 | Lalmonirhat | 70 | 1830
Manikganj | 81 | 1930 | Modern Steel | 14 | 1600 | Saidpur | 100 | 1830
Joydevpur | 202 | 1900 | Shahmirpur | 24.5 | 1800 | Purbasadipur | 76 | 1900
New Tongi | 98 | 1200 | Khagrachhari | 16 | 1830 | Thakurgaon | 54 | 1830
Korda | 246 | 1830 | Matarbari | 22 | 1900 | Palashbari | 81 | 1830
Dhamrai | 44 | 1830 | Baroiar Hat | 9 | 1000 | Barapukuria | 40 | 1830
Tangail | 145 | 1900 | Rangamati | 10 | 1800 | Panchagar | 36 | 1830
Mymensing | 195 | 1800 | Abul Khair 230 | 194 | 1500
Kishorganj | 74 | 1830 | BSRM | 107 | 300
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-10-16
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 388 | 1:00 | 373 | 23:00 | Kaliakoir | 368 | 6:00 | 356 | 18:30
Bheramara | 402 | 7:00 | 396 | 19:00 | Bhulta | 382 | 6:00 | 367 | 12:00
Ashuganj(N) | 388 | 1:00 | 379 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 225 | 1:00 | 225 | 1:00 | Hathazari | 220 | 3:00 | 214 | 16:00
Ishurdi | 235 | 1:00 | 225 | 12:00 | Megnaghat | 226 | 7:00 | 218 | 10:00
Ashuganj | 235 | 1:00 | 230 | 10:00 | Fenchuganj | 236 | 6:00 | 230 | 22:00
Serajganj | 227 | 3:00 | 216 | 21:00 | Siddhirganj | 222 | 4:00 | 214 | 11:00
Baghabari | 228 | 4:00 | 219 | 19:30 | Maniknagar | 221 | 6:00 | 212 | 15:00
Barapukuria | 235 | 3:00 | 227 | 18:00 | Old Airport | 222 | 6:00 | 211 | 12:00
Bogra | 226 | 6:00 | 213 | 18:30 | Barisal | 222 | 17:00 | 213 | 22:00
Khulna South | 237 | 4:00 | 225 | 18:30 | AKSML | 217 | 1:00 | 211 | 15:00
Rampura | 221 | 5:00 | 213 | 15:00 | BSRM | 219 | 1:00 | 214 | 10:00
Haripur | 220 | 1:00 | 213 | 11:00 | Bibiyana | 232 | 1:00 | 226 | 12:00
Hasnabad | 222 | 5:00 | 212 | 12:00 | Bhulta | 222 | 2:00 | 214 | 11:00
Aminbazar | 223 | 8:00 | 212 | 12:00 | Ashuganj (S) | 232 | 4:00 | 226 | 12:00
Tongi | 221 | 7:00 | 210 | 11:00 | Kaliakoir | 224 | 5:00 | 218 | 11:00
Comilla (N) | 230 | 6:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 400 | 128 | 1100 | Ramganj | 126 | 900 | 118 | 2100
Munsiganj | 132 | 300 | 127 | 1500 | Madanhat | 131 | 1700 | 129 | 300
Megnaghat | 133 | 600 | 127 | 1000 | Hathazari | 131 | 2100 | 127 | 1600
Shyampur | 129 | 500 | 123 | 1100 | Khulshi | 127 | 1700 | 123 | 800
Bhulta | 127 | 700 | 122 | 1000 | Halishahar | 131 | 1700 | 125 | 900
Madanganj | 135 | 1930 | 124 | 1200 | Baraulia | 128 | 100 | 124 | 900
Shitalakhya | 135 | 1930 | 124 | 1200 | Sikalbaha | 130 | 1900 | 124 | 900
Rahim steal | 133 | 100 | 128 | 1200 | Dohazari | 129 | 1700 | 125 | 300
Matuail | 132 | 300 | 126 | 1200 | Cox'sbazar | 136 | 700 | 119 | 2100
Ghorasal | 136 | 200 | 135 | 900 | Chandraghona | 129 | 700 | 128 | 900
Narsinghdi | 130 | 800 | 126 | 1500 | Kaptai | 131 | 700 | 130 | 300
Haripur (SBU) | 134 | 600 | 131 | 900 | A. Khaer Stl. | 128 | 1830 | 125 | 800
Ullon | 136 | 400 | 128 | 1500 | Bakulia | 128 | 1700 | 123 | 900
Hasnabad | 133 | 300 | 127 | 1300 | Julda | 130 | 1800 | 124 | 800
Magbazar | 135 | 500 | 125 | 1200 | TK Chemical | 132 | 1400 | 128 | 600
Maniknagar | 132 | 400 | 125 | 1100 | Modern Steel | 128 | 1700 | 124 | 300
Bangabhaban | 131 | 600 | 119 | 1200 | Shahmirpur | 129 | 1700 | 125 | 300
Narinda | 136 | 600 | 127 | 1200 | Khagrachhari | 130 | 400 | 128 | 100
Dhanmondi | 136 | 400 | 128 | 1500 | Matarbari | 128 | 1300 | 122 | 500
Lalbag | 131 | 600 | 119 | 1200 | Baroiar Hat | 129 | 700 | 124 | 1830
Madartek | 136 | 600 | 127 | 1200 | Rangamati | 130 | 1700 | 128 | 200
Mirpur | 135 | 600 | 128 | 1200 | Goalpara | 140 | 500 | 129 | 1830
Kalyanpur | 135 | 600 | 128 | 1200 | Central s/s | 136 | 300 | 130 | 1300
Gulshan | 135 | 700 | 127 | 1500 | Noapara | 136 | 600 | 125 | 1830
Uttara | 132 | 600 | 123 | 1600 | Jessore | 130 | 100 | 120 | 1500
Uttara(New) | 131 | 100 | 125 | 1200 | Jhenida | 133 | 600 | 120 | 1830
Kamrangirchar | 133 | 2000 | 123 | 1200 | Bottail | 137 | 400 | 129 | 1900
Savar | 132 | 1000 | 125 | 1200 | G.K.Project | 143 | 300 | 136 | 1830
Bhasantec | 135 | 400 | 127 | 1200 | Faridpur | 134 | 1700 | 125 | 1300
Agargaon | 136 | 400 | 128 | 1200 | Madaripur | 134 | 600 | 126 | 1400
Satmosjid | 136 | 600 | 128 | 1200 | Gopalganj | 137 | 1700 | 122 | 2200
Tongi | 133 | 800 | 126 | 1600 | Bagerhat | 136 | 400 | 129 | 1300
Kabirpur | 135 | 400 | 129 | 1500 | Mongla | 131 | 800 | 126 | 1800
Basundhara | 130 | 800 | 125 | 1300 | Satkhira | 134 | 300 | 128 | 1830
Manikganj | 136 | 500 | 128 | 1830 | Gallamari | 135 | 300 | 130 | 1800
Joydevpur | 140 | 2000 | 132 | 1500 | Magura | 135 | 600 | 119 | 1800
New Tongi | 134 | 500 | 126 | 1500 | Chuadanga | 130 | 500 | 114 | 1830
Kodda | 138 | 1830 | 130 | 2200 | Barisal | 140 | 500 | 132 | 1830
Dhamrai | 135 | 800 | 125 | 1200 | Patuakhali | 137 | 1700 | 129 | 1830
Tangail | 135 | 600 | 129 | 1200 | Bhandaria | 135 | 600 | 128 | 1800
Mymensing | 131 | 400 | 123 | 1200 | Ishurdi | 140 | 100 | 135 | 1300
Kishorganj | 130 | 100 | 125 | 1100 | Ruppur Paromanobik | 140 | 700 | 134 | 1830
Netrokona | 130 | 200 | 124 | 1500 | Natore | 136 | 200 | 130 | 1200
Jamalpur | 134 | 1830 | 122 | 1500 | Bogra | 135 | 500 | 125 | 1830
Sherpur | 134 | 1900 | 120 | 1200 | Noagaon | 131 | 600 | 122 | 1830
Srimongal | 137 | 100 | 135 | 1100 | Rajshahi | 134 | 1900 | 127 | 1200
Shahjibazar | 136 | 800 | 132 | 1500 | C.Nawabganj | 133 | 1900 | 125 | 1300
Fenchuganj | 135 | 100 | 133 | 2200 | Amnura | 138 | 1900 | 126 | 1200
Khulawara | 136 | 500 | 133 | 1500 | Pabna | 135 | 100 | 130 | 1100
Sylhet | 135 | 100 | 132 | 1500 | Shahjadpur | 141 | 100 | 135 | 1100
Chatak | 135 | 100 | 132 | 1500 | Serajganj | 135 | 500 | 128 | 1830
Sunamganj | 135 | 100 | 131 | 1500 | Niyamatpur | 132 | 600 | 118 | 1830
Biani Bazar | 136 | 100 | 132 | 1500 | Joypurhat | 134 | 1900 | 121 | 1830
Comilla(s) | 129 | 700 | 126 | 1800 | Rangpur | 132 | 500 | 114 | 1830
Comilla(n) | 137 | 800 | 134 | 2000 | Lalmonirhat | 130 | 600 | 108 | 1830
Chandpur | 130 | 700 | 126 | 1100 | Saidpur | 132 | 500 | 112 | 1830
Feni | 121 | 700 | 117 | 1800 | Purbasadipur | 139 | 700 | 124 | 1830
Chowmuhani | 125 | 700 | 118 | 1830 | Thakurgaon | 129 | 400 | 109 | 1830
Ashuganj | 138 | 800 | 135 | 1700 | Palashbari | 128 | 400 | 115 | 1830
Daudkandi | 131 | 700 | 126 | 1500 | Barapukuria | 135 | 300 | 127 | 1800
B.Baria | 135 | 700 | 130 | 1500 | Panchagar | 128 | 500 | 118 | 1830

## L-Curve
Date | 2018-10-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 50 | 5632 | 2130 | 7762 |  |  |  | QF-LDC-12
0:30 | 35 | 5566 | 2069.5 | 7635.5 | Date: | 2018-10-16
1:00 | 20 | 5500 | 2009 | 7509
1:30 | 30 | 5373.5 | 1969.5 | 7343
2:00 | 40 | 5247 | 1930 | 7177
2:30 | 40 | 5154.5 | 1874.5 | 7029 | [5 empty] | Gen. at Eve. Peak | 9886 | 9886 MW (19:00 )
3:00 | 40 | 5062 | 1819 | 6881 | [6 empty] | 19:00
3:30 | 70 | 4951 | 1797 | 6748 | [5 empty] | Gen. at Day Peak | 7746.1 | 7746.1 MW (12:00 )
4:00 | 100 | 4840 | 1775 | 6615 | [6 empty] | 12:00
4:30 | 85 | 4805 | 1765 | 6570 | [5 empty] | Highest Generation | 9886
5:00 | 70 | 4770 | 1755 | 6525 | [6 empty] | 19:00
5:30 | 60 | 4704.5 | 1725 | 6429.5
6:00 | 50 | 4639 | 1695 | 6334
6:30 | 155 | 4703 | 1619.5 | 6322.5
7:00 | 260 | 4767 | 1544 | 6311
7:30 | 255 | 4841.2 | 1570.5 | 6411.7
8:00 | 250 | 4915.4 | 1597 | 6512.4
8:30 | 215 | 5136.95 | 1596.5 | 6733.45
9:00 | 180 | 5358.5 | 1596 | 6954.5
9:30 | 150 | 5388.3 | 1739.5 | 7127.8
10:00 | 120 | 5418.1 | 1883 | 7301.1
10:30 | 120 | 5521 | 1908 | 7429
11:00 | 120 | 5623.9 | 1933 | 7556.9
11:30 | 90 | 5685.5 | 1966 | 7651.5
12:00 | 60 | 5747.1 | 1999 | 7746.1
12:30 | 35 | 5752.5 | 1999.5 | 7752
13:00 | 10 | 5757.9 | 2000 | 7757.9
13:30 | 45 | 5721.05 | 2018 | 7739.05
14:00 | 80 | 5684.2 | 2036 | 7720.2
14:30 | 140 | 5736 | 2105.5 | 7841.5
15:00 | 200 | 5787.8 | 2175 | 7962.8
15:30 | 230 | 5754.8 | 2168.5 | 7923.3
16:00 | 260 | 5721.8 | 2162 | 7883.8
16:30 | 280 | 5639.75 | 2160.5 | 7800.25
17:00 | 300 | 5557.7 | 2159 | 7716.7
17:30 | 180 | 6145.85 | 2423.5 | 8569.35
18:00 | 60 | 6734 | 2688 | 9422
18:30 | 140 | 6864 | 2790 | 9654
19:00 | 220 | 6994 | 2892 | 9886
19:30 | 230 | 6886 | 2794 | 9680
20:00 | 290 | 6838 | 2656 | 9494 |  |  |  | Executive Engineer
20:30 | 225 | 6704.5 | 2689 | 9393.5 |  |  |  | Network Operation Division
21:00 | 160 | 6571 | 2722 | 9293
21:30 | 100 | 6364.5 | 2616.5 | 8981
22:00 | 40 | 6158 | 2511 | 8669 |  |  |  |  | Page 6 of 7
22:30 | 25 | 6035 | 2381 | 8416
23:00 | 10 | 5912 | 2251 | 8163
23:30 | 30 | 5772 | 2190.5 | 7962.5
24:00 | 50 | 5632 | 2130 | 7762
9886 MW (19:00 )
7746.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-10-16 |  | Energy | 187103073
[10 empty] | 2018-10-16 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4572 | 758 | 1544 | 356 | 150 | 134 | 128 | 0 | 120
0:30 | 4449.5 | 760 | 1558 | 345 | 150 | 133 | 124 | 0 | 116 | Date: | 2018-10-16
1:00 | 4327 | 762 | 1572 | 334 | 150 | 132 | 120 | 0 | 112
1:30 | 4293.5 | 762 | 1516 | 258.5 | 150 | 132 | 120 | 0 | 111 | [7 empty] | Total Energy | 187.1031 | Total Energy Gen 187.103 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.103 MKWHr
2:00 | 4260 | 762 | 1460 | 183 | 150 | 132 | 120 | 0 | 110 | [7 empty] | Energy not Served | 0
2:30 | 4237 | 762 | 1345.5 | 174.5 | 150 | 132 | 120 | 0 | 108 | [7 empty] | Energy Requirement | 187.1031
3:00 | 4214 | 762 | 1231 | 166 | 150 | 132 | 120 | 0 | 106
3:30 | 4168 | 762 | 1163 | 148 | 150 | 132 | 120 | 0 | 105 | [6 empty] | Shortage
4:00 | 4122 | 762 | 1095 | 130 | 150 | 132 | 120 | 0 | 104
4:30 | 4077 | 762 | 1094.5 | 130 | 150 | 133.5 | 120 | 0 | 103
5:00 | 4032 | 762 | 1094 | 130 | 150 | 135 | 120 | 0 | 102
5:30 | 3959.5 | 762 | 1073 | 132 | 150 | 135 | 120 | 0 | 97
6:00 | 3887 | 762 | 1052 | 134 | 150 | 135 | 120 | 0 | 92
6:30 | 3947 | 651.5 | 1090.5 | 137.5 | 150 | 135 | 120 | 0 | 88 |  |  |  |  | Coal
7:00 | 4007 | 541 | 1129 | 141 | 150 | 135 | 120 | 0 | 84
7:30 | 4015.5 | 540.5 | 1156 | 202.5 | 149.5 | 135 | 120 | 0 | 85 |  |  |  | Oil |  |  |  | ,
8:00 | 4024 | 540 | 1183 | 264 | 149 | 135 | 120 | 0 | 86
8:30 | 4105 | 540.5 | 1274.5 | 304.5 | 149.5 | 135 | 120 | 0 | 90
9:00 | 4186 | 541 | 1366 | 345 | 150 | 135 | 120 | 0 | 94
9:30 | 4175 | 651.5 | 1377.5 | 401.5 | 150 | 135 | 120 | 0 | 98
10:00 | 4164 | 762 | 1389 | 458 | 150 | 135 | 120 | 0 | 102
10:30 | 4233 | 762 | 1412 | 492.5 | 150 | 135 | 120 | 0 | 103
11:00 | 4302 | 762 | 1435 | 527 | 150 | 135 | 120 | 0 | 104
11:30 | 4373.5 | 762 | 1438.5 | 547 | 150 | 135.5 | 120 | 0 | 104
12:00 | 4445 | 762 | 1442 | 567 | 150 | 136 | 120 | 0 | 104
12:30 | 4407 | 762 | 1426 | 622.5 | 150 | 136 | 120 | 0 | 108
13:00 | 4369 | 762 | 1410 | 678 | 150 | 136 | 120 | 0 | 112
13:30 | 4369 | 762 | 1410 | 678 | 150 | 136 | 120 | 0 | 112
14:00 | 4369 | 762 | 1410 | 678 | 150 | 136 | 120 | 0 | 112
14:30 | 4493 | 762 | 1371 | 701.5 | 149.5 | 134 | 120 | 0 | 114
15:00 | 4617 | 762 | 1332 | 725 | 149 | 132 | 120 | 0 | 116
15:30 | 4580.5 | 762 | 1332 | 725.5 | 149 | 132 | 122.5 | 0 | 112
16:00 | 4544 | 762 | 1332 | 726 | 149 | 132 | 125 | 0 | 108
16:30 | 4451.5 | 762 | 1278 | 772.5 | 149 | 132 | 142 | 0 | 110
17:00 | 4359 | 762 | 1224 | 819 | 149 | 132 | 159 | 0 | 112
17:30 | 4489 | 762 | 1437 | 1102.5 | 149.5 | 132 | 367 | 0 | 130
18:00 | 4619 | 762 | 1650 | 1386 | 150 | 132 | 575 | 0 | 148
18:30 | 4635 | 762 | 1648 | 1571 | 149.5 | 132 | 610.5 | 0 | 146
19:00 | 4651 | 762 | 1646 | 1756 | 149 | 132 | 646 | 0 | 144
19:30 | 4471 | 762 | 1562 | 1839 | 149 | 132 | 621 | 0 | 144
20:00 | 4506 | 761 | 1573 | 1816 | 149 | 132 | 415 | 0 | 142
20:30 | 4569 | 761.5 | 1631 | 1654 | 149 | 132 | 357 | 0 | 140
21:00 | 4632 | 762 | 1689 | 1492 | 149 | 132 | 299 | 0 | 138
21:30 | 4622.5 | 762 | 1573 | 1370 | 149.5 | 132 | 238 | 0 | 134
22:00 | 4613 | 762 | 1457 | 1248 | 150 | 132 | 177 | 0 | 130
22:30 | 4644 | 759.5 | 1459.5 | 992.5 | 150 | 131 | 152.5 | 0 | 127
23:00 | 4675 | 757 | 1462 | 737 | 150 | 130 | 128 | 0 | 124
23:30 | 4623.5 | 757.5 | 1503 | 546.5 | 150 | 132 | 128 | 0 | 122 | Max Temp. in Dhaka |  | 33.2° C
24:00 | 4572 | 758 | 1544 | 356 | 150 | 134 | 128 | 0 | 120
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.103 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.103 MKWHr
Note on W13: Author:

## Generation
2018-10-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 82 | 82 | 82 | 82 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 80 | 84 | 1928571
2 | Kaptai Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1179000
3 | Chittagong ST-1 (Raozan) | 150 | 150 | 150 | 150 | 150 | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3600000
4 | Chittgong ST-2 (Raozan) | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 | 140 | 140 | 140 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3600000
5 | Raozan 25 MW (RPCL) | 8 | 0 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 193680
| Teknaf Solartech 20MW | [5 empty] | 2 | 4 | 11 | 16.7 | 19.7 | 19.8 | 18 | 19 | 16.5 | 9.8 | 5.8 | 0.7 | 0 | [8 empty] | 138100
6 | Sikalbaha 225MW (Gas) | 228 | 228 | 229 | 227 | 205 | 202 | 203 | 202 | 204 | 204 | 216 | 204 | 204 | 205 | 218 | 202 | 203 | 211 |  | 202 | 202 | 214 | 202 | 209 | 203 | 202 | 4867856
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 0 | 47 |  | 49 | 31 | 16 | 0 | 0 |  |  | 110844
12 | Hathazari peaking | [17 empty] | 48 |  | 40 | 40 | 8 | 0 | 0 |  |  | 96348
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 17 | 15 | 17 | 15 | 15 | 17 | 15 | 15 | 17 | 17 | 17 | 32 | 47 | 45 | 45 | 45 | 62 | 172 |  | 170 | 172 | 171 | 172 | 117 | 60 | 55 | 1310000
19 | Ashuganj 195MW Modular | 68 | 68 | 15 | 12 | 12 | 8 | 8 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 77 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1555636
20 | Ghorasal ST: Unit-1,2 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1542000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4 | 258 | 258 | 257 | 258 | 257 | 264 | 265 | 262 | 264 | 257 | 257 | 255 | 254 | 254 | 253 | 253 | 253 | 253 |  | 201 | 200 | 200 | 196 | 204 | 262 | 256 | 6050000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 320 | 270 | 250 | 230 | 230 | 200 | 220 | 220 | 250 | 250 | 300 | 380 | 380 | 300 | 380 | 380 | 300 | 305 |  | 380 | 300 | 300 | 380 | 380 | 380 | 380 | 6228936
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2066174
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384695
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 41 | 41 | 41 | 25 | 25 | 25 | 25 | 802224
33 | Ashuganj CCPP 225 MW | 51 | 110 | 186 | 211 | 189 | 182 | 191 | 160 | 197 | 198 | 199 | 223 | 184 | 197 | 205 | 183 | 183 | 195 |  | 228 | 214 | 193 | 175 | 176 | 171 | 180 | 4321200
34 | Ashuganj CCPP(South) | 301 | 301 | 301 | 301 | 316 | 301 | 320 | 268 | 290 | 290 | 294 | 305 | 305 | 316 | 331 | 305 | 305 | 323 |  | 305 | 305 | 331 | 327 | 323 | 309 | 301 | 7414000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 330 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8967300
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 100 | 100 |  | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 2359700
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 511000
39 | Haripur 412 MW CCPP | 345 | 345 | 320 | 300 | 305 | 309 | 309 | 320 | 364 | 358 | 356 | 355 | 350 | 354 | 377 | 359 | 349 | 352 |  | 349 | 347 | 352 | 365 | 347 | 344 | 334 | 8299520
40 | Meghnaghat CCPP 450MW | 360 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 370 | 340 | 340 | 370 | 370 | 370 | 420 | 420 | 400 | 380 |  | 450 | 380 | 350 | 430 | 430 | 430 | 430 | 8818150
41 | Haripur Power CCPP 360MW | 303 | 302 | 262 | 232 | 232 | 212 | 242 | 223 | 291 | 291 | 356 | 352 | 316 | 316 | 351 | 322 | 272 | 307 |  | 322 | 306 | 326 | 353 | 355 | 358 | 357 | 7200000
42 | Mymensingh RPCL 210MW | 117 | 108 | 106 | 107 | 107 | 109 | 108 | 106 | 105 | 88 | 87 | 78 | 65 | 65 | 66 | 68 | 69 | 69 |  | 69 | 70 | 69 | 69 | 71 | 69 | 71 | 2068360
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 56 | 56 | 56 | 40 | 40 | 40 | 40 | 40 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 1222000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1886600
46 | Shajibazar 330 MW | 310 | 307 | 304 | 307 | 240 | 240 | 240 | 303 | 317 | 315 | 315 | 309 | 313 | 315 | 317 | 310 | 307 | 312 |  | 306 | 310 | 320 | 306 | 308 | 323 | 311 | 6902391
47 | Shahjibazar GT: Unit- 8, 9 | 48 | 40 | 40 | 40 | 67 | 65 | 62 | 67 | 65 | 65 | 64 | 56 | 55 | 63 | 62 | 62 | 62 | 63 |  | 62 | 67 | 67 | 67 | 66 | 66 | 66 | 1401000
48 | Shahjibazar 86MW | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 89 |  | 89 | 89 | 89 | 89 | 50 | 50 | 50 | 842880
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 46 |  | 46 | 47 | 47 | 47 | 5 | 5 | 5 | 415800
50 | Sylhet GT 150 MW | 78 | 79 | 77 | 77 | 77 | 78 | 78 | 79 | 79 | 78 | 78 | 78 | 78 | 78 | 78 | 98 | 78 | 126 |  | 98 | 98 | 98 | 98 | 77 | 78 | 80 | 2061700
51 | Sylhet GT 20 MW | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 123000
52 | Sylhet (EPL) 50MW | 45 | 45 | 22 | 5 | 5 | 5 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 42 | 42 | 44 |  | 43 | 43 | 45 | 45 | 6 | 6 | 30 | 517840
53 | Sylhet (Desh) 10MW | 9 | 0 | [15 empty] | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 56880
54 | Hobiganj 11MW | 11 | 11 | 6 | 3 | 3 | 3 | 5 | 0 | 5 | 5 | 8 | 8 | 8 | 0 | 0 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 170640
55 | Fenchugonj (Barakatullah) 51MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 13 | 14 | 44 |  | 44 | 44 | 44 | 44 | 5 | 5 | 5 | 393000
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 581520
57 | Summit Bibiana- 2 | 260 | 265 | 270 | 270 | 290 | 270 | 280 | 290 | 300 | 310 | 320 | 300 | 300 | 290 | 130 | 90 | 80 | 80 |  | 0 | 0 | 0 |  |  |  |  | 4805700
58 | Southern 55MW | 55 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 1006000
59 | Sikalbaha (Energis) | 24 | 0 | [5 empty] | 4 | 8 | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 |  | 32 | 40 | 40 | 40 | 40 | 40 | 8 | 628800
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 527768
61 | Narshingdi (Doreen) | 22 | 0 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 0 | 0 | 19 | 19 | 380052
62 | Tangail (Doreen) 22MW | [6 empty] | 0 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 372564
63 | Tripura | 112 | 110 | 106 | 104 | 102 | 92 | 84 | 86 | 94 | 102 | 104 | 104 | 112 | 114 | 116 | 108 | 112 | 148 |  | 144 | 144 | 142 | 138 | 130 | 124 | 120 | 2733120
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 5 | 5 | 2 | 2 | 2 | 6 | 4 | 2 | 2 | 3 | 8 |  | 7 | 8 | 26 | 35 | 37 | 40 | 38 | 512160
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 441000
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 0 | 8 | 8 | 8 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 173160
67 | Jangalia (Summit) 33MW | 8 | 0 | [5 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 311900
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 12 | 12 | 12 | 12 | 15 | 15 | 17 | 17 | 17 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 435000
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 732280
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 621100
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 681100
73 | Ghorashal (Regent) | 12 | 12 | 12 | 12 | 6 | 6 | 6 | 42 | 42 | 42 | 42 | 42 | 42 | 12 | 12 | 12 | 12 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 973841
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [7 empty] | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 30 | 50 | 50 | 7 | 7 | 0 |  | 258240
78 | Gazipur (RPCL) | 25 | 8 | 8 | 0 |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 25 | 38 |  | 40 | 42 | 42 | 42 | 25 | 0 |  | 365736
79 | Kodda 149 MW | [16 empty] | 6 | 64 |  | 64 | 64 | 48 | 0 | 0 |  |  | 183840
80 | Jamalpur 95MW | 7 | 0 | [14 empty] | 0 | 56 |  | 73 | 73 | 73 | 72 | 36 | 0 | 0 | 344640
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [11 empty] | 15 | 15 | 7 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 16 | 15 | 0 | 246000
83 | Pagla (DPA ) | [8 empty] | 11 | 10 | 10 | 11 | 10 | 11 | 10 | 10 | 10 | 10 |  | 0 | 0 | 0 |  |  |  |  | 95940
84 | B.Baria (Aggreko) 85MW | 85 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 6 | 5 | 5 | 85 |  | 85 | 85 | 85 | 85 | 50 | 50 | 50 | 246000
85 | Keraniganj (Powerpac) 100MW | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 26 |  | 92 | 100 | 100 | 10 | 10 | 0 |  | 456335
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [6 empty] | 0 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 27 | 49 | 48 | 20 | 7 | 7 | 0 | 219840
88 | Ghorashal 78MW (MAX) | 35 | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 |  | 80 | 80 | 79 | 80 | 81 | 80 | 80 | 1077216
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 50 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 1491480
92 | Fenchuganj (EPL) 44MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 32 |  | 46 | 44 | 44 | 47 | 5 | 5 | 5 | 354000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | [5 empty] | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 |  | 32 | 50 | 16 | 7 | 7 | 0 | 0 | 211248
95 | Patenga 50MW | 26 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 44 | 45 | 45 | 0 | 756960
96 | Chittagong ECPV 108 MW | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 51 | 51 | 52 | 52 | 65 | 93 |  | 93 | 93 | 93 | 93 | 95 | 35 | 12 | 987840
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 28 |  | 39 | 39 | 39 | 39 | 18 | 18 | 18 | 337056
98 | Bosila 108MW | 8 | 8 | 8 | 0 |  | 0 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 50 | 50 | 50 | 8 | 8 | 0 |  | 243840
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 23 | 41 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 15 | 15 | 15 | 0 | 657619
100 | Northern 55 MW | [7 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 55 | 55 | 55 | 55 | 55 | 18 | 0 | 487522
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 130 | 163 | 130 | 163 |  | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 3114221
102 | Sarishabari (Solar) | [6 empty] | 0 | 0.4 | 0.8 | 1.4 | 2.1 | 2.1 | 1.9 | 1.7 | 0 | 0 | 0 | [9 empty] | 10100
103 | Banco Energy 54MW | 18 | 18 | 18 | 0 |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 45 |  | 54 | 54 | 54 | 18 | 18 | 18 | 18 | 441360
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 36 | 17 | 17 | 17 | 17 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 46 | 46 | 45 | 45 | 48 | 144 |  | 168 | 180 | 182 | 173 | 163 | 173 | 65 | 1555200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 70 | 95 | 98 | 98 | 98 | 98 | 98 | 97 | 99 | 102 |  | 113 | 104 | 115 | 113 | 112 | 70 | 54 | 1673280
115
116
117
118
120 | Eastern Zone Total | 5500 | 5247 | 5062 | 4840 | 4770 | 4639 | 4767 | 4915.4 | 5358.5 | 5418.1 | 5623.9 | 5747.1 | 5757.9 | 5684.2 | 5787.8 | 5721.8 | 5557.7 | 6734 |  | 6994 | 6886 | 6838 | 6571 | 6158 | 5912 | 5632 | 136059603
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 49 | 49 | 49 | 32 | 32 | 0 |  | 324480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 8 | 43 |  | 37 | 37 | 37 | 37 | 5 | 0 |  | 162720
| Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3043200
129 | Labon Chora 105 MW | [15 empty] | 0 | 18 | 18 |  | 54 | 54 | 54 | 54 | 45 | 0 |  | 237600
130
131
132
133
| Summit Barisal 110 MW | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 110 |  | 110 | 110 | 110 | 110 | 80 | 16 | 0 | 769920
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 82 | 44 | 22 | 22 | 7 | 11 | 50 | 51 | 60 | 81 | 81 | 82 | 82 | 94 | 94 | 94 | 97 | 96 |  | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 1757389
| Bhola CCPP 194MW | 153 | 151 | 165 | 176 | 185 | 153 | 185 | 182 | 183 | 182 | 182 | 168 | 155 | 176 | 180 | 180 | 182 | 185 |  | 147 | 180 | 184 | 185 | 185 | 185 | 169 | 4267000
140 | Bhola (Venture) 33MW | 25 | 24 | 23 | 22 | 22 | 20 | 19 | 12 | 2 | 17 | 17 | 17 | 19 | 20 | 19 | 20 | 20 | 26 |  | 27 | 29 | 31 | 27 | 26 | 27 | 25 | 500029
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [7 empty] | 8 | 8 | 0 | [7 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 200250
143 | Gopalganj Peaking | [15 empty] | 5 | 25 | 41 |  | 75 | 68 | 48 | 48 | 7 | 0 |  | 240384
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 762 | 762 | 762 | 762 | 762 | 762 | 541 | 540 | 541 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 |  | 762 | 762 | 761 | 762 | 762 | 757 | 758 | 17840727
147 | Bheramara 360 MW | 360 | 360 | 300 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 300 | 330 | 300 | 300 | 412 | 416 | 350 | 419 |  | 426 | 300 | 300 | 420 | 427 | 425 | 425 | 8285472
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 |  | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 3653200
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 50 |  | 50 | 40 | 0 | 0 | 0 |  |  | 111784
157 | Sirajgonj Unit-1 225MW (Gas) | 175 | 177 | 160 | 151 | 152 | 152 | 152 | 150 | 157 | 189 | 188 | 183 | 189 | 184 | 194 | 185 | 176 | 180 |  | 219 | 219 | 219 | 220 | 219 | 221 | 188 | 4655155
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 137 | 103 | 91 | 66 | 51 | 51 | 51 | 66 | 50 | 50 | 50 | 101 | 123 | 123 | 138 | 124 | 120 | 123 |  | 150 | 150 | 150 | 150 | 150 | 150 | 124 | 2525818
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [17 empty] | 31 |  | 48 | 48 | 48 | 48 | 0 |  |  | 180540
162 | Bogra (GBB) | 21 | 18 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 408720
163 | Bogra (EPL) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 85824
164 | Ullapara (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 180792
165 | Amnura 50MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 555670
166 | Katakhali (Northern) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 24 | 457728
167 | Katakhali Peaking | [16 empty] | 0 | 38 |  | 38 | 38 | 40 | 38 | 37 | 0 |  | 176544
168 | Santahar Peaking | [16 empty] | 0 | 33 |  | 35 | 35 | 0 | 0 | 0 |  |  | 67798
169 | Rajlanka 52 MW | [16 empty] | 0 | 0 |  | 35 | 35 | 35 | 43 | 25 | 0 |  | 152640
170 | Chapainawabganj-100 MW | [16 empty] | 0 | 60 |  | 90 | 100 | 50 | 8 | 8 | 8 | 8 | 202086
171
172
173 | Rangpur GT | [16 empty] | 0 | 0 |  | 0
175 | Saidpur GT | [16 empty] | 0 | 0 |  | 0
176
177
178
178 | Western Zone Total | 2009 | 1930 | 1819 | 1775 | 1755 | 1695 | 1544 | 1597 | 1596 | 1883 | 1933 | 1999 | 2000 | 2036 | 2175 | 2162 | 2159 | 2688 | 0 | 2892 | 2794 | 2656 | 2722 | 2511 | 2251 | 2130 | 51043470