## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-10-13 | Saturday
|  | Date (day): | 2018-10-13 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10551 | MW |  |  | (b) At Evening Peak Hour : |  | 12679 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-10-12 | 2018-10-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 68 | 68 | 68 | 68 | 17 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 190 | 335 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 81 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 90 | 90 | 90 | 18 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 369 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 250 | 278 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 380 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 16 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100 |  | 0
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 90 | 90 |  | 10 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint. |  | 21/10/18
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 46 | 46 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 6 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 18 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 18 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 8 | 50 | 50 |  | 58 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 57 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 42 | 42 |  | 10 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 45 | 270 | 270 |  | 30 | Engine problem
35 | APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 0 | 100 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | Reserve
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | Reserve
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 30 | 94 | 110 | 110 |  | 39 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 1520 | 2090 | 3715 | 4420 | 390 | 1053
39 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 1.4 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 43 | 46 | 46 |  | 4 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 62 | 70 | 72 | 76 |  | 154 | #2,3,5 Under maint.
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 214 | 203 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint. |  | 14/10/2018
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 39 | 50 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 80
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 50
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 42 | 10 | 20
51 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 13 | 54 | 102 | 102 |  | 6
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 617.4 | 853 | 952 | 1076 | 80 | 354
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint.
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 153 | 226 | 225 | 225 |  |  | FGMO
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 330 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 279 | 360 | 360 |  |  | FGMO
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 41 | 41 | 41 | 4 |  | Gas shortage
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage.
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 24 | 68 | 127 |  | Gas Shortage.
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Devolopment work.
61 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 5 | 85 | 85 | 85
62 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 41 |  | 11
63 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 51 | 100 | 100
64 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
65 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 86 | 120 | 0 | 130
66 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
67 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
68 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 21 | 22 | 22
69 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1114 | 1409 | 1537 | 1952 | 243 | 251
70 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 89 | 105 | 105 | 105 | 97 |  | Gas shortage
71 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
72 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 7 | 7 | 71 | 71 |  | 24 | Engine problem.
73 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 2 | 0
74 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 46 | 144 | 150 | 160 |  | 40 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 142.7 | 278 | 350 | 358 | 97 | 24
75 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 68 | 68
76 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 36 | 36 | 30 | 60
77 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 130 | 130 |  |  | Engine problem
78 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 243 | 187 | 330 | 330
79 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 38 | 47 | 47
80 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 47 | 50 | 50
81 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
82 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 66 | 66
83 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 86 | 86 | 86
84 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 5 | 47 | 45 | 45 |  | 5
85 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 100 | 77 | 80 | 130 |  | 12
86 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 19 | 19
87 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 5 | 45 | 45 | 45 |  | 5
88 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 25 | 25
89 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 325 | 341 | 341 |  |  | FGMO
90 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 942 | 1137 | 1382 | 1462 | 0 | 22
91 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 522 | 724 | 528 | 747
92 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Contract expired
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 32
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 28 | 0 | 80
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 350 | 410 | 410
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 8 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| Labon Chora 105 MW |  | HFO | IPP | 105 | 0 | 0 | 108 | 108 | 36 | 108
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 1050 | 1354 | 1354 | 1889 | 0 | 0
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 80 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 32
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 28 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 75 | 154 | 156 | 156 |  | 38 | Machine problem.
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 81 | 93 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 175 | 355 | 364 | 426 | 0 | 38
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 53
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 40
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 150 | 150 | 210 | 210
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 169 | 132 | 220 | 220
113 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 0 | 0 | 0 | 0 |  | 141 | under maint.
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
114 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 39
115 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 5 | 22 | 22 | 22
116 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 12 | 12
117 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
118 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
119 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 25 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 341 | 477 | 727 | 909 | 71 | 241
120 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
121 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 170 | 170 | 104 |  | Coal shortage
122 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
123 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 150 | 170 | 187 | 189 | 85
| Total |  |  |  |  | 17043 | 16445 | 6052.1 | 8103 | 10551 | 12679 | 1070 | 2068
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5659.9795 | 7578 | 9867.3921 | 11857.5172
A. |  | 2018-10-12 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8103 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 5506.94 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8103 | MW
3 | Day peak Generation : |  |  | 6052.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7578 | MW
4 | Evening peak Generation : |  |  | 8103 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 159.7362 | MKWHr | By Solar | 0.0291 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 122.674 | MKWHr |  | By Oil: | 16.6188 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6958 | MKWHr |  | By Hydro: | 1.6259 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1070 | MW | Dhaka | 2801 | 2801 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2068 | MW | Chittagong | 840 | 840 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3138 | MW | Khulna | 977 | 977 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1007.98 |  | MMCFD |  |  | Rajshahi | 753 | 753 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88058465.89 | ii) Oil : | Taka | 131203659.45 | Comilla | 729 | 729 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14265788 | Total | Taka | 233527913.34 | Mymensingh | 519 | 519 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 0.7825 | MKWHr. | Sylhet | 275 | 275 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -310 | MW at | 20:00 | hrs | Barisal | 214 | 214 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -310 | MW at | 20:00 | hrs | Rangpur | 470 | 470 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.2° C |  |  | Total | 7578 | 7578 |  | 0
B. |  | 2018-10-13 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 30.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12679 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 3179 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 187.2756 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5397.7 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.8116 | MKWHr. | ii) HVDC Flow at Peak Time |  | 724 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.281 | MKWHr. | iii) Maximum HVDC Flow : |  | 724 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.56 |  | (b) Today: | 102.56 |  | (c) Rule Curve: |  | 107.1
.

## YesterdayGen
2018-10-12
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 68 | 0 | 0 | 0 | 380 | 94 | 40 | 345 | 363 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 43 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 80 | 12 | 18 | 22 | 31 | 100 | 100 | 0 | 360 | 309 | 191 | 8 | 100 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 100 | 50 | 7 | 22 | 0 | 58 | 73 | 11 | 50 | 130 | 228 | 67 | 10 | 47 | 79 | 0 | 45 | 9 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 67 | 0 |  | 466 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 127 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 17 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 175 | 0 | 220 | 0 | 53 | 0 | 0 | 0 | 0 | 108 |  | 5337 | 1866 | 7203 | 4186 | 466 | 1578 | 510 | 154 | 73 | 136 | 100 | 0 | 0 | 102.61
2:00 | 68 | 0 | 0 | 0 | 380 | 42 | 40 | 345 | 363 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 80 | 12 | 18 | 22 | 21 | 100 | 100 | 0 | 360 | 300 | 185 | 8 | 100 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 98 | 50 | 7 | 22 | 0 | 58 | 73 | 11 | 50 | 100 | 228 | 67 | 10 | 47 | 78 | 0 | 45 | 9 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 67 | 0 |  | 404 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 119 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 182 | 0 | 206 | 0 | 11 | 0 | 0 | 0 | 0 | 108 |  | 5216 | 1725 | 6941 | 4155 | 404 | 1430 | 494 | 154 | 70 | 136 | 98 | 0 | 0 | 102.6
3:00 | 68 | 0 | 0 | 0 | 300 | 42 | 35 | 345 | 325 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 90 | 12 | 18 | 22 | 30 | 100 | 100 | 0 | 360 | 300 | 183 | 8 | 95 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 96 | 50 | 7 | 22 | 0 | 58 | 73 | 11 | 50 | 100 | 230 | 55 | 10 | 47 | 78 | 0 | 44 | 9 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 40 | 0 |  | 404 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 119 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 182 | 0 | 158 | 0 | 12 | 0 | 0 | 0 | 0 | 108 |  | 5055 | 1679 | 6734 | 4010 | 404 | 1387 | 477 | 154 | 70 | 136 | 96 | 0 | 0 | 102.59
4:00 | 68 | 0 | 0 | 0 | 250 | 12 | 35 | 345 | 304 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 40 | 12 | 18 | 22 | 31 | 100 | 100 | 0 | 360 | 300 | 183 | 8 | 95 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 94 | 50 | 7 | 0 | 0 | 58 | 73 | 11 | 50 | 100 | 229 | 53 | 10 | 5 | 79 | 0 | 44 | 9 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 44 | 0 |  | 404 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 112 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 181 | 0 | 130 | 0 | 12 | 0 | 0 | 0 | 0 | 108 |  | 4825 | 1642 | 6467 | 3900 | 404 | 1294 | 415 | 154 | 70 | 136 | 94 | 0 | 0 | 102.58
5:00 | 68 | 0 | 0 | 0 | 250 | 12 | 35 | 346 | 306 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 40 | 12 | 6 | 22 | 32 | 100 | 100 | 0 | 360 | 309 | 189 | 8 | 95 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 90 | 50 | 7 | 0 | 0 | 58 | 73 | 5 | 5 | 100 | 227 | 54 | 5 | 5 | 78 | 0 | 6 | 0 | 285 | 25 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 44 | 0 |  | 404 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 128 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 184 | 0 | 130 | 0 | 12 | 0 | 0 | 0 | 0 | 108 |  | 4738 | 1631 | 6369 | 3903 | 404 | 1209 | 403 | 154 | 70 | 136 | 90 | 0 | 0 | 102.57
6:00 | 68 | 0 | 0 | 0 | 200 | 12 | 35 | 300 | 247 | 0 | 0 | 300 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 46 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 12 | 6 | 22 | 33 | 100 | 100 | 0 | 330 | 272 | 183 | 8 | 95 | 41 | 0 | 5 | 0 | 10 | 0 | 0 | 19 | 8 | 8 | 15 | 80 | 51 | 7 | 0 | 0 | 58 | 73 | 5 | 5 | 100 | 229 | 40 | 5 | 5 | 79 | 0 | 6 | 0 | 245 | 25 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 46 | 0.6 |  | 404 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 126 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 10 | 5 | 0 | 0 | 154 | 0 | 0 | 182 | 0 | 130 | 0 | 11 | 0 | 0 | 0 | 0 | 108 |  | 4436.6 | 1555 | 5991.6 | 3647 | 404 | 1069 | 431 | 154 | 70 | 136 | 80 | 0.6 | 0 | 102.56
7:00 | 68 | 0 | 0 | 0 | 180 | 12 | 35 | 300 | 222 | 0 | 0 | 300 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 46 | 6 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 0 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 12 | 6 | 22 | 36 | 90 | 90 | 0 | 330 | 272 | 183 | 8 | 95 | 21 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 8 | 8 | 15 | 80 | 51 | 7 | 0 | 0.3 | 30 | 60 | 5 | 5 | 100 | 227 | 40 | 5 | 5 | 79 | 0 | 5 | 0 | 250 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 30 | 2.3 |  | 404 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 127 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 174 | 0 | 130 | 0 | 11 | 0 | 0 | 0 | 0 | 108 |  | 4262.6 | 1530 | 5792.6 | 3503 | 404 | 1032 | 415 | 150 | 70 | 136 | 80 | 2.6 | 0 | 102.55
8:00 | 68 | 0 | 0 | 0 | 200 | 12 | 35 | 280 | 222 | 0 | 0 | 300 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 46 | 6 | 18 | 18 | 17 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 200 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 12 | 6 | 22 | 38 | 80 | 100 | 0 | 330 | 270 | 183 | 8 | 50 | 21 | 0 | 5 | 0 | 5 | 0 | 0 | 19 | 8 | 8 | 15 | 78 | 105 | 7 | 0 | 0.3 | 30 | 40 | 5 | 5 | 100 | 227 | 27 | 5 | 5 | 80 | 0 | 1 | 0 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 30 | 3.25 |  | 404 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 105 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 154 | 0 | 130 | 0 | 12 | 0 | 0 | 0 | 0 | 108 |  | 4273.55 | 1488 | 5761.55 | 3445 | 404 | 1060 | 415 | 150 | 70 | 136 | 78 | 3.55 | 0 | 102.54
9:00 | 68 | 0 | 0 | 0 | 170 | 12 | 20 | 280 | 240 | 0 | 0 | 280 | 0 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 45 | 6 | 18 | 18 | 17 | 22 | 25 | 24 | 0 | 33 | 0 | 0 | 42 | 30 | 150 | 130 | 0 | 183 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 20 | 12 | 6 | 22 | 33 | 80 | 100 | 0 | 330 | 270 | 150 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 8 | 15 | 76 | 88 | 7 | 0 | 0.4 | 30 | 36 | 5 | 5 | 100 | 248 | 40 | 5 | 1 | 80 | 0 | 1 | 0 | 260 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 30 | 4.54 |  | 404 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 11 | 0 | 0 | 0 | 0 | 108 |  | 4091.94 | 1415 | 5506.94 | 3255 | 404 | 1015 | 394 | 150 | 72 | 136 | 76 | 4.94 | 0 | 102.53
10:00 | 68 | 0 | 0 | 0 | 180 | 12 | 20 | 280 | 241 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 22 | 25 | 24 | 0 | 33 | 0 | 0 | 42 | 30 | 150 | 130 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 5 | 80 | 100 | 0 | 330 | 270 | 150 | 8 | 51 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 12 | 78 | 88 | 7 | 0 | 0.6 | 30 | 36 | 5 | 5 | 100 | 247 | 58 | 5 | 1 | 80 | 0 | 1 | 0 | 240 | 24 | 11 | 0 | 15 | 0 | 0 | 17 | 0 | 30 | 5.07 |  | 404 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 8 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 43 | 0 | 0 | 0 | 0 | 108 |  | 4040.67 | 1442 | 5482.67 | 3289 | 404 | 1041 | 323 | 150 | 72 | 120 | 78 | 5.67 | 0 | 102.52
11:00 | 68 | 0 | 0 | 0 | 180 | 12 | 20 | 330 | 240 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 22 | 25 | 24 | 0 | 33 | 0 | 0 | 72 | 30 | 150 | 130 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 5 | 80 | 100 | 0 | 330 | 270 | 152 | 8 | 51 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 12 | 80 | 87 | 7 | 0 | 0.4 | 30 | 36 | 8 | 5 | 100 | 242 | 65 | 5 | 1 | 80 | 0 | 1 | 0 | 295 | 24 | 3 | 0 | 15 | 0 | 0 | 34 | 0 | 30 | 2.82 |  | 522 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 63 | 0 | 0 | 0 | 0 | 108 |  | 4192.22 | 1607 | 5799.22 | 3367 | 522 | 1115 | 340 | 150 | 102 | 120 | 80 | 3.22 | 0 | 102.51
12:00 | 68 | 0 | 0 | 0 | 190 | 12 | 20 | 370 | 250 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 0 | 25 | 20 | 25 | 33 | 0 | 0 | 32 | 30 | 150 | 130 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 0 | 22 | 5 | 80 | 100 | 0 | 330 | 270 | 153 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 9 | 86 | 89 | 7 | 0 | 0.7 | 30 | 36 | 8 | 5 | 100 | 243 | 65 | 5 | 5 | 100 | 0 | 5 | 0 | 310 | 22 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 30 | 1.4 |  | 522 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 169 | 0 | 81 | 0 | 0 | 0 | 0 | 108 |  | 4336.1 | 1716 | 6052.1 | 3549 | 522 | 1208 | 353 | 150 | 62 | 120 | 86 | 2.1 | 0 | 102.5
13:00 | 68 | 0 | 0 | 0 | 250 | 12 | 20 | 370 | 260 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 45 | 6 | 18 | 0 | 17 | 22 | 25 | 20 | 25 | 33 | 0 | 0 | 32 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 7 | 80 | 100 | 0 | 330 | 270 | 153 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 12 | 92 | 89 | 7 | 22 | 0.2 | 30 | 36 | 5 | 5 | 100 | 225 | 66 | 5 | 5 | 120 | 0 | 5 | 0 | 300 | 22 | 8 | 0 | 15 | 0 | 0 | 65 | 0 | 30 | 6.81 |  | 522 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 195 | 0 | 83 | 0 | 0 | 0 | 0 | 108 |  | 4458.01 | 1821 | 6279.01 | 3720 | 522 | 1220 | 386 | 150 | 62 | 120 | 92 | 7.01 | 0 | 102.49
14:00 | 68 | 0 | 0 | 0 | 250 | 12 | 20 | 348 | 241 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 45 | 6 | 18 | 0 | 17 | 0 | 25 | 0 | 25 | 24 | 0 | 0 | 32 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 7 | 80 | 100 | 0 | 330 | 272 | 152 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 12 | 86 | 107 | 7 | 22 | 0.3 | 30 | 36 | 5 | 5 | 100 | 186 | 67 | 5 | 5 | 80 | 0 | 6 | 0 | 265 | 22 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 30 | 0.9 |  | 522 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 133 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 173 | 0 | 63 | 0 | 0 | 0 | 0 | 108 |  | 4212.2 | 1790 | 6002.2 | 3574 | 522 | 1120 | 367 | 150 | 62 | 120 | 86 | 1.2 | 0 | 102.48
15:00 | 68 | 0 | 0 | 0 | 250 | 12 | 20 | 345 | 240 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 0 | 25 | 6 | 25 | 24 | 0 | 0 | 32 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 7 | 80 | 100 | 0 | 330 | 272 | 152 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 12 | 86 | 106 | 7 | 22 | 0.2 | 30 | 36 | 7 | 5 | 100 | 190 | 42 | 5 | 5 | 80 | 0 | 6 | 0 | 275 | 24 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 30 | 0.5 |  | 522 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 126 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 132 | 0 | 63 | 0 | 0 | 0 | 0 | 108 |  | 4209.7 | 1741 | 5950.7 | 3512 | 522 | 1130 | 368 | 150 | 62 | 120 | 86 | 0.7 | 0 | 102.47
16:00 | 68 | 0 | 0 | 0 | 200 | 12 | 20 | 345 | 242 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 0 | 25 | 6 | 25 | 24 | 0 | 0 | 30 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 10 | 80 | 100 | 0 | 330 | 272 | 152 | 8 | 51 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 13 | 84 | 106 | 7 | 22 | 0.2 | 30 | 36 | 5 | 5 | 100 | 186 | 48 | 5 | 5 | 79 | 0 | 6 | 0 | 290 | 24 | 8 | 0 | 12 | 0 | 0 | 46 | 0 | 30 | 0.2 |  | 522 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 138 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 22 | 0 | 0 | 0 | 0 | 108 |  | 4143.4 | 1659 | 5802.4 | 3425 | 522 | 1076 | 365 | 150 | 60 | 120 | 84 | 0.4 | 0 | 102.47
17:00 | 68 | 0 | 0 | 0 | 200 | 12 | 20 | 366 | 233 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 36 | 22 | 25 | 20 | 25 | 24 | 0 | 0 | 30 | 30 | 150 | 130 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 22 | 10 | 80 | 100 | 0 | 330 | 287 | 152 | 8 | 51 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 13 | 92 | 105 | 7 | 22 | 0 | 30 | 36 | 5 | 5 | 100 | 190 | 59 | 5 | 5 | 78 | 0 | 6 | 0 | 280 | 23 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 30 | 0 |  | 573 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 50 | 0 | 154 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 22 | 0 | 0 | 0 | 0 | 108 |  | 4252 | 1786 | 6038 | 3539 | 573 | 1059 | 395 | 150 | 60 | 170 | 92 | 0 | 0 | 102.46
18:00 | 68 | 0 | 0 | 0 | 200 | 83 | 60 | 356 | 231 | 0 | 0 | 300 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 98 | 6 | 31 | 46 | 6 | 18 | 18 | 36 | 22 | 25 | 20 | 25 | 33 | 8 | 0 | 30 | 30 | 150 | 130 | 26 | 200 | 0 | 0 | 0 | 0 | 7 | 40 | 34 | 90 | 76 | 1 | 22 | 10 | 80 | 100 | 0 | 330 | 250 | 228 | 8 | 51 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 14 | 116 | 106 | 42 | 22 | 0 | 30 | 36 | 27 | 18 | 100 | 186 | 45 | 86 | 46 | 78 | 19 | 44 | 7 | 300 | 24 | 8 | 0 | 37 | 0 | 0 | 168 | 0 | 72 | 0 |  | 723 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 43 | 87 | 8 | 154 | 26 | 100 | 0 | 0 | 0 | 22 | 25 | 84 | 50 | 50 | 20 | 8 | 25 | 22 | 0 | 8 | 0 | 0 | 150 | 17 | 0 | 150 | 0 | 133 | 0 | 22 | 0 | 0 | 0 | 0 | 108 |  | 5438 | 2421 | 7859 | 3657 | 723 | 1480 | 1058 | 150 | 60 | 615 | 116 | 0 | 0 | 102.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 68 | 0 | 0 | 0 | 200 | 94 | 81 | 348 | 231 | 0 | 0 | 300 | 0 | 7 | 12 | 7 | 0 | 0 | 0 | 0 | 2 | 7 | 48 | 10 | 8 | 46 | 6 | 18 | 18 | 55 | 22 | 25 | 24 | 25 | 33 | 26 | 0 | 38 | 30 | 150 | 130 | 25 | 202 | 0 | 0 | 0 | 0 | 23 | 40 | 16 | 100 | 97 | 28 | 22 | 32 | 80 | 100 | 0 | 330 | 272 | 226 | 8 | 51 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 14 | 120 | 106 | 24 | 22 | 0 | 30 | 36 | 38 | 50 | 100 | 186 | 67 | 86 | 46 | 78 | 19 | 45 | 7 | 280 | 25 | 8 | 0 | 75 | 0 | 0 | 168 | 0 | 94 | 0 |  | 723 | 0 | 250 | 0 | 16 | 120 | 0 | 0 | 30 | 55 | 8 | 154 | 28 | 80 | 0 | 0 | 0 | 26 | 30 | 25 | 50 | 50 | 23 | 16 | 33 | 22 | 1 | 8 | 0 | 0 | 150 | 17 | 18 | 150 | 0 | 130 | 0 | 88 | 0 | 0 | 0 | 0 | 108 |  | 5639 | 2409 | 8048 | 3695 | 723 | 1627 | 1184 | 150 | 68 | 481 | 120 | 0 | 0 | 102.45
19:30 | 68 | 0 | 0 | 0 | 250 | 87 | 81 | 361 | 251 | 0 | 0 | 320 | 0 | 7 | 16 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 46 | 6 | 18 | 18 | 55 | 22 | 25 | 24 | 25 | 33 | 26 | 0 | 40 | 30 | 150 | 130 | 26 | 224 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 100 | 100 | 40 | 22 | 37 | 80 | 100 | 0 | 330 | 276 | 226 | 8 | 51 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 17 | 120 | 106 | 7 | 22 | 0 | 30 | 36 | 38 | 47 | 100 | 187 | 66 | 86 | 47 | 77 | 19 | 45 | 7 | 325 | 24 | 8 | 0 | 45 | 0 | 0 | 168 | 0 | 94 | 0 |  | 723 | 0 | 300 | 0 | 16 | 120 | 0 | 0 | 5 | 50 | 8 | 154 | 28 | 80 | 0 | 0 | 0 | 0 | 25 | 25 | 50 | 50 | 23 | 16 | 33 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 132 | 0 | 91 | 0 | 0 | 0 | 0 | 108 |  | 5711 | 2367 | 8078 | 3837 | 723 | 1710 | 1187 | 150 | 70 | 281 | 120 | 0 | 0 | 0
20:00 | 68 | 0 | 0 | 0 | 335 | 90 | 81 | 369 | 278 | 0 | 0 | 380 | 0 | 7 | 16 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 46 | 6 | 18 | 18 | 55 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 100 | 54 | 43 | 22 | 42 | 80 | 100 | 0 | 330 | 279 | 226 | 8 | 51 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 120 | 105 | 7 | 22 | 0 | 30 | 36 | 38 | 47 | 100 | 187 | 67 | 86 | 47 | 77 | 19 | 45 | 9 | 325 | 24 | 0 | 0 | 45 | 0 | 0 | 144 | 0 | 94 | 0 |  | 724 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 8 | 154 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 24 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 132 | 0 | 93 | 0 | 0 | 0 | 0 | 108 |  | 5767 | 2336 | 8103 | 3966 | 724 | 1809 | 1067 | 150 | 70 | 197 | 120 | 0 | 0 | 102.45
21:00 | 68 | 0 | 0 | 0 | 380 | 91 | 81 | 347 | 281 | 0 | 0 | 380 | 0 | 7 | 16 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 45 | 6 | 18 | 18 | 36 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 15 | 24 | 22 | 42 | 80 | 100 | 0 | 330 | 250 | 223 | 16 | 91 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 120 | 106 | 7 | 22 | 0 | 30 | 36 | 38 | 47 | 100 | 190 | 66 | 86 | 47 | 79 | 19 | 45 | 9 | 310 | 25 | 0 | 0 | 15 | 0 | 0 | 105 | 0 | 32 | 0 |  | 724 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 10 | 8 | 153 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 32 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 132 | 0 | 93 | 0 | 0 | 0 | 0 | 108 |  | 5546 | 2255 | 7801 | 4001 | 724 | 1806 | 775 | 150 | 70 | 155 | 120 | 0 | 0 | 102.44
22:00 | 68 | 0 | 0 | 0 | 380 | 90 | 40 | 347 | 282 | 0 | 0 | 380 | 0 | 7 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 18 | 18 | 36 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 215 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 12 | 6 | 22 | 42 | 80 | 100 | 0 | 330 | 287 | 228 | 16 | 91 | 41 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 33 | 21 | 112 | 105 | 7 | 22 | 0 | 30 | 36 | 5 | 47 | 100 | 187 | 67 | 50 | 5 | 76 | 19 | 45 | 9 | 290 | 24 | 0 | 0 | 15 | 0 | 0 | 57 | 0 | 32 | 0 |  | 723 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 155 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 130 | 0 | 96 | 0 | 0 | 0 | 0 | 108 |  | 5236 | 2139 | 7375 | 4046 | 723 | 1601 | 553 | 150 | 70 | 120 | 112 | 0 | 0 | 102.44
23:00 | 68 | 0 | 0 | 0 | 380 | 94 | 40 | 353 | 282 | 0 | 0 | 380 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 29 | 25 | 17 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 15 | 12 | 6 | 22 | 42 | 80 | 100 | 0 | 330 | 250 | 207 | 16 | 90 | 25 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 106 | 0 | 22 | 0 | 30 | 36 | 5 | 47 | 100 | 186 | 63 | 50 | 5 | 78 | 20 | 45 | 9 | 310 | 24 | 0 | 0 | 15 | 0 | 0 | 9 | 0 | 0 | 0 |  | 724 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 156 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 132 | 0 | 96 | 0 | 0 | 0 | 0 | 108 |  | 4918 | 2076 | 6994 | 3944 | 724 | 1618 | 281 | 149 | 70 | 120 | 88 | 0 | 0 | 102.43
24:00 | 68 | 0 | 0 | 0 | 380 | 94 | 40 | 355 | 283 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 202 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 15 | 4 | 6 | 22 | 42 | 80 | 100 | 0 | 330 | 250 | 192 | 16 | 85 | 10 | 0 | 5 | 0 | 50 | 0 | 0 | 19 | 8 | 8 | 15 | 82 | 106 | 0 | 22 | 0 | 30 | 36 | 5 | 47 | 100 | 185 | 58 | 10 | 5 | 80 | 0 | 45 | 0 | 275 | 24 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 724 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 143 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 19 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 150 | 0 | 132 | 0 | 94 | 0 | 0 | 0 | 0 | 108 |  | 4704 | 2033 | 6737 | 3873 | 724 | 1529 | 190 | 149 | 70 | 120 | 82 | 0 | 0 | 102.43
KWH | 1223000 | 0 | 0 | 0 | 6185490 | 959727 | 1086624 | 8278490 | 6385000 | 0 | 0 | 8256375 | 0 | 116160 | 221232 | 180625 | 0 | 0 | 0 | 0 | 107860 | 199872 | 266880 | 52021 | 201600 | 710410 | 153408 | 419760 | 264384 | 581000 | 404388 | 600000 | 584820 | 716200 | 788300 | 55236 | 0 | 900996 | 724900 | 3500000 | 3200000 | 55440 | 4802021 | 0 | 0 | 0 | 0 | 288000 | 101928 | 39945 | 1100520 | 507840 | 247680 | 530448 | 649440 | 2115604 | 2444065 | 0 | 8429000 | 6675500 | 4401000 | 234182 | 1686850 | 631296 | 0 | 120000 | 0 | 221232 | 0 | 0 | 275544 | 210600 | 287700 | 360330 | 2280960 | 2030240 | 213120 | 322200 | 3300 | 908000 | 1103520 | 288600 | 568000 | 2855847 | 4828119 | 1347000 | 612480 | 463320 | 1989300 | 104000 | 565740 | 83520 | 7301700 | 579840 | 187152 | 0 | 474220 | 0 | 0 | 1142400 | 0 | 1031040 | 25800 |  | 12811636 | 0 | 7481952 | 0 | 68160 | 3064322 | 0 | 0 | 76800 | 219392 | 35250 | 2787977 | 509600 | 696000 | 0 | 0 | 0 | 36488 | 64845 | 150208 | 461520 | 237936 | 56257 | 74880 | 66133 | 331200 | 62748 | 147510 | 0 | 0 | 3695800 | 28000 | 17000 | 4114273 | 0 | 3704463 | 0 | 1152501 | 0 | 0 | 0 | 0 | 2533000 |  | 115050341 | 44685851 | 159736192 | 89966192 | 12811636 | 32707836 | 12430574 | 3695800 | 1625896 | 4188198 | 2280960 | 29100 | 0
Fuel Cost | 1051780 | 0 | 0 | 0 | 3958713.6 | 777378.87 | 1021426.56 | 5049878.9 | 3894850 | 0 | 0 | 5531771.25 | 0 | 729484.8 | 1477829.76 | 1103618.75 | 0 | 0 | 0 | 0 | 674125 | 1317156.48 | 2580729.6 | 331373.77 | 1207584 | 11359455.9 | 1023231.36 | 2992888.8 | 1652400 | 3642870 | 303291 | 450000 | 0 | 0 | 0 | 522532.56 | 0 | 0 | 0 | 3850000 | 3520000 | 525016.8 | 3169333.86 | 0 | 0 | 0 | 0 | 2531520 | 1097764.56 | 388664.85 | 6812218.8 | 3280646.4 | 1619827.2 | 450880.8 | 0 | 1925199.64 | 2224099.15 | 0 | 5225980 | 4606095 | 3080700 | 161585.58 | 1619376 | 422968.32 | 0 | 110400 | 0 | 210170.4 | 0 | 0 | 212168.88 | 157950 | 221529 | 270247.5 | 15601766.4 | 1522680 | 1958572.8 | 248094 | 0 | 944320 | 1147660.8 | 277056 | 511200 | 2227560.66 | 3379683.3 | 1535580 | 655353.6 | 509652 | 2267802 | 133120 | 526138.2 | 77673.6 | 4673088 | 434880 | 142235.52 | 0 | 3442837.2 | 0 | 0 | 8168160 | 0 | 0 | 0 |  | 65339343.6 | 0 | 5012907.84 | 0 | 565046.4 | 49274297.76 | 0 | 0 | 864768 | 2584437.76 | 277770 | 1923704.13 | 504504 | 5150400 | 0 | 0 | 0 | 417787.6 | 695138.4 | 1345863.68 | 3992148 | 2117630.4 | 599137.05 | 742809.6 | 778385.41 | 364320 | 58983.12 | 111665.07 | 0 | 0 | 14265788 | 902440 | 455090 | 2797705.64 | 0 | 2593124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150733827.78 | 163735195.56 | 314469023.34 | 65965354.05 | 65339343.6 | 22093111.84 | 69219154.78 | 14265788 | 0 | 61984504.67 | 15601766.4 | 0 | 0
Yesterday Day Peak | 68 | 0 | 0 | 0 | 190 | 12 | 20 | 370 | 250 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 46 | 6 | 18 | 0 | 17 | 0 | 25 | 20 | 25 | 33 | 0 | 0 | 32 | 30 | 150 | 130 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 0 | 22 | 5 | 80 | 100 | 0 | 330 | 270 | 153 | 8 | 50 | 10 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 9 | 86 | 89 | 7 | 0 | 0.7 | 30 | 36 | 8 | 5 | 100 | 243 | 65 | 5 | 5 | 100 | 0 | 5 | 0 | 310 | 22 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 30 | 1.4 |  | 522 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 75 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 169 | 0 | 81 | 0 | 0 | 0 | 0 | 108 |  | 6052.1 | DayPeak
Yesterday Evening Peak | 68 | 0 | 0 | 0 | 335 | 90 | 81 | 369 | 278 | 0 | 0 | 380 | 0 | 7 | 16 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 46 | 6 | 18 | 18 | 55 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 30 | 150 | 130 | 0 | 203 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 100 | 54 | 43 | 22 | 42 | 80 | 100 | 0 | 330 | 279 | 226 | 8 | 51 | 41 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 120 | 105 | 7 | 22 | 0 | 30 | 36 | 38 | 47 | 100 | 187 | 67 | 86 | 47 | 77 | 19 | 45 | 9 | 325 | 24 | 0 | 0 | 45 | 0 | 0 | 144 | 0 | 94 | 0 |  | 724 | 0 | 350 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 8 | 154 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 24 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 132 | 0 | 93 | 0 | 0 | 0 | 0 | 108 |  | 8103 | EvPeak
Forecast for Evening | 68 | 0 | 0 | 0 | 380 | 90 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 90 | 102 | 149 | 100 | 50 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 46 | 30 | 150 | 130 | 25 | 225 | 0 | 0 | 0 | 0 | 50 | 80 | 50 | 100 | 102 | 46 | 22 | 20 | 100 | 100 | 0 | 360 | 360 | 225 | 68 | 100 | 41 | 0 | 5 | 0 | 85 | 41 | 52 | 19 | 11 | 33 | 22 | 130 | 105 | 71 | 22 | 0 | 68 | 60 | 47 | 50 | 130 | 330 | 66 | 86 | 45 | 130 | 19 | 45 | 9 | 341 | 25 | 11 | 200 | 270 | 300 | 100 | 160 | 100 | 110 | 0 |  | 747 | 32 | 410 | 0 | 115 | 225 | 0 | 0 | 32 | 80 | 40 | 156 | 33 | 110 | 32 | 0 | 0 | 50 | 53 | 100 | 50 | 50 | 40 | 52 | 39 | 22 | 12 | 11 | 0 | 0 | 170 | 17 | 0 | 210 | 0 | 220 | 0 | 95 | 100 | 0 |  | 0 | 108
Forecast for Day | 68 | 0 | 0 | 0 | 380 | 90 | 78 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 90 | 102 | 149 | 100 | 50 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 42 | 30 | 150 | 130 | 25 | 225 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 100 | 102 | 46 | 22 | 10 | 100 | 100 | 0 | 360 | 360 | 225 | 24 | 100 | 41 | 0 | 5 | 0 | 85 | 0 | 52 | 19 | 11 | 33 | 22 | 0 | 105 | 71 | 22 | 2 | 68 | 30 | 47 | 50 | 130 | 330 | 66 | 86 | 45 | 80 | 19 | 45 | 9 | 341 | 25 | 11 | 0 | 270 | 100 | 0 | 150 | 0 | 110 | 20 |  | 528 | 0 | 410 | 0 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 156 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 50 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 0 | 170 |  | 0 | 210 | 0 | 220 | 0 | 95 | 0 | 0 |  | 0 | 36
Generation at 08:00(Today) | 68 | 0 | 0 | 0 | 250 | 6 | 20 | 380 | 353 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 2 | 0 | 33 | 30 | 150 | 130 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 6 | 22 | 8 | 80 | 100 | 0 | 360 | 272 | 201 | 8 | 100 | 10 | 0 | 5 | 0 | 10 | 0 | 0 | 10 | 5 | 0 | 12 | 0 | 160 | 0 | 0 | 0 | 58 | 30 | 5 | 30 | 100 | 211 | 61 | 5 | 2 | 78 | 0 | 5 | 0 | 310 | 24 | 0 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | 484 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 150 | 0 | 0 | 169 | 0 | 151 | 0 | 12 | 0 | 0 | 0 | 0 | 36 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [66 empty] | 199
| Minimum Generation |  | 5506.94 | 9:00
| Highest Generation |  | 8103 | 20:00
| Day Peak Generation |  | 6052.1 | 12:00
| Evening Peak Generation |  | 8103 | 20:00
| HVDC Max Flow |  | 724 | 20:00
| HVDC EvPeak Flow |  | 724 | 20:00
| Load factor L.F |  | 82.14%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-10-13
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-10-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6052.1 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 5397.7 | MW
Evening Peak Generation : |  | 8103 | MW Hour : | 20:00 | Available Max Generation : |  | 12679 | MW
E.P. Demand (at gen end) : |  | 8103 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 8103 | MW Hour : | 20:00 | Reserve(Generation end) |  | 3179 | MW
Total Gen. (MKWH) : |  | 159.7362 | System Load Factor : | 82.14% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -310 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-10-13
Actual : | 102.56 | Ft.(MSL) , | Rule curve : | 107.1 | Ft.( MSL )
Gas Consumed : | Total = | 1007.98 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88058465.89
|  | Coal : | 14265788 | Oil : | 131203659.45 | Total : | 233527913.34
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3318.2616 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1123.8274 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1006.0986 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 908.8062 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 821.4342 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 662.8568 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 376.5116 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 170.8233 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 511.2 |  |  | 0 | 0%
Total | 0 |  | 8899.8199 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Kaptai #5
|  |  |  | 3) Ghorasal Unit-3,4,5 |  | 11) Siddhirganj CCPP-335 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Sirajganj unit-3 255 MW
|  |  |  | 5) Tongi GT |  | 13) Ashuganj (Precision) 55 MW
6) Ashuganj Midland 51 MW
7) Baghabari-71 MW
8) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bibiyana-Shahjibazar 230 kV Ckt-2 was under shut down from 08:51 to 17:28 for D/W.
b) Ashuganj-Kishoreganj 132 kV Ckt-1 was under shut down since11:01 for D/W.
c) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 12:04 to 12:35 for D/W.
d) After maintenance Kaptai unit-1 was synchronized at 10:49.
e) After maintenance Bhola STG(with GT-2) was synchronized at 13:16.
f) Kaptai-3 was shut down at 11:13 for maintenance work.
g) After maint Haripur-Bhulta 132 kV Ckt-2 was switched on 15:13 from both end.
h) After maint Aggreko(Brahamongaon)-Shyampur 230/132 kV S/S 132 kV Ckt was switched on 17:40 from Aggreko end.
i) After maint Shyampur 230/132 kV S/S 132 kV bus-1 was switched on 17:45 .
j) After maint Shyampur 230/132 kV S/S 132 kV bus-2 was switched on 17:49 .
k) After maint Shyampur 230/132 kV S/S-Shyampur 132/33 kV S/S 132 kV Ckt was switched on 17:59 .
l) Bagerhat 132/33 kV T3 transformer was shut down from 19:28 to 21:41 due to red hot maint at 33 kV Y-phase CT. |  |  |  | About 05 MW Power interruption occurred under Bagerhat S/S
area from 19:28 to 21:41.
m) After maint Shyampur 230/132/33 kV 300MVA T-1 transformer was switched on 20:28 .
n) Kabirpur 132/33 kV T2 transformer was shut down from 10:42 to 20:13 due to problem with 33 kV incoming breaker.
o) Kulaura 132/33 kV T1 transformer tripped at 20:40 from 132 kV side showing O/C relay and was switched on at 20:59.
p) After maint Bagerhat-Bhandaria 132 kV Ckt was switched on at 22:20.
q) Comilla(S)-Tripura 132 kV Ckt-1,2 was under shut down since 06:02(13/10/2018) for C/M. |  |  |  | About 70 MW Power interruption occurred under Comilla(S) S/S
r) Comilla(n)-Feni 132 kV Ckt-2 was under shut down since 06:41(13/10/2018) for C/M. |  |  |  | area since 06:02 (13/10/2018).
s) Hathazari 132/33 kV T2 transformer was shut down from 06:25 to 07:10(13/10/2018) for C/M.
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-10-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 68 | 1223000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 335 | 6185490 | Low demand
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 81 | 1086624
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 90 | 959727 | Engine problem
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 369 | 8278490 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 278 | 6385000 | Low demand
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 380 | 8256375 | Frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 7 | 116160 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 16 | 221232 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 180625 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 10 | 52021 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 404388
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 107860 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 46 | 710410 | Low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 199872 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 6 | 153408 | Low demand
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 18 | 419760 | Low demand
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 266880 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 18 | 264384 | Low demand
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 581000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 201600 | Low demand
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1184820 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 716200
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 788300
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 55236 | Reserve
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 45 | 474220 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 0 | 0 | Rererve.
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 94 | 1031040 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 2090 | 40504122
39 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3500000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 130 | 3200000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 0 | 55440 | Reserve
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 25800
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 43 | 247680 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1625896 | Unit-5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4802021
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 39 | 288000 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 101928 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 0 | 39945 | Reserve
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1100520
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 530448
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 649440
51 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 54 | 507840 | Low demand
| Chittagong area Total |  |  |  | 1561 | 853 | 16674958
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2115604 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2444065 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 226 | 4401000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 8429000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 279 | 6675500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 41 | 631296
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 234182 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Under maint.
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 221232
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1686850 | ST Under maint.
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 275544
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210600
** | Tripura |  | Imported power | 0 | 160 | 120 | 2280960 | Low demand
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 287700
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 360330
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Comilla Area Total |  |  |  | 2541 | 1409 | 30373863
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 105 | 2030240 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 322200
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 7 | 213120 | Low demand
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 3300
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 144 | 1142400 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 278 | 3711260
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 908000 | Low demand
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 36 | 1103520 | Low demand
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 2855847 | Frequency control.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 187 | 4828119 | FGMO.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 38 | 288600 | Engine problem
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 568000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 0 | 187152
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 67 | 1347000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 612480
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 463320
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 77 | 1989300 | Frequency control.
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 104000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 45 | 565740 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 579840
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 325 | 7301700 | FGMO
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 83520
| Sylhet Area Total |  |  |  | 1549 | 1137 | 23786138
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 724 | 12811636
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 68160 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 0 | 76800 | Reserve
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3064322 | Low demand
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 28 | 219392 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 350 | 7481952 | Frequency control.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 8 | 35250 | Low demand
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 105 | 0 | 108 | 2533000 | RRT
| Khulna Area Total |  |  |  | 2214 | 1354 | 26290512
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 696000 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 28 | 509600 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 154 | 2787977
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 93 | 1152501
| Barisal Area Total |  |  |  | 462 | 355 | 5146078
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 36488 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 64845 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 461520
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 237936
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 24 | 56257 | Low demand
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 4114273 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3704463 | FGMO.
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 | 0 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 66133 | Reserve
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 331200
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 0 | 62748 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 147510
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 16 | 74880 | Low demand
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 25 | 150208 | Low demand
| Rajshahi Area Total |  |  |  | 1264 | 477 | 9508461
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 150 | 3695800 | Coal shortage
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 28000 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 17000
| Rangpur Area Total |  |  |  | 484 | 150 | 3740800
| Total |  |  |  | 16445 | 8103 | 159736192
| Eastern Grid Total |  |  |  | 12021 | 5767 | 115050341
| Western Grid Total |  |  |  | 4424 | 2336 | 44685851
| National Grid Total |  |  |  | 16445 | 8103 | 159736192
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-10-12 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5164 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2414 | MW
i) Dhaka area |  |  | 2801 | MW | i) Khulna area |  |  | 977 | MW
ii) Chittagong area |  |  | 840 | MW | ii) Rajshahi area |  |  | 753 | MW
iii) Comilla area |  |  | 729 | MW | iii) Barisal area |  |  | 214 | MW
iv) Mymensingh area |  |  | 519 | MW | iv) Rangpur area |  |  | 470 | MW
v) Sylhet area |  |  | 275 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7578 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 86 | 100 | Netrokona | 59 | 1800 | Central s/s | 60 | 1830
Munsiganj | 83 | 2000 | Jamalpur | 81 | 1900 | Noapara | 64 | 1930
Sonargaon | 46 | 1800 | Sherpur | 60 | 1930 | Jessore | 104 | 1830
Shyampur | 155 | 500 | Srimongal | 25 | 1800 | Jhenida | 72 | 1800
Bhulta | 145 | 100 | Shahjibazar | 72 | 1800 | Bottail | 82 | 1830
Madanganj | 52 | 1100 | Fenchuganj | 30 | 1900 | G.K Project | 39 | 1830
Shitalakhya | 81 | 100 | Kulawara | 20 | 100 | Faridpur | 120 | 1830
Rahim steel | 10 | 1000 | Sylhet | 89 | 1900 | Madaripur | 110 | 2000
Matuail | 68 | 500 | Chatak | 18 | 1800 | Gopalganj | 63 | 1900
Ghorasal | 57 | 100 | Sunamganj | 24 | 1900 | Bagerhat | 62 | 1900
Narsingdi | 94 | 100 | Biani Bazar | 29 | 1930 | Mongla | 28 | 100
Haripur (SBU) | 88 | 200 | Comilla (S) | 122 | 1830 | Satkhira | 70 | 1800
Ullon | 75 | 1800 | Comilla(N) | 77 | 1800 | Gallamari | 38 | 1300
Hasnabad | 163 | 1830 | Chandpur | 85 | 1800 | Magura | 38 | 1830
Magbazar | 85 | 1400 | Feni | 90 | 2200 | Chuadanga | 58 | 2000
Maniknagar | 62 | 1800 | Chowmuhani | 142 | 1900 | Barisal | 88 | 1930
Bangabhaban | 14 | 1800 | Ashuganj | 41 | 2100 | Patuakhali | 68 | 2000
Narinda | 60 | 100 | Daudkandi | 74 | 1930 | Bhandaria | 41 | 2000
Dhanmondi | 81 | 1830 | B.Baria | 94 | 1830 | Ishurdi | 38 | 1830
Lalbag | 51 | 1800 | Ramganj | 25 | 1800 | Ruppur Paromanobik | 2 | 100
Madartek | 39 | 1830 | Madunaghat | 45 | 1830 | Natore | 80 | 1830
Mirpur | 75 | 1830 | Hathazari | 74 | 2000 | Bogra | 163 | 1930
Kalyanpur | 90 | 1900 | Khulshi | 144 | 1900 | Noagaon | 73 | 1930
Gulshan | 84 | 1900 | Halishahar | 95 | 2100 | Rajshahi | 93 | 1900
Uttara | 67 | 1830 | Baraulia | 131 | 400 | C.Nawabganj | 46 | 2000
Uttara(New) | 4 | 1900 | Sikalbaha | 28 | 1900 | Amnura | 27 | 1830
Kamrangirchar | 48 | 1830 | Dohazari | 66 | 2000 | Pabna | 69 | 1930
Savar | 84 | 1830 | Cox'sbazar | 52 | 1900 | Shahjadpur | 64 | 1830
Bhasantec | 114 | 1830 | Chandraghona | 24 | 1800 | Serajganj | 50 | 1830
Agargaon | 34 | 1830 | Kaptai | 4 | 1800 | Niyamatpur | 41 | 1900
Satmosjid | 74 | 1830 | A. Khaer Stl. | 12 | 1200 | Joypurhat | 42 | 1900
Tongi | 91 | 800 | Bakulia | 80 | 600 | Rangpur | 88 | 1830
Kabirpur | 117 | 100 | Julda | 15 | 100 | Lalmonirhat | 68 | 1830
Basundhara | 89 | 1800 | TK chemical | 5 | 1200 | Saidpur | 84 | 1900
Manikganj | 62 | 100 | Modern Steel | 10 | 200 | Purbasadipur | 69 | 2000
Joydevpur | 154 | 100 | Shahmirpur | 17 | 1930 | Thakurgaon | 50 | 1930
New Tongi | 69 | 100 | Khagrachhari | 14 | 1930 | Palashbari | 72 | 1830
Korda | 178 | 100 | Matarbari | 19 | 2000 | Barapukuria | 37 | 2100
Dhamrai | 36 | 1830 | Baroiar Hat | 7 | 1800 | Panchagar | 36 | 1830
Tangail | 125 | 2000 | Abul Khair 230 | 180 | 100
Mymensing | 161 | 1930 | BSRM | 120 | 1800
Kishorganj | 61 | 100 | Goalpara | 27 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-10-12
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 389 | 8:00 | 383 | 1:00 | Kaliakoir | 371 | 9:00 | 361 | 1:00
Bheramara | 403 | 2:00 | 393 | 18:30 | Bhulta | 388 | 9:00 | 375 | 23:00
Ashuganj(N) | 389 | 7:00 | 384 | 23:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 16:00 | 224 | 1:00 | Hathazari | 222 | 8:00 | 218 | 1:00
Ishurdi | 236 | 4:00 | 228 | 20:00 | Megnaghat | 224 | 6:00 | 220 | 1:00
Ashuganj | 236 | 9:00 | 232 | 1:00 | Fenchuganj | 238 | 18:00 | 231 | 3:00
Serajganj | 227 | 17:00 | 222 | 20:00 | Siddhirganj | 226 | 8:00 | 219 | 1:00
Baghabari | 230 | 4:00 | 222 | 1:00 | Maniknagar | 223 | 8:00 | 218 | 15:00
Barapukuria | 238 | 5:00 | 230 | 19:00 | Old Airport | 226 | 8:00 | 218 | 1:00
Bogra | 228 | 6:00 | 217 | 20:00 | Barisal | 224 | 13:00 | 216 | 22:00
Khulna South | 238 | 6:00 | 230 | 19:00 | AKSML | 221 | 19:00 | 211 | 1:00
Rampura | 222 | 7:00 | 219 | 1:00 | BSRM | 223 | 8:00 | 215 | 1:00
Haripur | 223 | 7:00 | 217 | 1:00 | Bibiyana | 233 | 8:00 | 228 | 24:00
Hasnabad | 228 | 9:00 | 218 | 24:00 | Bhulta | 226 | 9:00 | 219 | 1:00
Aminbazar | 225 | 6:00 | 219 | 1:00 | Ashuganj (S) | 234 | 9:00 | 228 | 1:00
Tongi | 220 | 4:00 | 216 | 21:00 | Kaliakoir | 228 | 9:00 | 223 | 1:00
Comilla (N) | 232 | 8:00 | 226 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 600 | 134 | 100 | Ramganj | 129 | 1000 | 122 | 1900
Munsiganj | 136 | 600 | 133 | 100 | Madanhat | 135 | 200 | 130 | 400
Megnaghat | 135 | 800 | 131 | 500 | Hathazari | 132 | 800 | 129 | 300
Shyampur | 132 | 600 | 127 | 300 | Khulshi | 130 | 1800 | 125 | 1700
Bhulta | 130 | 900 | 127 | 300 | Halishahar | 132 | 1830 | 127 | 1700
Madanganj | 137 | 900 | 130 | 300 | Baraulia | 132 | 1930 | 127 | 300
Shitalakhya | 138 | 800 | 130 | 100 | Sikalbaha | 133 | 1800 | 127 | 300
Rahim steal | 137 | 700 | 133 | 100 | Dohazari | 132 | 1800 | 126 | 300
Matuail | 136 | 900 | 132 | 300 | Cox'sbazar | 127 | 1900 | 121 | 300
Ghorasal | 138 | 1800 | 135 | 100 | Chandraghona | 133 | 1830 | 123 | 1300
Narsinghdi | 137 | 1800 | 124 | 100 | Kaptai | 134 | 1800 | 130 | 300
Haripur (SBU) | 138 | 800 | 134 | 100 | A. Khaer Stl. | 132 | 1800 | 126 | 300
Ullon | 137 | 600 | 134 | 1200 | Bakulia | 131 | 1900 | 122 | 400
Hasnabad | 135 | 600 | 132 | 1200 | Julda | 133 | 1900 | 127 | 300
Magbazar | 135 | 600 | 133 | 1300 | TK Chemical | 135 | 1900 | 128 | 400
Maniknagar | 135 | 800 | 131 | 1200 | Modern Steel | 131 | 1900 | 126 | 400
Bangabhaban | 137 | 800 | 131 | 1200 | Shahmirpur | 132 | 1800 | 126 | 600
Narinda | 138 | 900 | 133 | 100 | Khagrachhari | 133 | 1830 | 123 | 2100
Dhanmondi | 135 | 800 | 131 | 1200 | Matarbari | 129 | 800 | 120 | 100
Lalbag | 137 | 800 | 131 | 1200 | Baroiar Hat | 132 | 900 | 127 | 300
Madartek | 138 | 900 | 133 | 100 | Goalpara | 138 | 800 | 132 | 1900
Mirpur | 134 | 300 | 131 | 1200 | Central s/s | 138 | 800 | 132 | 1830
Kalyanpur | 135 | 300 | 134 | 1200 | Noapara | 137 | 1000 | 128 | 1900
Gulshan | 135 | 400 | 133 | 1200 | Jessore | 133 | 800 | 122 | 2000
Uttara | 132 | 600 | 130 | 1200 | Jhenida | 135 | 600 | 125 | 1900
Uttara(New) | 132 | 300 | 131 | 1200 | Bottail | 138 | 1400 | 133 | 1930
Kamrangirchar | 134 | 500 | 131 | 1200 | G.K.Project | 142 | 500 | 139 | 1930
Savar | 134 | 600 | 130 | 1200 | Faridpur | 135 | 700 | 127 | 2000
Bhasantec | 134 | 300 | 133 | 1200 | Madaripur | 135 | 700 | 127 | 2000
Agargaon | 135 | 300 | 133 | 1200 | Gopalganj | 137 | 1800 | 125 | 2000
Satmosjid | 135 | 300 | 134 | 1200 | Bagerhat | 140 | 1000 | 132 | 2200
Tongi | 134 | 1500 | 131 | 2100 | Mongla | 136 | 900 | 130 | 1800
Kabirpur | 137 | 1400 | 132 | 100 | Satkhira | 137 | 600 | 129 | 1900
Basundhara | 132 | 800 | 128 | 100 | Gallamari | 139 | 600 | 132 | 1900
Manikganj | 139 | 900 | 133 | 100 | Magura | 136 | 1100 | 123 | 2000
Joydevpur | 144 | 1800 | 133 | 500 | Chuadanga | 132 | 600 | 121 | 2000
New Tongi | 136 | 900 | 130 | 100 | Barisal | 140 | 1300 | 135 | 100
Kodda | 141 | 1900 | 131 | 100 | Patuakhali | 138 | 700 | 132 | 100
Dhamrai | 136 | 1400 | 131 | 100 | Bhandaria | 137 | 1600 | 130 | 2200
Tangail | 139 | 1400 | 130 | 100 | Ishurdi | 142 | 800 | 136 | 2000
Mymensing | 136 | 1830 | 121 | 100 | Ruppur Paromanobik | 141 | 800 | 136 | 2000
Kishorganj | 132 | 1000 | 125 | 100 | Natore | 137 | 500 | 132 | 2100
Netrokona | 135 | 1300 | 121 | 100 | Bogra | 136 | 500 | 128 | 2000
Jamalpur | 139 | 1800 | 119 | 100 | Noagaon | 133 | 600 | 125 | 2000
Sherpur | 137 | 1800 | 121 | 100 | Rajshahi | 135 | 1800 | 129 | 2100
Srimongal | 142 | 1800 | 135 | 100 | C.Nawabganj | 135 | 1800 | 126 | 1100
Shahjibazar | 140 | 1800 | 134 | 100 | Amnura | 138 | 1800 | 130 | 100
Fenchuganj | 138 | 1800 | 134 | 200 | Pabna | 135 | 300 | 130 | 2000
Khulawara | 137 | 1800 | 134 | 100 | Shahjadpur | 142 | 1800 | 137 | 2100
Sylhet | 137 | 1800 | 134 | 500 | Serajganj | 136 | 1000 | 132 | 2100
Chatak | 137 | 1800 | 134 | 100 | Niyamatpur | 132 | 600 | 121 | 2000
Sunamganj | 135 | 1400 | 132 | 500 | Joypurhat | 135 | 600 | 125 | 2100
Biani Bazar | 137 | 1800 | 134 | 100 | Rangpur | 134 | 400 | 121 | 1900
Comilla(s) | 129 | 600 | 120 | 1830 | Lalmonirhat | 135 | 500 | 115 | 1930
Comilla(n) | 139 | 800 | 135 | 1400 | Saidpur | 135 | 600 | 121 | 2000
Chandpur | 132 | 800 | 127 | 2000 | Purbasadipur | 136 | 600 | 128 | 2000
Feni | 125 | 800 | 121 | 200 | Thakurgaon | 131 | 600 | 119 | 2000
Chowmuhani | 128 | 800 | 123 | 1930 | Palashbari | 134 | 1200 | 115 | 1800
Ashuganj | 140 | 1800 | 134 | 100 | Barapukuria | 138 | 500 | 130 | 1900
Daudkandi | 136 | 900 | 131 | 1930 | Panchagar | 131 | 600 | 117 | 1930
B.Baria | 138 | 1830 | 129 | 100

## L-Curve
Date | 2018-10-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 180 | 4704 | 2033 | 6737 |  |  |  | QF-LDC-12
0:30 | 90 | 5020.5 | 1949.5 | 6970 | Date: | 2018-10-12
1:00 | 0 | 5337 | 1866 | 7203
1:30 | 5 | 5276.5 | 1795.5 | 7072
2:00 | 10 | 5216 | 1725 | 6941
2:30 | 15 | 5135.5 | 1702 | 6837.5 | [5 empty] | Gen. at Eve. Peak | 8103 | 8103 MW (20:00 )
3:00 | 20 | 5055 | 1679 | 6734 | [6 empty] | 20:00
3:30 | 45 | 4940 | 1660.5 | 6600.5 | [5 empty] | Gen. at Day Peak | 6052.1 | 6052.1 MW (12:00 )
4:00 | 70 | 4825 | 1642 | 6467 | [6 empty] | 12:00
4:30 | 70 | 4781.5 | 1636.5 | 6418 | [5 empty] | Highest Generation | 8103
5:00 | 70 | 4738 | 1631 | 6369 | [6 empty] | 20:00
5:30 | 65 | 4587.3 | 1593 | 6180.3
6:00 | 60 | 4436.6 | 1555 | 5991.6
6:30 | 55 | 4349.6 | 1542.5 | 5892.1
7:00 | 50 | 4262.6 | 1530 | 5792.6
7:30 | 99 | 4268.075 | 1509 | 5777.075
8:00 | 148 | 4273.55 | 1488 | 5761.55
8:30 | 134 | 4182.745 | 1451.5 | 5634.245
9:00 | 120 | 4091.94 | 1415 | 5506.94
9:30 | 113 | 4066.305 | 1428.5 | 5494.805
10:00 | 106 | 4040.67 | 1442 | 5482.67
10:30 | 163 | 4116.445 | 1524.5 | 5640.945
11:00 | 220 | 4192.22 | 1607 | 5799.22
11:30 | 210 | 4264.16 | 1661.5 | 5925.66
12:00 | 200 | 4336.1 | 1716 | 6052.1
12:30 | 170 | 4397.055 | 1768.5 | 6165.555
13:00 | 140 | 4458.01 | 1821 | 6279.01
13:30 | 180 | 4335.105 | 1805.5 | 6140.605
14:00 | 220 | 4212.2 | 1790 | 6002.2
14:30 | 215 | 4210.95 | 1765.5 | 5976.45
15:00 | 210 | 4209.7 | 1741 | 5950.7
15:30 | 200 | 4176.55 | 1700 | 5876.55
16:00 | 190 | 4143.4 | 1659 | 5802.4
16:30 | 180 | 4197.7 | 1722.5 | 5920.2
17:00 | 170 | 4252 | 1786 | 6038
17:30 | 125 | 4845 | 2103.5 | 6948.5
18:00 | 80 | 5438 | 2421 | 7859
18:30 | 170 | 5538.5 | 2415 | 7953.5
19:00 | 260 | 5639 | 2409 | 8048
19:30 | 300 | 5711 | 2367 | 8078
20:00 | 310 | 5767 | 2336 | 8103 |  |  |  | Executive Engineer
20:30 | 305 | 5656.5 | 2295.5 | 7952 |  |  |  | Network Operation Division
21:00 | 300 | 5546 | 2255 | 7801
21:30 | 250 | 5391 | 2197 | 7588
22:00 | 200 | 5236 | 2139 | 7375 |  |  |  |  | Page 6 of 7
22:30 | 115 | 5077 | 2107.5 | 7184.5
23:00 | 30 | 4918 | 2076 | 6994
23:30 | 105 | 4811 | 2054.5 | 6865.5
24:00 | 180 | 4704 | 2033 | 6737
8103 MW (20:00 )
6052.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-10-12 |  | Energy | 159736192
[10 empty] | 2018-10-12 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3873 | 724 | 1529 | 190 | 149 | 70 | 120 | 0 | 82
0:30 | 4029.5 | 595 | 1553.5 | 350 | 151.5 | 71.5 | 128 | 0 | 91 | Date: | 2018-10-12
1:00 | 4186 | 466 | 1578 | 510 | 154 | 73 | 136 | 0 | 100
1:30 | 4170.5 | 435 | 1504 | 502 | 154 | 71.5 | 136 | 0 | 99 | [7 empty] | Total Energy | 159.7362 | Total Energy Gen 159.736 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.736 MKWHr
2:00 | 4155 | 404 | 1430 | 494 | 154 | 70 | 136 | 0 | 98 | [7 empty] | Energy not Served | 0
2:30 | 4082.5 | 404 | 1408.5 | 485.5 | 154 | 70 | 136 | 0 | 97 | [7 empty] | Energy Requirement | 159.7362
3:00 | 4010 | 404 | 1387 | 477 | 154 | 70 | 136 | 0 | 96
3:30 | 3955 | 404 | 1340.5 | 446 | 154 | 70 | 136 | 0 | 95 | [6 empty] | Shortage
4:00 | 3900 | 404 | 1294 | 415 | 154 | 70 | 136 | 0 | 94
4:30 | 3901.5 | 404 | 1251.5 | 409 | 154 | 70 | 136 | 0 | 92
5:00 | 3903 | 404 | 1209 | 403 | 154 | 70 | 136 | 0 | 90
5:30 | 3775 | 404 | 1139 | 417 | 154 | 70 | 136 | 0 | 85
6:00 | 3647 | 404 | 1069 | 431 | 154 | 70 | 136 | 0 | 80
6:30 | 3575 | 404 | 1050.5 | 423 | 152 | 70 | 136 | 0 | 80 |  |  |  |  | Coal
7:00 | 3503 | 404 | 1032 | 415 | 150 | 70 | 136 | 0 | 80
7:30 | 3474 | 404 | 1046 | 415 | 150 | 70 | 136 | 0 | 79 |  |  |  | Oil |  |  |  | ,
8:00 | 3445 | 404 | 1060 | 415 | 150 | 70 | 136 | 0 | 78
8:30 | 3350 | 404 | 1037.5 | 404.5 | 150 | 71 | 136 | 0 | 77
9:00 | 3255 | 404 | 1015 | 394 | 150 | 72 | 136 | 0 | 76
9:30 | 3272 | 404 | 1028 | 358.5 | 150 | 72 | 128 | 0 | 77
10:00 | 3289 | 404 | 1041 | 323 | 150 | 72 | 120 | 0 | 78
10:30 | 3328 | 463 | 1078 | 331.5 | 150 | 87 | 120 | 0 | 79
11:00 | 3367 | 522 | 1115 | 340 | 150 | 102 | 120 | 0 | 80
11:30 | 3458 | 522 | 1161.5 | 346.5 | 150 | 82 | 120 | 0 | 83
12:00 | 3549 | 522 | 1208 | 353 | 150 | 62 | 120 | 0 | 86
12:30 | 3634.5 | 522 | 1214 | 369.5 | 150 | 62 | 120 | 0 | 89
13:00 | 3720 | 522 | 1220 | 386 | 150 | 62 | 120 | 0 | 92
13:30 | 3720 | 522 | 1220 | 386 | 150 | 62 | 120 | 0 | 92
14:00 | 3720 | 522 | 1220 | 386 | 150 | 62 | 120 | 0 | 92
14:30 | 3616 | 522 | 1175 | 377 | 150 | 62 | 120 | 0 | 89
15:00 | 3512 | 522 | 1130 | 368 | 150 | 62 | 120 | 0 | 86
15:30 | 3468.5 | 522 | 1103 | 366.5 | 150 | 61 | 120 | 0 | 85
16:00 | 3425 | 522 | 1076 | 365 | 150 | 60 | 120 | 0 | 84
16:30 | 3482 | 547.5 | 1067.5 | 380 | 150 | 60 | 145 | 0 | 88
17:00 | 3539 | 573 | 1059 | 395 | 150 | 60 | 170 | 0 | 92
17:30 | 3598 | 648 | 1269.5 | 726.5 | 150 | 60 | 392.5 | 0 | 104
18:00 | 3657 | 723 | 1480 | 1058 | 150 | 60 | 615 | 0 | 116
18:30 | 3676 | 723 | 1553.5 | 1121 | 150 | 64 | 548 | 0 | 118
19:00 | 3695 | 723 | 1627 | 1184 | 150 | 68 | 481 | 0 | 120
19:30 | 3837 | 723 | 1710 | 1187 | 150 | 70 | 281 | 0 | 120
20:00 | 3966 | 724 | 1809 | 1067 | 150 | 70 | 197 | 0 | 120
20:30 | 3983.5 | 724 | 1807.5 | 921 | 150 | 70 | 176 | 0 | 120
21:00 | 4001 | 724 | 1806 | 775 | 150 | 70 | 155 | 0 | 120
21:30 | 4023.5 | 723.5 | 1703.5 | 664 | 150 | 70 | 137.5 | 0 | 116
22:00 | 4046 | 723 | 1601 | 553 | 150 | 70 | 120 | 0 | 112
22:30 | 3995 | 723.5 | 1609.5 | 417 | 149.5 | 70 | 120 | 0 | 100
23:00 | 3944 | 724 | 1618 | 281 | 149 | 70 | 120 | 0 | 88
23:30 | 3908.5 | 724 | 1573.5 | 235.5 | 149 | 70 | 120 | 0 | 85 | Max Temp. in Dhaka |  | 26.2° C
24:00 | 3873 | 724 | 1529 | 190 | 149 | 70 | 120 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 159.736 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.736 MKWHr
Note on W13: Author:

## Generation
2018-10-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 43 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 42 | 72 | 32 | 32 | 32 | 32 | 30 | 30 | 30 |  | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 900996
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 724900
3 | Chittagong ST-1 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3500000
4 | Chittgong ST-2 (Raozan) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3200000
5 | Raozan 25 MW (RPCL) | 0 | [16 empty] | 26 |  | 25 | 26 | 0 |  |  |  |  | 55440
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.6 | 2.3 | 3.25 | 4.54 | 5.07 | 2.82 | 1.4 | 6.81 | 0.9 | 0.5 | 0.2 | 0 | [9 empty] | 25800
6 | Sikalbaha 225MW (Gas) | 203 | 203 | 203 | 203 | 202 | 202 | 202 | 200 | 183 | 190 | 193 | 214 | 202 | 202 | 202 | 202 | 216 | 200 |  | 202 | 224 | 203 | 202 | 215 | 202 | 202 | 4802021
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 34 |  | 16 | 0 | 0 |  |  |  |  | 39945
12 | Hathazari peaking | [17 empty] | 40 |  | 40 | 0 | 0 |  |  |  |  | 101928
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 15 | 37 |  | 75 | 45 | 45 | 15 | 15 | 15 | 15 | 474220
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 234182
20 | Ghorasal ST: Unit-1,2 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1223000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 380 | 380 | 300 | 250 | 250 | 200 | 180 | 200 | 170 | 180 | 180 | 190 | 250 | 250 | 250 | 200 | 200 | 200 |  | 200 | 250 | 335 | 380 | 380 | 380 | 380 | 6185490
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2115604
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2444065
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 41 | 41 | 41 | 41 | 41 | 41 | 21 | 21 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 41 |  | 41 | 41 | 41 | 41 | 41 | 25 | 10 | 631296
33 | Ashuganj CCPP 225 MW | 191 | 185 | 183 | 183 | 189 | 183 | 183 | 183 | 150 | 150 | 152 | 153 | 153 | 152 | 152 | 152 | 152 | 228 |  | 226 | 226 | 226 | 223 | 228 | 207 | 192 | 4401000
34 | Ashuganj CCPP(South) | 309 | 300 | 300 | 300 | 309 | 272 | 272 | 270 | 270 | 270 | 270 | 270 | 270 | 272 | 272 | 272 | 287 | 250 |  | 272 | 276 | 279 | 250 | 287 | 250 | 250 | 6675500
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 8429000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 51 | 51 | 50 | 50 | 50 | 50 | 51 | 51 | 51 |  | 51 | 51 | 51 | 91 | 91 | 90 | 85 | 1686850
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 345 | 345 | 345 | 346 | 300 | 300 | 280 | 280 | 280 | 330 | 370 | 370 | 348 | 345 | 345 | 366 | 356 |  | 348 | 361 | 369 | 347 | 347 | 353 | 355 | 8278490
40 | Meghnaghat CCPP 450MW | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 300 | 280 | 320 | 320 | 360 | 360 | 330 | 330 | 300 | 300 | 300 |  | 300 | 320 | 380 | 380 | 380 | 380 | 380 | 8256375
41 | Haripur Power CCPP 360MW | 363 | 363 | 325 | 304 | 306 | 247 | 222 | 222 | 240 | 241 | 240 | 250 | 260 | 241 | 240 | 242 | 233 | 231 |  | 231 | 251 | 278 | 281 | 282 | 282 | 283 | 6385000
42 | Mymensingh RPCL 210MW | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 105 | 88 | 88 | 87 | 89 | 89 | 107 | 106 | 106 | 105 | 106 |  | 106 | 106 | 105 | 106 | 105 | 106 | 106 | 2030240
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 908000
45 | Fenchugonj CCPP-2 | 73 | 73 | 73 | 73 | 73 | 73 | 60 | 40 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 1103520
46 | Shajibazar 330 MW | 228 | 228 | 230 | 229 | 227 | 229 | 227 | 227 | 248 | 247 | 242 | 243 | 225 | 186 | 190 | 186 | 190 | 186 |  | 186 | 187 | 187 | 190 | 187 | 186 | 185 | 4828119
47 | Shahjibazar GT: Unit- 8, 9 | 67 | 67 | 55 | 53 | 54 | 40 | 40 | 27 | 40 | 58 | 65 | 65 | 66 | 67 | 42 | 48 | 59 | 45 |  | 67 | 66 | 67 | 66 | 67 | 63 | 58 | 1347000
48 | Shahjibazar 86MW | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 86 |  | 86 | 86 | 86 | 86 | 50 | 50 | 10 | 612480
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 5 | 5 | 5 | 5 | 5 | 1 | 1 | 1 | 5 | 5 | 5 | 5 | 5 | 5 | 46 |  | 46 | 47 | 47 | 47 | 5 | 5 | 5 | 463320
50 | Sylhet GT 150 MW | 79 | 78 | 78 | 79 | 78 | 79 | 79 | 80 | 80 | 80 | 80 | 100 | 120 | 80 | 80 | 79 | 78 | 78 |  | 78 | 77 | 77 | 79 | 76 | 78 | 80 | 1989300
51 | Sylhet GT 20 MW | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 | 20 | 0 | 104000
52 | Sylhet (EPL) 50MW | 45 | 45 | 44 | 44 | 6 | 6 | 5 | 1 | 1 | 1 | 1 | 5 | 5 | 6 | 6 | 6 | 6 | 44 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 565740
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 0 | [12 empty] | 7 |  | 7 | 7 | 9 | 9 | 9 | 9 | 0 | 83520
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 0 | 0 | 0 | 0 | 11 | 187152
55 | Fenchugonj (Barakatullah) 51MW | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 7 | 5 | 5 | 27 |  | 38 | 38 | 38 | 38 | 5 | 5 | 5 | 288600
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 24 | 24 | 23 | 24 |  | 25 | 24 | 24 | 25 | 24 | 24 | 24 | 579840
57 | Summit Bibiana- 2 | 280 | 280 | 270 | 270 | 285 | 245 | 250 | 280 | 260 | 240 | 295 | 310 | 300 | 265 | 275 | 290 | 280 | 300 |  | 280 | 325 | 325 | 310 | 290 | 310 | 275 | 7301700
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 |  | 55 | 55 | 55 | 36 | 36 | 17 | 0 | 581000
59 | Sikalbaha (Energis) | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [7 empty] | 7 |  | 23 | 40 | 39 | 24 | 24 | 8 | 8 | 288000
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530448
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 0 | 0 | 0 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 404388
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 0 | 0 | 0 | [5 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 322200
63 | Tripura | 100 | 98 | 96 | 94 | 90 | 80 | 80 | 78 | 76 | 78 | 80 | 86 | 92 | 86 | 86 | 84 | 92 | 116 |  | 120 | 120 | 120 | 120 | 112 | 88 | 82 | 2280960
64 | Malancha, Ctg. EPZ (United) | 31 | 21 | 30 | 31 | 32 | 33 | 36 | 38 | 33 | 5 | 5 | 5 | 7 | 7 | 7 | 10 | 10 | 10 |  | 32 | 37 | 42 | 42 | 42 | 42 | 42 | 649440
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | [8 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 275544
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 210600
67 | Jangalia (Summit) 33MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [7 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 287700
68 | Summit Comilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 9 | 12 | 12 | 12 | 13 | 13 | 14 |  | 14 | 17 | 21 | 21 | 21 | 21 | 15 | 360330
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 10 | 24 | 24 | 24 | 20 | 20 | 0 | 6 | 6 | 20 | 20 |  | 24 | 24 | 32 | 32 | 32 | 29 | 32 | 584820
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 716200
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 33 |  | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 788300
73 | Ghorashal (Regent) | 94 | 42 | 42 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 83 |  | 94 | 87 | 90 | 91 | 90 | 94 | 94 | 959727
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | [9 empty] | 2 | 7 | 7 | 7 | 7 | 0 | 0 | 107860
78 | Gazipur (RPCL) | 8 | 0 | [15 empty] | 8 |  | 26 | 26 | 0 |  |  |  |  | 55236
79 | Kodda 149 MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | [7 empty] | 98 |  | 48 | 0 | 0 |  |  |  |  | 266880
80 | Jamalpur 95MW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 42 |  | 24 | 7 | 7 | 7 | 7 | 0 |  | 213120
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10 | 0 | [7 empty] | 0 |  | 12 | 16 | 16 | 16 | 15 | 15 | 0 | 221232
83 | Pagla (DPA ) |  |  |  |  | 0 | 46 | 46 | 46 | 45 | 46 | 46 | 46 | 45 | 45 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 45 | 0 | 0 |  | 710410
84 | B.Baria (Aggreko) 85MW | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 85 |  | 85 | 85 | 85 | 85 | 50 | 50 | 50 | 221232
85 | Keraniganj (Powerpac) 100MW | 0 | [16 empty] | 6 |  | 10 | 10 | 10 | 10 | 0 | 0 |  | 52021
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | [7 empty] | 6 |  | 7 | 7 | 7 | 7 | 7 | 0 | 0 | 116160
88 | Ghorashal 78MW (MAX) | 40 | 40 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 60 |  | 81 | 81 | 81 | 81 | 40 | 40 | 40 | 1086624
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 80 | 90 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 90 |  | 100 | 100 | 100 | 70 | 70 | 15 | 15 | 1100520
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 18 |  | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 568000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 |  | 7 | 7 | 7 | 7 | 7 | 0 |  | 199872
95 | Patenga 50MW | 18 | 18 | 18 | 18 | 6 | 6 | 6 | 6 | 6 | 0 | [7 empty] | 1 |  | 28 | 40 | 43 | 24 | 6 | 6 | 6 | 247680
96 | Chittagong ECPV 108 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 76 |  | 97 | 100 | 54 | 15 | 12 | 12 | 4 | 507840
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 153408
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 31 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 201600
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | [8 empty] | 0 |  | 7 | 15 | 15 | 15 | 0 | 0 |  | 180625
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | [7 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 264384
101 | Kushiara 163 MW CCPP GT | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2855847
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.3 | 0.3 | 0.4 | 0.6 | 0.4 | 0.7 | 0.2 | 0.3 | 0.2 | 0.2 | 0 | [9 empty] | 3300
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 419760
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 46 | 65 | 46 | 46 | 46 | 46 | 168 |  | 168 | 168 | 144 | 105 | 57 | 9 | 0 | 1142400
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 67 | 67 | 40 | 44 | 44 | 46 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 72 |  | 94 | 94 | 94 | 32 | 32 | 0 | 0 | 1031040
115
116
117
118
120 | Eastern Zone Total | 5337 | 5216 | 5055 | 4825 | 4738 | 4436.6 | 4262.6 | 4273.55 | 4091.94 | 4040.67 | 4192.22 | 4336.1 | 4458.01 | 4212.2 | 4209.7 | 4143.4 | 4252 | 5438 |  | 5639 | 5711 | 5767 | 5546 | 5236 | 4918 | 4704 | 115050341
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 |  |  |  | 68160
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [17 empty] | 43 |  | 30 | 5 | [5 empty] | 76800
| Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3064322
129 | Labon Chora 105 MW | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2533000
130
131
132
133
| Summit Barisal 110 MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  | 0 | 16 | 16 | 16 | 16 | 16 | 100 |  | 80 | 80 | 80 | 80 | 48 | 16 |  | 696000
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 53 | 11 | 12 | 12 | 12 | 11 | 11 | 12 | 11 | 43 | 63 | 81 | 83 | 63 | 63 | 22 | 22 | 22 |  | 88 | 91 | 93 | 93 | 96 | 96 | 94 | 1152501
| Bhola CCPP 194MW | 127 | 119 | 119 | 112 | 128 | 126 | 127 | 105 | 65 | 75 | 75 | 75 | 75 | 133 | 126 | 138 | 154 | 154 |  | 154 | 154 | 154 | 153 | 155 | 156 | 143 | 2787977
140 | Bhola (Venture) 33MW | 25 | 23 | 24 | 23 | 23 | 22 | 18 | 17 | 19 | 17 | 17 | 19 | 17 | 20 | 20 | 19 | 20 | 26 |  | 28 | 28 | 28 | 28 | 27 | 20 | 19 | 509600
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [17 empty] | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 35250
143 | Gopalganj Peaking | [16 empty] | 50 | 87 |  | 55 | 50 | 28 | 10 |  |  |  | 219392
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 466 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 522 | 522 | 522 | 522 | 522 | 522 | 573 | 723 |  | 723 | 723 | 724 | 724 | 723 | 724 | 724 | 12811636
147 | Bheramara 360 MW | 350 | 350 | 350 | 350 | 320 | 250 | 250 | 250 | 220 | 220 | 250 | 300 | 350 | 300 | 300 | 250 | 250 | 250 |  | 250 | 300 | 350 | 350 | 350 | 350 | 350 | 7481952
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 154 | 154 | 154 | 154 | 154 | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3695800
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 22 |  | 26 | 0 | 0 |  |  |  |  | 36488
157 | Sirajgonj Unit-1 225MW (Gas) | 175 | 182 | 182 | 181 | 184 | 182 | 174 | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4114273
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 220 | 206 | 158 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 169 | 195 | 173 | 132 | 130 | 130 | 133 |  | 130 | 132 | 132 | 132 | 130 | 132 | 132 | 3704463
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [17 empty] | 25 |  | 30 | 25 | 0 |  |  |  |  | 64845
162 | Bogra (GBB) | 17 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 18 | 18 | 17 | 17 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 331200
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | [13 empty] | 1 | 0 | 0 |  |  |  |  | 62748
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 147510
165 | Amnura 50MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 50 |  | 50 | 50 | 50 | 30 | 12 | 12 | 12 | 461520
166 | Katakhali (Northern) | 8 | 0 | [14 empty] | 8 | 50 |  | 50 | 50 | 50 | 32 | 32 | 8 | 0 | 237936
167 | Katakhali Peaking | [17 empty] | 20 |  | 23 | 23 | 24 | 0 |  |  |  | 56257
168 | Santahar Peaking | [17 empty] | 25 |  | 33 | 33 | 0 |  |  |  |  | 66133
169 | Rajlanka 52 MW | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 8 |  | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 74880
170 | Chapainawabganj-100 MW | [17 empty] | 84 |  | 25 | 25 | 25 | 25 | 0 | 0 |  | 150208
171
172
173 | Rangpur GT | [17 empty] | 17 |  | 17 | [6 empty] | 28000
175 | Saidpur GT | [19 empty] | 18 | [6 empty] | 17000
176
177
178
178 | Western Zone Total | 1866 | 1725 | 1679 | 1642 | 1631 | 1555 | 1530 | 1488 | 1415 | 1442 | 1607 | 1716 | 1821 | 1790 | 1741 | 1659 | 1786 | 2421 | 0 | 2409 | 2367 | 2336 | 2255 | 2139 | 2076 | 2033 | 44685851