## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-10-06 | Saturday
|  | Date (day): | 2018-10-06 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12040 | MW |  |  | (b) At Evening Peak Hour : |  | 12786 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-10-05 | 2018-10-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 | 15 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 380 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 79 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 90 | 90 | 90 | 18 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 365 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 352 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 65 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 305 | 305 |  |  | Reserve.
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 47 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 60 | 60 |  | 40
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 89 | 90 | 90 |  | 10 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint. |  | 21/10/18
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 46 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 10 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 36 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 8 | 8 | 8 |  | 100 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 24 | 57 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 49 | 49 | 49
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 270 | 275 | 275 |  | 25 | Engine problem
35 | APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 0 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 64 | 102 | 105 | 105 |  | 44 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 2288 | 3099 | 4522 | 4522 | 388 | 935
39 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 130 | 130 | 130 | 50 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 20 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 40 | 45 | 45 |  | 5 | Engine problem.
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 142 | 142 | 142 | 142 |  | 50 | #5 Under maint.
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 33 | 0 | 35 | 35
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 35 | 213 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 80 | 115 | 0 | 0 |  |  | Under maint. |  | 14/10/2018
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 40 | 50 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 81 | 72 | 72
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 46 | 50 | 50
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 90 | 90 | 90 |  | 10 | Engine problem
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 15 | 42 | 25 | 25
51 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 53 | 99 | 99 | 99 |  | 9 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 807 | 1215 | 1160 | 1140 | 100 | 74
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 90 | 100 | 100
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 90 | 100 | 100 |  | 34 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 184 | 225 | 225
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 309 | 323 | 360 | 360 |  |  | FGMO
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 19 | 19 | 19 | 26 |  | Gas shortage
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage.
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 68 | 68 | 68 | 127 |  | Gas Shortage.
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Devolopment work.
61 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 80 | 85 | 85 | 85
62 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 41
63 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 140 | 140
64 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
65 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 114 | 166 | 125 | 176
66 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
67 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
68 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
69 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1549 | 1617 | 1926 | 2018 | 201 | 269
70 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 45 | 46 | 50 | 50 | 152 |  | Gas shortage
71 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
72 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 64 | 71 | 71 | 71 |  | 24 | Engine problem.
73 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 2 | 0
74 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 166 | 177 | 170 | 190 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 297 | 316 | 315 | 333 | 152 | 24
75 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 55 | 56 | 56
76 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
77 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
78 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 319 | 325 | 330 | 330
79 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
80 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
81 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
82 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 63 | 66 | 66
83 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 89 | 86 | 86
84 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 44 | 45 | 45 |  | 5 | Engine problem
85 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
86 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 19 | 19
87 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 44 | 45 | 45 |  | 8 | Engine problem
88 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
89 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 |  |  | FGMO
90 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1255 | 1293 | 1356 | 1356 | 0 | 155
91 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 773 | 719 | 779 | 779
92 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 98 | 100 | 100 |  | 10 | Engine problem
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 99 | 99 |  | 16 | Engine problem
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 37
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 243 | 230 | 230
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 2 | 71 | 0 | 80
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 80 | 0 | 350 | 60 |  | Gas shortage
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 32 | 32
| Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 95 | 95
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 929 | 1478 | 1335 | 1834 | 60 | 26
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 19 | 96 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 36 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 179 | 180 | 180 |  | 14
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 313 | 409 | 418 | 444 | 0 | 14
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 53 | 0 | 53
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 37 | 37
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 189 | 220 | 225 | 225
113 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 0 | 0 | 0 | 0 |  | 141 | under maint.
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 291 | 295 | 300 | 300 |  |  | On test.
114 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maint.
115 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
116 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
117 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
118 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
119 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 90 | 90 |  | 14 | Engine problem
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 673 | 934 | 848 | 951 | 281 | 305
120 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
121 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 159 | 160 | 160 | 114 |  | Coal shortage
122 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 10
123 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 160 | 187 | 160 | 188 | 199 | 85
| Total |  |  |  |  | 17043 | 16445 | 8271 | 10548 | 12040 | 12786 | 1381 | 1887
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7740.1442 | 9871 | 11267.2393 | 11965.3589
A. |  | 2018-10-05 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10548 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7640 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10548 | MW
3 | Day peak Generation : |  |  | 8271 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9871 | MW
4 | Evening peak Generation : |  |  | 10548 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 216.6885 | MKWHr | By Solar | 0.14251 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 143.1268 | MKWHr |  | By Oil: | 44.8276 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.1676 | MKWHr |  | By Hydro: | 3.1226 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1381 | MW | Dhaka | 3517 | 3517 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1887 | MW | Chittagong | 977 | 977 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3268 | MW | Khulna | 1262 | 1262 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1187.46 |  | MMCFD |  |  | Rajshahi | 1065 | 1065 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 99560822.216 | ii) Oil : | Taka | 381772865.76 | Comilla | 998 | 998 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16086936 | Total | Taka | 497420623.976 | Mymensingh | 744 | 744 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 5.4465 | MKWHr. | Sylhet | 436 | 436 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -500 | MW at | 21:00 | hrs | Barisal | 271 | 271 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -600 | MW at | 5:00 | hrs | Rangpur | 601 | 601 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 9871 | 9871 |  | 0
B. |  | 2018-10-06 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12786 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 1286 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 236.2455 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7660.8 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.1055 | MKWHr. | ii) HVDC Flow at Peak Time |  | 719 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1958 | MKWHr. | iii) Maximum HVDC Flow : |  | 774 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.75 |  | (b) Today: | 102.75 |  | (c) Rule Curve: |  | 106.36
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-10-05
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 366 | 354 | 0 | 0 | 450 | 0 | 100 | 98 | 55 | 0 | 0 | 0 | 0 | 90 | 96 | 149 | 85 | 8 | 11 | 40 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 109 | 30 | 120 | 130 | 25 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 92 | 43 | 22 | 39 | 100 | 0 | 90 | 360 | 290 | 164 | 68 | 121 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 150 | 46 | 71 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 304 | 65 | 89 | 47 | 100 | 19 | 43 | 9 | 285 | 24 | 11 | 0 | 238 | 0 | 0 | 185 | 0 | 105 | 0 |  | 773 | 0 | 350 | 99 | 115 | 80 | 0 | 0 | 17 | 48 | 32 | 178 | 34 | 110 | 0 | 0 | 0 | 0 | 53 | 70 | 12 | 50 | 36 | 52 | 0 | 22 | 9 | 11 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 197 | 96 | 0 | 0 | 0 | 301 |  | 7407 | 2928 | 10335 | 4078 | 773 | 2130 | 2121 | 183 | 139 | 761 | 150 | 0 | 0 | 102.76
2:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 379 | 357 | 0 | 0 | 450 | 0 | 100 | 98 | 55 | 0 | 0 | 0 | 0 | 90 | 60 | 115 | 85 | 8 | 11 | 40 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 120 | 130 | 25 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 98 | 44 | 22 | 39 | 100 | 0 | 90 | 360 | 290 | 173 | 68 | 126 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 146 | 46 | 71 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 300 | 66 | 89 | 47 | 100 | 19 | 43 | 9 | 265 | 24 | 0 | 0 | 240 | 0 | 0 | 187 | 0 | 105 | 0 |  | 774 | 0 | 350 | 51 | 115 | 0 | 0 | 0 | 0 | 43 | 32 | 172 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 30 | 12 | 50 | 36 | 50 | 0 | 22 | 9 | 11 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 130 | 96 | 0 | 0 | 0 | 301 |  | 7344 | 2610 | 9954 | 4085 | 774 | 2111 | 2047 | 184 | 142 | 465 | 146 | 0 | 0 | 102.76
3:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 397 | 358 | 0 | 0 | 450 | 0 | 78 | 98 | 55 | 0 | 0 | 0 | 0 | 90 | 7 | 32 | 40 | 8 | 11 | 40 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 120 | 130 | 8 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 98 | 43 | 22 | 40 | 100 | 0 | 90 | 360 | 301 | 173 | 68 | 127 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 142 | 46 | 71 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 300 | 40 | 89 | 47 | 100 | 19 | 43 | 9 | 280 | 24 | 11 | 0 | 238 | 0 | 0 | 182 | 0 | 105 | 0 |  | 773 | 0 | 350 | 10 | 86 | 0 | 0 | 0 | 0 | 19 | 32 | 179 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 30 | 12 | 24 | 28 | 25 | 0 | 22 | 9 | 11 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 126 | 96 | 0 | 0 | 0 | 300 |  | 7144 | 2458 | 9602 | 4107 | 773 | 2127 | 1781 | 184 | 142 | 346 | 142 | 0 | 0 | 102.76
4:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 412 | 356 | 0 | 0 | 450 | 0 | 46 | 98 | 55 | 0 | 0 | 0 | 0 | 90 | 7 | 32 | 10 | 8 | 11 | 40 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 84 | 30 | 120 | 130 | 8 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 94 | 43 | 22 | 40 | 100 | 0 | 90 | 360 | 301 | 173 | 68 | 126 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 138 | 47 | 71 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 307 | 54 | 89 | 47 | 100 | 19 | 43 | 9 | 290 | 24 | 11 | 0 | 240 | 0 | 0 | 187 | 0 | 105 | 0 |  | 773 | 0 | 200 | 10 | 83 | 15 | 0 | 0 | 0 | 17 | 32 | 169 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 30 | 12 | 24 | 28 | 25 | 0 | 22 | 9 | 8 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 121 | 0 | 96 | 0 | 0 | 0 | 301 |  | 7081 | 2271 | 9352 | 4101 | 773 | 2136 | 1673 | 184 | 114 | 233 | 138 | 0 | 0 | 102.75
5:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 416 | 355 | 0 | 0 | 450 | 0 | 7 | 98 | 55 | 0 | 0 | 0 | 0 | 40 | 7 | 16 | 10 | 8 | 11 | 40 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 84 | 30 | 120 | 130 | 8 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 98 | 38 | 22 | 40 | 100 | 0 | 90 | 360 | 302 | 167 | 68 | 126 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 134 | 47 | 24 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 308 | 65 | 89 | 47 | 100 | 19 | 44 | 9 | 290 | 24 | 11 | 0 | 238 | 0 | 0 | 180 | 0 | 105 | 0 |  | 774 | 0 | 0 | 10 | 32 | 15 | 0 | 0 | 0 | 17 | 24 | 178 | 31 | 80 | 0 | 0 | 0 | 0 | 0 | 30 | 12 | 24 | 28 | 25 | 0 | 22 | 9 | 8 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 172 | 0 | 96 | 0 | 0 | 0 | 301 |  | 6926 | 2072 | 8998 | 3972 | 774 | 2135 | 1468 | 184 | 114 | 217 | 134 | 0 | 0 | 102.75
6:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 390 | 354 | 0 | 0 | 400 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 39 | 18 | 35 | 36 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 30 | 120 | 130 | 8 | 71 | 0 | 80 | 0 | 33 | 50 | 78 | 33 | 90 | 94 | 40 | 22 | 30 | 100 | 0 | 90 | 360 | 301 | 173 | 68 | 121 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 47 | 7 | 22 | 0 | 56 | 60 | 44 | 50 | 100 | 302 | 68 | 89 | 47 | 100 | 19 | 43 | 9 | 265 | 24 | 11 | 0 | 210 | 0 | 0 | 85 | 0 | 100 | 0.04 |  | 773 | 0 | 0 | 10 | 16 | 15 | 0 | 0 | 0 | 0 | 8 | 154 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 43 | 28 | 52 | 0 | 17 | 9 | 8 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 174 | 0 | 96 | 0 | 0 | 0 | 301 |  | 6430.04 | 1990 | 8420.04 | 3921 | 773 | 2034 | 1074 | 178 | 114 | 200 | 126 | 0.04 | 0 | 102.75
7:00 | 72 | 0 | 0 | 190 | 380 | 0 | 0 | 340 | 292 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 30 | 120 | 130 | 8 | 71 | 0 | 80 | 0 | 33 | 40 | 78 | 33 | 90 | 83 | 37 | 19 | 30 | 100 | 0 | 90 | 360 | 301 | 176 | 68 | 120 | 19 | 0 | 5 | 0 | 10 | 0 | 0 | 22 | 11 | 33 | 18 | 104 | 46 | 7 | 22 | 0.3 | 56 | 60 | 44 | 50 | 100 | 302 | 63 | 10 | 47 | 22 | 19 | 12 | 9 | 260 | 24 | 11 | 0 | 87 | 0 | 0 | 55 | 0 | 64 | 4.1 |  | 773 | 0 | 0 | 10 | 16 | 15 | 0 | 0 | 0 | 0 | 8 | 169 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 36 | 52 | 0 | 15 | 9 | 8 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 171 | 0 | 97 | 0 | 0 | 0 | 301 |  | 5686.4 | 2005 | 7691.4 | 3795 | 773 | 1722 | 798 | 178 | 114 | 203 | 104 | 4.4 | 0 | 102.74
8:00 | 70 | 0 | 0 | 190 | 380 | 0 | 0 | 300 | 271 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 0 | 18 | 18 | 17 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 30 | 120 | 130 | 8 | 70 | 0 | 80 | 0 | 34 | 40 | 78 | 32 | 90 | 85 | 37 | 22 | 33 | 100 | 0 | 90 | 360 | 301 | 180 | 68 | 142 | 19 | 0 | 5 | 0 | 10 | 0 | 0 | 22 | 11 | 33 | 18 | 98 | 47 | 7 | 22 | 0 | 56 | 60 | 42 | 50 | 100 | 300 | 66 | 10 | 47 | 0 | 19 | 12 | 9 | 275 | 25 | 11 | 0 | 47 | 0 | 0 | 57 | 0 | 64 | 11 |  | 773 | 0 | 0 | 10 | 16 | 20 | 0 | 0 | 0 | 0 | 8 | 154 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 36 | 52 | 0 | 22 | 9 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 171 | 0 | 96 | 0 | 0 | 0 | 301 |  | 5647 | 2009 | 7656 | 3748 | 773 | 1722 | 803 | 180 | 114 | 207 | 98 | 11 | 0 | 102.74
9:00 | 70 | 0 | 0 | 190 | 380 | 0 | 0 | 320 | 311 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 1 | 18 | 18 | 17 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 30 | 120 | 130 | 8 | 40 | 0 | 80 | 0 | 33 | 40 | 0 | 0 | 90 | 74 | 37 | 22 | 32 | 100 | 0 | 90 | 360 | 276 | 175 | 68 | 140 | 19 | 0 | 5 | 0 | 10 | 0 | 0 | 22 | 11 | 33 | 18 | 100 | 46 | 7 | 22 | 1 | 55 | 60 | 42 | 50 | 100 | 312 | 63 | 10 | 45 | 0 | 0 | 36 | 9 | 280 | 25 | 11 | 0 | 45 | 0 | 0 | 127 | 0 | 64 | 14 |  | 773 | 0 | 0 | 10 | 16 | 40 | 0 | 0 | 0 | 0 | 8 | 179 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 36 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 175 | 0 | 95 | 0 | 0 | 0 | 296 |  | 5612 | 2028 | 7640 | 3722 | 773 | 1784 | 861 | 179 | 114 | 92 | 100 | 15 | 0 | 102.74
10:00 | 70 | 0 | 0 | 190 | 380 | 0 | 0 | 345 | 340 | 0 | 0 | 340 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 6 | 18 | 18 | 17 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 30 | 120 | 130 | 8 | 40 | 0 | 80 | 0 | 33 | 32 | 0 | 0 | 80 | 53 | 37 | 22 | 32 | 100 | 0 | 90 | 360 | 287 | 190 | 68 | 140 | 0 | 0 | 5 | 0 | 10 | 0 | 0 | 22 | 11 | 33 | 18 | 110 | 45 | 11 | 22 | 1 | 54 | 60 | 42 | 47 | 100 | 310 | 63 | 10 | 45 | 0 | 0 | 42 | 9 | 310 | 25 | 11 | 0 | 45 | 0 | 0 | 178 | 0 | 64 | 18 |  | 773 | 0 | 0 | 10 | 16 | 90 | 0 | 0 | 0 | 0 | 8 | 179 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 28 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 0 | 0 | 293 |  | 5737 | 2072 | 7809 | 3755 | 773 | 1842 | 882 | 180 | 114 | 134 | 110 | 19 | 0 | 102.73
11:00 | 70 | 0 | 0 | 190 | 380 | 0 | 0 | 350 | 345 | 0 | 0 | 370 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 6 | 18 | 18 | 17 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 120 | 130 | 8 | 40 | 0 | 80 | 0 | 33 | 32 | 0 | 0 | 80 | 53 | 37 | 22 | 15 | 100 | 0 | 90 | 360 | 301 | 187 | 68 | 140 | 0 | 0 | 5 | 0 | 10 | 0 | 0 | 22 | 11 | 33 | 18 | 114 | 44 | 58 | 22 | 2 | 54 | 60 | 47 | 47 | 130 | 312 | 62 | 10 | 43 | 0 | 0 | 42 | 9 | 310 | 24 | 11 | 0 | 45 | 0 | 0 | 175 | 0 | 64 | 20 |  | 773 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 179 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 28 | 52 | 0 | 22 | 9 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 195 | 0 | 91 | 0 | 0 | 0 | 292 |  | 5882 | 2112 | 7994 | 3785 | 773 | 1888 | 926 | 180 | 142 | 164 | 114 | 22 | 0 | 102.72
12:00 | 70 | 0 | 0 | 190 | 380 | 80 | 0 | 350 | 346 | 0 | 0 | 450 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 10 | 18 | 18 | 36 | 0 | 0 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 120 | 130 | 8 | 35 | 0 | 80 | 0 | 33 | 32 | 0 | 0 | 80 | 53 | 37 | 22 | 15 | 100 | 0 | 100 | 360 | 309 | 189 | 68 | 140 | 0 | 0 | 5 | 0 | 80 | 0 | 0 | 19 | 11 | 33 | 21 | 114 | 45 | 64 | 22 | 0 | 55 | 60 | 47 | 50 | 130 | 319 | 62 | 86 | 45 | 0 | 0 | 42 | 9 | 315 | 24 | 11 | 0 | 47 | 0 | 0 | 166 | 0 | 64 | 20 |  | 773 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 2 | 8 | 180 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 189 | 0 | 92 | 0 | 0 | 0 | 291 |  | 6196 | 2075 | 8271 | 3757 | 773 | 2206 | 961 | 160 | 142 | 138 | 114 | 20 | 0 | 102.72
13:00 | 70 | 0 | 0 | 190 | 356 | 94 | 0 | 360 | 246 | 0 | 0 | 450 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 45 | 34 | 18 | 18 | 36 | 22 | 25 | 22 | 33 | 33 | 8 | 0 | 112 | 30 | 120 | 130 | 8 | 40 | 0 | 80 | 0 | 33 | 32 | 0 | 0 | 90 | 50 | 36 | 22 | 15 | 100 | 0 | 100 | 360 | 301 | 185 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 122 | 45 | 64 | 22 | 1.1 | 54 | 60 | 47 | 50 | 130 | 304 | 63 | 88 | 45 | 0 | 0 | 41 | 9 | 310 | 8 | 11 | 0 | 80 | 0 | 0 | 175 | 0 | 64 | 20 |  | 773 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 3 | 8 | 160 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 193 | 0 | 90 | 0 | 0 | 0 | 293 |  | 6184.1 | 2053 | 8237.1 | 3734 | 773 | 2123 | 1023 | 160 | 142 | 139 | 122 | 21.1 | 0 | 102.71
14:00 | 70 | 0 | 0 | 190 | 330 | 92 | 10 | 345 | 311 | 0 | 0 | 380 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 40 | 18 | 18 | 36 | 22 | 25 | 22 | 33 | 33 | 8 | 0 | 112 | 30 | 120 | 130 | 8 | 13 | 0 | 80 | 0 | 33 | 24 | 0 | 0 | 90 | 52 | 36 | 22 | 34 | 100 | 0 | 100 | 360 | 316 | 194 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 126 | 44 | 24 | 0 | 1.6 | 53 | 60 | 47 | 47 | 100 | 312 | 63 | 87 | 45 | 0 | 0 | 42 | 9 | 275 | 8 | 11 | 0 | 130 | 0 | 0 | 178 | 0 | 70 | 19.3 |  | 772 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 2 | 8 | 180 | 24 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 181 | 0 | 90 | 0 | 0 | 0 | 290 |  | 6101.9 | 2068 | 8169.9 | 3682 | 772 | 2074 | 1055 | 160 | 142 | 138 | 126 | 20.9 | 0 | 103.14
15:00 | 70 | 0 | 0 | 190 | 380 | 92 | 71 | 350 | 354 | 0 | 0 | 400 | 0 | 7 | 15 | 30 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 45 | 40 | 18 | 22 | 36 | 0 | 25 | 22 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 130 | 8 | 87 | 0 | 80 | 0 | 33 | 24 | 0 | 0 | 90 | 52 | 36 | 22 | 34 | 100 | 0 | 100 | 360 | 301 | 179 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 130 | 44 | 7 | 22 | 1 | 54 | 60 | 47 | 47 | 100 | 300 | 63 | 82 | 45 | 0 | 0 | 42 | 9 | 300 | 21 | 11 | 0 | 143 | 0 | 0 | 175 | 0 | 81 | 11.5 |  | 719 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 179 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 186 | 0 | 95 | 0 | 0 | 0 | 291 |  | 6377.5 | 2045 | 8422.5 | 3800 | 719 | 2226 | 1097 | 160 | 142 | 136 | 130 | 12.5 | 0 | 103.13
16:00 | 70 | 0 | 0 | 190 | 380 | 91 | 60 | 345 | 354 | 0 | 0 | 370 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 18 | 18 | 18 | 55 | 0 | 25 | 22 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 130 | 8 | 128 | 0 | 80 | 0 | 32 | 32 | 0 | 0 | 80 | 18 | 36 | 22 | 33 | 100 | 0 | 100 | 360 | 301 | 178 | 68 | 140 | 0 | 0 | 5 | 0 | 11 | 0 | 0 | 22 | 11 | 33 | 20 | 120 | 45 | 7 | 22 | 0.6 | 54 | 60 | 47 | 50 | 100 | 302 | 65 | 40 | 45 | 0 | 0 | 40 | 9 | 280 | 24 | 11 | 0 | 155 | 0 | 0 | 175 | 0 | 76 | 7.2 |  | 719 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 6 | 3 | 8 | 153 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 8 | 0 | 22 | 9 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 171 | 0 | 96 | 0 | 0 | 0 | 292 |  | 6175.8 | 1935 | 8110.8 | 3800 | 719 | 2046 | 971 | 160 | 142 | 145 | 120 | 7.8 | 0 | 103.12
17:00 | 70 | 0 | 0 | 190 | 300 | 22 | 40 | 345 | 283 | 0 | 0 | 370 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 18 | 18 | 18 | 55 | 22 | 25 | 22 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 130 | 8 | 206 | 0 | 80 | 0 | 23 | 32 | 0 | 0 | 80 | 18 | 24 | 22 | 35 | 100 | 0 | 100 | 360 | 301 | 179 | 68 | 138 | 0 | 0 | 5 | 0 | 11 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 45 | 7 | 22 | 0.1 | 54 | 60 | 11 | 20 | 100 | 299 | 51 | 10 | 10 | 0 | 0 | 20 | 9 | 280 | 24 | 11 | 0 | 170 | 0 | 0 | 175 | 0 | 50 | 1.5 |  | 719 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 12 | 15 | 8 | 155 | 23 | 48 | 0 | 0 | 0 | 0 | 10 | 0 | 12 | 8 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 146 | 0 | 40 | 0 | 0 | 0 | 295 |  | 5827.6 | 1846 | 7673.6 | 3771 | 719 | 1685 | 906 | 160 | 142 | 173 | 116 | 1.6 | 0 | 103.11
18:00 | 70 | 0 | 0 | 190 | 380 | 48 | 50 | 345 | 332 | 13 | 0 | 400 | 0 | 18 | 15 | 15 | 0 | 0 | 0 | 0 | 10 | 24 | 28 | 10 | 8 | 45 | 18 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 15 | 0 | 112 | 30 | 130 | 130 | 25 | 200 | 0 | 120 | 0 | 0 | 40 | 36 | 0 | 80 | 37 | 20 | 22 | 42 | 100 | 0 | 100 | 360 | 302 | 192 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 40 | 0 | 22 | 5 | 33 | 21 | 152 | 45 | 40 | 22 | 0 | 54 | 40 | 50 | 31 | 100 | 312 | 64 | 50 | 10 | 0 | 0 | 41 | 9 | 290 | 24 | 11 | 0 | 203 | 0 | 0 | 168 | 0 | 69 | 0 |  | 719 | 0 | 0 | 84 | 56 | 180 | 0 | 0 | 30 | 42 | 32 | 179 | 28 | 96 | 0 | 0 | 0 | 50 | 53 | 90 | 34 | 24 | 29 | 15 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 136 | 0 | 75 | 20 | 0 | 0 | 293 |  | 6613 | 2497 | 9110 | 3893 | 719 | 2040 | 1398 | 160 | 142 | 606 | 152 | 0 | 0 | 103.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 0 | 0 | 190 | 380 | 82 | 79 | 345 | 354 | 0 | 0 | 370 | 0 | 95 | 70 | 47 | 0 | 0 | 0 | 0 | 70 | 32 | 105 | 50 | 8 | 0 | 30 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 37 | 0 | 112 | 30 | 130 | 130 | 25 | 199 | 0 | 115 | 0 | 0 | 40 | 81 | 32 | 80 | 94 | 29 | 22 | 42 | 100 | 0 | 100 | 360 | 305 | 217 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 5 | 33 | 21 | 160 | 17 | 68 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 301 | 65 | 86 | 44 | 0 | 19 | 44 | 9 | 280 | 24 | 11 | 0 | 253 | 0 | 0 | 165 | 0 | 105 | 0 |  | 719 | 32 | 75 | 95 | 83 | 241 | 0 | 0 | 43 | 88 | 32 | 154 | 35 | 96 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 30 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 193 | 0 | 95 | 96 | 0 | 0 | 300 |  | 7330 | 2984 | 10314 | 4033 | 719 | 2211 | 2016 | 160 | 142 | 873 | 160 | 0 | 0 | 103.1
19:30 | 70 | 0 | 0 | 190 | 380 | 85 | 79 | 345 | 355 | 0 | 0 | 370 | 0 | 100 | 75 | 48 | 0 | 0 | 0 | 0 | 89 | 32 | 115 | 50 | 8 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 199 | 0 | 115 | 0 | 0 | 40 | 81 | 46 | 80 | 99 | 40 | 22 | 42 | 100 | 0 | 100 | 360 | 305 | 217 | 68 | 140 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 162 | 33 | 66 | 22 | 0 | 60 | 60 | 50 | 50 | 130 | 300 | 65 | 89 | 44 | 0 | 19 | 44 | 9 | 300 | 24 | 11 | 0 | 253 | 0 | 0 | 177 | 0 | 106 | 0 |  | 719 | 32 | 80 | 101 | 99 | 243 | 0 | 0 | 43 | 80 | 32 | 169 | 35 | 98 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 30 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 158 | 95 | 96 | 0 | 0 | 295 |  | 7513 | 2982 | 10495 | 3881 | 719 | 2263 | 2119 | 160 | 142 | 1049 | 162 | 0 | 0 | 103.1
20:00 | 70 | 0 | 0 | 180 | 380 | 86 | 79 | 345 | 353 | 0 | 0 | 370 | 0 | 75 | 80 | 40 | 0 | 0 | 0 | 0 | 89 | 7 | 115 | 10 | 8 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 199 | 0 | 115 | 0 | 0 | 40 | 81 | 45 | 90 | 99 | 40 | 22 | 42 | 100 | 0 | 100 | 360 | 305 | 211 | 68 | 140 | 16 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 164 | 31 | 65 | 22 | 0 | 60 | 60 | 50 | 50 | 130 | 318 | 64 | 89 | 44 | 0 | 19 | 44 | 9 | 300 | 24 | 11 | 0 | 266 | 0 | 0 | 177 | 0 | 106 | 0 |  | 719 | 32 | 78 | 101 | 99 | 242 | 0 | 0 | 43 | 80 | 32 | 179 | 35 | 96 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 32 | 52 | 0 | 22 | 9 | 11 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 97 | 96 | 0 | 0 | 297 |  | 7459 | 3052 | 10511 | 3906 | 719 | 2264 | 2046 | 159 | 142 | 1111 | 164 | 0 | 0 | 103.1
21:00 | 70 | 0 | 0 | 190 | 380 | 90 | 79 | 365 | 352 | 0 | 0 | 400 | 0 | 65 | 80 | 47 | 0 | 0 | 0 | 0 | 89 | 7 | 115 | 10 | 8 | 0 | 40 | 36 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 213 | 0 | 115 | 0 | 0 | 40 | 81 | 46 | 90 | 99 | 40 | 22 | 42 | 90 | 0 | 90 | 360 | 323 | 184 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 166 | 46 | 71 | 22 | 0 | 55 | 60 | 50 | 50 | 130 | 325 | 63 | 89 | 44 | 0 | 19 | 44 | 9 | 320 | 24 | 11 | 0 | 270 | 0 | 0 | 177 | 0 | 102 | 0 |  | 719 | 0 | 80 | 98 | 99 | 243 | 0 | 0 | 40 | 71 | 32 | 179 | 36 | 96 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 30 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 98 | 96 | 0 | 0 | 295 |  | 7540 | 3008 | 10548 | 3948 | 719 | 2319 | 2028 | 159 | 142 | 1067 | 166 | 0 | 0 | 102.98
22:00 | 70 | 0 | 0 | 190 | 380 | 91 | 78 | 370 | 354 | 0 | 0 | 450 | 0 | 65 | 80 | 47 | 0 | 0 | 0 | 0 | 89 | 7 | 115 | 10 | 8 | 0 | 40 | 0 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 41 | 0 | 112 | 30 | 130 | 130 | 25 | 201 | 0 | 115 | 0 | 0 | 40 | 81 | 46 | 80 | 99 | 45 | 22 | 42 | 90 | 0 | 90 | 360 | 296 | 190 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 166 | 53 | 71 | 22 | 0 | 55 | 60 | 50 | 50 | 130 | 325 | 64 | 89 | 45 | 0 | 19 | 44 | 9 | 320 | 25 | 11 | 0 | 270 | 0 | 0 | 180 | 0 | 103 | 0 |  | 713 | 0 | 68 | 93 | 115 | 243 | 0 | 0 | 36 | 60 | 32 | 179 | 36 | 98 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 30 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 12 | 18 | 0 | 0 | 0 | 220 | 98 | 96 | 0 | 0 | 299 |  | 7529 | 2995 | 10524 | 3917 | 713 | 2376 | 1996 | 160 | 142 | 1054 | 166 | 0 | 0 | 103.09
23:00 | 70 | 0 | 0 | 190 | 380 | 90 | 80 | 345 | 354 | 0 | 0 | 450 | 0 | 65 | 80 | 47 | 0 | 0 | 0 | 0 | 89 | 7 | 82 | 10 | 8 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 202 | 0 | 115 | 0 | 0 | 40 | 72 | 46 | 90 | 99 | 45 | 22 | 42 | 90 | 0 | 90 | 360 | 300 | 202 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 162 | 93 | 71 | 22 | 0 | 54 | 60 | 50 | 50 | 130 | 300 | 65 | 89 | 45 | 0 | 19 | 44 | 9 | 300 | 25 | 11 | 0 | 275 | 0 | 0 | 180 | 0 | 105 | 0 |  | 713 | 0 | 40 | 88 | 115 | 210 | 0 | 0 | 35 | 57 | 32 | 178 | 35 | 96 | 0 | 0 | 0 | 0 | 53 | 85 | 50 | 50 | 30 | 25 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 12 | 19 | 0 | 0 | 0 | 220 | 97 | 62 | 0 | 0 | 300 |  | 7514 | 2806 | 10320 | 3895 | 713 | 2356 | 1971 | 160 | 142 | 921 | 162 | 0 | 0 | 103.08
24:00 | 70 | 0 | 0 | 190 | 380 | 90 | 80 | 345 | 357 | 0 | 0 | 450 | 0 | 50 | 94 | 47 | 0 | 0 | 0 | 0 | 90 | 7 | 48 | 10 | 8 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 41 | 0 | 112 | 30 | 130 | 130 | 25 | 200 | 0 | 115 | 0 | 0 | 50 | 72 | 46 | 90 | 99 | 46 | 22 | 42 | 90 | 0 | 90 | 360 | 300 | 206 | 68 | 137 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 156 | 93 | 71 | 22 | 0 | 53 | 60 | 50 | 50 | 130 | 300 | 66 | 89 | 45 | 0 | 19 | 45 | 9 | 280 | 25 | 11 | 0 | 270 | 0 | 0 | 180 | 0 | 103 | 0 |  | 713 | 0 | 40 | 89 | 115 | 165 | 0 | 0 | 35 | 51 | 32 | 154 | 35 | 98 | 0 | 0 | 0 | 0 | 53 | 64 | 35 | 50 | 30 | 25 | 0 | 22 | 10 | 11 | 0 | 0 | 160 | 12 | 19 | 0 | 0 | 0 | 220 | 96 | 20 | 0 | 0 | 301 |  | 7453 | 2655 | 10108 | 3870 | 713 | 2339 | 1913 | 160 | 142 | 815 | 156 | 0 | 0 | 103.08
KWH | 1525000 | 0 | 0 | 4504500 | 8922581 | 934636 | 715008 | 8699910 | 8045000 | 0 | 0 | 9292500 | 0 | 946560 | 1240488 | 826489 | 0 | 0 | 0 | 0 | 1074240 | 433728 | 1165440 | 613790 | 159360 | 537240 | 731280 | 547200 | 901354 | 1032440 | 418248 | 550000 | 597060 | 817296 | 824100 | 568356 | 0 | 2396618 | 726000 | 3000000 | 3200000 | 344520 | 2593388 | 0 | 2164187 | 0 | 519400 | 967680 | 1098068 | 526808 | 2031360 | 1828800 | 884640 | 518496 | 848160 | 2362754 | 0 | 2264068 | 8974700 | 7375000 | 4503000 | 1672727 | 3152780 | 239688 | 0 | 120000 | 0 | 1240488 | 41072 | 0 | 509904 | 234900 | 823200 | 521070 | 3195840 | 1143400 | 1039680 | 514800 | 12700 | 1261000 | 1396400 | 1076400 | 1139000 | 2973837 | 6883570 | 1454000 | 1596480 | 1001160 | 691290 | 270000 | 933440 | 215820 | 7376800 | 523056 | 253056 | 0 | 4220289 | 0 | 0 | 3852000 | 0 | 2059200 | 129810 |  | 18105454 | 69500 | 1794240 | 912000 | 1298880 | 2692800 | 0 | 0 | 287040 | 597504 | 471375 | 4224220 | 679482 | 1632000 | 0 | 0 | 0 | 271888 | 427022 | 773976 | 746200 | 1010928 | 535935 | 1004640 | 0 | 496560 | 233604 | 217188 | 0 | 0 | 4167600 | 71000 | 122000 | 0 | 0 | 2756750 | 1711486 | 2222169 | 519360 | 0 | 0 | 7115364 |  | 159520308 | 57168165 | 216688473 | 93198200 | 18105454 | 49928635 | 34436077 | 4167600 | 3122618 | 10391539 | 3195840 | 142510 | 0
Fuel Cost | 1311500 | 0 | 0 | 3873870 | 5710451.84 | 757055.16 | 672107.52 | 5306945.1 | 4907450 | 0 | 0 | 6225975 | 0 | 5944396.8 | 8286459.84 | 5049847.79 | 0 | 0 | 0 | 0 | 6714000 | 2858267.52 | 11269804.8 | 3909842.3 | 954566.4 | 8590467.6 | 4877637.6 | 3901536 | 5633462.5 | 6473398.8 | 313686 | 412500 | 0 | 0 | 0 | 5376647.76 | 0 | 0 | 0 | 3300000 | 3520000 | 3262604.4 | 1711636.08 | 0 | 2488815.05 | 0 | 529788 | 8505907.2 | 11826192.36 | 5125841.84 | 12574118.4 | 11814048 | 5785545.6 | 440721.6 | 0 | 2150106.14 | 0 | 2060301.88 | 5564314 | 5088750 | 3152100 | 1154181.63 | 3026668.8 | 160590.96 | 0 | 110400 | 0 | 1178463.6 | 445220.48 | 0 | 392626.08 | 176175 | 633864 | 390802.5 | 21859545.6 | 857550 | 9554659.2 | 396396 | 0 | 1311440 | 1452256 | 1033344 | 1025100 | 2319592.86 | 4818499 | 1657560 | 1708233.6 | 1101276 | 788070.6 | 345600 | 868099.2 | 200712.6 | 4721152 | 392292 | 192322.56 | 0 | 30639298.14 | 0 | 0 | 27541800 | 0 | 0 | 0 |  | 92337815.4 | 2025925 | 1202140.8 | 7305120 | 10767715.2 | 43300224 | 0 | 0 | 3232070.4 | 7038597.12 | 3714435 | 2914711.8 | 672687.18 | 12076800 | 0 | 0 | 0 | 3113117.6 | 4577675.84 | 6934824.96 | 6454630 | 8997259.2 | 5707707.75 | 9966028.8 | 0 | 546216 | 219587.76 | 164411.316 | 0 | 0 | 16086936 | 2288330 | 3265940 | 0 | 0 | 1929725 | 25090384.76 | 0 | 9000508.8 | 0 | 0 | 0 |  | 320686459.29 | 290931525.686 | 611617984.976 | 70139188.106 | 92337815.4 | 29421634.11 | 246531008.85 | 16086936 | 0 | 135241856.91 | 21859545.6 | 0 | 0
Yesterday Day Peak | 70 | 0 | 0 | 190 | 380 | 80 | 0 | 350 | 346 | 0 | 0 | 450 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 46 | 10 | 18 | 18 | 36 | 0 | 0 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 120 | 130 | 8 | 35 | 0 | 80 | 0 | 33 | 32 | 0 | 0 | 80 | 53 | 37 | 22 | 15 | 100 | 0 | 100 | 360 | 309 | 189 | 68 | 140 | 0 | 0 | 5 | 0 | 80 | 0 | 0 | 19 | 11 | 33 | 21 | 114 | 45 | 64 | 22 | 0 | 55 | 60 | 47 | 50 | 130 | 319 | 62 | 86 | 45 | 0 | 0 | 42 | 9 | 315 | 24 | 11 | 0 | 47 | 0 | 0 | 166 | 0 | 64 | 20 |  | 773 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 2 | 8 | 180 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 52 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 189 | 0 | 92 | 0 | 0 | 0 | 291 |  | 8271 | DayPeak
Yesterday Evening Peak | 70 | 0 | 0 | 190 | 380 | 90 | 79 | 365 | 352 | 0 | 0 | 400 | 0 | 65 | 80 | 47 | 0 | 0 | 0 | 0 | 89 | 7 | 115 | 10 | 8 | 0 | 40 | 36 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 213 | 0 | 115 | 0 | 0 | 40 | 81 | 46 | 90 | 99 | 40 | 22 | 42 | 90 | 0 | 90 | 360 | 323 | 184 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 166 | 46 | 71 | 22 | 0 | 55 | 60 | 50 | 50 | 130 | 325 | 63 | 89 | 44 | 0 | 19 | 44 | 9 | 320 | 24 | 11 | 0 | 270 | 0 | 0 | 177 | 0 | 102 | 0 |  | 719 | 0 | 80 | 98 | 99 | 243 | 0 | 0 | 40 | 71 | 32 | 179 | 36 | 96 | 0 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 30 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 98 | 96 | 0 | 0 | 295 |  | 10548 | EvPeak
Forecast for Evening | 70 | 0 | 0 | 190 | 365 | 90 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 60 | 90 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 225 | 0 | 0 | 0 | 35 | 50 | 72 | 50 | 90 | 99 | 45 | 22 | 25 | 100 | 0 | 100 | 360 | 360 | 225 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 41 | 52 | 22 | 11 | 33 | 21 | 176 | 50 | 71 | 22 | 0 | 56 | 60 | 50 | 50 | 163 | 330 | 66 | 86 | 45 | 0 | 19 | 45 | 9 | 341 | 25 | 11 | 200 | 275 | 300 | 100 | 190 | 100 | 105 | 0 |  | 779 | 32 | 350 | 100 | 99 | 230 | 0 | 0 | 37 | 80 | 32 | 180 | 33 | 110 | 26 | 0 | 0 | 50 | 53 | 90 | 50 | 50 | 37 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 225 | 0 | 95 | 95 | 0 |  | 300
Forecast for Day | 70 | 0 | 0 | 190 | 365 | 90 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 60 | 90 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 112 | 30 | 130 | 130 | 25 | 225 | 0 | 0 | 0 | 35 | 50 | 72 | 50 | 90 | 99 | 45 | 22 | 25 | 100 | 0 | 100 | 360 | 360 | 225 | 68 | 140 | 19 | 0 | 5 | 0 | 85 | 0 | 52 | 22 | 11 | 33 | 21 | 125 | 50 | 71 | 22 | 2 | 56 | 60 | 50 | 50 | 163 | 330 | 66 | 86 | 45 | 0 | 19 | 45 | 9 | 341 | 25 | 11 | 200 | 275 | 300 | 100 | 170 | 100 | 105 | 20 |  | 779 | 0 | 0 | 100 | 99 | 230 | 0 | 0 | 0 | 0 | 32 | 180 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 50 | 37 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 160 |  | 0 | 0 | 0 | 225 | 0 | 95 | 95 | 0 |  | 300
Generation at 08:00(Today) | 70 | 0 | 0 | 190 | 380 | 22 | 81 | 345 | 254 | 0 | 0 | 300 | 0 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 47 | 10 | 8 | 50 | 6 | 18 | 18 | 55 | 22 | 25 | 32 | 33 | 33 | 24 | 0 | 113 | 30 | 150 | 130 | 25 | 75 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 90 | 99 | 31 | 22 | 5 | 90 | 0 | 90 | 360 | 301 | 204 | 68 | 140 | 19 | 0 | 5 | 0 | 11 | 0 | 0 | 22 | 11 | 25 | 19 | 112 | 50 | 7 | 22 | 0.8 | 56 | 60 | 5 | 30 | 100 | 305 | 66 | 10 | 5 | 0 | 19 | 12 | 9 | 270 | 0 | 11 | 0 | 45 | 0 | 0 | 106 | 0 | 47 | 0 | 0 | 719 | 0 | 180 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 177 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 8 | 0 | 22 | 9 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 149 | 96 | 0 | 0 | 0 | 297 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [65 empty] | 199
| Minimum Generation |  | 7640 | 9:00
| Highest Generation |  | 10548 | 21:00
| Day Peak Generation |  | 8271 | 12:00
| Evening Peak Generation |  | 10548 | 21:00
| HVDC Max Flow |  | 774 | 2:00
| HVDC EvPeak Flow |  | 719 | 21:00
| Load factor L.F |  | 85.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-10-06
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-10-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8271 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7660.8 | MW
Evening Peak Generation : |  | 10548 | MW Hour : | 21:00 | Available Max Generation : |  | 12786 | MW
E.P. Demand (at gen end) : |  | 10548 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 10548 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1286 | MW
Total Gen. (MKWH) : |  | 216.6885 | System Load Factor : | 85.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -600 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-10-06
Actual : | 102.75 | Ft.(MSL) , | Rule curve : | 106.36 | Ft.( MSL )
Gas Consumed : | Total = | 1187.46 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 99560822.216
|  | Coal : | 16086936 | Oil : | 381772865.76 | Total : | 497420623.976
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4007.9665 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1363.3656 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1221.6079 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1103.8533 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 997.5211 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 804.9653 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 449.537 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 207.2421 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 620.8319 |  |  | 0 | 0%
Total | 0 |  | 10776.8909 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Kaptai #5
|  |  |  | 3) Ghorasal Unit-3,4 |  | 11) Siddhirganj CCPP-335 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Sylhet-150 MW
|  |  |  | 5) Tongi GT |  | 13) Santahar-50 MW
|  |  |  | 6) Ashuganj Midland 51 MW |  | 14) Sirajganj unit-3 255 MW
|  |  |  | 7) Baghabari-71 MW |  | 15) Ashuganj (Precision) 55 MW
8) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Baraulia-KSRM 132 kV line was under shut down from 09:03 to 14:12 for corrective maintenance.
b) Khulna 225 MW CCPP ST synchronized at 09:06.
c) Daudkandi- Cumilla(North) 132 kV ckt-1 tripped at 11:31 from both end showing distance Z1 at both sides and
switched on at 11:43.
d) Khulna (C) 132/33 kV T1 transformer was under shut down from 08:34 to 09:11 for corrective maintenance.
e) Chuadanga 132/33 kV T2 transformer was under shut down from 10:32 to11:18 for corrective maintenance.
f) Ashuganj- Kishoreganj 132 kV ckt-2 was under shut down from 10:38 to 12:47 for corrective maintenance.
g) Shyampur-Brammangaon 132 kV line was under shut down from 08:27 to 18:00 for development work.
h) Tangail 132/33 kV T1 & T2 transformers were under shut down from 10:02 to 11:12 and 11:23 to 12:34 respectively
due to corrective maintenance.
i) Hathazari 230/132 kV T4 transformer was under shut down from 08:52 to 10:53 due to corrective maintenance.
j) Halishahar 132/33 kV T1 transformer was under shut down from 08:05 to 13:05 due to annual maintenance.
k) Tongi-Kabirpur 132 kV line-2 tripped at 14:49 from both ends showing CD, CE, CSW at Tongi end and |  |  |  | About 120 MW power interruption occurred at Manikganj & Kodda S/S
Dist. C phase at Kabirpur end and switched on at 14:58. |  |  |  | area from 14:49 to 14:58.
l) Tongi- Kabirpur 132 kV line-1 tripped at 14:49 from Tongi end showing Dist. zone-1 and switched on at 14:57.
m) Halishahar-Khulshi 132 kV line-2 was switched on at 16:47.
n) Tongi- Uttara 132 kV line switched on at 16:25 and again switched off at 20:51.
o) Mirpur- Uttara 132 kV line switched off at 16:26 at Uttara end and switched on at 20:50.
p) Bheramara 410 MW GT was synchronized at 18:20.
q) Kodda 132 kV bus-2 was shut down at 07:59 (06/10/2018) for corrective maintenance.
r) Sikalbaha150 MW GT was shut down at 01:05(06/10/2018) for air filter cleaning.
s) Sikalbaha 225 MW CCPP tripped at 03:29(06/10/2018) due to gas regulating valve.
t) Tongi-Uttara 132 kV line was under shut down from 05:02(06/10/2018) to 07:02 for red hot maintenance at Uttara end.
u) Bheramara CCPP ST was synchronized at 05:02(06/10/2018).
v) Bakulia-Sikalbaha 132 kV ckt-1 was shut down at 07:07(06/10/2018) for corrective maintenance.
w) Shyampur-Brammangaon power plant 132/33 kV line was shut down at 06:30(06/10/2018) for development work.
x) Mymensing 132 kV bus-2 & Mymensing S/S-Mymensing RPCL 132 kV ckt-2 were shut down at 07:29(06/10/2018)
for development work.
y) Hathazari 230 kV bus-2 was under shut down from 06:40(06/10/2018) to 07:35 due to corrective maintenance.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-10-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 70 | 1525000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 190 | 4504500
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 8922581
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 79 | 715008
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 90 | 934636
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 8699910 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 352 | 8045000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 9292500 | frequency Control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 65 | 946560 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 1240488 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 47 | 826489 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 10 | 613790 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 418248
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas restriction
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Engine problem
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 89 | 1074240 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 537240 | Reserve
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 433728 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 731280 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 36 | 547200 | Low demand
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1165440 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 901354
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1032440
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 159360 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1147060 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 817296
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 824100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 49 | 568356
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 270 | 4220289 | Engine problem
35 | APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 0 | 0 | Low demand
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Low demand
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Low demand
38 | Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 102 | 2059200 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3099 | 62903293
39 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 130 | 3000000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 130 | 3200000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 344520
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 129810
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 40 | 884640 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 142 | 3122618 | Unit-5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 519400
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 213 | 2593388 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 115 | 2164187 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 967680 | Low demand
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 81 | 1098068
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 46 | 526808
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2031360
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 518496
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 848160
51 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 1828800 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 1215 | 23777935
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 90 | 2362754 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 2264068 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4503000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8974700
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 323 | 7375000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 19 | 239688 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 1672727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Under maint.
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1240488
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 41072 | Low demand
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3152780
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509904
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 234900
** | Tripura |  | Imported power | 0 | 160 | 166 | 3195840
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 823200
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Line O/L
68 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 521070 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1617 | 37231191
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 46 | 1143400 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 514800
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 71 | 1039680 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12700
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 177 | 3852000 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 316 | 6562580
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 55 | 1261000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1396400
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 2973837 | Frequency Control.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 325 | 6883570 | FGMO.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 1076400
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1139000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 253056
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 63 | 1454000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 89 | 1596480
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 1001160 | Engine problem
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 691290
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 270000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 44 | 933440 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 523056
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7376800 | FGMO
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 215820
| Sylhet Area Total |  |  |  | 1549 | 1293 | 29045309
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 69500 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 719 | 18105454
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 98 | 912000 | Engine problem
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1298880 | Engine problem
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 287040
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 243 | 2692800
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 71 | 597504
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 80 | 1794240 | Gas restriction
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 32 | 471375 | Engine problem
| Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 96 | 519360
| Khulna Area Total |  |  |  | 2214 | 1478 | 26748153
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 96 | 1632000 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 679482
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 179 | 4224220
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 2222169
| Barisal Area Total |  |  |  | 462 | 409 | 8757871
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 271888
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 53 | 427022
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 746200
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 1010928
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 30 | 535935
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas restriction
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 2756750 | FGMO.
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 MW | 0 | 295 | 7115364 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | under maint.
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 496560
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 233604
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217188
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 1004640 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 773976
| Rajshahi Area Total |  |  |  | 1264 | 934 | 15590055
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 159 | 4167600
122 | Rangpur GT |  | PDB | 1*20 | 20 | 10 | 71000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 122000
| Rangpur Area Total |  |  |  | 484 | 187 | 4360600
| Total |  |  |  | 16445 | 10548 | 214976987
| Eastern Grid Total |  |  |  | 12021 | 7540 | 159520308
| Western Grid Total |  |  |  | 4424 | 3008 | 55456679
| National Grid Total |  |  |  | 16445 | 10548 | 214976987
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-10-05 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6672 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3199 | MW
i) Dhaka area |  |  | 3517 | MW | i) Khulna area |  |  | 1262 | MW
ii) Chittagong area |  |  | 977 | MW | ii) Rajshahi area |  |  | 1065 | MW
iii) Comilla area |  |  | 998 | MW | iii) Barisal area |  |  | 271 | MW
iv) Mymensingh area |  |  | 744 | MW | iv) Rangpur area |  |  | 601 | MW
v) Sylhet area |  |  | 436 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9871 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 100 | Netrokona | 83 | 1930 | Central s/s | 81 | 1900
Munsiganj | 107 | 2100 | Jamalpur | 115 | 2100 | Noapara | 86 | 2000
Sonargaon | 46 | 2000 | Sherpur | 72 | 2300 | Jessore | 137 | 1930
Shyampur | 158 | 100 | Srimongal | 36 | 1930 | Jhenida | 96 | 2000
Bhulta | 155 | 100 | Shahjibazar | 101 | 2000 | Bottail | 100 | 100
Madanganj | 53 | 2000 | Fenchuganj | 43 | 1830 | G.K Project | 53 | 2000
Shitalakhya | 93 | 100 | Kulawara | 42 | 1930 | Faridpur | 146 | 2000
Rahim steel | 10 | 2100 | Sylhet | 125 | 1930 | Madaripur | 135 | 2200
Matuail | 84 | 100 | Chatak | 26 | 1900 | Gopalganj | 82 | 2000
Ghorasal | 72 | 1930 | Sunamganj | 34 | 2000 | Bagerhat | 72 | 2000
Narsingdi | 120 | 1930 | Biani Bazar | 40 | 1830 | Mongla | 24 | 100
Haripur (SBU) | 105 | 400 | Comilla (S) | 166 | 2100 | Satkhira | 96 | 2000
Ullon | 90 | 2000 | Comilla(N) | 101 | 1900 | Gallamari | 46 | 2300
Hasnabad | 190 | 2000 | Chandpur | 118 | 1830 | Magura | 48 | 1930
Magbazar | 102 | 2100 | Feni | 131 | 1900 | Chuadanga | 72 | 2200
Maniknagar | 76 | 2000 | Chowmuhani | 184 | 1930 | Barisal | 110 | 2000
Bangabhaban | 16 | 2000 | Ashuganj | 55 | 2300 | Patuakhali | 89 | 2100
Narinda | 70 | 100 | Daudkandi | 98 | 1830 | Bhandaria | 46 | 1900
Dhanmondi | 107 | 1800 | B.Baria | 135 | 2000 | Ishurdi | 47 | 1830
Lalbag | 67 | 100 | Ramganj | 36 | 2100 | Ruppur Paromanobik | 2 | 1600
Madartek | 50 | 2000 | Madunaghat | 57 | 2000 | Natore | 104 | 2000
Mirpur | 98 | 1800 | Hathazari | 51 | 1830 | Bogra | 224 | 2000
Kalyanpur | 120 | 2000 | Khulshi | 188 | 1500 | Noagaon | 104 | 1900
Gulshan | 104 | 1830 | Halishahar | 128 | 2000 | Rajshahi | 133 | 100
Uttara | 85 | 2000 | Baraulia | 141 | 200 | C.Nawabganj | 68 | 100
Uttara(New) | 5 | 1200 | Sikalbaha | 34 | 1800 | Amnura | 45 | 1930
Kamrangirchar | 61 | 2000 | Dohazari | 92 | 1930 | Pabna | 103 | 2000
Savar | 102 | 1930 | Cox'sbazar | 72 | 1930 | Shahjadpur | 82 | 2100
Bhasantec | 145 | 2000 | Chandraghona | 33 | 1830 | Serajganj | 83 | 1930
Agargaon | 46 | 1930 | Kaptai | 4 | 1800 | Niyamatpur | 63 | 1830
Satmosjid | 95 | 1930 | A. Khaer Stl. | 15 | 1900 | Joypurhat | 45 | 2100
Tongi | 111 | 1500 | Bakulia | 89 | 2000 | Rangpur | 116 | 1930
Kabirpur | 134 | 100 | Julda | 19 | 100 | Lalmonirhat | 87 | 1930
Basundhara | 110 | 2100 | TK chemical | 5 | 1500 | Saidpur | 104 | 1930
Manikganj | 89 | 2100 | Modern Steel | 12 | 300 | Purbasadipur | 81 | 2000
Joydevpur | 208 | 100 | Shahmirpur | 31 | 100 | Thakurgaon | 63 | 2000
New Tongi | 84 | 2100 | Khagrachhari | 21 | 1800 | Palashbari | 98 | 1830
Korda | 219 | 2100 | Matarbari | 24 | 1900 | Barapukuria | 44 | 2100
Dhamrai | 48 | 2100 | Baroiar Hat | 10 | 1800 | Panchagar | 38 | 1930
Tangail | 177 | 2100 | Abul Khair 230 | 155 | 1000
Mymensing | 218 | 1830 | BSRM | 120 | 100
Kishorganj | 102 | 1900 | Goalpara | 24 | 2300
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-10-05
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 396 | 19:00 | 378 | 18:30 | Kaliakoir | 368 | 18:00 | 358 | 20:00
Bheramara | 399 | 7:00 | 392 | 1:00 | Bhulta | 381 | 18:30 | 374 | 11:00
Ashuganj(N) | 390 | 17:00 | 383 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 23:00 | 228 | 1:00 | Hathazari | 221 | 7:00 | 217 | 1:00
Ishurdi | 235 | 6:00 | 223 | 20:00 | Megnaghat | 222 | 5:00 | 219 | 12:00
Ashuganj | 238 | 7:00 | 231 | 19:00 | Fenchuganj | 235 | 8:00 | 229 | 21:00
Serajganj | 230 | 17:00 | 220 | 19:00 | Siddhirganj | 222 | 17:00 | 217 | 11:00
Baghabari | 230 | 6:00 | 219 | 19:30 | Maniknagar | 220 | 17:00 | 216 | 15:00
Barapukuria | 234 | 6:00 | 220 | 18:30 | Old Airport | 221 | 17:00 | 212 | 13:00
Bogra | 223 | 6:00 | 204 | 20:00 | Barisal | 221 | 1:00 | 212 | 12:00
Khulna South | 233 | 18:00 | 218 | 3:00 | AKSML | 220 | 6:00 | 213 | 1:00
Rampura | 220 | 3:00 | 217 | 10:00 | BSRM | 220 | 6:00 | 214 | 1:00
Haripur | 220 | 17:00 | 217 | 12:00 | Bibiyana | 232 | 6:00 | 226 | 23:00
Hasnabad | 220 | 1:00 | 216 | 11:00 | Bhulta | 223 | 16:00 | 218 | 11:00
Aminbazar | 222 | 17:00 | 213 | 11:00 | Ashuganj (S) | 233 | 17:00 | 228 | 20:00
Tongi | 220 | 15:00 | 214 | 11:00 | Kaliakoir | 225 | 4:00 | 219 | 11:00
Comilla (N) | 227 | 9:00 | 224 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 1830 | 133 | 100 | Ramganj | 122 | 900 | 112 | 1830
Munsiganj | 138 | 1830 | 132 | 1000 | Madanhat | 132 | 800 | 130 | 300
Megnaghat | 135 | 1800 | 130 | 500 | Hathazari | 132 | 700 | 128 | 300
Shyampur | 133 | 1830 | 127 | 1200 | Khulshi | 129 | 600 | 125 | 1000
Bhulta | 129 | 1700 | 126 | 800 | Halishahar | 132 | 600 | 128 | 1100
Madanganj | 137 | 1830 | 130 | 100 | Baraulia | 130 | 600 | 127 | 1000
Shitalakhya | 136 | 100 | 129 | 1200 | Sikalbaha | 131 | 600 | 127 | 1300
Rahim steal | 135 | 1800 | 132 | 100 | Dohazari | 130 | 600 | 124 | 1200
Matuail | 136 | 1830 | 132 | 900 | Cox'sbazar | 125 | 600 | 117 | 1100
Ghorasal | 135 | 800 | 124 | 100 | Chandraghona | 132 | 600 | 129 | 1100
Narsinghdi | 132 | 1300 | 120 | 1900 | Kaptai | 132 | 700 | 130 | 300
Haripur (SBU) | 136 | 1500 | 132 | 300 | A. Khaer Stl. | 129 | 700 | 126 | 1100
Ullon | 135 | 600 | 131 | 1200 | Bakulia | 130 | 600 | 126 | 1100
Hasnabad | 135 | 1700 | 130 | 1200 | Julda | 131 | 600 | 128 | 1000
Magbazar | 134 | 600 | 130 | 1300 | TK Chemical | 133 | 800 | 127 | 1930
Maniknagar | 130 | 600 | 129 | 1200 | Modern Steel | 130 | 600 | 126 | 300
Bangabhaban | 133 | 1700 | 127 | 1200 | Shahmirpur | 132 | 800 | 128 | 300
Narinda | 135 | 800 | 131 | 1200 | Khagrachhari | 132 | 500 | 129 | 1000
Dhanmondi | 135 | 600 | 131 | 1200 | Matarbari | 128 | 700 | 119 | 600
Lalbag | 133 | 1700 | 127 | 1200 | Baroiar Hat | 127 | 700 | 121 | 2100
Madartek | 135 | 800 | 131 | 1200 | Goalpara | 137 | 1800 | 132 | 400
Mirpur | 133 | 300 | 129 | 1200 | Central s/s | 136 | 100 | 131 | 500
Kalyanpur | 134 | 1700 | 128 | 1200 | Noapara | 136 | 1800 | 124 | 300
Gulshan | 134 | 300 | 130 | 1200 | Jessore | 130 | 1800 | 123 | 2000
Uttara | 128 | 600 | 123 | 1200 | Jhenida | 128 | 700 | 119 | 2000
Uttara(New) | 129 | 500 | 123 | 1200 | Bottail | 135 | 400 | 126 | 2000
Kamrangirchar | 133 | 1800 | 128 | 1200 | G.K.Project | 141 | 600 | 132 | 2000
Savar | 131 | 500 | 125 | 1200 | Faridpur | 130 | 600 | 123 | 2100
Bhasantec | 133 | 600 | 128 | 1200 | Madaripur | 134 | 600 | 126 | 2100
Agargaon | 133 | 400 | 129 | 1200 | Gopalganj | 132 | 1800 | 122 | 1200
Satmosjid | 133 | 600 | 129 | 1200 | Bagerhat | 135 | 1700 | 130 | 1200
Tongi | 132 | 1500 | 128 | 1900 | Mongla | 133 | 1700 | 128 | 1500
Kabirpur | 134 | 1700 | 125 | 1800 | Satkhira | 134 | 100 | 129 | 1200
Basundhara | 129 | 1600 | 126 | 1900 | Gallamari | 135 | 100 | 126 | 300
Manikganj | 136 | 1500 | 128 | 2000 | Magura | 130 | 1700 | 117 | 2000
Joydevpur | 138 | 100 | 133 | 1200 | Chuadanga | 125 | 700 | 113 | 2000
New Tongi | 133 | 1500 | 127 | 2000 | Barisal | 137 | 100 | 133 | 1200
Kodda | 138 | 1900 | 130 | 1200 | Patuakhali | 136 | 600 | 129 | 2100
Dhamrai | 134 | 1700 | 128 | 2100 | Bhandaria | 135 | 100 | 130 | 1200
Tangail | 134 | 500 | 125 | 2000 | Ishurdi | 140 | 600 | 130 | 2000
Mymensing | 129 | 1000 | 108 | 1830 | Ruppur Paromanobik | 140 | 1700 | 131 | 2000
Kishorganj | 126 | 1100 | 114 | 2000 | Natore | 137 | 600 | 125 | 2000
Netrokona | 128 | 600 | 115 | 1800 | Bogra | 132 | 1700 | 117 | 2000
Jamalpur | 134 | 300 | 119 | 2000 | Noagaon | 127 | 600 | 107 | 1930
Sherpur | 136 | 1300 | 114 | 1830 | Rajshahi | 132 | 500 | 123 | 2100
Srimongal | 136 | 1300 | 131 | 2000 | C.Nawabganj | 130 | 1800 | 120 | 1400
Shahjibazar | 136 | 500 | 130 | 1930 | Amnura | 132 | 800 | 121 | 1300
Fenchuganj | 136 | 600 | 130 | 2000 | Pabna | 132 | 1800 | 125 | 2100
Khulawara | 135 | 300 | 130 | 2100 | Shahjadpur | 140 | 800 | 134 | 2100
Sylhet | 135 | 600 | 127 | 1930 | Serajganj | 134 | 1700 | 123 | 2100
Chatak | 135 | 500 | 126 | 1900 | Niyamatpur | 124 | 1700 | 105 | 2100
Sunamganj | 134 | 500 | 125 | 1830 | Joypurhat | 126 | 1700 | 110 | 2100
Biani Bazar | 135 | 600 | 126 | 1900 | Rangpur | 126 | 800 | 106 | 2000
Comilla(s) | 126 | 600 | 122 | 1800 | Lalmonirhat | 125 | 600 | 95 | 2000
Comilla(n) | 135 | 1300 | 133 | 1830 | Saidpur | 126 | 800 | 105 | 2000
Chandpur | 126 | 700 | 121 | 1930 | Purbasadipur | 131 | 700 | 114 | 1930
Feni | 120 | 700 | 115 | 2000 | Thakurgaon | 128 | 600 | 100 | 1930
Chowmuhani | 122 | 900 | 115 | 1830 | Palashbari | 125 | 1700 | 105 | 2000
Ashuganj | 136 | 1400 | 130 | 2000 | Barapukuria | 134 | 700 | 120 | 2000
Daudkandi | 132 | 1700 | 128 | 2200 | Panchagar | 122 | 600 | 97 | 2000
B.Baria | 134 | 1300 | 126 | 1930

## L-Curve
Date | 2018-10-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 500 | 7453 | 2655 | 10108 |  |  |  | QF-LDC-12
0:30 | 440 | 7430 | 2791.5 | 10221.5 | Date: | 2018-10-05
1:00 | 380 | 7407 | 2928 | 10335
1:30 | 400 | 7375.5 | 2769 | 10144.5
2:00 | 420 | 7344 | 2610 | 9954
2:30 | 455 | 7244 | 2534 | 9778 | [5 empty] | Gen. at Eve. Peak | 10548 | 10548 MW (21:00 )
3:00 | 490 | 7144 | 2458 | 9602 | [6 empty] | 21:00
3:30 | 520 | 7112.5 | 2364.5 | 9477 | [5 empty] | Gen. at Day Peak | 8271 | 8271 MW (12:00 )
4:00 | 550 | 7081 | 2271 | 9352 | [6 empty] | 12:00
4:30 | 575 | 7003.5 | 2171.5 | 9175 | [5 empty] | Highest Generation | 10548
5:00 | 600 | 6926 | 2072 | 8998 | [6 empty] | 21:00
5:30 | 545 | 6678.02 | 2031 | 8709.02
6:00 | 490 | 6430.04 | 1990 | 8420.04
6:30 | 425 | 6058.22 | 1997.5 | 8055.72
7:00 | 360 | 5686.4 | 2005 | 7691.4
7:30 | 390 | 5666.7 | 2007 | 7673.7
8:00 | 420 | 5647 | 2009 | 7656
8:30 | 345 | 5629.5 | 2018.5 | 7648
9:00 | 270 | 5612 | 2028 | 7640
9:30 | 265 | 5674.5 | 2050 | 7724.5
10:00 | 260 | 5737 | 2072 | 7809
10:30 | 250 | 5809.5 | 2092 | 7901.5
11:00 | 240 | 5882 | 2112 | 7994
11:30 | 300 | 6039 | 2093.5 | 8132.5
12:00 | 360 | 6196 | 2075 | 8271
12:30 | 410 | 6190.05 | 2064 | 8254.05
13:00 | 460 | 6184.1 | 2053 | 8237.1
13:30 | 450 | 6143 | 2060.5 | 8203.5
14:00 | 440 | 6101.9 | 2068 | 8169.9
14:30 | 445 | 6239.7 | 2056.5 | 8296.2
15:00 | 450 | 6377.5 | 2045 | 8422.5
15:30 | 430 | 6276.65 | 1990 | 8266.65
16:00 | 410 | 6175.8 | 1935 | 8110.8
16:30 | 385 | 6001.7 | 1890.5 | 7892.2
17:00 | 360 | 5827.6 | 1846 | 7673.6
17:30 | 340 | 6220.3 | 2171.5 | 8391.8
18:00 | 320 | 6613 | 2497 | 9110
18:30 | 390 | 6971.5 | 2740.5 | 9712
19:00 | 460 | 7330 | 2984 | 10314
19:30 | 500 | 7513 | 2982 | 10495
20:00 | 470 | 7459 | 3052 | 10511 |  |  |  | Executive Engineer
20:30 | 485 | 7499.5 | 3030 | 10529.5 |  |  |  | Network Operation Division
21:00 | 500 | 7540 | 3008 | 10548
21:30 | 480 | 7534.5 | 3001.5 | 10536
22:00 | 460 | 7529 | 2995 | 10524 |  |  |  |  | Page 6 of 7
22:30 | 460 | 7521.5 | 2900.5 | 10422
23:00 | 460 | 7514 | 2806 | 10320
23:30 | 480 | 7483.5 | 2730.5 | 10214
24:00 | 500 | 7453 | 2655 | 10108
10548 MW (21:00 )
8271 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-10-05 |  | Energy | 216688473
[10 empty] | 2018-10-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3870 | 713 | 2339 | 1913 | 160 | 142 | 815 | 0 | 156
0:30 | 3974 | 743 | 2234.5 | 2017 | 171.5 | 140.5 | 788 | 0 | 153 | Date: | 2018-10-05
1:00 | 4078 | 773 | 2130 | 2121 | 183 | 139 | 761 | 0 | 150
1:30 | 4081.5 | 773.5 | 2120.5 | 2084 | 183.5 | 140.5 | 613 | 0 | 148 | [7 empty] | Total Energy | 216.6885 | Total Energy Gen 216.688 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.688 MKWHr
2:00 | 4085 | 774 | 2111 | 2047 | 184 | 142 | 465 | 0 | 146 | [7 empty] | Energy not Served | 0
2:30 | 4096 | 773.5 | 2119 | 1914 | 184 | 142 | 405.5 | 0 | 144 | [7 empty] | Energy Requirement | 216.6885
3:00 | 4107 | 773 | 2127 | 1781 | 184 | 142 | 346 | 0 | 142
3:30 | 4104 | 773 | 2131.5 | 1727 | 184 | 128 | 289.5 | 0 | 140 | [6 empty] | Shortage
4:00 | 4101 | 773 | 2136 | 1673 | 184 | 114 | 233 | 0 | 138
4:30 | 4036.5 | 773.5 | 2135.5 | 1570.5 | 184 | 114 | 225 | 0 | 136
5:00 | 3972 | 774 | 2135 | 1468 | 184 | 114 | 217 | 0 | 134
5:30 | 3946.5 | 773.5 | 2084.5 | 1271 | 181 | 114 | 208.5 | 0 | 130
6:00 | 3921 | 773 | 2034 | 1074 | 178 | 114 | 200 | 0 | 126
6:30 | 3858 | 773 | 1878 | 936 | 178 | 114 | 201.5 | 0 | 115 |  |  |  |  | Coal
7:00 | 3795 | 773 | 1722 | 798 | 178 | 114 | 203 | 0 | 104
7:30 | 3771.5 | 773 | 1722 | 800.5 | 179 | 114 | 205 | 0 | 101 |  |  |  | Oil |  |  |  | ,
8:00 | 3748 | 773 | 1722 | 803 | 180 | 114 | 207 | 0 | 98
8:30 | 3735 | 773 | 1753 | 832 | 179.5 | 114 | 149.5 | 0 | 99
9:00 | 3722 | 773 | 1784 | 861 | 179 | 114 | 92 | 0 | 100
9:30 | 3738.5 | 773 | 1813 | 871.5 | 179.5 | 114 | 113 | 0 | 105
10:00 | 3755 | 773 | 1842 | 882 | 180 | 114 | 134 | 0 | 110
10:30 | 3770 | 773 | 1865 | 904 | 180 | 128 | 149 | 0 | 112
11:00 | 3785 | 773 | 1888 | 926 | 180 | 142 | 164 | 0 | 114
11:30 | 3771 | 773 | 2047 | 943.5 | 170 | 142 | 151 | 0 | 114
12:00 | 3757 | 773 | 2206 | 961 | 160 | 142 | 138 | 0 | 114
12:30 | 3745.5 | 773 | 2164.5 | 992 | 160 | 142 | 138.5 | 0 | 118
13:00 | 3734 | 773 | 2123 | 1023 | 160 | 142 | 139 | 0 | 122
13:30 | 3734 | 773 | 2123 | 1023 | 160 | 142 | 139 | 0 | 122
14:00 | 3734 | 773 | 2123 | 1023 | 160 | 142 | 139 | 0 | 122
14:30 | 3767 | 746 | 2174.5 | 1060 | 160 | 142 | 137.5 | 0 | 126
15:00 | 3800 | 719 | 2226 | 1097 | 160 | 142 | 136 | 0 | 130
15:30 | 3800 | 719 | 2136 | 1034 | 160 | 142 | 140.5 | 0 | 125
16:00 | 3800 | 719 | 2046 | 971 | 160 | 142 | 145 | 0 | 120
16:30 | 3785.5 | 719 | 1865.5 | 938.5 | 160 | 142 | 159 | 0 | 118
17:00 | 3771 | 719 | 1685 | 906 | 160 | 142 | 173 | 0 | 116
17:30 | 3832 | 719 | 1862.5 | 1152 | 160 | 142 | 389.5 | 0 | 134
18:00 | 3893 | 719 | 2040 | 1398 | 160 | 142 | 606 | 0 | 152
18:30 | 3963 | 719 | 2125.5 | 1707 | 160 | 142 | 739.5 | 0 | 156
19:00 | 4033 | 719 | 2211 | 2016 | 160 | 142 | 873 | 0 | 160
19:30 | 3881 | 719 | 2263 | 2119 | 160 | 142 | 1049 | 0 | 162
20:00 | 3906 | 719 | 2264 | 2046 | 159 | 142 | 1111 | 0 | 164
20:30 | 3927 | 719 | 2291.5 | 2037 | 159 | 142 | 1089 | 0 | 165
21:00 | 3948 | 719 | 2319 | 2028 | 159 | 142 | 1067 | 0 | 166
21:30 | 3932.5 | 716 | 2347.5 | 2012 | 159.5 | 142 | 1060.5 | 0 | 166
22:00 | 3917 | 713 | 2376 | 1996 | 160 | 142 | 1054 | 0 | 166
22:30 | 3906 | 713 | 2366 | 1983.5 | 160 | 142 | 987.5 | 0 | 164
23:00 | 3895 | 713 | 2356 | 1971 | 160 | 142 | 921 | 0 | 162
23:30 | 3882.5 | 713 | 2347.5 | 1942 | 160 | 142 | 868 | 0 | 159 | Max Temp. in Dhaka |  | 34.2° C
24:00 | 3870 | 713 | 2339 | 1913 | 160 | 142 | 815 | 0 | 156
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 216.688 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.688 MKWHr
Note on W13: Author:

## Generation
2018-10-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 109 | 112 | 112 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2396618
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 726000
3 | Chittagong ST-1 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3000000
4 | Chittgong ST-2 (Raozan) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3200000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 344520
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.04 | 4.1 | 11 | 14 | 18 | 20 | 20 | 20 | 19.3 | 11.5 | 7.2 | 1.5 | 0 |  | 0 | [6 empty] | 129810
6 | Sikalbaha 225MW (Gas) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 40 | 40 | 40 | 35 | 40 | 13 | 87 | 128 | 206 | 200 |  | 199 | 199 | 199 | 213 | 201 | 202 | 200 | 2593388
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 23 | 0 | [8 empty] | 519400
9 | Sikalbaha GT 150MW (Gas) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2164187
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 0 | [8 empty] | 0 |  | 32 | 46 | 45 | 46 | 46 | 46 | 46 | 526808
12 | Hathazari peaking | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 0 | [7 empty] | 0 | 36 |  | 81 | 81 | 81 | 81 | 81 | 72 | 72 | 1098068
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 40 |  | 0 | [6 empty] | 41072
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 238 | 240 | 238 | 240 | 238 | 210 | 87 | 47 | 45 | 45 | 45 | 47 | 80 | 130 | 143 | 155 | 170 | 203 |  | 253 | 253 | 266 | 270 | 270 | 275 | 270 | 4220289
19 | Ashuganj 195MW Modular | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1672727
20 | Ghorasal ST: Unit-1,2 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1525000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 180 | 190 | 190 | 190 | 190 | 4504500
24
25 | Ghorasal ST: Unit-7 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 356 | 330 | 380 | 380 | 300 | 380 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8922581
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 2362754
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 2264068
32 | Ashuganj Engines TSK | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | [11 empty] | 16 | 19 | 19 | 19 | 19 | 239688
33 | Ashuganj CCPP 225 MW | 164 | 173 | 173 | 173 | 167 | 173 | 176 | 180 | 175 | 190 | 187 | 189 | 185 | 194 | 179 | 178 | 179 | 192 |  | 217 | 217 | 211 | 184 | 190 | 202 | 206 | 4503000
34 | Ashuganj CCPP(South) | 290 | 290 | 301 | 301 | 302 | 301 | 301 | 301 | 276 | 287 | 301 | 309 | 301 | 316 | 301 | 301 | 301 | 302 |  | 305 | 305 | 305 | 323 | 296 | 300 | 300 | 7375000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8974700
35 | Ashuganj (Precision) 55MW | [14 empty] | 0
36 | Chandpur CCPP | 121 | 126 | 127 | 126 | 126 | 121 | 120 | 142 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 137 | 3152780
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 366 | 379 | 397 | 412 | 416 | 390 | 340 | 300 | 320 | 345 | 350 | 350 | 360 | 345 | 350 | 345 | 345 | 345 |  | 345 | 345 | 345 | 365 | 370 | 345 | 345 | 8699910
40 | Meghnaghat CCPP 450MW | 450 | 450 | 450 | 450 | 450 | 400 | 340 | 340 | 340 | 340 | 370 | 450 | 450 | 380 | 400 | 370 | 370 | 400 |  | 370 | 370 | 370 | 400 | 450 | 450 | 450 | 9292500
41 | Haripur Power CCPP 360MW | 354 | 357 | 358 | 356 | 355 | 354 | 292 | 271 | 311 | 340 | 345 | 346 | 246 | 311 | 354 | 354 | 283 | 332 |  | 354 | 355 | 353 | 352 | 354 | 354 | 357 | 8045000
42 | Mymensingh RPCL 210MW | 46 | 46 | 46 | 47 | 47 | 47 | 46 | 47 | 46 | 45 | 44 | 45 | 45 | 44 | 44 | 45 | 45 | 45 |  | 17 | 33 | 31 | 46 | 53 | 93 | 93 | 1143400
43 | Haripur NEPC 110MW | [16 empty] | 0 | 13 |  | 0
44 | Fenchugonj CCPP-1 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 54 | 54 | 55 | 54 | 53 | 54 | 54 | 54 | 54 |  | 60 | 60 | 60 | 55 | 55 | 54 | 53 | 1261000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1396400
46 | Shajibazar 330 MW | 304 | 300 | 300 | 307 | 308 | 302 | 302 | 300 | 312 | 310 | 312 | 319 | 304 | 312 | 300 | 302 | 299 | 312 |  | 301 | 300 | 318 | 325 | 325 | 300 | 300 | 6883570
47 | Shahjibazar GT: Unit- 8, 9 | 65 | 66 | 40 | 54 | 65 | 68 | 63 | 66 | 63 | 63 | 62 | 62 | 63 | 63 | 63 | 65 | 51 | 64 |  | 65 | 65 | 64 | 63 | 64 | 65 | 66 | 1454000
48 | Shahjibazar 86MW | 89 | 89 | 89 | 89 | 89 | 89 | 10 | 10 | 10 | 10 | 10 | 86 | 88 | 87 | 82 | 40 | 10 | 50 |  | 86 | 89 | 89 | 89 | 89 | 89 | 89 | 1596480
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 45 | 45 | 43 | 45 | 45 | 45 | 45 | 45 | 10 | 10 |  | 44 | 44 | 44 | 44 | 45 | 45 | 45 | 1001160
50 | Sylhet GT 150 MW | 100 | 100 | 100 | 100 | 100 | 100 | 22 | 0 | [18 empty] | 691290
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | [10 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 270000
52 | Sylhet (EPL) 50MW | 43 | 43 | 43 | 43 | 44 | 43 | 12 | 12 | 36 | 42 | 42 | 42 | 41 | 42 | 42 | 40 | 20 | 41 |  | 44 | 44 | 44 | 44 | 44 | 44 | 45 | 933440
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 215820
54 | Hobiganj 11MW | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253056
55 | Fenchugonj (Barakatullah) 51MW | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 47 | 11 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1076400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 24 | 24 | 8 | 8 | 21 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 523056
57 | Summit Bibiana- 2 | 285 | 265 | 280 | 290 | 290 | 265 | 260 | 275 | 280 | 310 | 310 | 315 | 310 | 275 | 300 | 280 | 280 | 290 |  | 280 | 300 | 300 | 320 | 320 | 300 | 280 | 7376800
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 36 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1032440
59 | Sikalbaha (Energis) | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 24 | 24 | 32 | 32 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 967680
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 518496
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 0 | 0 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 418248
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 514800
63 | Tripura | 150 | 146 | 142 | 138 | 134 | 126 | 104 | 98 | 100 | 110 | 114 | 114 | 122 | 126 | 130 | 120 | 116 | 152 |  | 160 | 162 | 164 | 166 | 166 | 162 | 156 | 3195840
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 40 | 40 | 40 | 30 | 30 | 33 | 32 | 32 | 15 | 15 | 15 | 34 | 34 | 33 | 35 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 848160
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509904
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 234900
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823200
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 521070
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 550000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 20 |  | 24 | 24 | 26 | 32 | 32 | 32 | 32 | 597060
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817296
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 824100
73 | Ghorashal (Regent) | [11 empty] | 80 | 94 | 92 | 92 | 91 | 22 | 48 |  | 82 | 85 | 86 | 90 | 91 | 90 | 90 | 934636
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | 90 | 90 | 90 | 90 | 40 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 |  | 70 | 89 | 89 | 89 | 89 | 89 | 90 | 1074240
78 | Gazipur (RPCL) | 41 | 41 | 41 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 |  | 37 | 49 | 49 | 49 | 41 | 49 | 41 | 568356
79 | Kodda 149 MW | 149 | 115 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 28 |  | 105 | 115 | 115 | 115 | 115 | 82 | 48 | 1165440
80 | Jamalpur 95MW | 71 | 71 | 71 | 71 | 24 | 7 | 7 | 7 | 7 | 11 | 58 | 64 | 64 | 24 | 7 | 7 | 7 | 40 |  | 68 | 66 | 65 | 71 | 71 | 71 | 71 | 1039680
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | 98 | 98 | 98 | 98 | 98 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 70 | 75 | 80 | 80 | 80 | 80 | 94 | 1240488
83 | Pagla (DPA ) | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 46 | 46 | 46 | 46 | 46 | 45 | 46 | 45 | 46 | 46 | 45 |  | 0 | 0 | 0 |  |  |  |  | 537240
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 10 | 10 | 10 | 10 | 10 | 80 | 85 | 85 | 85 | 11 | 11 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1240488
85 | Keraniganj (Powerpac) 100MW | 85 | 85 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 613790
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 100 | 100 | 78 | 46 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 18 |  | 95 | 100 | 75 | 65 | 65 | 65 | 50 | 946560
88 | Ghorashal 78MW (MAX) | [13 empty] | 10 | 71 | 60 | 40 | 50 |  | 79 | 79 | 79 | 79 | 78 | 80 | 80 | 715008
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 90 | 90 | 90 | 80 | 80 | 80 |  | 80 | 80 | 90 | 90 | 80 | 90 | 90 | 2031360
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 47 | 47 | 50 | 20 | 31 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1139000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 96 | 60 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 |  | 32 | 32 | 7 | 7 | 7 | 7 | 7 | 433728
95 | Patenga 50MW | 43 | 44 | 43 | 43 | 38 | 40 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 24 | 20 |  | 29 | 40 | 40 | 40 | 45 | 45 | 46 | 884640
96 | Chittagong ECPV 108 MW | 92 | 98 | 98 | 94 | 98 | 94 | 83 | 85 | 74 | 53 | 53 | 53 | 50 | 52 | 52 | 18 | 18 | 37 |  | 94 | 99 | 99 | 99 | 99 | 99 | 99 | 1828800
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 40 | 39 | 12 | 0 | 1 | 6 | 6 | 10 | 34 | 40 | 40 | 18 | 18 | 18 |  | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 731280
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159360
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 15 | 15 | 15 |  | 47 | 48 | 40 | 47 | 47 | 47 | 47 | 826489
100 | Northern 55 MW | 55 | 56 | 56 | 56 | 56 | 35 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 | 18 | 18 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 901354
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 |  | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 2973837
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.3 | 0 | 1 | 1 | 2 | 0 | 1.1 | 1.6 | 1 | 0.6 | 0.1 | 0 |  | 0 | [6 empty] | 12700
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 36 | 0 | 18 | 18 | 547200
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 185 | 187 | 182 | 187 | 180 | 85 | 55 | 57 | 127 | 178 | 175 | 166 | 175 | 178 | 175 | 175 | 175 | 168 |  | 165 | 177 | 177 | 177 | 180 | 180 | 180 | 3852000
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 105 | 105 | 105 | 105 | 105 | 100 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 70 | 81 | 76 | 50 | 69 |  | 105 | 106 | 106 | 102 | 103 | 105 | 103 | 2059200
115
116
117
118
120 | Eastern Zone Total | 7407 | 7344 | 7144 | 7081 | 6926 | 6430.04 | 5686.4 | 5647 | 5612 | 5737 | 5882 | 6196 | 6184.1 | 6101.9 | 6377.5 | 6175.8 | 5827.6 | 6613 |  | 7330 | 7513 | 7459 | 7540 | 7529 | 7514 | 7453 | 159520308
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 99 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 84 |  | 95 | 101 | 101 | 98 | 93 | 88 | 89 | 912000
125 | Khulna (KPCL-2) | 115 | 115 | 86 | 83 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 56 |  | 83 | 99 | 99 | 99 | 115 | 115 | 115 | 1298880
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 17 | 0 | [13 empty] | 6 | 12 | 30 |  | 43 | 43 | 43 | 40 | 36 | 35 | 35 | 287040
129 | Khulna CCPP 225MW | 80 | 0 | 0 | 15 | 15 | 15 | 15 | 20 | 40 | 90 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 180 |  | 241 | 243 | 242 | 243 | 243 | 210 | 165 | 2692800
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 80 | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 48 | 60 | 80 | 48 | 48 | 96 |  | 96 | 98 | 96 | 96 | 98 | 96 | 98 | 1632000
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 96 | 96 | 96 | 97 | 96 | 95 | 93 | 91 | 92 | 90 | 90 | 95 | 96 | 40 | 75 |  | 95 | 95 | 97 | 98 | 98 | 97 | 96 | 2222169
| Bhola CCPP 194MW | 178 | 172 | 179 | 169 | 178 | 154 | 169 | 154 | 179 | 179 | 179 | 180 | 160 | 180 | 179 | 153 | 155 | 179 |  | 154 | 169 | 179 | 179 | 179 | 178 | 154 | 4224220
140 | Bhola (Venture) 33MW | 34 | 32 | 32 | 32 | 31 | 22 | 23 | 22 | 22 | 23 | 23 | 22 | 24 | 24 | 26 | 24 | 23 | 28 |  | 35 | 35 | 35 | 36 | 36 | 35 | 35 | 679482
141 | Bangla Trak Noapara | [17 empty] | 20 |  | 96 | 96 | 96 | 96 | 96 | 62 | 20 | 519360
142 | Noapara (KZA) 40MW | 32 | 32 | 32 | 32 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 471375
143 | Gopalganj Peaking | 48 | 43 | 19 | 17 | 17 | 0 |  |  |  |  | 0 | 2 | 3 | 2 | 0 | 3 | 15 | 42 |  | 88 | 80 | 80 | 71 | 60 | 57 | 51 | 597504
144 | Bheramara GT-1,2,3 | [19 empty] | 32 | 32 | 32 | 0 |  |  |  | 69500
145
146 | Bheramara HVDC | 773 | 774 | 773 | 773 | 774 | 773 | 773 | 773 | 773 | 773 | 773 | 773 | 773 | 772 | 719 | 719 | 719 | 719 |  | 719 | 719 | 719 | 719 | 713 | 713 | 713 | 18105454
147 | Bheramara 360 MW | 350 | 350 | 350 | 200 | 0 | [14 empty] | 75 | 80 | 78 | 80 | 68 | 40 | 40 | 1794240
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 183 | 184 | 184 | 184 | 184 | 178 | 178 | 180 | 179 | 180 | 180 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 159 | 159 | 160 | 160 | 160 | 4167600
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 |  | 271888
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) |  |  | 0 | 121 | 172 | 174 | 171 | 171 | 175 | 180 | 195 | 189 | 193 | 181 | 186 | 171 | 146 | 136 |  | 193 | 0 | 0 |  |  |  |  | 2756750
| Sirajgonj Unit-2 225MW (Oil) | 197 | 130 | 126 | 0 | [16 empty] | 158 | 220 | 220 | 220 | 220 | 220 | 1711486
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 301 | 301 | 300 | 301 | 301 | 301 | 301 | 301 | 296 | 293 | 292 | 291 | 293 | 290 | 291 | 292 | 295 | 293 |  | 300 | 295 | 297 | 295 | 299 | 300 | 301 | 7115364
161 | Bera Peaking | 53 | 0 | [14 empty] | 10 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 427022
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 17 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496560
163 | Bogra (EPL) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 11 | 9 | 11 | 11 | 11 | 11 | 9 | 11 | 11 |  | 11 | 11 | 9 | 11 | 11 | 11 | 10 | 233604
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 217188
165 | Amnura 50MW | 12 | 12 | 12 | 12 | 12 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 12 | 12 | 12 | 12 | 12 | 34 |  | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 746200
166 | Katakhali (Northern) | 50 | 50 | 24 | 24 | 24 | 43 | 43 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 8 | 24 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1010928
167 | Katakhali Peaking | 36 | 36 | 28 | 28 | 28 | 28 | 36 | 36 | 36 | 28 | 28 | 0 |  | 0 | 0 | 0 |  | 29 |  | 30 | 30 | 32 | 30 | 30 | 30 | 30 | 535935
168 | Santahar Peaking
169 | Rajlanka 52 MW | 52 | 50 | 25 | 25 | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 15 |  | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 1004640
170 | Chapainawabganj-100 MW | 70 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 0 | [8 empty] | 90 |  | 90 | 90 | 90 | 90 | 90 | 85 | 64 | 773976
171
172
173 | Rangpur GT | [17 empty] | 10 |  | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 71000
175 | Saidpur GT | [17 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 122000
176
177
178
178 | Western Zone Total | 2928 | 2610 | 2458 | 2271 | 2072 | 1990 | 2005 | 2009 | 2028 | 2072 | 2112 | 2075 | 2053 | 2068 | 2045 | 1935 | 1846 | 2497 | 0 | 2984 | 2982 | 3052 | 3008 | 2995 | 2806 | 2655 | 57168165