## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-10-02 | Tuesday
|  | Date (day): | 2018-10-02 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12020 | MW |  |  | (b) At Evening Peak Hour : |  | 12765 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-10-01 | 2018-10-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 74 | 74 | 11 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120 | 70 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 280 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 389 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 110 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 350 | 321 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 83 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 78 | 50 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 60 | 100 | 100 | 110
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 90 | 29 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 83 | 85 | 90 | 90 |  | 10
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint. |  | 21/10/18
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 45 | 48 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 39 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 52 | 59 | 59 | 59 |  | 49 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 50 | 50 |  | 30 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 48 | 40 | 40 |  | 12 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 218 | 270 | 275 | 275 |  | 25 | Engine problem
35 | APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 106 | 300 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 50 | 100 | 96 | 100
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 100 | 100 | 100 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 97 | 90 | 107 | 107 |  | 34 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 3545 | 3590 | 4156 | 4465 | 522 | 853
39 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 125 | 120 | 120 | 60 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 170 | 120 | 120 |  |  | Gas shortage
40 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 3.5 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 42 | 43 | 43
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 142 | 144 | 145 | 145 |  |  | #5 Under maint.
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint. |  | 2018-04-10
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 135 | 135 | 135
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 38 | 50 | 40 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 82 | 86 | 86
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 23 | 31 | 50 | 50
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 90 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 15 | 15
51 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 92 | 92 | 92 |  | 16 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 855.5 | 1019 | 1010 | 1000 | 60 | 281
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 120 | 110 | 100
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 110 | 0 | 0 | 0 |  | 129 | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 120 | 130 | 110 | 120 |  |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 100 | 205 | 225 | 225
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 253 | 309 | 360 | 360 |  |  | FGMO
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 19 | 42 | 42
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 73 | 68 | 68
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Devolopment work.
61 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
62 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 0 | 41
63 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 0 | 130 | 130
64 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
65 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 136 | 156 | 129 | 174
66 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
67 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 0 | 52 | 52
68 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
69 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 10 | 200 | 200 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1472 | 1782 | 1955 | 2041 | 0 | 235
70 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 67 | 48 | 70 | 70 | 132 |  | Gas shortage
71 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
72 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 70 | 68 | 80 | 80
73 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
74 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 177 | 187 | 190 | 190 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 336.1 | 325 | 364 | 362 | 132 | 0
75 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 60 | 60 | 60
76 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 |  | 30
77 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
78 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 301 | 300 | 330 | 330
79 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
80 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 50
81 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
82 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 62 | 66 | 66
83 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
84 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 46 | 45 | 45
85 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 98 | 80 | 100 | 100
86 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under Maint.
87 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 43 | 44 | 44
88 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
89 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 265 | 341 | 341 |  |  | FGMO
90 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1353 | 1246 | 1434 | 1440 | 0 | 30
91 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 103 | 762 | 772 | 772
92 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 67 | 91 | 100 | 100 |  | 10 | Engine problem
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 97 | 115 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 0 | 36
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 232 | 234 | 230 | 230
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 85 | 0 | 85
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 413 | 350 | 410 | 410
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 24 | 24 | 40 | 40
| Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 95 | 95
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 936 | 1793 | 1762 | 1931 | 0 | 10
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 24 | 0 | 26
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 35 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 128 | 148 | 188 | 188 |  | 6
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 356 | 414 | 426 | 452 | 0 | 6
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 51 | 0 | 52
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 40 | 40
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 214 | 216 | 216
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 203 | 220 | 220
113 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 0 | 0 | 0 | 0 |  | 141 | under maint.
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
114 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 31
115 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 0 | 22 | 22
116 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 6 | 8 | 11 | 11
117 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
118 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
119 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 90 | 90 |  |  | Engine problem
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 519 | 841 | 753 | 886 | 71 | 250
120 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
121 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 | 114 |  | Coal shortage
122 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 10
123 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 160 | 188 | 160 | 188 | 199 | 85
| Total |  |  |  |  | 17043 | 16445 | 9532.6 | 11198 | 12020 | 12765 | 984 | 1750
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9072.0591 | 10657 | 11439.2874 | 12148.2948
A. |  | 2018-10-01 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11198 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8265.9 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11198 | MW
3 | Day peak Generation : |  |  | 9532.6 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10657 | MW
4 | Evening peak Generation : |  |  | 11198 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 239.3922 | MKWHr | By Solar | 0.08716 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 143.644 | MKWHr |  | By Oil: | 72.5523 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.2238 | MKWHr |  | By Hydro: | 3.302 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 984 | MW | Dhaka | 4092 | 4092 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1750 | MW | Chittagong | 1070 | 1070 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2734 | MW | Khulna | 1339 | 1339 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1183.77 |  | MMCFD |  |  | Rajshahi | 1122 | 1122 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 106855306.464 | ii) Oil : | Taka | 686340956.83 | Comilla | 918 | 918 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16303868 | Total | Taka | 809500131.294 | Mymensingh | 781 | 781 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 4.0185 | MKWHr. | Sylhet | 473 | 473 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -380 | MW at | 19:00 | hrs | Barisal | 267 | 267 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -580 | MW at | 13:00 | hrs | Rangpur | 595 | 595 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.1° C |  |  | Total | 10657 | 10657 |  | 0
B. |  | 2018-10-02 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12765 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
4 | Reserve(Generation end) |  |  |  | 1165 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 247.9862 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8120.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.0473 | MKWHr. | ii) HVDC Flow at Peak Time |  | 762 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5357 | MKWHr. | iii) Maximum HVDC Flow : |  | 763 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.43 |  | (b) Today: | 103.43 |  | (c) Rule Curve: |  | 105.28
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-10-01
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 345 | 350 | 13 | 0 | 450 | 0 | 65 | 80 | 55 | 0 | 0 | 102 | 0 | 50 | 50 | 149 | 50 | 59 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 111 | 30 | 100 | 140 | 25 | 158 | 0 | 70 | 0 | 0 | 50 | 72 | 47 | 80 | 86 | 43 | 19 | 40 | 100 | 130 | 120 | 360 | 309 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 156 | 89 | 76 | 20 | 0 | 58 | 60 | 47 | 50 | 130 | 312 | 64 | 89 | 45 | 130 | 0 | 45 | 9 | 300 | 24 | 11 | 10 | 273 | 0 | 0 | 180 | 0 | 89 | 0 |  | 763 | 0 | 418 | 95 | 115 | 238 | 0 | 0 | 35 | 70 | 24 | 126 | 35 | 110 | 0 | 0 | 0 | 50 | 45 | 73 | 50 | 50 | 36 | 43 | 31 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 19 | 217 | 0 | 0 | 220 | 96 | 95 | 0 | 0 | 0 |  | 7497 | 3267 | 10764 | 4408 | 763 | 1876 | 2124 | 160 | 141 | 1136 | 156 | 0 | 0 | 103.48
2:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 345 | 352 | 13 | 0 | 450 | 0 | 30 | 80 | 55 | 0 | 0 | 104 | 0 | 20 | 7 | 135 | 20 | 59 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 113 | 30 | 100 | 140 | 25 | 141 | 0 | 100 | 0 | 0 | 50 | 72 | 47 | 80 | 86 | 43 | 19 | 40 | 100 | 130 | 120 | 360 | 305 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 154 | 89 | 76 | 20 | 0 | 58 | 60 | 47 | 50 | 130 | 300 | 64 | 89 | 45 | 100 | 0 | 45 | 9 | 300 | 16 | 11 | 10 | 260 | 0 | 0 | 180 | 0 | 102 | 0 |  | 763 | 0 | 424 | 97 | 115 | 239 | 0 | 0 | 35 | 65 | 32 | 129 | 37 | 110 | 0 | 0 | 0 | 0 | 45 | 73 | 50 | 50 | 36 | 43 | 14 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 18 | 217 | 0 | 0 | 220 | 97 | 50 | 0 | 0 | 0 |  | 7267 | 3172 | 10439 | 4378 | 763 | 1881 | 1951 | 160 | 143 | 1009 | 154 | 0 | 0 | 103.47
3:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 346 | 352 | 13 | 0 | 450 | 0 | 7 | 73 | 55 | 0 | 0 | 103 | 0 | 7 | 7 | 100 | 10 | 51 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 112 | 30 | 100 | 140 | 25 | 94 | 0 | 100 | 0 | 0 | 40 | 72 | 47 | 80 | 92 | 43 | 19 | 25 | 100 | 130 | 120 | 360 | 305 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 148 | 88 | 7 | 20 | 0 | 58 | 60 | 47 | 50 | 130 | 300 | 64 | 89 | 45 | 130 | 0 | 45 | 9 | 300 | 8 | 11 | 10 | 275 | 0 | 0 | 180 | 0 | 88 | 0 |  | 763 | 0 | 425 | 99 | 115 | 200 | 0 | 0 | 35 | 25 | 24 | 130 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 73 | 50 | 50 | 36 | 27 | 0 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 18 | 217 | 0 | 0 | 220 | 96 | 0 | 0 | 0 | 0 |  | 7051 | 2963 | 10014 | 4354 | 763 | 1865 | 1746 | 160 | 142 | 836 | 148 | 0 | 0 | 103.46
4:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 365 | 350 | 13 | 0 | 450 | 0 | 7 | 48 | 14 | 0 | 0 | 103 | 0 | 7 | 7 | 60 | 10 | 8 | 0 | 40 | 18 | 18 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 112 | 30 | 100 | 140 | 26 | 25 | 0 | 100 | 0 | 0 | 40 | 64 | 47 | 80 | 86 | 43 | 20 | 35 | 100 | 130 | 120 | 360 | 327 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 148 | 88 | 7 | 20 | 0 | 58 | 60 | 47 | 50 | 163 | 300 | 64 | 89 | 45 | 130 | 0 | 45 | 9 | 310 | 8 | 11 | 10 | 273 | 0 | 0 | 182 | 0 | 88 | 0 |  | 763 | 0 | 421 | 96 | 98 | 140 | 0 | 0 | 35 | 20 | 24 | 130 | 36 | 110 | 0 | 0 | 0 | 0 | 0 | 73 | 50 | 50 | 36 | 25 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 12 | 18 | 216 | 0 | 0 | 220 | 97 | 0 | 0 | 0 | 0 |  | 6876 | 2870 | 9746 | 4319 | 763 | 1916 | 1573 | 160 | 142 | 725 | 148 | 0 | 0 | 103.45
5:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 360 | 354 | 13 | 0 | 450 | 0 | 7 | 48 | 14 | 0 | 0 | 103 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 40 | 18 | 18 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 112 | 30 | 100 | 140 | 26 | 0 | 0 | 135 | 0 | 0 | 40 | 64 | 47 | 80 | 93 | 43 | 20 | 35 | 100 | 130 | 120 | 360 | 323 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 146 | 88 | 7 | 20 | 0 | 58 | 60 | 47 | 50 | 163 | 300 | 65 | 89 | 45 | 100 | 0 | 45 | 9 | 320 | 15 | 11 | 10 | 275 | 0 | 0 | 182 | 0 | 103 | 0 |  | 763 | 0 | 423 | 96 | 102 | 120 | 0 | 0 | 35 | 15 | 24 | 132 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 73 | 50 | 50 | 36 | 25 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 217 | 0 | 0 | 200 | 97 | 0 | 0 | 0 | 0 |  | 6879 | 2799 | 9678 | 4303 | 763 | 1925 | 1601 | 160 | 142 | 638 | 146 | 0 | 0 | 103.44
6:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 360 | 291 | 0 | 0 | 370 | 0 | 7 | 50 | 14 | 0 | 0 | 38 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 40 | 18 | 18 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 112 | 30 | 100 | 140 | 26 | 0 | 0 | 135 | 0 | 0 | 40 | 4 | 17 | 80 | 86 | 43 | 20 | 37 | 100 | 130 | 120 | 360 | 305 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 136 | 89 | 7 | 20 | 0 | 58 | 60 | 47 | 50 | 100 | 292 | 64 | 86 | 45 | 100 | 0 | 45 | 9 | 300 | 16 | 11 | 10 | 273 | 0 | 0 | 182 | 0 | 103 | 0 |  | 763 | 0 | 345 | 10 | 115 | 120 | 0 | 0 | 10 | 0 | 24 | 132 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 0 | 25 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 217 | 0 | 0 | 140 | 97 | 0 | 0 | 0 | 0 |  | 6377 | 2484 | 8861 | 4070 | 763 | 1693 | 1508 | 160 | 142 | 389 | 136 | 0 | 0 | 103.43
7:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 365 | 339 | 0 | 0 | 420 | 0 | 7 | 15 | 14 | 0 | 0 | 38 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 40 | 18 | 18 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 113 | 30 | 100 | 140 | 8 | 0 | 0 | 135 | 0 | 0 | 40 | 0 | 17 | 80 | 83 | 43 | 19 | 37 | 100 | 130 | 120 | 360 | 305 | 0 | 68 | 100 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 118 | 90 | 7 | 20 | 0 | 58 | 60 | 47 | 50 | 100 | 300 | 57 | 84 | 45 | 97 | 0 | 45 | 9 | 310 | 24 | 11 | 0 | 183 | 0 | 0 | 182 | 0 | 103 | 3 |  | 690 | 0 | 380 | 10 | 82 | 120 | 0 | 0 | 0 | 0 | 24 | 130 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 25 | 0 | 22 | 10 | 8 | 0 | 0 | 159 | 0 | 0 | 217 | 0 | 0 | 130 | 97 | 0 | 0 | 0 | 0 |  | 6288 | 2339 | 8627 | 4114 | 690 | 1798 | 1319 | 159 | 143 | 283 | 118 | 3 | 0 | 103.42
8:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 390 | 348 | 0 | 0 | 450 | 0 | 8 | 15 | 14 | 0 | 0 | 101 | 0 | 7 | 7 | 16 | 35 | 62 | 0 | 40 | 18 | 30 | 55 | 22 | 25 | 24 | 33 | 33 | 40 | 0 | 112 | 30 | 100 | 140 | 8 | 0 | 0 | 138 | 0 | 0 | 40 | 0 | 16 | 80 | 80 | 43 | 19 | 7 | 100 | 130 | 120 | 360 | 287 | 0 | 68 | 30 | 42 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 118 | 70 | 7 | 20 | 0.9 | 58 | 60 | 47 | 50 | 163 | 300 | 62 | 84 | 45 | 128 | 0 | 44 | 9 | 320 | 24 | 11 | 0 | 155 | 0 | 0 | 173 | 0 | 84 | 9 |  | 101 | 0 | 416 | 10 | 82 | 120 | 0 | 0 | 0 | 0 | 24 | 127 | 17 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 25 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 216 | 0 | 0 | 130 | 97 | 0 | 0 | 0 | 0 |  | 6490.9 | 1775 | 8265.9 | 4230 | 101 | 1871 | 1352 | 160 | 142 | 282 | 118 | 9.9 | 0 | 103.41
9:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 381 | 350 | 26 | 0 | 450 | 0 | 62 | 54 | 55 | 0 | 0 | 103 | 5 | 20 | 50 | 92 | 100 | 61 | 51 | 39 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 0 | 40 | 0 | 112 | 30 | 100 | 140 | 8 | 0 | 0 | 135 | 0 | 0 | 40 | 0 | 16 | 80 | 92 | 43 | 20 | 2 | 100 | 130 | 120 | 360 | 253 | 0 | 68 | 30 | 42 | 0 | 5 | 0 | 85 | 0 | 1 | 22 | 11 | 25 | 21 | 118 | 67 | 54 | 20 | 1.4 | 51 | 60 | 47 | 50 | 163 | 300 | 60 | 84 | 45 | 128 | 0 | 44 | 9 | 270 | 16 | 11 | 50 | 173 | 0 | 50 | 170 | 51 | 92 | 10.6 |  | 0 | 0 | 418 | 67 | 91 | 140 | 0 | 0 | 0 | 0 | 24 | 109 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 216 | 0 | 0 | 130 | 96 | 0 | 0 | 0 | 0 |  | 7014 | 1767 | 8781 | 4118 | 0 | 1823 | 2030 | 160 | 142 | 378 | 118 | 12 | 0 | 103.4
10:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 354 | 350 | 55 | 0 | 450 | 0 | 83 | 64 | 55 | 0 | 0 | 100 | 40 | 60 | 94 | 149 | 100 | 61 | 0 | 40 | 18 | 55 | 0 | 22 | 25 | 24 | 33 | 33 | 33 | 0 | 112 | 30 | 100 | 140 | 26 | 0 | 0 | 135 | 0 | 0 | 40 | 0 | 16 | 80 | 92 | 43 | 19 | 2 | 100 | 130 | 120 | 360 | 253 | 0 | 68 | 30 | 39 | 0 | 5 | 0 | 85 | 0 | 12 | 22 | 11 | 25 | 21 | 124 | 69 | 80 | 20 | 1.4 | 56 | 60 | 44 | 50 | 130 | 311 | 64 | 84 | 45 | 98 | 0 | 44 | 9 | 280 | 16 | 11 | 50 | 225 | 0 | 50 | 173 | 50 | 100 | 2.7 |  | 103 | 0 | 410 | 67 | 98 | 200 | 0 | 0 | 0 | 0 | 24 | 129 | 18 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 21 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 216 | 0 | 0 | 130 | 96 | 0 | 0 | 0 | 0 |  | 7218.1 | 1943 | 9161.1 | 4121 | 103 | 1791 | 2221 | 160 | 142 | 495 | 124 | 4.1 | 0 | 103.39
11:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 360 | 350 | 110 | 0 | 450 | 0 | 83 | 78 | 55 | 0 | 0 | 100 | 90 | 83 | 102 | 149 | 100 | 52 | 45 | 39 | 18 | 56 | 36 | 19 | 25 | 24 | 33 | 33 | 33 | 0 | 112 | 30 | 100 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 38 | 0 | 23 | 80 | 85 | 43 | 19 | 2 | 100 | 110 | 120 | 360 | 253 | 100 | 68 | 30 | 0 | 0 | 5 | 0 | 85 | 0 | 16 | 22 | 11 | 25 | 21 | 136 | 67 | 70 | 20 | 2.1 | 57 | 60 | 44 | 50 | 163 | 301 | 64 | 84 | 45 | 98 | 0 | 43 | 9 | 300 | 24 | 11 | 10 | 218 | 0 | 50 | 177 | 100 | 97 | 3.5 |  | 103 | 0 | 413 | 67 | 97 | 232 | 0 | 0 | 0 | 0 | 24 | 128 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 18 | 6 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 130 | 95 | 0 | 0 | 0 | 0 |  | 7561.6 | 1971 | 9532.6 | 4182 | 103 | 1840 | 2430 | 160 | 142 | 534 | 136 | 5.6 | 0 | 103.38
12:00 | 72 | 0 | 0 | 120 | 345 | 0 | 0 | 360 | 320 | 110 | 0 | 450 | 0 | 91 | 70 | 55 | 0 | 0 | 101 | 100 | 83 | 102 | 149 | 100 | 52 | 45 | 40 | 18 | 55 | 50 | 19 | 25 | 0 | 17 | 0 | 25 | 0 | 113 | 30 | 100 | 160 | 26 | 0 | 0 | 135 | 0 | 0 | 32 | 0 | 30 | 80 | 92 | 43 | 20 | 2 | 100 | 0 | 100 | 360 | 260 | 142 | 68 | 30 | 0 | 0 | 5 | 0 | 85 | 0 | 16 | 22 | 8 | 25 | 21 | 139 | 47 | 70 | 22 | 2.2 | 55 | 60 | 44 | 50 | 130 | 160 | 62 | 82 | 44 | 126 | 0 | 43 | 9 | 260 | 25 | 0 | 100 | 230 | 52 | 100 | 180 | 100 | 95 | 6.8 |  | 103 | 0 | 350 | 76 | 97 | 233 | 0 | 0 | 0 | 0 | 32 | 128 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 21 | 6 | 8 | 0 | 0 | 190 | 0 | 0 | 215 | 0 | 0 | 220 | 93 | 92 | 0 | 0 | 0 |  | 7373 | 2142 | 9515 | 3800 | 103 | 1737 | 2762 | 190 | 143 | 632 | 139 | 9 | 0 | 103.37
13:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 356 | 345 | 110 | 0 | 450 | 0 | 91 | 98 | 55 | 0 | 0 | 101 | 100 | 81 | 102 | 149 | 100 | 52 | 45 | 40 | 18 | 55 | 50 | 19 | 25 | 14 | 17 | 0 | 28 | 0 | 113 | 30 | 100 | 160 | 26 | 0 | 0 | 135 | 0 | 0 | 32 | 0 | 30 | 80 | 92 | 43 | 20 | 5 | 100 | 0 | 100 | 360 | 294 | 144 | 68 | 30 | 0 | 0 | 5 | 0 | 85 | 0 | 16 | 22 | 11 | 25 | 21 | 140 | 47 | 70 | 22 | 2.1 | 51 | 60 | 44 | 50 | 130 | 300 | 43 | 82 | 44 | 126 | 0 | 40 | 9 | 280 | 24 | 11 | 100 | 225 | 52 | 99 | 177 | 100 | 95 | 8 |  | 104 | 0 | 410 | 76 | 97 | 231 | 0 | 0 | 0 | 0 | 32 | 65 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 21 | 6 | 8 | 0 | 0 | 215 | 0 | 0 | 214 | 0 | 0 | 220 | 93 | 92 | 0 | 0 | 0 |  | 7571.1 | 2159 | 9730.1 | 3927 | 104 | 1779 | 2782 | 215 | 143 | 630 | 140 | 10.1 | 0 | 103.36
14:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 393 | 335 | 110 | 0 | 430 | 0 | 100 | 98 | 55 | 0 | 0 | 101 | 90 | 83 | 102 | 149 | 100 | 52 | 45 | 40 | 18 | 55 | 50 | 19 | 25 | 10 | 25 | 0 | 36 | 0 | 114 | 30 | 100 | 160 | 26 | 0 | 0 | 135 | 0 | 0 | 36 | 0 | 30 | 80 | 92 | 43 | 19 | 2 | 100 | 0 | 100 | 360 | 305 | 30 | 68 | 30 | 0 | 0 | 5 | 0 | 85 | 0 | 16 | 22 | 11 | 25 | 21 | 150 | 47 | 68 | 22 | 1.8 | 56 | 60 | 47 | 50 | 100 | 300 | 61 | 81 | 44 | 78 | 0 | 43 | 9 | 270 | 24 | 11 | 100 | 225 | 13 | 96 | 177 | 100 | 90 | 11.6 |  | 103 | 0 | 360 | 83 | 96 | 232 | 0 | 0 | 0 | 0 | 32 | 93 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 20 | 8 | 8 | 0 | 0 | 210 | 0 | 0 | 214 | 0 | 0 | 220 | 95 | 73 | 0 | 0 | 0 |  | 7393.4 | 2125 | 9518.4 | 3817 | 103 | 1717 | 2733 | 210 | 144 | 631 | 150 | 13.4 | 0 | 103.35
15:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 407 | 335 | 110 | 0 | 420 | 0 | 100 | 98 | 55 | 0 | 0 | 98 | 100 | 83 | 102 | 149 | 100 | 52 | 45 | 40 | 18 | 55 | 50 | 19 | 25 | 10 | 25 | 33 | 44 | 0 | 114 | 30 | 100 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 32 | 0 | 31 | 80 | 94 | 42 | 19 | 2 | 120 | 0 | 128 | 360 | 327 | 42 | 68 | 90 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 152 | 46 | 70 | 22 | 1.3 | 59 | 60 | 47 | 50 | 163 | 316 | 61 | 81 | 44 | 130 | 0 | 43 | 9 | 300 | 24 | 11 | 200 | 236 | 55 | 97 | 178 | 10 | 84 | 10.7 |  | 103 | 0 | 410 | 82 | 95 | 230 | 0 | 0 | 0 | 5 | 32 | 75 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 20 | 8 | 8 | 0 | 0 | 212 | 0 | 0 | 214 | 0 | 0 | 215 | 93 | 93 | 0 | 0 | 0 |  | 7858 | 2175 | 10033 | 4170 | 103 | 1800 | 2810 | 212 | 144 | 630 | 152 | 12 | 0 | 103.34
16:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 340 | 346 | 110 | 0 | 430 | 0 | 92 | 70 | 40 | 0 | 0 | 101 | 0 | 83 | 102 | 149 | 100 | 51 | 45 | 37 | 18 | 55 | 50 | 19 | 25 | 24 | 25 | 33 | 46 | 0 | 114 | 30 | 100 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 32 | 8 | 18 | 80 | 92 | 35 | 19 | 2 | 120 | 0 | 130 | 360 | 310 | 49 | 68 | 0 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 154 | 46 | 69 | 22 | 0.7 | 29 | 60 | 47 | 50 | 163 | 300 | 42 | 81 | 44 | 130 | 0 | 41 | 9 | 260 | 24 | 11 | 150 | 246 | 199 | 89 | 188 | 89 | 84 | 6.7 |  | 549 | 0 | 410 | 93 | 95 | 232 | 0 | 0 | 0 | 18 | 32 | 73 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 43 | 0 | 20 | 8 | 8 | 0 | 0 | 213 | 0 | 0 | 214 | 0 | 0 | 215 | 95 | 94 | 0 | 0 | 0 |  | 7573.4 | 2641 | 10214.4 | 3890 | 549 | 1780 | 2837 | 213 | 144 | 640 | 154 | 7.4 | 0 | 103.33
17:00 | 72 | 0 | 0 | 120 | 280 | 0 | 0 | 392 | 344 | 110 | 0 | 420 | 0 | 100 | 50 | 52 | 0 | 0 | 36 | 0 | 85 | 102 | 149 | 100 | 51 | 11 | 33 | 36 | 55 | 50 | 19 | 25 | 24 | 25 | 33 | 44 | 0 | 114 | 30 | 100 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 32 | 82 | 30 | 80 | 92 | 26 | 19 | 0 | 120 | 0 | 130 | 360 | 310 | 49 | 78 | 0 | 0 | 0 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 134 | 47 | 69 | 22 | 0.2 | 29 | 60 | 47 | 50 | 100 | 303 | 41 | 40 | 44 | 80 | 0 | 11 | 9 | 270 | 24 | 11 | 10 | 250 | 12 | 10 | 187 | 10 | 86 | 2.3 |  | 302 | 0 | 413 | 10 | 95 | 232 | 0 | 0 | 0 | 27 | 8 | 107 | 24 | 110 | 0 | 0 | 0 | 0 | 10 | 0 | 50 | 50 | 0 | 43 | 0 | 21 | 8 | 8 | 0 | 0 | 213 | 0 | 0 | 215 | 0 | 0 | 220 | 95 | 10 | 0 | 0 | 0 |  | 6917.5 | 2271 | 9188.5 | 3848 | 302 | 1651 | 2144 | 213 | 144 | 750 | 134 | 2.5 | 0 | 0
18:00 | 72 | 0 | 0 | 120 | 280 | 0 | 0 | 300 | 310 | 110 | 0 | 430 | 0 | 100 | 50 | 55 | 0 | 0 | 60 | 20 | 85 | 102 | 149 | 100 | 59 | 49 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 33 | 46 | 0 | 114 | 30 | 120 | 180 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 31 | 90 | 94 | 35 | 19 | 0 | 120 | 0 | 130 | 360 | 305 | 101 | 78 | 0 | 0 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 0 | 25 | 21 | 168 | 47 | 68 | 22 | 0 | 60 | 60 | 18 | 50 | 100 | 309 | 64 | 70 | 46 | 80 | 0 | 37 | 9 | 270 | 24 | 11 | 50 | 250 | 101 | 50 | 180 | 48 | 84 | 0 |  | 762 | 0 | 410 | 33 | 112 | 233 | 0 | 0 | 31 | 48 | 16 | 154 | 32 | 110 | 12 | 0 | 0 | 50 | 52 | 50 | 50 | 50 | 38 | 43 | 27 | 0 | 8 | 8 | 0 | 0 | 190 | 17 | 18 | 215 | 0 | 0 | 170 | 95 | 70 | 0 | 0 | 0 |  | 7401 | 3104 | 10505 | 3960 | 762 | 1643 | 2589 | 190 | 144 | 1049 | 168 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 0 | 120 | 280 | 0 | 0 | 389 | 321 | 110 | 0 | 450 | 0 | 100 | 50 | 55 | 0 | 0 | 60 | 29 | 85 | 102 | 149 | 100 | 59 | 48 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 0 | 48 | 0 | 114 | 30 | 125 | 170 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 31 | 90 | 92 | 42 | 19 | 14 | 120 | 0 | 130 | 360 | 309 | 205 | 73 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 156 | 48 | 68 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 300 | 62 | 86 | 46 | 80 | 0 | 43 | 9 | 265 | 24 | 11 | 200 | 270 | 106 | 100 | 187 | 100 | 90 | 0 |  | 762 | 0 | 350 | 91 | 115 | 234 | 0 | 0 | 36 | 85 | 24 | 148 | 35 | 110 | 24 | 0 | 0 | 50 | 51 | 90 | 50 | 50 | 39 | 43 | 32 | 0 | 8 | 11 | 0 | 0 | 160 | 10 | 18 | 214 | 0 | 0 | 203 | 97 | 96 | 0 | 0 | 0 |  | 7962 | 3236 | 11198 | 4075 | 762 | 1737 | 2989 | 160 | 144 | 1175 | 156 | 0 | 0 | 0
19:30 | 72 | 0 | 0 | 120 | 280 | 0 | 0 | 422 | 321 | 110 | 0 | 450 | 0 | 100 | 65 | 55 | 0 | 0 | 60 | 30 | 85 | 102 | 149 | 100 | 52 | 49 | 40 | 54 | 56 | 55 | 19 | 25 | 3 | 25 | 33 | 48 | 0 | 114 | 30 | 120 | 170 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 40 | 90 | 96 | 42 | 19 | 15 | 120 | 0 | 130 | 360 | 310 | 218 | 73 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 160 | 48 | 69 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 300 | 60 | 86 | 46 | 80 | 0 | 44 | 9 | 295 | 24 | 11 | 150 | 272 | 12 | 100 | 187 | 50 | 90 | 0 |  | 762 | 0 | 350 | 96 | 115 | 237 | 0 | 0 | 36 | 75 | 24 | 148 | 35 | 110 | 24 | 0 | 0 | 50 | 46 | 90 | 50 | 50 | 39 | 43 | 31 | 22 | 8 | 11 | 0 | 0 | 160 | 10 | 18 | 213 | 0 | 0 | 220 | 98 | 96 | 0 | 0 | 0 |  | 7883 | 3267 | 11150 | 4126 | 762 | 1792 | 2818 | 160 | 144 | 1188 | 160 | 0 | 0 | 0
20:00 | 72 | 0 | 0 | 120 | 300 | 0 | 0 | 420 | 337 | 110 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 60 | 32 | 86 | 102 | 149 | 100 | 51 | 11 | 40 | 54 | 56 | 55 | 0 | 25 | 3 | 25 | 33 | 48 | 0 | 114 | 30 | 120 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 47 | 90 | 96 | 43 | 19 | 22 | 120 | 0 | 130 | 360 | 310 | 220 | 73 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 160 | 48 | 76 | 22 | 0 | 59 | 60 | 50 | 50 | 100 | 306 | 61 | 86 | 46 | 78 | 0 | 44 | 9 | 285 | 24 | 11 | 100 | 273 | 12 | 100 | 187 | 10 | 92 | 0 |  | 762 | 0 | 410 | 95 | 115 | 235 | 0 | 0 | 36 | 75 | 32 | 156 | 37 | 110 | 24 | 0 | 0 | 50 | 45 | 90 | 50 | 50 | 39 | 43 | 31 | 22 | 8 | 11 | 0 | 0 | 160 | 10 | 18 | 214 | 0 | 0 | 220 | 97 | 96 | 0 | 0 | 0 |  | 7799 | 3341 | 11140 | 4190 | 762 | 1806 | 2726 | 160 | 144 | 1192 | 160 | 0 | 0 | 0
21:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 363 | 352 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 60 | 32 | 87 | 102 | 149 | 100 | 51 | 11 | 40 | 54 | 55 | 55 | 0 | 25 | 10 | 25 | 33 | 48 | 0 | 114 | 30 | 120 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 47 | 90 | 92 | 43 | 19 | 23 | 120 | 0 | 130 | 360 | 327 | 220 | 73 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 160 | 49 | 77 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 314 | 65 | 84 | 46 | 78 | 0 | 44 | 9 | 290 | 24 | 0 | 50 | 274 | 0 | 0 | 180 | 10 | 92 | 0 |  | 761 | 0 | 412 | 97 | 99 | 237 | 0 | 0 | 36 | 75 | 40 | 158 | 38 | 110 | 24 | 0 | 0 | 50 | 45 | 90 | 50 | 50 | 37 | 43 | 31 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 19 | 217 | 0 | 0 | 220 | 97 | 96 | 0 | 0 | 0 |  | 7572 | 3345 | 10917 | 4232 | 761 | 1828 | 2439 | 160 | 144 | 1193 | 160 | 0 | 0 | 0
22:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 357 | 355 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 102 | 32 | 87 | 40 | 149 | 100 | 52 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 17 | 25 | 33 | 48 | 0 | 114 | 30 | 120 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 47 | 90 | 92 | 43 | 19 | 24 | 120 | 0 | 130 | 360 | 309 | 220 | 68 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 172 | 0 | 77 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 305 | 64 | 84 | 46 | 127 | 0 | 43 | 9 | 300 | 24 | 5 | 50 | 273 | 0 | 0 | 180 | 11 | 103 | 0 |  | 762 | 0 | 418 | 96 | 115 | 238 | 0 | 0 | 36 | 72 | 40 | 158 | 37 | 110 | 24 | 0 | 0 | 50 | 45 | 90 | 50 | 50 | 36 | 43 | 29 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 18 | 218 | 0 | 0 | 220 | 98 | 96 | 0 | 0 | 0 |  | 7620 | 3362 | 10982 | 4278 | 762 | 1836 | 2443 | 160 | 144 | 1187 | 172 | 0 | 0 | 0
23:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 350 | 349 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 87 | 32 | 87 | 40 | 149 | 100 | 52 | 49 | 40 | 18 | 55 | 55 | 19 | 25 | 17 | 33 | 33 | 45 | 0 | 114 | 30 | 120 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 48 | 90 | 92 | 44 | 19 | 32 | 120 | 0 | 130 | 360 | 309 | 218 | 68 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 170 | 10 | 77 | 22 | 0 | 58 | 60 | 50 | 50 | 110 | 300 | 53 | 86 | 46 | 99 | 0 | 45 | 9 | 290 | 24 | 11 | 50 | 273 | 0 | 0 | 180 | 11 | 103 | 0 |  | 762 | 0 | 422 | 92 | 115 | 238 | 0 | 0 | 36 | 72 | 40 | 152 | 36 | 110 | 24 | 0 | 0 | 50 | 45 | 90 | 50 | 50 | 36 | 43 | 31 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 18 | 217 | 0 | 0 | 220 | 97 | 70 | 0 | 0 | 0 |  | 7540 | 3329 | 10869 | 4229 | 762 | 1840 | 2374 | 160 | 144 | 1190 | 170 | 0 | 0 | 0
24:00 | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 345 | 356 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 64 | 32 | 87 | 40 | 149 | 100 | 52 | 11 | 40 | 18 | 55 | 55 | 19 | 25 | 17 | 33 | 33 | 45 | 0 | 114 | 30 | 120 | 180 | 25 | 0 | 0 | 135 | 0 | 0 | 40 | 82 | 48 | 90 | 93 | 43 | 19 | 33 | 120 | 0 | 130 | 360 | 309 | 217 | 68 | 100 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 166 | 18 | 77 | 22 | 0 | 58 | 60 | 50 | 50 | 110 | 303 | 65 | 86 | 46 | 98 | 0 | 44 | 9 | 280 | 24 | 11 | 10 | 274 | 0 | 0 | 177 | 11 | 103 | 0 |  | 762 | 0 | 380 | 94 | 115 | 238 | 0 | 0 | 36 | 72 | 40 | 150 | 36 | 110 | 0 | 0 | 0 | 50 | 45 | 80 | 50 | 50 | 30 | 43 | 31 | 22 | 10 | 11 | 0 | 0 | 160 | 10 | 18 | 217 | 0 | 0 | 220 | 97 | 10 | 0 | 0 | 0 |  | 7556 | 3187 | 10743 | 4298 | 762 | 1837 | 2226 | 160 | 144 | 1150 | 166 | 0 | 0 | 0
KWH | 1570000 | 0 | 0 | 2850750 | 8086000 | 0 | 0 | 8850430 | 8113000 | 1170800 | 0 | 9636150 | 0 | 1710720 | 1688328 | 1121821 | 0 | 0 | 2184000 | 792000 | 1476480 | 1602432 | 2956800 | 1759118 | 1089469 | 527500 | 954480 | 609768 | 1146622 | 1217000 | 390708 | 600000 | 479880 | 685400 | 756000 | 976164 | 0 | 2582021 | 720000 | 2500000 | 3700000 | 532980 | 507713 | 0 | 3097298 | 0 | 0 | 1003200 | 1017104 | 803029 | 1937040 | 2181120 | 994080 | 468096 | 404640 | 2639562 | 1454565 | 2915238 | 8985000 | 7357000 | 1795000 | 1689454 | 1647000 | 521640 | 0 | 120000 | 0 | 1688328 | 328144 | 93619 | 514224 | 243900 | 620200 | 524650 | 3535680 | 1378570 | 1367040 | 494244 | 13750 | 1276000 | 1440000 | 1110600 | 1200000 | 3298450 | 6873117 | 1459000 | 2014080 | 1039320 | 2527970 | 0 | 1001520 | 213660 | 7427000 | 504528 | 220224 | 1361280 | 5851197 | 601092 | 736920 | 4305600 | 820692 | 2273760 | 73410 |  | 12047273 | 0 | 9709632 | 1678080 | 2429760 | 4860480 | 0 | 0 | 423360 | 721152 | 661125 | 3597170 | 696905 | 2671680 | 135750 | 0 | 0 | 381880 | 431906 | 920755 | 1167990 | 1156112 | 408172 | 935040 | 261200 | 445440 | 211032 | 224272 | 0 | 0 | 4223800 | 107000 | 194000 | 5400400 | 0 | 0 | 4783155 | 2285022 | 1216320 | 0 | 0 | 0 |  | 175006369 | 64385863 | 239392232 | 101049381 | 12047273 | 42594601 | 53818429 | 4223800 | 3302021 | 18733887 | 3535680 | 87160 | 0
Fuel Cost | 1350200 | 0 | 0 | 2451645 | 5175040 | 0 | 0 | 5398762.3 | 4948930 | 11251388 | 0 | 6456220.5 | 0 | 10743321.6 | 11278031.04 | 6854326.31 | 0 | 0 | 2424240 | 12323520 | 9228000 | 10560026.88 | 28592256 | 11205581.66 | 6525919.31 | 8434725 | 6366381.6 | 4347645.84 | 7166387.5 | 7630590 | 293031 | 450000 | 0 | 0 | 0 | 9234511.44 | 0 | 0 | 0 | 2750000 | 4070000 | 5047320.6 | 335090.58 | 0 | 3561892.7 | 0 | 0 | 8818128 | 10954210.08 | 7813472.17 | 11990277.6 | 14090035.2 | 6501283.2 | 397881.6 | 0 | 2402001.42 | 1323654.15 | 2652866.58 | 5570700 | 5076330 | 1256500 | 1165723.26 | 1581120 | 349498.8 | 0 | 110400 | 0 | 1603911.6 | 3557080.96 | 694652.98 | 395952.48 | 182925 | 477554 | 393487.5 | 24184051.2 | 1033927.5 | 12563097.6 | 380567.88 | 0 | 1327040 | 1497600 | 1066176 | 1080000 | 2572791 | 4811181.9 | 1663260 | 2155065.6 | 1143252 | 2881885.8 | 0 | 931413.6 | 198703.8 | 4753280 | 378396 | 167370.24 | 23590982.4 | 42479690.22 | 10416924.36 | 12564486 | 30785040 | 13992798.6 | 0 | 0 |  | 61441092.3 | 0 | 6505453.44 | 13441420.8 | 20142710.4 | 78156518.4 | 0 | 0 | 4767033.6 | 8495170.56 | 5209665 | 2482047.3 | 689935.95 | 19770432 | 4572060 | 0 | 0 | 4372526 | 4630032.32 | 8249964.8 | 10103113.5 | 10289396.8 | 4347031.8 | 9275596.8 | 3074324 | 489984 | 198370.08 | 169773.904 | 0 | 0 | 16303868 | 3448610 | 5193380 | 3672272 | 0 | 0 | 70121052.3 | 0 | 21078825.6 | 0 | 0 | 0 |  | 494433613.14 | 400691661.654 | 895125274.794 | 77291149.074 | 61441092.3 | 29564157.39 | 435996233.84 | 16303868 | 0 | 250344722.99 | 24184051.2 | 0 | 0
Yesterday Day Peak | 72 | 0 | 0 | 120 | 365 | 0 | 0 | 360 | 350 | 110 | 0 | 450 | 0 | 83 | 78 | 55 | 0 | 0 | 100 | 90 | 83 | 102 | 149 | 100 | 52 | 45 | 39 | 18 | 56 | 36 | 19 | 25 | 24 | 33 | 33 | 33 | 0 | 112 | 30 | 100 | 160 | 25 | 0 | 0 | 135 | 0 | 0 | 38 | 0 | 23 | 80 | 85 | 43 | 19 | 2 | 100 | 110 | 120 | 360 | 253 | 100 | 68 | 30 | 0 | 0 | 5 | 0 | 85 | 0 | 16 | 22 | 11 | 25 | 21 | 136 | 67 | 70 | 20 | 2.1 | 57 | 60 | 44 | 50 | 163 | 301 | 64 | 84 | 45 | 98 | 0 | 43 | 9 | 300 | 24 | 11 | 10 | 218 | 0 | 50 | 177 | 100 | 97 | 3.5 |  | 103 | 0 | 413 | 67 | 97 | 232 | 0 | 0 | 0 | 0 | 24 | 128 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 18 | 6 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 130 | 95 | 0 | 0 | 0 | 0 |  | 9532.6 | DayPeak
Yesterday Evening Peak | 72 | 0 | 0 | 120 | 280 | 0 | 0 | 389 | 321 | 110 | 0 | 450 | 0 | 100 | 50 | 55 | 0 | 0 | 60 | 29 | 85 | 102 | 149 | 100 | 59 | 48 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 0 | 48 | 0 | 114 | 30 | 125 | 170 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 82 | 31 | 90 | 92 | 42 | 19 | 14 | 120 | 0 | 130 | 360 | 309 | 205 | 73 | 0 | 19 | 0 | 5 | 0 | 85 | 41 | 0 | 22 | 11 | 25 | 21 | 156 | 48 | 68 | 22 | 0 | 60 | 60 | 50 | 50 | 100 | 300 | 62 | 86 | 46 | 80 | 0 | 43 | 9 | 265 | 24 | 11 | 200 | 270 | 106 | 100 | 187 | 100 | 90 | 0 |  | 762 | 0 | 350 | 91 | 115 | 234 | 0 | 0 | 36 | 85 | 24 | 148 | 35 | 110 | 24 | 0 | 0 | 50 | 51 | 90 | 50 | 50 | 39 | 43 | 32 | 0 | 8 | 11 | 0 | 0 | 160 | 10 | 18 | 214 | 0 | 0 | 203 | 97 | 96 | 0 | 0 | 0 |  | 11198 | EvPeak
Forecast for Evening | 74 | 0 | 0 | 120 | 365 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 90 | 102 | 149 | 100 | 59 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 40 | 0 | 115 | 30 | 120 | 120 | 25 | 0 | 0 | 135 | 0 | 0 | 50 | 86 | 50 | 100 | 92 | 43 | 19 | 15 | 100 | 0 | 120 | 360 | 360 | 225 | 68 | 130 | 42 | 0 | 5 | 0 | 85 | 41 | 52 | 22 | 11 | 25 | 21 | 174 | 70 | 80 | 22 | 0 | 60 | 60 | 50 | 50 | 163 | 330 | 66 | 86 | 45 | 100 | 0 | 44 | 9 | 341 | 25 | 11 | 200 | 275 | 300 | 100 | 190 | 100 | 107 | 0 |  | 772 | 48 | 410 | 100 | 115 | 230 | 0 | 0 | 36 | 85 | 40 | 188 | 33 | 110 | 26 | 0 | 0 | 50 | 52 | 90 | 50 | 50 | 40 | 43 | 31 | 22 | 11 | 11 | 0 | 0 | 160 | 10 | 18 | 216 | 0 | 0 | 220 | 95 | 95 | 0
Forecast for Day | 74 | 0 | 0 | 120 | 365 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 100 | 100 | 90 | 102 | 149 | 100 | 59 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 40 | 0 | 115 | 30 | 120 | 120 | 25 | 0 | 0 | 135 | 0 | 0 | 40 | 86 | 50 | 100 | 92 | 43 | 19 | 15 | 110 | 0 | 110 | 360 | 360 | 225 | 68 | 130 | 42 | 0 | 5 | 0 | 85 | 0 | 52 | 22 | 11 | 25 | 21 | 129 | 70 | 80 | 22 | 2 | 60 | 60 | 50 | 44 | 163 | 330 | 66 | 86 | 45 | 100 | 0 | 44 | 9 | 341 | 25 | 11 | 200 | 275 | 300 | 96 | 190 | 100 | 107 | 20 |  | 772 | 0 | 410 | 100 | 115 | 230 | 0 | 0 | 0 | 0 | 40 | 188 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 50 | 40 | 43 | 0 | 22 | 11 | 11 | 0 | 0 | 160 |  | 0 | 216 | 0 | 0 | 220 | 95 | 95 | 0
Generation at 08:00(Today) | 72 | 0 | 0 | 120 | 250 | 0 | 0 | 345 | 311 | 0 | 0 | 350 | 0 | 7 | 15 | 15 | 0 | 0 | 65 | 0 | 7 | 7 | 16 | 10 | 53 | 0 | 40 | 18 | 18 | 17 | 0 | 25 | 17 | 33 | 33 | 18 | 0 | 114 | 30 | 120 | 120 | 8 | 0 | 0 | 130 | 0 | 0 | 32 | 48 | 31 | 80 | 53 | 30 | 17 | 7 | 110 | 0 | 110 | 360 | 305 | 210 | 68 | 100 | 19 | 0 | 5 | 0 | 40 | 0 | 0 | 22 | 5 | 25 | 21 | 122 | 46 | 7 | 22 | 1 | 60 | 60 | 47 | 30 | 110 | 304 | 63 | 40 | 46 | 78 | 0 | 42 | 9 | 320 | 24 | 11 | 0 | 201 | 0 | 0 | 182 | 0 | 105 | 1.06 | 0 | 762 | 0 | 300 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 158 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 43 | 0 | 18 | 10 | 5 | 0 | 0 | 159 | 0 | 0 | 180 | 0 | 0 | 131 | 98 | 0 | 0 | 0 | 0 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [65 empty] | 199
| Minimum Generation |  | 8265.9 | 8:00
| Highest Generation |  | 11198 | 19:00
| Day Peak Generation |  | 9532.6 | 11:00
| Evening Peak Generation |  | 11198 | 19:00
| HVDC Max Flow |  | 763 | 1:00
| HVDC EvPeak Flow |  | 762 | 19:00
| Load factor L.F |  | 89.08%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-10-02
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-10-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9532.6 | MW Hour : | 11:00 | Min. Gen. at | 7:00 | 8120.4 | MW
Evening Peak Generation : |  | 11198 | MW Hour : | 19:00 | Available Max Generation : |  | 12765 | MW
E.P. Demand (at gen end) : |  | 11198 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11600 | MW
Maximum Generation : |  | 11198 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1165 | MW
Total Gen. (MKWH) : |  | 239.3922 | System Load Factor : | 89.08% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -580 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-10-02
Actual : | 103.43 | Ft.(MSL) , | Rule curve : | 105.28 | Ft.( MSL )
Gas Consumed : | Total = | 1183.77 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106855306.464
|  | Coal : | 16303868 | Oil : | 686340956.83 | Total : | 809500131.294
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4108.5286 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1398.2914 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1253.0302 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1132.2921 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1023.1954 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 825.6854 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 460.1844 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 212.5521 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 636.8167 |  |  | 0 | 0%
Total | 0 |  | 11050.5764 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Kaptai #5
|  |  |  | 3) Ghorasal Unit-3,4 |  | 11) Siddhirganj CCPP-335 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Sikalbaha ST 60 MW
|  |  |  | 5) Tongi GT |  | 13) Sikalbaha 225 MW
|  |  |  | 6) Ashuganj Midland 51 MW |  | 14) Ashuganj CCPP 225 MW
|  |  |  | 7) Baghabari-71 MW |  | 15) Ashuganj (Precision) 55 MW
|  |  |  | 8) Haripur GT-1,2 |  | 16) Sirajganj unit-3 255 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bheramara-Ishurdi 132 kV Ckt-1 tripped at 08:44 from both ends showing dist C-phase E/F at Bheramara end
only and was switched on at 08:51.
b) Ashuganj CCPP 225 MW GT & ST were synchronized at 10:20 & 17:28 respectively..
c) Shahjibazar-Sreemongal 132 kV Ckt-1 was shut down from 11:05 to 19:11 for project work at Shahjibazar end.
d) Ashuganj Unit-4 was shut down at 11:30 due to gas shortage.
e) Haripur-Bhulta 132 kV Ckt tripped at 11:46 showing dist Z1 C-phase at Haripur end and was switched on at 11:55. |  |  |  | About 100 MW Power interruption occurred under Bhulta S/S
area from 11:46 to 11:55.
f) Tongi-Kabirpur 132 kV Ckt-1 & 2 tripped at 13:05 from Tongi end showing dist Z1 of Ckt-1 & CAT,CD,CSW of |  |  |  | About 173 MW Power interruption occurred under Tongi S/S
Ckt-2 and were switched on at 13:18 & 13:20 respectively. |  |  |  | area from 13:05 to 13:18.
g) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 12:12 showing dist RST Z1 at Ashuganj end only and was
switched on at 12:24.
h) Chandpur STG was synchronized at 14:15.
i) Chandpur GT & ST tripped at 15:05 showing 132 kV breaker differential relay.
j) Siddhirganj Desh 100 MW tripped at 15:28 due to 11 kV cable fault and was synchronized at 17:05.
k) B.Baria-Norsingdi 132 kV Ckt-1 was switched on at 18:03.
l) Bhulta 132/33 kV T1 transformer tripped at 18:15 showing self protection trip,HVTH on VAJ relay and was |  |  |  | About 40 MW Power interruption occurred under Bhulta S/S
switched on at 18:50. |  |  |  | area from 18:15 to 18:50.
m) Juldah-Halishahar 132 kV Ckt tripped at 16:47 showing directional O/C relay at Julda end and was
switched on at 16:55.
n) Halishahar 132/33 kV T1 & T3 transformers tripped at 16:52 from 33 kV sides showing E/F of T1 & E/F, O/C of |  |  |  | About 92 MW Power interruption occurred under Halishahar S/S
T3 and were switched on at 16:57. |  |  |  | area from 16:52 to 16:57.
o) Mymensingh 132/33 kV T2 transformer was under shut down from 19:21 to 21:20 due to 33 kV bus coupler |  |  |  | About 80 MW Power interruption occurred under Mymensingh S/S
isolator red hot. |  |  |  | area from 19:21 to 21:20.
p) Savar 132/33 kV T1 transformer was under shut down from 19:27 to 21:08 due to 132 kV main bus DS
B-phase finger red hot.
q) Mymensingh RPCL tripped at 21:38.
r) Baghabari 230/132 kV T02 Transformer was shut down at 06:20(02/10/2018) from LT side for C/M by PDB.
s) Baghabari-Ishurdi 132 kV Ckt was shut down at 06:25(02/10/2018) for C/M.
t) Baghabari-Shahjadpur 132 kv Ckt-1 was shut down at 06:25 (02/10/2018) for C/M.
u) Baghabari-Sirajganj 132 kV Ckt was shut down at 06:25(02/010/2018) for C/M.
v) Chapainawabganj 132/33 kV T1 transformer was shut down at 07:50(02/10/2018) for A/M.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-10-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 72 | 1570000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2850750 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 8086000
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 389 | 8850430 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 1170800
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 321 | 8113000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 9636150
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1710720
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 50 | 1688328 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1121821
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1759118
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 390708 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 60 | 2184000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 29 | 792000 | Engine problem
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 85 | 1476480 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 48 | 527500
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1602432
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 954480 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 609768
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2956800
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1146622
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1217000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 59 | 1089469 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1079880 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 685400 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 0 | 756000 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 976164
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 270 | 5851197 | Engine problem
35 | APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 106 | 601092 | Low demand
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 100 | 736920
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 820692
38 | Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 90 | 2273760 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3590 | 75285481
39 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 125 | 2500000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 170 | 3700000
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 532980
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 73410
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 42 | 994080 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 144 | 3302021 | Unit-5 under maint.
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 507713
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 3097298
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 1003200
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 82 | 1017104
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 31 | 803029 | Engine problem
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1937040 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 468096
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 404640
51 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 92 | 2181120 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 1019 | 22521731
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2639562 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 1454565 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 2915238
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 205 | 1795000
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8985000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 309 | 7357000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 19 | 521640 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 73 | 1689454 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Under maint.
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1688328
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 41 | 328144
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1647000 | Under maint.
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 514224
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243900
** | Tripura |  | Imported power | 0 | 160 | 156 | 3535680
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 620200 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 93619 | Comilla (N)-Feni O/L
68 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 524650 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 200 | 1361280
| Comilla Area Total |  |  |  | 2541 | 1782 | 38034484
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 48 | 1378570 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 494244
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 68 | 1367040 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 13750
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 187 | 4305600
| Mymensingh Area Total |  |  |  | 522 | 325 | 7559204
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1276000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1440000
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3298450
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 300 | 6873117 | FGMO.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 1110600
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1200000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 220224
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 1459000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 2014080
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 1039320 | Engine problem
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 80 | 2527970
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 1001520 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 504528
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 265 | 7427000 | FGMO
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 213660
| Sylhet Area Total |  |  |  | 1549 | 1246 | 31605469
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 762 | 12047273
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 91 | 1678080 | Engine problem
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2429760
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 36 | 423360
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 234 | 4860480
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 85 | 721152
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 350 | 9709632 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 24 | 661125 | Engine problem
| Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 96 | 1216320
| Khulna Area Total |  |  |  | 2214 | 1793 | 33747182
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2671680
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 24 | 135750
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 35 | 696905
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 148 | 3597170
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2285022
| Barisal Area Total |  |  |  | 462 | 414 | 9386527
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 381880
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 51 | 431906
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1167990
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 1156112
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 39 | 408172
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 5400400
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 203 | 0 | FGMO.
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 32 | 261200
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 0 | 445440 | Engine problem
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 8 | 211032 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224272
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 935040
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 920755
| Rajshahi Area Total |  |  |  | 1264 | 841 | 11944199
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 160 | 4223800 | Coal shortage
122 | Rangpur GT |  | PDB | 1*20 | 20 | 10 | 107000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 194000
| Rangpur Area Total |  |  |  | 484 | 188 | 4524800
| Total |  |  |  | 16445 | 11198 | 234609077
| Eastern Grid Total |  |  |  | 12021 | 7962 | 175006369
| Western Grid Total |  |  |  | 4424 | 3236 | 59602708
| National Grid Total |  |  |  | 16445 | 11198 | 234609077
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-10-01 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7334 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3323 | MW
i) Dhaka area |  |  | 4092 | MW | i) Khulna area |  |  | 1339 | MW
ii) Chittagong area |  |  | 1070 | MW | ii) Rajshahi area |  |  | 1122 | MW
iii) Comilla area |  |  | 918 | MW | iii) Barisal area |  |  | 267 | MW
iv) Mymensingh area |  |  | 781 | MW | iv) Rangpur area |  |  | 595 | MW
v) Sylhet area |  |  | 473 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10657 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 1200 | Netrokona | 74 | 1830 | Central s/s | 90 | 1930
Munsiganj | 109 | 2100 | Jamalpur | 122 | 2000 | Noapara | 94 | 1930
Sonargaon | 47 | 2000 | Sherpur | 82 | 1830 | Jessore | 148 | 1930
Shyampur | 175 | 1200 | Srimongal | 38 | 1830 | Jhenida | 101 | 1900
Bhulta | 161 | 2100 | Shahjibazar | 109 | 1930 | Bottail | 116 | 1930
Madanganj | 59 | 1300 | Fenchuganj | 47 | 1830 | G.K Project | 51 | 1900
Shitalakhya | 124 | 1600 | Kulawara | 45 | 1830 | Faridpur | 150 | 100
Rahim steel | 14 | 1400 | Sylhet | 139 | 1900 | Madaripur | 143 | 2100
Matuail | 98 | 1200 | Chatak | 28 | 2000 | Gopalganj | 87 | 1900
Ghorasal | 78 | 2100 | Sunamganj | 35 | 1900 | Bagerhat | 80 | 1830
Narsingdi | 125 | 1930 | Biani Bazar | 42 | 1930 | Mongla | 36 | 100
Haripur (SBU) | 114 | 1830 | Comilla (S) | 172 | 2200 | Satkhira | 94 | 2000
Ullon | 99 | 1830 | Comilla(N) | 123 | 2100 | Gallamari | 47 | 2300
Hasnabad | 205 | 2000 | Chandpur | 106 | 2400 | Magura | 50 | 1830
Magbazar | 144 | 1600 | Feni | 124 | 1800 | Chuadanga | 77 | 2000
Maniknagar | 106 | 1200 | Chowmuhani | 180 | 2400 | Barisal | 116 | 1930
Bangabhaban | 42 | 1300 | Ashuganj | 60 | 2100 | Patuakhali | 96 | 2100
Narinda | 88 | 1300 | Daudkandi | 110 | 1900 | Bhandaria | 48 | 2100
Dhanmondi | 153 | 1200 | B.Baria | 135 | 2000 | Ishurdi | 55 | 1930
Lalbag | 94 | 1300 | Ramganj | 38 | 2300 | Ruppur Paromanobik | 1 | 100
Madartek | 51 | 2100 | Madunaghat | 62 | 1300 | Natore | 113 | 2000
Mirpur | 110 | 1830 | Hathazari | 97 | 1830 | Bogra | 225 | 1830
Kalyanpur | 126 | 1830 | Khulshi | 200 | 1400 | Noagaon | 114 | 2100
Gulshan | 152 | 1200 | Halishahar | 147 | 1500 | Rajshahi | 146 | 2000
Uttara | 95 | 1600 | Baraulia | 139 | 1600 | C.Nawabganj | 74 | 1900
Uttara(New) | 7 | 1200 | Sikalbaha | 40 | 1700 | Amnura | 43 | 1830
Kamrangirchar | 77 | 1300 | Dohazari | 78 | 100 | Pabna | 115 | 1930
Savar | 118 | 1500 | Cox'sbazar | 69 | 2100 | Shahjadpur | 98 | 2000
Bhasantec | 172 | 1300 | Chandraghona | 31 | 1800 | Serajganj | 93 | 1900
Agargaon | 52 | 1300 | Kaptai | 6 | 200 | Niyamatpur | 64 | 2000
Satmosjid | 103 | 1830 | A. Khaer Stl. | 10 | 700 | Joypurhat | 46 | 2100
Tongi | 140 | 4800 | Bakulia | 106 | 1800 | Rangpur | 121 | 1830
Kabirpur | 204 | 1500 | Julda | 22 | 900 | Lalmonirhat | 85 | 1830
Basundhara | 135 | 1600 | TK chemical | 5 | 1200 | Saidpur | 115 | 1830
Manikganj | 91 | 100 | Modern Steel | 14 | 1100 | Purbasadipur | 86 | 1830
Joydevpur | 226 | 900 | Shahmirpur | 26 | 1800 | Thakurgaon | 59 | 1830
New Tongi | 108 | 1830 | Khagrachhari | 21 | 1830 | Palashbari | 98 | 1830
Korda | 264 | 1900 | Matarbari | 24.5 | 2100 | Barapukuria | 51 | 2100
Dhamrai | 50 | 2100 | Baroiar Hat | 11 | 1800 | Panchagar | 38 | 1830
Tangail | 162 | 100 | Abul Khair 230 | 102 | 1300
Mymensing | 257 | 1900 | BSRM | 118 | 300
Kishorganj | 104 | 1900 | Goalpara | 26 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-10-01
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 386 | 6:00 | 377 | 19:30 | Kaliakoir | 366 | 6:00 | 352 | 18:00
Bheramara | 404 | 9:00 | 389 | 19:00 | Bhulta | 379 | 9:00 | 370 | 18:00
Ashuganj(N) | 387 | 6:00 | 378 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 3:00 | 226 | 1:00 | Hathazari | 220 | 3:00 | 215 | 11:00
Ishurdi | 235 | 6:00 | 225 | 15:00 | Megnaghat | 222 | 1:00 | 220 | 4:00
Ashuganj | 235 | 5:00 | 230 | 15:00 | Fenchuganj | 237 | 12:00 | 229 | 18:00
Serajganj | 227 | 6:00 | 216 | 18:30 | Siddhirganj | 220 | 9:00 | 217 | 15:00
Baghabari | 225 | 7:00 | 215 | 18:30 | Maniknagar | 218 | 6:00 | 214 | 15:00
Barapukuria | 231 | 7:00 | 217 | 18:30 | Old Airport | 219 | 9:00 | 213 | 18:00
Bogra | 219 | 6:00 | 201 | 18:30 | Barisal | 224 | 7:00 | 211 | 15:00
Khulna South | 237 | 16:00 | 227 | 19:00 | AKSML | 216 | 17:00 | 212 | 13:00
Rampura | 220 | 4:00 | 215 | 16:00 | BSRM | 218 | 4:00 | 214 | 15:00
Haripur | 220 | 9:00 | 216 | 18:00 | Bibiyana | 233 | 13:00 | 227 | 18:00
Hasnabad | 220 | 9:00 | 215 | 15:00 | Bhulta | 221 | 9:00 | 215 | 15:00
Aminbazar | 219 | 2:00 | 212 | 15:00 | Ashuganj (S) | 231 | 6:00 | 226 | 18:30
Tongi | 218 | 4:00 | 209 | 15:00 | Kaliakoir | 224 | 6:00 | 216 | 18:00
Comilla (N) | 226 | 9:00 | 222 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 1200 | 133 | 100 | Ramganj | 120 | 1000 | 112 | 1800
Munsiganj | 137 | 1800 | 132 | 600 | Madanhat | 131 | 300 | 128 | 1500
Megnaghat | 135 | 1830 | 131 | 400 | Hathazari | 131 | 200 | 127 | 1100
Shyampur | 136 | 1830 | 128 | 600 | Khulshi | 127 | 700 | 123 | 1500
Bhulta | 130 | 1830 | 125 | 400 | Halishahar | 130 | 100 | 125 | 1500
Madanganj | 138 | 1400 | 129 | 100 | Baraulia | 129 | 300 | 124 | 1500
Shitalakhya | 139 | 1400 | 129 | 500 | Sikalbaha | 130 | 100 | 125 | 800
Rahim steal | 136 | 1300 | 133 | 1700 | Dohazari | 128 | 500 | 125 | 1100
Matuail | 135 | 1200 | 130 | 1500 | Cox'sbazar | 119 | 1800 | 116 | 2000
Ghorasal | 135 | 900 | 132 | 1700 | Chandraghona | 131 | 600 | 127 | 1800
Narsinghdi | 133 | 200 | 117 | 1500 | Kaptai | 130 | 100 | 128 | 300
Haripur (SBU) | 137 | 1830 | 131 | 100 | A. Khaer Stl. | 128 | 100 | 125 | 1000
Ullon | 131 | 600 | 125 | 1500 | Bakulia | 128 | 100 | 124 | 1000
Hasnabad | 135 | 900 | 129 | 600 | Julda | 129 | 100 | 125 | 1100
Magbazar | 134 | 600 | 124 | 1600 | TK Chemical | 131 | 100 | 128 | 1100
Maniknagar | 128 | 600 | 126 | 1600 | Modern Steel | 128 | 200 | 125 | 1500
Bangabhaban | 128 | 600 | 126 | 1600 | Shahmirpur | 128 | 100 | 124 | 800
Narinda | 128 | 600 | 126 | 1600 | Khagrachhari | 130 | 200 | 127 | 1500
Dhanmondi | 131 | 600 | 125 | 1500 | Matarbari | 128 | 1200 | 120 | 400
Lalbag | 133 | 900 | 127 | 700 | Baroiar Hat | 125 | 700 | 119 | 1800
Madartek | 132 | 600 | 126 | 1800 | Goalpara | 138 | 900 | 133 | 1830
Mirpur | 133 | 600 | 128 | 1600 | Central s/s | 138 | 1200 | 133 | 2000
Kalyanpur | 133 | 900 | 128 | 1500 | Noapara | 136 | 900 | 128 | 1830
Gulshan | 131 | 600 | 125 | 1600 | Jessore | 130 | 500 | 122 | 1800
Uttara | 130 | 700 | 123 | 1800 | Jhenida | 131 | 600 | 119 | 1830
Uttara(New) | 128 | 600 | 125 | 1700 | Bottail | 137 | 600 | 128 | 1830
Kamrangirchar | 135 | 1300 | 129 | 600 | G.K.Project | 142 | 600 | 135 | 1830
Savar | 130 | 200 | 126 | 1500 | Faridpur | 133 | 700 | 124 | 1830
Bhasantec | 132 | 600 | 126 | 1800 | Madaripur | 135 | 700 | 124 | 1500
Agargaon | 133 | 600 | 128 | 1700 | Gopalganj | 134 | 700 | 122 | 1500
Satmosjid | 132 | 600 | 127 | 1800 | Bagerhat | 135 | 900 | 130 | 1800
Tongi | 131 | 400 | 123 | 1500 | Mongla | 133 | 800 | 127 | 1800
Kabirpur | 133 | 900 | 124 | 1800 | Satkhira | 136 | 1200 | 130 | 1830
Basundhara | 129 | 600 | 122 | 1800 | Gallamari | 138 | 500 | 134 | 1700
Manikganj | 132 | 600 | 122 | 1800 | Magura | 130 | 600 | 116 | 1900
Joydevpur | 139 | 500 | 133 | 1100 | Chuadanga | 126 | 600 | 112 | 1900
New Tongi | 130 | 600 | 124 | 1800 | Barisal | 137 | 600 | 131 | 1500
Kodda | 137 | 2000 | 132 | 1500 | Patuakhali | 137 | 700 | 127 | 1500
Dhamrai | 134 | 600 | 125 | 2000 | Bhandaria | 137 | 600 | 130 | 1500
Tangail | 135 | 600 | 120 | 1830 | Ishurdi | 140 | 600 | 131 | 1830
Mymensing | 132 | 2100 | 115 | 2300 | Ruppur Paromanobik | 139 | 600 | 133 | 1830
Kishorganj | 123 | 1100 | 114 | 1830 | Natore | 135 | 600 | 124 | 1830
Netrokona | 130 | 700 | 110 | 1830 | Bogra | 129 | 600 | 113 | 1900
Jamalpur | 135 | 1100 | 122 | 2300 | Noagaon | 126 | 900 | 109 | 1830
Sherpur | 135 | 1000 | 122 | 2300 | Rajshahi | 132 | 800 | 120 | 1500
Srimongal | 136 | 500 | 132 | 1800 | C.Nawabganj | 130 | 900 | 120 | 1500
Shahjibazar | 134 | 600 | 129 | 1830 | Amnura | 132 | 400 | 120 | 1500
Fenchuganj | 137 | 900 | 131 | 2100 | Pabna | 132 | 600 | 124 | 1830
Khulawara | 135 | 600 | 131 | 1800 | Shahjadpur | 138 | 500 | 131 | 1900
Sylhet | 135 | 500 | 130 | 1830 | Serajganj | 131 | 600 | 121 | 1830
Chatak | 136 | 600 | 129 | 1800 | Niyamatpur | 122 | 600 | 107 | 2000
Sunamganj | 134 | 600 | 128 | 1800 | Joypurhat | 125 | 800 | 109 | 1800
Biani Bazar | 135 | 400 | 128 | 1800 | Rangpur | 121 | 600 | 101 | 1830
Comilla(s) | 126 | 900 | 120 | 1500 | Lalmonirhat | 116 | 900 | 90 | 1830
Comilla(n) | 135 | 700 | 132 | 1500 | Saidpur | 125 | 600 | 100 | 1830
Chandpur | 124 | 100 | 116 | 2100 | Purbasadipur | 130 | 600 | 114 | 1830
Feni | 119 | 800 | 112 | 2100 | Thakurgaon | 124 | 600 | 100 | 1830
Chowmuhani | 122 | 1700 | 111 | 2100 | Palashbari | 120 | 600 | 100 | 1830
Ashuganj | 133 | 1300 | 126 | 100 | Barapukuria | 131 | 700 | 117 | 1830
Daudkandi | 137 | 1830 | 128 | 1500 | Panchagar | 120 | 600 | 95 | 1830
B.Baria | 130 | 1300 | 126 | 1900

## L-Curve
Date | 2018-10-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 100 | 7556 | 3187 | 10743 |  |  |  | QF-LDC-12
0:30 | 100 | 7526.5 | 3227 | 10753.5 | Date: | 2018-10-01
1:00 | 100 | 7497 | 3267 | 10764
1:30 | 90 | 7382 | 3219.5 | 10601.5
2:00 | 80 | 7267 | 3172 | 10439
2:30 | 80 | 7159 | 3067.5 | 10226.5 | [5 empty] | Gen. at Eve. Peak | 11198 | 11198 MW (19:00 )
3:00 | 80 | 7051 | 2963 | 10014 | [6 empty] | 19:00
3:30 | 85 | 6963.5 | 2916.5 | 9880 | [5 empty] | Gen. at Day Peak | 9532.6 | 9532.6 MW (11:00 )
4:00 | 90 | 6876 | 2870 | 9746 | [6 empty] | 11:00
4:30 | 85 | 6877.5 | 2834.5 | 9712 | [5 empty] | Highest Generation | 11198
5:00 | 80 | 6879 | 2799 | 9678 | [6 empty] | 19:00
5:30 | 75 | 6628 | 2641.5 | 9269.5
6:00 | 70 | 6377 | 2484 | 8861
6:30 | 155 | 6332.5 | 2411.5 | 8744
7:00 | 240 | 6288 | 2339 | 8627
7:30 | 380 | 6389.45 | 2057 | 8446.45
8:00 | 520 | 6490.9 | 1775 | 8265.9
8:30 | 525 | 6752.45 | 1771 | 8523.45
9:00 | 530 | 7014 | 1767 | 8781
9:30 | 510 | 7116.05 | 1855 | 8971.05
10:00 | 490 | 7218.1 | 1943 | 9161.1
10:30 | 530 | 7389.85 | 1957 | 9346.85
11:00 | 570 | 7561.6 | 1971 | 9532.6
11:30 | 525 | 7467.3 | 2056.5 | 9523.8
12:00 | 480 | 7373 | 2142 | 9515
12:30 | 530 | 7472.05 | 2150.5 | 9622.55
13:00 | 580 | 7571.1 | 2159 | 9730.1
13:30 | 555 | 7482.25 | 2142 | 9624.25
14:00 | 530 | 7393.4 | 2125 | 9518.4
14:30 | 505 | 7625.7 | 2150 | 9775.7
15:00 | 480 | 7858 | 2175 | 10033
15:30 | 415 | 7715.7 | 2408 | 10123.7
16:00 | 350 | 7573.4 | 2641 | 10214.4
16:30 | 265 | 7245.45 | 2456 | 9701.45
17:00 | 180 | 6917.5 | 2271 | 9188.5
17:30 | 200 | 7159.25 | 2687.5 | 9846.75
18:00 | 220 | 7401 | 3104 | 10505
18:30 | 300 | 7681.5 | 3170 | 10851.5
19:00 | 380 | 7962 | 3236 | 11198
19:30 | 360 | 7883 | 3267 | 11150
20:00 | 310 | 7799 | 3341 | 11140 |  |  |  | Executive Engineer
20:30 | 295 | 7685.5 | 3343 | 11028.5 |  |  |  | Network Operation Division
21:00 | 280 | 7572 | 3345 | 10917
21:30 | 250 | 7596 | 3353.5 | 10949.5
22:00 | 220 | 7620 | 3362 | 10982 |  |  |  |  | Page 6 of 7
22:30 | 155 | 7580 | 3345.5 | 10925.5
23:00 | 90 | 7540 | 3329 | 10869
23:30 | 95 | 7548 | 3258 | 10806
24:00 | 100 | 7556 | 3187 | 10743
11198 MW (19:00 )
9532.6 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-10-01 |  | Energy | 239392232
[10 empty] | 2018-10-01 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4298 | 762 | 1837 | 2226 | 160 | 144 | 1150 | 0 | 166
0:30 | 4353 | 762.5 | 1856.5 | 2175 | 160 | 142.5 | 1143 | 0 | 161 | Date: | 2018-10-01
1:00 | 4408 | 763 | 1876 | 2124 | 160 | 141 | 1136 | 0 | 156
1:30 | 4393 | 763 | 1878.5 | 2037.5 | 160 | 142 | 1072.5 | 0 | 155 | [7 empty] | Total Energy | 239.3922 | Total Energy Gen 239.392 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 239.392 MKWHr
2:00 | 4378 | 763 | 1881 | 1951 | 160 | 143 | 1009 | 0 | 154 | [7 empty] | Energy not Served | 0
2:30 | 4366 | 763 | 1873 | 1848.5 | 160 | 142.5 | 922.5 | 0 | 151 | [7 empty] | Energy Requirement | 239.3922
3:00 | 4354 | 763 | 1865 | 1746 | 160 | 142 | 836 | 0 | 148
3:30 | 4336.5 | 763 | 1890.5 | 1659.5 | 160 | 142 | 780.5 | 0 | 148 | [6 empty] | Shortage
4:00 | 4319 | 763 | 1916 | 1573 | 160 | 142 | 725 | 0 | 148
4:30 | 4311 | 763 | 1920.5 | 1587 | 160 | 142 | 681.5 | 0 | 147
5:00 | 4303 | 763 | 1925 | 1601 | 160 | 142 | 638 | 0 | 146
5:30 | 4186.5 | 763 | 1809 | 1554.5 | 160 | 142 | 513.5 | 0 | 141
6:00 | 4070 | 763 | 1693 | 1508 | 160 | 142 | 389 | 0 | 136
6:30 | 4092 | 726.5 | 1745.5 | 1413.5 | 159.5 | 142.5 | 336 | 0 | 127 |  |  |  |  | Coal
7:00 | 4114 | 690 | 1798 | 1319 | 159 | 143 | 283 | 0 | 118
7:30 | 4172 | 395.5 | 1834.5 | 1335.5 | 159.5 | 142.5 | 282.5 | 0 | 118 |  |  |  | Oil |  |  |  | ,
8:00 | 4230 | 101 | 1871 | 1352 | 160 | 142 | 282 | 0 | 118
8:30 | 4174 | 50.5 | 1847 | 1691 | 160 | 142 | 330 | 0 | 118
9:00 | 4118 | 0 | 1823 | 2030 | 160 | 142 | 378 | 0 | 118
9:30 | 4119.5 | 51.5 | 1807 | 2125.5 | 160 | 142 | 436.5 | 0 | 121
10:00 | 4121 | 103 | 1791 | 2221 | 160 | 142 | 495 | 0 | 124
10:30 | 4151.5 | 103 | 1815.5 | 2325.5 | 160 | 142 | 514.5 | 0 | 130
11:00 | 4182 | 103 | 1840 | 2430 | 160 | 142 | 534 | 0 | 136
11:30 | 3991 | 103 | 1788.5 | 2596 | 175 | 142.5 | 583 | 0 | 137.5
12:00 | 3800 | 103 | 1737 | 2762 | 190 | 143 | 632 | 0 | 139
12:30 | 3863.5 | 103.5 | 1758 | 2772 | 202.5 | 143 | 631 | 0 | 139.5
13:00 | 3927 | 104 | 1779 | 2782 | 215 | 143 | 630 | 0 | 140
13:30 | 3927 | 104 | 1779 | 2782 | 215 | 143 | 630 | 0 | 140
14:00 | 3927 | 104 | 1779 | 2782 | 215 | 143 | 630 | 0 | 140
14:30 | 4048.5 | 103.5 | 1789.5 | 2796 | 213.5 | 143.5 | 630 | 0 | 146
15:00 | 4170 | 103 | 1800 | 2810 | 212 | 144 | 630 | 0 | 152
15:30 | 4030 | 326 | 1790 | 2823.5 | 212.5 | 144 | 635 | 0 | 153
16:00 | 3890 | 549 | 1780 | 2837 | 213 | 144 | 640 | 0 | 154
16:30 | 3869 | 425.5 | 1715.5 | 2490.5 | 213 | 144 | 695 | 0 | 144
17:00 | 3848 | 302 | 1651 | 2144 | 213 | 144 | 750 | 0 | 134
17:30 | 3904 | 532 | 1647 | 2366.5 | 201.5 | 144 | 899.5 | 0 | 151
18:00 | 3960 | 762 | 1643 | 2589 | 190 | 144 | 1049 | 0 | 168
18:30 | 4017.5 | 762 | 1690 | 2789 | 175 | 144 | 1112 | 0 | 162
19:00 | 4075 | 762 | 1737 | 2989 | 160 | 144 | 1175 | 0 | 156
19:30 | 4126 | 762 | 1792 | 2818 | 160 | 144 | 1188 | 0 | 160
20:00 | 4190 | 762 | 1806 | 2726 | 160 | 144 | 1192 | 0 | 160
20:30 | 4211 | 761.5 | 1817 | 2582.5 | 160 | 144 | 1192.5 | 0 | 160
21:00 | 4232 | 761 | 1828 | 2439 | 160 | 144 | 1193 | 0 | 160
21:30 | 4255 | 761.5 | 1832 | 2441 | 160 | 144 | 1190 | 0 | 166
22:00 | 4278 | 762 | 1836 | 2443 | 160 | 144 | 1187 | 0 | 172
22:30 | 4253.5 | 762 | 1838 | 2408.5 | 160 | 144 | 1188.5 | 0 | 171
23:00 | 4229 | 762 | 1840 | 2374 | 160 | 144 | 1190 | 0 | 170
23:30 | 4263.5 | 762 | 1838.5 | 2300 | 160 | 144 | 1170 | 0 | 168 | Max Temp. in Dhaka |  | 36.1° C
24:00 | 4298 | 762 | 1837 | 2226 | 160 | 144 | 1150 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 239.392 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 239.392 MKWHr
Note on W13: Author:

## Generation
2018-10-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 111 | 113 | 112 | 112 | 112 | 112 | 113 | 112 | 112 | 112 | 112 | 113 | 113 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2582021
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
3 | Chittagong ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 |  | 125 | 120 | 120 | 120 | 120 | 120 | 120 | 2500000
4 | Chittgong ST-2 (Raozan) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 180 |  | 170 | 170 | 160 | 160 | 160 | 160 | 180 | 3700000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 26 | 26 | 26 | 8 | 8 | 8 | 26 | 25 | 26 | 26 | 26 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 532980
| Teknaf Solartech 20MW | [5 empty] | 0 | 3 | 9 | 10.6 | 2.7 | 3.5 | 6.8 | 8 | 11.6 | 10.7 | 6.7 | 2.3 | 0 |  | 0 | [6 empty] | 73410
6 | Sikalbaha 225MW (Gas) | 158 | 141 | 94 | 25 | 0 | [21 empty] | 507713
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 70 | 100 | 100 | 100 | 135 | 135 | 135 | 138 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3097298
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 47 | 47 | 47 | 47 | 47 | 17 | 17 | 16 | 16 | 16 | 23 | 30 | 30 | 30 | 31 | 18 | 30 | 31 |  | 31 | 40 | 47 | 47 | 47 | 48 | 48 | 803029
12 | Hathazari peaking | 72 | 72 | 72 | 64 | 64 | 4 | 0 | 0 | [7 empty] | 8 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1017104
| Daudkandi bangla trak | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 50 | 50 | 10 | 100 | 100 | 100 | 200 | 150 | 10 | 50 |  | 200 | 150 | 100 | 50 | 50 | 50 | 10 | 1361280
14 | Daudkandi Peaking 52MW | 41 | 0 | [15 empty] | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 328144
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 102 | 104 | 103 | 103 | 103 | 38 | 38 | 101 | 103 | 100 | 100 | 101 | 101 | 101 | 98 | 101 | 36 | 60 |  | 60 | 60 | 60 | 60 | 102 | 87 | 64 | 2184000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 273 | 260 | 275 | 273 | 275 | 273 | 183 | 155 | 173 | 225 | 218 | 230 | 225 | 225 | 236 | 246 | 250 | 250 |  | 270 | 272 | 273 | 274 | 273 | 273 | 274 | 5851197
19 | Ashuganj 195MW Modular | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 78 | 78 |  | 73 | 73 | 73 | 73 | 68 | 68 | 68 | 1689454
20 | Ghorasal ST: Unit-1,2 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1570000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2850750
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 300 | 300 | 365 | 365 | 365 | 365 | 345 | 300 | 300 | 365 | 300 | 280 | 280 |  | 280 | 280 | 300 | 365 | 365 | 365 | 365 | 8086000
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2639562
29 | Ashuganj ST: Unit- 4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 0 | [14 empty] | 1454565
30 | Ashuganj ST: Unit- 5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 128 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2915238
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 39 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 521640
33 | Ashuganj CCPP 225 MW | [10 empty] | 100 | 142 | 144 | 30 | 42 | 49 | 49 | 101 |  | 205 | 218 | 220 | 220 | 220 | 218 | 217 | 1795000
34 | Ashuganj CCPP(South) | 309 | 305 | 305 | 327 | 323 | 305 | 305 | 287 | 253 | 253 | 253 | 260 | 294 | 305 | 327 | 310 | 310 | 305 |  | 309 | 310 | 310 | 327 | 309 | 309 | 309 | 7357000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8985000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 90 | 0 | 0 | [8 empty] | 100 | 1647000
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 345 | 346 | 365 | 360 | 360 | 365 | 390 | 381 | 354 | 360 | 360 | 356 | 393 | 407 | 340 | 392 | 300 |  | 389 | 422 | 420 | 363 | 357 | 350 | 345 | 8850430
40 | Meghnaghat CCPP 450MW | 450 | 450 | 450 | 450 | 450 | 370 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 430 | 420 | 430 | 420 | 430 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9636150
41 | Haripur Power CCPP 360MW | 350 | 352 | 352 | 350 | 354 | 291 | 339 | 348 | 350 | 350 | 350 | 320 | 345 | 335 | 335 | 346 | 344 | 310 |  | 321 | 321 | 337 | 352 | 355 | 349 | 356 | 8113000
42 | Mymensingh RPCL 210MW | 89 | 89 | 88 | 88 | 88 | 89 | 90 | 70 | 67 | 69 | 67 | 47 | 47 | 47 | 46 | 46 | 47 | 47 |  | 48 | 48 | 48 | 49 | 0 | 10 | 18 | 1378570
43 | Haripur NEPC 110MW | 13 | 13 | 13 | 13 | 13 | 0 |  |  | 26 | 55 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 0 |  |  |  | 1170800
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 51 | 56 | 57 | 55 | 51 | 56 | 59 | 29 | 29 | 60 |  | 60 | 60 | 59 | 60 | 60 | 58 | 58 | 1276000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440000
46 | Shajibazar 330 MW | 312 | 300 | 300 | 300 | 300 | 292 | 300 | 300 | 300 | 311 | 301 | 160 | 300 | 300 | 316 | 300 | 303 | 309 |  | 300 | 300 | 306 | 314 | 305 | 300 | 303 | 6873117
47 | Shahjibazar GT: Unit- 8, 9 | 64 | 64 | 64 | 64 | 65 | 64 | 57 | 62 | 60 | 64 | 64 | 62 | 43 | 61 | 61 | 42 | 41 | 64 |  | 62 | 60 | 61 | 65 | 64 | 53 | 65 | 1459000
48 | Shahjibazar 86MW | 89 | 89 | 89 | 89 | 89 | 86 | 84 | 84 | 84 | 84 | 84 | 82 | 82 | 81 | 81 | 81 | 40 | 70 |  | 86 | 86 | 86 | 84 | 84 | 86 | 86 | 2014080
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 44 | 44 | 44 | 44 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1039320
50 | Sylhet GT 150 MW | 130 | 100 | 130 | 130 | 100 | 100 | 97 | 128 | 128 | 98 | 98 | 126 | 126 | 78 | 130 | 130 | 80 | 80 |  | 80 | 80 | 78 | 78 | 127 | 99 | 98 | 2527970
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 44 | 43 | 43 | 40 | 43 | 43 | 41 | 11 | 37 |  | 43 | 44 | 44 | 44 | 43 | 45 | 44 | 1001520
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213660
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 0 | 5 | 11 | 11 | 220224
55 | Fenchugonj (Barakatullah) 51MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 18 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1110600
56 | Shahjahanulla 25 MW | 24 | 16 | 8 | 8 | 15 | 16 | 24 | 24 | 16 | 16 | 24 | 25 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 504528
57 | Summit Bibiana- 2 | 300 | 300 | 300 | 310 | 320 | 300 | 310 | 320 | 270 | 280 | 300 | 260 | 280 | 270 | 300 | 260 | 270 | 270 |  | 265 | 295 | 285 | 290 | 300 | 290 | 280 | 7427000
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1217000
59 | Sikalbaha (Energis) | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 32 | 32 | 36 | 32 | 32 | 32 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 1003200
60 | Barabkunda (Regent) | 19 | 19 | 19 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 19 | 20 | 20 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 468096
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 0 | 0 | 19 | 19 | 19 | 390708
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494244
63 | Tripura | 156 | 154 | 148 | 148 | 146 | 136 | 118 | 118 | 118 | 124 | 136 | 139 | 140 | 150 | 152 | 154 | 134 | 168 |  | 156 | 160 | 160 | 160 | 172 | 170 | 166 | 3535680
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 25 | 35 | 35 | 37 | 37 | 7 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 0 | 0 |  | 14 | 15 | 22 | 23 | 24 | 32 | 33 | 404640
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 514224
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243900
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 620200
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 524650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 14 | 10 | 10 | 24 | 24 | 24 |  | 24 | 3 | 3 | 10 | 17 | 17 | 17 | 479880
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 685400
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 33 | 33 | 33 |  | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 756000
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh) | [8 empty] | 5 | 40 | 90 | 100 | 100 | 90 | 100 | 0 |  | 20 |  | 29 | 30 | 32 | 32 | 32 | 32 | 32 | 792000
77 | Siddhirganj (Dutch Bangla) | 50 | 20 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 60 | 83 | 83 | 81 | 83 | 83 | 83 | 85 | 85 |  | 85 | 85 | 86 | 87 | 87 | 87 | 87 | 1476480
78 | Gazipur (RPCL) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 33 | 25 | 28 | 36 | 44 | 46 | 44 | 46 |  | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 976164
79 | Kodda 149 MW | 149 | 135 | 100 | 60 | 48 | 48 | 16 | 16 | 92 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2956800
80 | Jamalpur 95MW | 76 | 76 | 7 | 7 | 7 | 7 | 7 | 7 | 54 | 80 | 70 | 70 | 70 | 68 | 70 | 69 | 69 | 68 |  | 68 | 69 | 76 | 77 | 77 | 77 | 77 | 1367040
81 | Lakdhanvi 52 MW | [8 empty] | 1 | 12 | 16 | 16 | 16 | 16 | 0 | [11 empty] | 93619
82 | Madanganj 102MW | 80 | 80 | 73 | 48 | 48 | 50 | 15 | 15 | 54 | 64 | 78 | 70 | 98 | 98 | 98 | 70 | 50 | 50 |  | 50 | 65 | 81 | 81 | 81 | 81 | 81 | 1688328
83 | Pagla (DPA ) | [8 empty] | 51 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 11 | 49 |  | 48 | 49 | 11 | 11 | 50 | 49 | 11 | 527500
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1688328
85 | Keraniganj (Powerpac) 100MW | 50 | 20 | 10 | 10 | 10 | 10 | 10 | 35 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1759118
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 65 | 30 | 7 | 7 | 7 | 7 | 7 | 8 | 62 | 83 | 83 | 91 | 91 | 100 | 100 | 92 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1710720
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1937040
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 50 | 94 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 40 | 40 | 40 | 1602432
95 | Patenga 50MW | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 35 | 26 | 35 |  | 42 | 42 | 43 | 43 | 43 | 44 | 43 | 994080
96 | Chittagong ECPV 108 MW | 86 | 86 | 92 | 86 | 93 | 86 | 83 | 80 | 92 | 92 | 85 | 92 | 92 | 92 | 94 | 92 | 92 | 94 |  | 92 | 96 | 96 | 92 | 92 | 92 | 93 | 2181120
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 40 | 39 | 40 | 40 | 40 | 40 | 37 | 33 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 954480
98 | Bosila 108MW | 59 | 59 | 51 | 8 | 8 | 8 | 8 | 62 | 61 | 61 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 59 |  | 59 | 52 | 51 | 51 | 52 | 52 | 52 | 1089469
99 | Madanganj-55 MW | 55 | 55 | 55 | 14 | 14 | 14 | 14 | 14 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 52 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1121821
100 | Northern 55 MW | 55 | 55 | 55 | 18 | 18 | 18 | 18 | 30 | 55 | 55 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 56 | 56 | 55 | 55 | 55 | 55 | 1146622
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 163 | 163 | 130 | 163 | 130 | 130 | 100 | 163 | 163 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 110 | 110 | 3298450
102 | Sarishabari (Solar) | [5 empty] | 0 | 0 | 0.9 | 1.4 | 1.4 | 2.1 | 2.2 | 2.1 | 1.8 | 1.3 | 0.7 | 0.2 | 0 |  | 0 | [6 empty] | 13750
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 54 |  | 54 | 54 | 54 | 54 | 54 | 18 | 18 | 609768
104 | APR Energy , Keranigonj | [11 empty] | 52 | 52 | 13 | 55 | 199 | 12 | 101 |  | 106 | 12 | 12 | 0 | 0 | 0 |  | 601092
105 | Bramhangoan 100 MW (Aggreko) | [8 empty] | 50 | 50 | 50 | 100 | 99 | 96 | 97 | 89 | 10 | 50 |  | 100 | 100 | 100 | 0 | 0 | 0 |  | 736920
106 | United Mymensingh PPL | 180 | 180 | 180 | 182 | 182 | 182 | 182 | 173 | 170 | 173 | 177 | 180 | 177 | 177 | 178 | 188 | 187 | 180 |  | 187 | 187 | 187 | 180 | 180 | 180 | 177 | 4305600
112 | Aggreko Aurahati 100MW | [8 empty] | 51 | 50 | 100 | 100 | 100 | 100 | 10 | 89 | 10 | 48 |  | 100 | 50 | 10 | 10 | 11 | 11 | 11 | 820692
114 | Summit Gazipur-1 150MW | 89 | 102 | 88 | 88 | 103 | 103 | 103 | 84 | 92 | 100 | 97 | 95 | 95 | 90 | 84 | 84 | 86 | 84 |  | 90 | 90 | 92 | 92 | 103 | 103 | 103 | 2273760
115
116
117
118
120 | Eastern Zone Total | 7497 | 7267 | 7051 | 6876 | 6879 | 6377 | 6288 | 6490.9 | 7014 | 7218.1 | 7561.6 | 7373 | 7571.1 | 7393.4 | 7858 | 7573.4 | 6917.5 | 7401 |  | 7962 | 7883 | 7799 | 7572 | 7620 | 7540 | 7556 | 175006369
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 95 | 97 | 99 | 96 | 96 | 10 | 10 | 10 | 67 | 67 | 67 | 76 | 76 | 83 | 82 | 93 | 10 | 33 |  | 91 | 96 | 95 | 97 | 96 | 92 | 94 | 1678080
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 98 | 102 | 115 | 82 | 82 | 91 | 98 | 97 | 97 | 97 | 96 | 95 | 95 | 95 | 112 |  | 115 | 115 | 115 | 99 | 115 | 115 | 115 | 2429760
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 35 | 35 | 35 | 35 | 35 | 10 | 0 | [10 empty] | 31 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 423360
129 | Khulna CCPP 225MW | 238 | 239 | 200 | 140 | 120 | 120 | 120 | 120 | 140 | 200 | 232 | 233 | 231 | 232 | 230 | 232 | 232 | 233 |  | 234 | 237 | 235 | 237 | 238 | 238 | 238 | 4860480
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2671680
136 | Barisal GT: Unit-1, 2 | 0 | [16 empty] | 12 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 135750
137 | Bhola Aggreko 95MW | 96 | 97 | 96 | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 95 | 93 | 93 | 95 | 93 | 95 | 95 | 95 |  | 97 | 98 | 97 | 97 | 98 | 97 | 97 | 2285022
| Bhola CCPP 194MW | 126 | 129 | 130 | 130 | 132 | 132 | 130 | 127 | 109 | 129 | 128 | 128 | 65 | 93 | 75 | 73 | 107 | 154 |  | 148 | 148 | 156 | 158 | 158 | 152 | 150 | 3597170
140 | Bhola (Venture) 33MW | 35 | 37 | 37 | 36 | 31 | 26 | 25 | 17 | 23 | 18 | 23 | 25 | 22 | 25 | 27 | 26 | 24 | 32 |  | 35 | 35 | 37 | 38 | 37 | 36 | 36 | 696905
141 | Bangla Trak Noapara | 95 | 50 | 0 | [8 empty] | 92 | 92 | 73 | 93 | 94 | 10 | 70 |  | 96 | 96 | 96 | 96 | 96 | 70 | 10 | 1216320
142 | Noapara (KZA) 40MW | 24 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 8 | 16 |  | 24 | 24 | 32 | 40 | 40 | 40 | 40 | 661125
143 | Gopalganj Peaking | 70 | 65 | 25 | 20 | 15 | 0 | [8 empty] | 5 | 18 | 27 | 48 |  | 85 | 75 | 75 | 75 | 72 | 72 | 72 | 721152
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 763 | 763 | 763 | 763 | 763 | 763 | 690 | 101 | 0 | 103 | 103 | 103 | 104 | 103 | 103 | 549 | 302 | 762 |  | 762 | 762 | 762 | 761 | 762 | 762 | 762 | 12047273
147 | Bheramara 360 MW | 418 | 424 | 425 | 421 | 423 | 345 | 380 | 416 | 418 | 410 | 413 | 350 | 410 | 360 | 410 | 410 | 413 | 410 |  | 350 | 350 | 410 | 412 | 418 | 422 | 380 | 9709632
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 160 | 160 | 160 | 190 | 215 | 210 | 212 | 213 | 213 | 190 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4223800
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 0 | [15 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 381880
157 | Sirajgonj Unit-1 225MW (Gas) | 217 | 217 | 217 | 216 | 217 | 217 | 217 | 216 | 216 | 216 | 214 | 215 | 214 | 214 | 214 | 214 | 215 | 215 |  | 214 | 213 | 214 | 217 | 218 | 217 | 217 | 5400400
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 220 | 220 | 220 | 220 | 200 | 140 | 130 | 130 | 130 | 130 | 130 | 220 | 220 | 220 | 215 | 215 | 220 | 170 |  | 203 | 220 | 220 | 220 | 220 | 220 | 220 | 4783155
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | 45 | 45 | 0 | [13 empty] | 10 | 52 |  | 51 | 46 | 45 | 45 | 45 | 45 | 45 | 431906
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 21 | 21 | 20 | 20 | 20 | 21 | 0 |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 445440
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 211032
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224272
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1167990
166 | Katakhali (Northern) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 43 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1156112
167 | Katakhali Peaking | 36 | 36 | 36 | 36 | 36 | 0 | [11 empty] | 38 |  | 39 | 39 | 39 | 37 | 36 | 36 | 30 | 408172
168 | Santahar Peaking | 31 | 14 | 0 | [14 empty] | 27 |  | 32 | 31 | 31 | 31 | 29 | 31 | 31 | 261200
169 | Rajlanka 52 MW | 43 | 43 | 27 | 25 | 25 | 25 | 25 | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 935040
170 | Chapainawabganj-100 MW | 73 | 73 | 73 | 73 | 73 | 50 | 0 | [10 empty] | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 920755
171
172
173 | Rangpur GT | 10 | 10 | 10 | 12 | 0 | [12 empty] | 17 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 107000
175 | Saidpur GT | 19 | 18 | 18 | 18 | 0 | 0 | [11 empty] | 18 |  | 18 | 18 | 18 | 19 | 18 | 18 | 18 | 194000
176
177
178
178 | Western Zone Total | 3267 | 3172 | 2963 | 2870 | 2799 | 2484 | 2339 | 1775 | 1767 | 1943 | 1971 | 2142 | 2159 | 2125 | 2175 | 2641 | 2271 | 3104 | 0 | 3236 | 3267 | 3341 | 3345 | 3362 | 3329 | 3187 | 64385863