## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-09-24 | Monday
|  | Date (day): | 2018-09-24 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11410 | MW |  |  | (b) At Evening Peak Hour : |  | 12990 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-09-23 | 2018-09-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 74 | 74 | 74 | 74 | 11 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120 | 70 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 20 | 78 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 45 | 86 | 58 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 400 | 412 | 412 |  | 0
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 50 | 55 | 55 |  | 55 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 316 | 353 | 355 | 355
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 |  | 0
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 69 | 100 | 80 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 65 | 81 | 81 | 81 |  | 19 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100 |  | 0
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 5 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 104 | 103 | 100 | 105 | 105 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 82 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint. |  | 21/10/18
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 33 | 40 | 35 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 58 | 57 | 60 | 60 |  | 48 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 50 | 50 |  | 30 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 41 | 41 | 42 |  | 10 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 230 | 253 | 200 | 280 |  | 20 | Engine problem
35 | APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 53 | 150 | 300
36 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 96 | 96
37 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 50 | 50 | 100
38 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 95 | 102 | 100 | 100 |  | 34 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 2858 | 3617 | 3847 | 4562 | 362 | 1014
39 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 80 | 0 | 0 | 180 |  | Gas shortage
40 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 30 | 120 | 120 | 60 |  | Gas shortage
41 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 25 | 16 | 25
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 20 | 0 | 20 | 0
42 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 48 | 47 | 50
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 140 | 141 | 148 | 150 |  |  | #5 Under maint.
44 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
45 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 230 | 221 | 221
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 135 | 60 | 135
47 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 32 | 40 | 40 |  | 11 | Engine problem.
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 81 | 0 | 88
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 31 | 46 | 44 | 50
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 29 | 10 | 25
51 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 93 | 93 | 93 |  | 15 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 837 | 1079 | 928 | 1106 | 240 | 76
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 130 | 100 | 100 | 100 | 34 |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 170 | 225 | 225 |  |  | FGMO
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 301 | 320 | 360 | 360 |  |  | FGMO
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 30 | 43 | 43
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 0 | 0 | 55 |  | Under maint. |  | 19/10/2018
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 20 | 5 | 5 | 5 | 48 |  | Gas shortage
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 140 | 68 | 148 | 148 | 47 |  | Gas shortage
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Devolopment work.
61 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
62 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
63 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 156 | 157 | 155 | 155
64 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
65 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 8 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 138 | 180 | 128 | 180
66 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
67 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
68 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 21 | 21
69 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 100 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1633 | 1797 | 1945 | 2150 | 348 | 51
70 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 30 | 45 | 45 | 50 | 152 |  | Gas shortage
71 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
72 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 88 | 88 | 88 |  |  | Engine problem
73 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 2 | 0
74 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 178 | 184 | 185 | 185 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 280 | 337 | 340 | 343 | 152 | 0
75 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 28 | 60 | 60
76 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | under maint.
77 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
78 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 300 | 314 | 330 | 330
79 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
80 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 40 | 50
81 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
82 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 65 | 66 | 66
83 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
84 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 45 | 45 | 45
85 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 95 | 110 | 130 | 130
86 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
87 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 46 | 46 | 46
88 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
89 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 270 | 300 | 341 |  |  | FGMO
90 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1236 | 1290 | 1380 | 1431 | 0 | 0
91 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 770 | 768 | 781 | 781
92 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 66 | 89 | 100 | 100 |  | 10 | Engine problem
93 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 58 | 107 | 115 | 115
94 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 42
95 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 236 | 225 | 225
96 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 80 | 0 | 85
97 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 414 | 410 | 410
98 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
| Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 94 | 94 | 94
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 1396 | 1867 | 1765 | 1940 | 0 | 10
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 26 | 0 | 26
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 38 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 114 | 148 | 150 | 150 |  | 44
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 345 | 418 | 388 | 414 | 0 | 44
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 51 | 0 | 52
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 50 | 50 | 50 | 0
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | under maint.
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 220 | 220 | 220
113 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 127 | 150 | 150 | 150
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
114 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 35
115 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
116 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 12 | 12
117 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 9 | 11 | 11
118 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
119 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 50 | 102
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 422 | 840 | 647 | 846 | 71 | 100
120 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
121 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 159 | 170 | 170 | 104 |  | Coal shortage
122 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 10
123 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 160 | 187 | 170 | 198 | 189 | 85
| Total |  |  |  |  | 17043 | 16445 | 9167 | 11432 | 11410 | 12990 | 1362 | 1380
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8683.4712 | 10829 | 10808.1604 | 12304.8207
A. |  | 2018-09-23 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11432 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 8109.8 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11432 | MW
3 | Day peak Generation : |  |  | 9167 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10829 | MW
4 | Evening peak Generation : |  |  | 11432 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 233.7046 | MKWHr | By Solar | 0.14508 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 137.0862 | MKWHr |  | By Oil: | 67.2435 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.9067 | MKWHr |  | By Hydro: | 3.2956 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1362 | MW | Dhaka | 4044 | 4044 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1380 | MW | Chittagong | 1078 | 1078 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2742 | MW | Khulna | 1353 | 1353 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1153.9 |  | MMCFD |  |  | Rajshahi | 1159 | 1159 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 96415779.526 | ii) Oil : | Taka | 641665441.13 | Comilla | 1045 | 1045 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15079862 | Total | Taka | 753161082.656 | Mymensingh | 769 | 769 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 2.623 | MKWHr. | Sylhet | 467 | 467 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -370 | MW at | 20:00 | hrs | Barisal | 258 | 258 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -400 | MW at | 19:00 | hrs | Rangpur | 656 | 656 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.9° C |  |  | Total | 10829 | 10829 |  | 0
B. |  | 2018-09-24 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12990 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
4 | Reserve(Generation end) |  |  |  | 1290 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 239.1834 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8374.2 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.4698 | MKWHr. | ii) HVDC Flow at Peak Time |  | 768 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5578 | MKWHr. | iii) Maximum HVDC Flow : |  | 776 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.11 |  | (b) Today: | 103.99 |  | (c) Rule Curve: |  | 104.32
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-09-23
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 390 | 352 | 0 | 0 | 225 | 0 | 100 | 81 | 55 | 0 | 0 | 106 | 0 | 96 | 102 | 82 | 75 | 49 | 0 | 33 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 229 | 135 | 48 | 0 | 40 | 80 | 0 | 90 | 92 | 43 | 19 | 38 | 0 | 0 | 130 | 360 | 70 | 211 | 120 | 146 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 158 | 46 | 88 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 300 | 67 | 89 | 45 | 100 | 19 | 46 | 9 | 300 | 24 | 11 | 0 | 253 | 0 | 0 | 178 | 51 | 92 | 0 |  | 775 | 0 | 422 | 98 | 99 | 241 | 0 | 0 | 40 | 30 | 40 | 69 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 97 | 50 | 43 | 30 | 52 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 220 | 97 | 0 | 150 | 0 | 0 |  | 7260 | 2925 | 10185 | 3785 | 775 | 1835 | 2205 | 160 | 142 | 1125 | 158 | 0 | 0 | 104.11
2:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 373 | 356 | 0 | 0 | 225 | 0 | 100 | 81 | 55 | 0 | 0 | 105 | 0 | 92 | 102 | 16 | 63 | 64 | 0 | 33 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 229 | 135 | 48 | 0 | 40 | 80 | 0 | 90 | 92 | 43 | 19 | 30 | 0 | 0 | 130 | 360 | 70 | 210 | 152 | 149 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 156 | 46 | 56 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 312 | 66 | 89 | 44 | 98 | 19 | 46 | 9 | 290 | 24 | 11 | 0 | 265 | 0 | 0 | 178 | 0 | 96 | 0 |  | 775 | 0 | 423 | 95 | 99 | 180 | 0 | 0 | 40 | 30 | 40 | 69 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 97 | 50 | 43 | 30 | 34 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 187 | 97 | 0 | 151 | 0 | 0 |  | 7117 | 2812 | 9929 | 3780 | 775 | 1852 | 2099 | 160 | 142 | 965 | 156 | 0 | 0 | 104.11
3:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 347 | 355 | 0 | 0 | 225 | 0 | 100 | 81 | 55 | 0 | 0 | 105 | 0 | 92 | 40 | 16 | 63 | 57 | 0 | 32 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 229 | 135 | 48 | 0 | 40 | 72 | 0 | 90 | 92 | 43 | 19 | 38 | 0 | 0 | 130 | 360 | 18 | 210 | 152 | 151 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 150 | 46 | 40 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 302 | 66 | 89 | 44 | 98 | 19 | 46 | 9 | 310 | 24 | 11 | 0 | 220 | 0 | 0 | 178 | 0 | 96 | 0 |  | 776 | 0 | 421 | 51 | 70 | 135 | 0 | 0 | 40 | 28 | 40 | 69 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 75 | 50 | 43 | 30 | 34 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 146 | 97 | 0 | 151 | 0 | 0 |  | 6913 | 2628 | 9541 | 3692 | 776 | 1879 | 1895 | 160 | 142 | 847 | 150 | 0 | 0 | 104.11
4:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 348 | 356 | 0 | 0 | 225 | 0 | 100 | 81 | 55 | 0 | 0 | 107 | 0 | 92 | 7 | 16 | 20 | 57 | 0 | 33 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 229 | 135 | 48 | 0 | 40 | 72 | 0 | 90 | 85 | 43 | 19 | 39 | 0 | 0 | 130 | 360 | 30 | 210 | 152 | 155 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 150 | 46 | 40 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 300 | 66 | 89 | 44 | 98 | 19 | 46 | 9 | 300 | 24 | 11 | 0 | 273 | 0 | 0 | 178 | 0 | 96 | 0 |  | 775 | 0 | 421 | 27 | 49 | 120 | 0 | 0 | 40 | 28 | 40 | 66 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 42 | 50 | 43 | 30 | 34 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 149 | 97 | 0 | 151 | 0 | 0 |  | 6876 | 2534 | 9410 | 3706 | 775 | 1871 | 1804 | 160 | 142 | 802 | 150 | 0 | 0 | 104.11
5:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 350 | 355 | 0 | 0 | 240 | 0 | 70 | 81 | 55 | 0 | 0 | 107 | 0 | 50 | 7 | 16 | 10 | 57 | 0 | 26 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 203 | 100 | 48 | 0 | 40 | 72 | 0 | 90 | 92 | 43 | 19 | 39 | 0 | 0 | 130 | 360 | 33 | 210 | 152 | 155 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 140 | 46 | 7 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 331 | 67 | 89 | 44 | 98 | 19 | 46 | 9 | 300 | 24 | 11 | 0 | 270 | 0 | 0 | 175 | 0 | 96 | 0 |  | 775 | 0 | 420 | 10 | 16 | 120 | 0 | 0 | 12 | 0 | 0 | 69 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 42 | 50 | 43 | 30 | 8 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 147 | 96 | 0 | 151 | 0 | 0 |  | 6735 | 2329 | 9064 | 3710 | 775 | 1880 | 1567 | 160 | 142 | 690 | 140 | 0 | 0 | 104.11
6:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 360 | 360 | 0 | 0 | 240 | 0 | 30 | 70 | 15 | 0 | 0 | 106 | 0 | 7 | 7 | 16 | 10 | 57 | 0 | 25 | 18 | 18 | 36 | 22 | 25 | 24 | 33 | 33 | 8 | 0 | 112 | 30 | 130 | 0 | 25 | 0 | 165 | 60 | 34 | 0 | 40 | 0 | 0 | 90 | 70 | 39 | 19 | 39 | 0 | 0 | 130 | 360 | 85 | 210 | 152 | 156 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 130 | 46 | 7 | 22 | 0 | 30 | 0 | 47 | 50 | 163 | 298 | 67 | 89 | 44 | 78 | 19 | 46 | 9 | 290 | 24 | 11 | 0 | 270 | 0 | 0 | 182 | 0 | 95 | 0.6 |  | 776 | 0 | 424 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 70 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 13 | 8 | 0 | 22 | 12 | 8 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 153 | 96 | 0 | 151 | 0 | 0 |  | 6354.6 | 2262 | 8616.6 | 3684 | 776 | 1873 | 1326 | 159 | 142 | 526 | 130 | 0.6 | 0 | 104.11
7:00 | 74 | 0 | 0 | 120 | 365 | 93 | 0 | 345 | 358 | 0 | 0 | 260 | 0 | 8 | 15 | 15 | 0 | 0 | 107 | 0 | 7 | 7 | 16 | 10 | 37 | 0 | 31 | 18 | 18 | 17 | 0 | 25 | 24 | 33 | 33 | 8 | 0 | 111 | 30 | 130 | 0 | 16 | 204 | 0 | 60 | 32 | 0 | 35 | 0 | 0 | 90 | 92 | 36 | 19 | 13 | 0 | 0 | 130 | 360 | 147 | 210 | 148 | 154 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 106 | 46 | 7 | 22 | 0.4 | 30 | 0 | 47 | 50 | 163 | 300 | 67 | 89 | 44 | 78 | 19 | 45 | 9 | 290 | 25 | 11 | 0 | 218 | 0 | 0 | 106 | 0 | 30 | 4.7 |  | 775 | 0 | 425 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 8 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 96 | 0 | 153 | 0 | 0 |  | 6087.1 | 2170 | 8257.1 | 3916 | 775 | 1856 | 961 | 160 | 141 | 337 | 106 | 5.1 | 0 | 104.1
8:00 | 74 | 0 | 0 | 120 | 365 | 44 | 0 | 360 | 351 | 0 | 0 | 260 | 0 | 8 | 15 | 15 | 0 | 0 | 103 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 0 | 25 | 24 | 33 | 33 | 8 | 0 | 111 | 30 | 130 | 0 | 16 | 221 | 0 | 0 | 60 | 0 | 32 | 0 | 32 | 90 | 81 | 37 | 19 | 8 | 0 | 0 | 130 | 360 | 334 | 211 | 148 | 156 | 37 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 114 | 30 | 7 | 22 | 0.8 | 30 | 0 | 47 | 50 | 163 | 330 | 62 | 10 | 43 | 130 | 19 | 46 | 9 | 285 | 17 | 11 | 0 | 70 | 0 | 0 | 56 | 0 | 30 | 11 |  | 769 | 0 | 417 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 8 | 0 | 22 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 156 | 95 | 0 | 152 | 0 | 0 |  | 5965.8 | 2144 | 8109.8 | 4118 | 769 | 1710 | 702 | 160 | 141 | 384 | 114 | 11.8 | 0 | 104.1
9:00 | 74 | 0 | 0 | 120 | 365 | 0 | 0 | 395 | 353 | 0 | 0 | 450 | 0 | 22 | 18 | 15 | 0 | 0 | 65 | 0 | 8 | 16 | 30 | 35 | 58 | 0 | 18 | 18 | 36 | 36 | 19 | 25 | 24 | 33 | 0 | 24 | 0 | 114 | 30 | 130 | 0 | 16 | 198 | 0 | 0 | 80 | 0 | 40 | 0 | 32 | 90 | 86 | 39 | 19 | 12 | 0 | 0 | 130 | 360 | 301 | 216 | 148 | 155 | 40 | 5 | 20 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 18 | 124 | 30 | 7 | 20 | 1.3 | 30 | 0 | 47 | 50 | 130 | 303 | 53 | 86 | 43 | 87 | 19 | 45 | 9 | 260 | 24 | 11 | 0 | 72 | 0 | 0 | 178 | 0 | 46 | 15.7 |  | 769 | 0 | 422 | 10 | 30 | 120 | 0 | 0 | 0 | 0 | 32 | 60 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 8 | 0 | 22 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 157 | 95 | 0 | 153 | 0 | 0 |  | 6375 | 2195 | 8570 | 3973 | 769 | 1894 | 1070 | 160 | 144 | 419 | 124 | 17 | 0 | 104.1
10:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 351 | 0 | 0 | 450 | 0 | 56 | 55 | 55 | 0 | 0 | 39 | 0 | 40 | 32 | 48 | 50 | 58 | 0 | 33 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 17 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 204 | 0 | 0 | 100 | 0 | 40 | 0 | 32 | 90 | 86 | 44 | 16 | 5 | 0 | 0 | 130 | 360 | 298 | 181 | 140 | 157 | 40 | 5 | 20 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 18 | 130 | 30 | 7 | 20 | 2.1 | 30 | 0 | 47 | 50 | 100 | 306 | 65 | 86 | 43 | 77 | 19 | 45 | 9 | 260 | 25 | 11 | 0 | 145 | 0 | 0 | 178 | 0 | 84 | 20 |  | 769 | 0 | 350 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 32 | 66 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 8 | 0 | 22 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 134 | 96 | 0 | 118 | 0 | 0 |  | 6615.1 | 2138 | 8753.1 | 3759 | 769 | 1849 | 1488 | 160 | 142 | 434 | 130 | 22.1 | 0 | 0
11:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 342 | 0 | 0 | 450 | 0 | 56 | 65 | 55 | 0 | 0 | 39 | 0 | 50 | 32 | 48 | 50 | 58 | 11 | 33 | 18 | 56 | 55 | 0 | 25 | 24 | 33 | 33 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 215 | 0 | 0 | 100 | 0 | 40 | 0 | 31 | 90 | 79 | 42 | 16 | 3 | 0 | 0 | 130 | 360 | 334 | 198 | 140 | 156 | 40 | 5 | 20 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 18 | 132 | 29 | 7 | 20 | 2 | 30 | 0 | 47 | 50 | 100 | 315 | 65 | 86 | 42 | 78 | 19 | 44 | 9 | 315 | 25 | 11 | 0 | 223 | 0 | 0 | 180 | 0 | 93 | 20 |  | 769 | 0 | 350 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 32 | 117 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 8 | 0 | 21 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 139 | 96 | 0 | 120 | 0 | 0 |  | 6832 | 2212 | 9044 | 3875 | 769 | 1890 | 1616 | 160 | 142 | 438 | 132 | 22 | 0 | 104.13
12:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 316 | 13 | 0 | 450 | 0 | 69 | 65 | 55 | 0 | 0 | 104 | 0 | 50 | 48 | 64 | 50 | 58 | 21 | 33 | 18 | 56 | 36 | 5 | 25 | 24 | 33 | 33 | 33 | 0 | 110 | 30 | 0 | 0 | 16 | 204 | 0 | 0 | 140 | 0 | 40 | 0 | 31 | 90 | 85 | 46 | 19 | 6 | 0 | 0 | 130 | 360 | 301 | 180 | 140 | 156 | 40 | 5 | 20 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 18 | 138 | 30 | 50 | 20 | 2 | 30 | 0 | 47 | 50 | 130 | 300 | 64 | 86 | 43 | 95 | 19 | 44 | 9 | 290 | 24 | 5 | 0 | 230 | 0 | 0 | 178 | 0 | 95 | 20 |  | 770 | 0 | 350 | 66 | 58 | 120 | 0 | 0 | 0 | 0 | 32 | 114 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 25 | 0 | 22 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 160 | 96 | 0 | 127 | 0 | 0 |  | 6844 | 2323 | 9167 | 3755 | 770 | 1876 | 1791 | 160 | 140 | 515 | 138 | 22 | 0 | 104.13
13:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 415 | 332 | 13 | 0 | 450 | 0 | 98 | 65 | 55 | 0 | 0 | 85 | 17 | 70 | 84 | 84 | 60 | 57 | 20 | 33 | 18 | 56 | 36 | 22 | 25 | 24 | 33 | 33 | 33 | 0 | 109 | 30 | 70 | 0 | 25 | 204 | 0 | 0 | 100 | 0 | 32 | 40 | 31 | 90 | 92 | 47 | 19 | 7 | 0 | 0 | 130 | 360 | 301 | 153 | 140 | 156 | 35 | 5 | 10 | 0 | 85 | 0 | 0 | 21 | 8 | 33 | 18 | 142 | 29 | 64 | 20 | 1.1 | 30 | 0 | 47 | 50 | 130 | 303 | 59 | 86 | 43 | 78 | 19 | 46 | 9 | 270 | 24 | 5 | 0 | 235 | 0 | 0 | 170 | 0 | 92 | 20 |  | 770 | 0 | 350 | 83 | 83 | 120 | 0 | 0 | 0 | 0 | 32 | 77 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 25 | 0 | 20 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 131 | 96 | 0 | 119 | 0 | 0 |  | 7035.1 | 2317 | 9352.1 | 3763 | 770 | 1863 | 1988 | 160 | 139 | 506 | 142 | 21.1 | 0 | 104.13
14:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 350 | 13 | 0 | 450 | 0 | 100 | 70 | 55 | 0 | 0 | 64 | 17 | 85 | 102 | 84 | 60 | 56 | 22 | 33 | 18 | 55 | 36 | 22 | 25 | 24 | 33 | 33 | 34 | 0 | 110 | 30 | 80 | 0 | 25 | 204 | 0 | 0 | 70 | 0 | 40 | 39 | 31 | 90 | 92 | 46 | 19 | 5 | 0 | 0 | 120 | 360 | 295 | 149 | 140 | 153 | 30 | 5 | 10 | 0 | 85 | 0 | 0 | 21 | 8 | 33 | 21 | 142 | 30 | 64 | 20 | 1 | 30 | 0 | 44 | 28 | 100 | 306 | 63 | 86 | 44 | 97 | 19 | 46 | 9 | 265 | 24 | 11 | 0 | 253 | 0 | 0 | 180 | 0 | 90 | 19.4 |  | 769 | 0 | 350 | 83 | 83 | 120 | 0 | 0 | 0 | 0 | 40 | 79 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 25 | 0 | 20 | 12 | 11 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 131 | 95 | 0 | 118 | 0 | 0 |  | 6997.4 | 2324 | 9321.4 | 3726 | 769 | 1820 | 2070 | 159 | 140 | 475 | 142 | 20.4 | 0 | 104.05
15:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 344 | 40 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 100 | 20 | 80 | 102 | 84 | 50 | 56 | 21 | 33 | 18 | 55 | 48 | 0 | 25 | 24 | 33 | 33 | 40 | 0 | 110 | 30 | 80 | 0 | 25 | 205 | 0 | 0 | 135 | 0 | 40 | 42 | 31 | 90 | 92 | 46 | 19 | 4 | 0 | 0 | 100 | 360 | 327 | 199 | 68 | 155 | 30 | 5 | 5 | 0 | 85 | 0 | 1 | 21 | 11 | 33 | 21 | 139 | 45 | 78 | 20 | 1.3 | 28 | 0 | 44 | 28 | 163 | 315 | 65 | 86 | 44 | 130 | 19 | 46 | 9 | 300 | 24 | 11 | 0 | 202 | 0 | 0 | 180 | 0 | 92 | 14.5 |  | 769 | 0 | 410 | 75 | 99 | 120 | 0 | 0 | 0 | 0 | 40 | 77 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 34 | 0 | 22 | 12 | 11 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 147 | 96 | 0 | 131 | 0 | 0 |  | 7219.8 | 2431 | 9650.8 | 3936 | 769 | 1838 | 2096 | 158 | 140 | 559 | 139 | 15.8 | 0 | 104.04
16:00 | 74 | 0 | 25 | 120 | 300 | 0 | 0 | 410 | 321 | 55 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 62 | 35 | 80 | 102 | 133 | 74 | 56 | 21 | 35 | 18 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 41 | 0 | 110 | 30 | 80 | 0 | 25 | 203 | 0 | 0 | 100 | 0 | 40 | 41 | 31 | 90 | 92 | 0 | 19 | 4 | 0 | 90 | 100 | 360 | 301 | 199 | 68 | 147 | 30 | 5 | 5 | 0 | 85 | 0 | 22 | 12 | 0 | 33 | 21 | 142 | 44 | 79 | 20 | 0.9 | 28 | 0 | 44 | 28 | 100 | 305 | 63 | 50 | 44 | 110 | 19 | 46 | 9 | 265 | 24 | 11 | 0 | 203 | 0 | 0 | 178 | 0 | 92 | 8.2 |  | 769 | 0 | 410 | 83 | 98 | 120 | 0 | 0 | 0 | 6 | 40 | 77 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 43 | 0 | 34 | 0 | 22 | 12 | 11 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 134 | 96 | 0 | 121 | 0 | 0 |  | 7129.1 | 2421 | 9550.1 | 3944 | 769 | 1680 | 2142 | 159 | 140 | 565 | 142 | 9.1 | 0 | 104.12
17:00 | 74 | 0 | 25 | 120 | 300 | 0 | 0 | 380 | 303 | 50 | 0 | 400 | 0 | 75 | 81 | 55 | 0 | 0 | 103 | 35 | 60 | 64 | 105 | 50 | 56 | 20 | 37 | 18 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 36 | 0 | 110 | 30 | 80 | 0 | 25 | 203 | 0 | 0 | 80 | 0 | 40 | 41 | 31 | 90 | 92 | 6 | 19 | 10 | 0 | 100 | 100 | 360 | 301 | 190 | 68 | 149 | 30 | 5 | 5 | 0 | 85 | 0 | 25 | 22 | 11 | 33 | 21 | 140 | 45 | 80 | 20 | 0.2 | 28 | 0 | 48 | 28 | 100 | 302 | 50 | 50 | 10 | 78 | 19 | 44 | 9 | 270 | 24 | 11 | 0 | 200 | 0 | 0 | 178 | 0 | 93 | 2.5 |  | 769 | 0 | 380 | 51 | 102 | 120 | 0 | 0 | 0 | 22 | 8 | 63 | 25 | 110 | 0 | 0 | 0 | 0 | 46 | 0 | 50 | 43 | 0 | 34 | 0 | 22 | 12 | 11 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 130 | 96 | 0 | 118 | 0 | 0 |  | 6863.7 | 2371 | 9234.7 | 3885 | 769 | 1590 | 1974 | 159 | 140 | 575 | 140 | 2.7 | 0 | 104.12
18:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 350 | 330 | 50 | 0 | 330 | 0 | 74 | 81 | 55 | 0 | 0 | 101 | 35 | 60 | 70 | 98 | 70 | 56 | 11 | 33 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 110 | 30 | 80 | 0 | 25 | 203 | 0 | 0 | 60 | 0 | 40 | 80 | 45 | 90 | 93 | 31 | 19 | 6 | 0 | 100 | 100 | 360 | 301 | 191 | 68 | 156 | 30 | 5 | 5 | 0 | 60 | 50 | 25 | 22 | 11 | 33 | 22 | 150 | 44 | 88 | 17 | 0 | 28 | 0 | 50 | 31 | 100 | 301 | 65 | 30 | 10 | 98 | 19 | 45 | 9 | 265 | 24 | 11 | 0 | 203 | 11 | 20 | 180 | 17 | 93 | 0 |  | 768 | 0 | 320 | 59 | 103 | 140 | 0 | 0 | 11 | 43 | 8 | 103 | 30 | 110 | 0 | 0 | 0 | 26 | 51 | 83 | 50 | 50 | 24 | 34 | 30 | 22 | 12 | 11 | 0 | 0 | 159 | 12 | 18 | 0 | 0 | 0 | 136 | 65 | 10 | 119 | 0 | 0 |  | 7000 | 2607 | 9607 | 3870 | 768 | 1473 | 2140 | 159 | 140 | 907 | 150 | 0 | 0 | 104.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 414 | 357 | 50 | 0 | 430 | 0 | 100 | 81 | 55 | 0 | 0 | 105 | 80 | 70 | 102 | 149 | 87 | 59 | 50 | 38 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 41 | 0 | 111 | 30 | 80 | 10 | 25 | 231 | 0 | 0 | 135 | 0 | 32 | 80 | 41 | 90 | 93 | 48 | 19 | 20 | 0 | 100 | 100 | 360 | 301 | 185 | 68 | 151 | 30 | 5 | 5 | 0 | 85 | 50 | 0 | 22 | 11 | 33 | 22 | 172 | 46 | 88 | 17 | 0 | 27 | 0 | 50 | 50 | 163 | 301 | 40 | 86 | 45 | 108 | 19 | 46 | 9 | 270 | 24 | 11 | 100 | 241 | 154 | 70 | 180 | 99 | 93 | 0 |  | 769 | 0 | 416 | 93 | 107 | 210 | 0 | 0 | 38 | 70 | 40 | 137 | 37 | 110 | 24 | 0 | 0 | 50 | 50 | 102 | 50 | 50 | 39 | 43 | 32 | 22 | 12 | 11 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 204 | 97 | 94 | 142 | 0 | 0 |  | 8137 | 3236 | 11373 | 4096 | 769 | 1857 | 2877 | 159 | 141 | 1302 | 172 | 0 | 0 | 104.12
19:30 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 414 | 355 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 102 | 100 | 82 | 102 | 149 | 87 | 57 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 111 | 30 | 80 | 27 | 25 | 231 | 0 | 0 | 135 | 0 | 32 | 80 | 46 | 90 | 93 | 48 | 19 | 20 | 0 | 100 | 100 | 360 | 301 | 185 | 68 | 155 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 174 | 45 | 88 | 20 | 0 | 28 | 0 | 50 | 50 | 140 | 300 | 61 | 86 | 45 | 108 | 19 | 46 | 9 | 290 | 24 | 11 | 100 | 213 | 60 | 50 | 180 | 50 | 103 | 0 |  | 769 | 0 | 419 | 88 | 107 | 236 | 0 | 0 | 38 | 91 | 40 | 142 | 36 | 110 | 26 | 0 | 0 | 50 | 50 | 102 | 50 | 50 | 39 | 50 | 32 | 22 | 12 | 8 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 96 | 94 | 150 | 0 | 0 |  | 8058 | 3314 | 11372 | 4158 | 769 | 1870 | 2730 | 159 | 141 | 1371 | 174 | 0 | 0 | 0
20:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 400 | 353 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 103 | 100 | 82 | 102 | 149 | 100 | 57 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 111 | 30 | 80 | 30 | 25 | 230 | 0 | 0 | 135 | 0 | 32 | 81 | 46 | 90 | 93 | 48 | 19 | 29 | 0 | 100 | 100 | 360 | 320 | 170 | 68 | 157 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 180 | 45 | 88 | 20 | 0 | 28 | 0 | 50 | 50 | 163 | 314 | 65 | 86 | 45 | 110 | 19 | 46 | 9 | 270 | 24 | 11 | 80 | 253 | 53 | 50 | 184 | 50 | 102 | 0 |  | 768 | 0 | 414 | 89 | 107 | 236 | 0 | 0 | 39 | 80 | 40 | 148 | 38 | 110 | 26 | 0 | 0 | 50 | 51 | 102 | 50 | 50 | 40 | 52 | 32 | 22 | 12 | 9 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 96 | 94 | 150 | 0 | 0 |  | 8120 | 3312 | 11432 | 4175 | 768 | 1882 | 2763 | 159 | 141 | 1364 | 180 | 0 | 0 | 104.12
21:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 345 | 354 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 104 | 100 | 82 | 102 | 149 | 100 | 57 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 36 | 0 | 112 | 30 | 80 | 60 | 25 | 232 | 0 | 0 | 135 | 0 | 40 | 81 | 47 | 90 | 93 | 49 | 19 | 35 | 0 | 100 | 90 | 360 | 301 | 181 | 68 | 149 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 178 | 46 | 88 | 20 | 0 | 27 | 0 | 50 | 50 | 163 | 300 | 48 | 86 | 45 | 110 | 19 | 46 | 9 | 290 | 24 | 11 | 50 | 255 | 52 | 50 | 180 | 51 | 106 | 0 |  | 769 | 0 | 417 | 92 | 106 | 238 | 0 | 0 | 39 | 88 | 40 | 146 | 38 | 110 | 26 | 0 | 0 | 50 | 50 | 102 | 50 | 50 | 37 | 52 | 32 | 22 | 12 | 9 | 0 | 0 | 159 | 10 | 19 | 0 | 0 | 0 | 220 | 95 | 94 | 150 | 0 | 0 |  | 8044 | 3322 | 11366 | 4097 | 769 | 1908 | 2741 | 159 | 142 | 1372 | 178 | 0 | 0 | 104.12
22:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 345 | 350 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 87 | 100 | 82 | 102 | 149 | 100 | 57 | 51 | 39 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 112 | 30 | 80 | 70 | 25 | 232 | 0 | 0 | 135 | 0 | 40 | 81 | 47 | 90 | 93 | 49 | 19 | 38 | 0 | 100 | 90 | 360 | 327 | 183 | 68 | 155 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 176 | 45 | 88 | 20 | 0 | 28 | 0 | 50 | 50 | 130 | 308 | 65 | 86 | 45 | 88 | 19 | 46 | 9 | 290 | 24 | 11 | 0 | 273 | 0 | 50 | 180 | 51 | 103 | 0 |  | 769 | 0 | 416 | 97 | 115 | 238 | 0 | 0 | 37 | 76 | 40 | 147 | 38 | 110 | 26 | 0 | 0 | 50 | 45 | 102 | 50 | 50 | 37 | 52 | 32 | 22 | 12 | 9 | 0 | 0 | 159 | 10 | 19 | 0 | 0 | 0 | 220 | 95 | 94 | 150 | 0 | 0 |  | 7956 | 3317 | 11273 | 4127 | 769 | 1874 | 2673 | 159 | 142 | 1353 | 176 | 0 | 0 | 104.11
23:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 350 | 353 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 87 | 100 | 82 | 102 | 149 | 100 | 57 | 50 | 29 | 18 | 56 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 112 | 30 | 80 | 90 | 26 | 232 | 0 | 0 | 135 | 0 | 40 | 81 | 33 | 90 | 93 | 49 | 19 | 38 | 0 | 100 | 90 | 360 | 305 | 177 | 68 | 155 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 172 | 45 | 88 | 20 | 0 | 29 | 0 | 50 | 50 | 130 | 310 | 64 | 86 | 45 | 87 | 19 | 46 | 9 | 310 | 25 | 11 | 0 | 273 | 0 | 50 | 180 | 51 | 105 | 0 |  | 769 | 0 | 417 | 91 | 115 | 238 | 0 | 0 | 34 | 74 | 40 | 147 | 38 | 110 | 26 | 0 | 0 | 50 | 45 | 100 | 50 | 50 | 37 | 52 | 32 | 22 | 12 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 220 | 96 | 94 | 153 | 0 | 0 |  | 7917 | 3311 | 11228 | 4132 | 769 | 1898 | 2624 | 160 | 142 | 1331 | 172 | 0 | 0 | 104.11
24:00 | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 345 | 352 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 104 | 100 | 82 | 102 | 149 | 100 | 57 | 50 | 26 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 112 | 30 | 53 | 100 | 26 | 231 | 0 | 0 | 135 | 0 | 40 | 81 | 47 | 90 | 93 | 49 | 19 | 39 | 0 | 100 | 90 | 360 | 301 | 180 | 68 | 155 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 162 | 46 | 88 | 20 | 0 | 29 | 0 | 50 | 50 | 130 | 304 | 65 | 86 | 45 | 86 | 19 | 46 | 9 | 310 | 25 | 11 | 0 | 270 | 0 | 10 | 180 | 11 | 105 | 0 |  | 768 | 0 | 417 | 91 | 115 | 239 | 0 | 0 | 34 | 68 | 40 | 147 | 38 | 110 | 14 | 0 | 0 | 50 | 45 | 97 | 50 | 50 | 36 | 52 | 32 | 22 | 12 | 11 | 0 | 0 | 160 | 10 | 18 | 0 | 0 | 0 | 220 | 96 | 15 | 152 | 0 | 0 |  | 7822 | 3209 | 11031 | 4119 | 768 | 1898 | 2458 | 160 | 142 | 1324 | 162 | 0 | 0 | 104.11
KWH | 1685000 | 0 | 0 | 2835000 | 7807900 | 765272 | 0 | 9095240 | 8253000 | 498200 | 0 | 8291100 | 0 | 1905600 | 1669464 | 1213301 | 0 | 0 | 2315000 | 768000 | 1652160 | 1617120 | 1874880 | 1401752 | 1285440 | 444757 | 782400 | 597600 | 1201634 | 1133770 | 355824 | 600000 | 558360 | 814700 | 811100 | 734760 | 0 | 2573575 | 722000 | 2400000 | 400000 | 524880 | 3850473 | 1191911 | 0 | 2614583 | 0 | 937920 | 1113640 | 927633 | 2124360 | 2162880 | 986880 | 450960 | 504000 | 0 | 930130 | 2764968 | 8967600 | 5979000 | 4654000 | 2726545 | 3677290 | 817992 | 150240 | 190000 | 0 | 1669464 | 313928 | 92294 | 489852 | 216900 | 826500 | 520320 | 3557760 | 976720 | 1309440 | 459324 | 13900 | 657000 | 0 | 1123800 | 1093000 | 3492278 | 6873117 | 1488000 | 1954560 | 991800 | 2377310 | 458000 | 1067940 | 216540 | 7370000 | 584136 | 242976 | 238080 | 5439707 | 253935 | 275735 | 4056000 | 354921 | 2160000 | 131180 |  | 18469818 | 0 | 9475872 | 1322400 | 1775040 | 3844800 | 0 | 0 | 397440 | 625152 | 694125 | 2379244 | 703572 | 2505024 | 142903 | 0 | 0 | 307304 | 371135 | 1050352 | 1137300 | 860192 | 379995 | 737280 | 222408 | 508320 | 280260 | 231408 | 0 | 0 | 3906700 | 103000 | 198000 | 0 | 0 | 0 | 4188781 | 2284913 | 521280 | 3422400 | 0 | 0 |  | 170658211 | 63046418 | 233704629 | 93449616 | 18469818 | 43636604 | 47375631 | 3906700 | 3295575 | 19867845 | 3557760 | 145080 | 0
Fuel Cost | 1449100 | 0 | 0 | 2438100 | 4997056 | 619870.32 | 0 | 5548096.4 | 5034330 | 4787702 | 0 | 5555037 | 0 | 11967168 | 11152019.52 | 7413269.11 | 0 | 0 | 2569650 | 11950080 | 10326000 | 10656820.8 | 18130089.6 | 8929160.24 | 7699785.6 | 7111664.43 | 5218608 | 4260888 | 7510212.5 | 7108737.9 | 266868 | 450000 | 0 | 0 | 0 | 6950829.6 | 0 | 0 | 0 | 2640000 | 440000 | 4970613.6 | 2541312.18 | 16269585.15 | 0 | 57285513.53 | 0 | 8244316.8 | 11993902.8 | 9025869.09 | 13149788.4 | 13972204.8 | 6454195.2 | 383316 | 0 | 0 | 846418.3 | 2516120.88 | 5559912 | 4125510 | 3257800 | 1881316.05 | 3530198.4 | 548054.64 | 129206.4 | 174800 | 0 | 1585990.8 | 3402979.52 | 684821.48 | 377186.04 | 162675 | 636405 | 390240 | 24335078.4 | 732540 | 12033753.6 | 353679.48 | 0 | 683280 | 0 | 1078848 | 983700 | 2723976.84 | 4811181.9 | 1696320 | 2091379.2 | 1090980 | 2710133.4 | 586240 | 993184.2 | 201382.2 | 4716800 | 438102 | 184661.76 | 4125926.4 | 39492272.82 | 4400693.55 | 4701281.75 | 29000400 | 6051403.05 | 0 | 0 |  | 94196071.8 | 0 | 6348834.24 | 10592424 | 14715081.6 | 61824384 | 0 | 0 | 4475174.4 | 7364290.56 | 5469705 | 1641678.36 | 696536.28 | 18537177.6 | 4812973.04 | 0 | 0 | 3518630.8 | 3978567.2 | 9411153.92 | 9837645 | 7655708.8 | 4046946.75 | 7313817.6 | 2617742.16 | 559152 | 263444.4 | 175175.856 | 0 | 0 | 15079862 | 3319690 | 5300460 | 0 | 0 | 0 | 61407529.46 | 0 | 9033782.4 | 0 | 0 | 0 |  | 497498593.63 | 374193639.226 | 871692232.856 | 66035845.836 | 94196071.8 | 30379933.69 | 353479959.15 | 15079862 | 0 | 288185481.98 | 24335078.4 | 0 | 0
Yesterday Day Peak | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 380 | 316 | 13 | 0 | 450 | 0 | 69 | 65 | 55 | 0 | 0 | 104 | 0 | 50 | 48 | 64 | 50 | 58 | 21 | 33 | 18 | 56 | 36 | 5 | 25 | 24 | 33 | 33 | 33 | 0 | 110 | 30 | 0 | 0 | 16 | 204 | 0 | 0 | 140 | 0 | 40 | 0 | 31 | 90 | 85 | 46 | 19 | 6 | 0 | 0 | 130 | 360 | 301 | 180 | 140 | 156 | 40 | 5 | 20 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 18 | 138 | 30 | 50 | 20 | 2 | 30 | 0 | 47 | 50 | 130 | 300 | 64 | 86 | 43 | 95 | 19 | 44 | 9 | 290 | 24 | 5 | 0 | 230 | 0 | 0 | 178 | 0 | 95 | 20 |  | 770 | 0 | 350 | 66 | 58 | 120 | 0 | 0 | 0 | 0 | 32 | 114 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 25 | 0 | 22 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 160 | 96 | 0 | 127 | 0 | 0 |  | 9167 | DayPeak
Yesterday Evening Peak | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 400 | 353 | 50 | 0 | 450 | 0 | 100 | 81 | 55 | 0 | 0 | 103 | 100 | 82 | 102 | 149 | 100 | 57 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 111 | 30 | 80 | 30 | 25 | 230 | 0 | 0 | 135 | 0 | 32 | 81 | 46 | 90 | 93 | 48 | 19 | 29 | 0 | 100 | 100 | 360 | 320 | 170 | 68 | 157 | 30 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 11 | 33 | 22 | 180 | 45 | 88 | 20 | 0 | 28 | 0 | 50 | 50 | 163 | 314 | 65 | 86 | 45 | 110 | 19 | 46 | 9 | 270 | 24 | 11 | 80 | 253 | 53 | 50 | 184 | 50 | 102 | 0 |  | 768 | 0 | 414 | 89 | 107 | 236 | 0 | 0 | 39 | 80 | 40 | 148 | 38 | 110 | 26 | 0 | 0 | 50 | 51 | 102 | 50 | 50 | 40 | 52 | 32 | 22 | 12 | 9 | 0 | 0 | 159 | 10 | 18 | 0 | 0 | 0 | 220 | 96 | 94 | 150 | 0 | 0 |  | 11432 | EvPeak
Forecast for Evening | 74 | 0 | 0 | 120 | 365 | 86 | 78 | 412 | 355 | 55 | 0 | 450 | 305 | 100 | 81 | 55 | 0 | 0 | 105 | 100 | 100 | 102 | 149 | 100 | 60 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 42 | 0 | 120 | 30 | 0 | 120 | 25 | 221 | 0 | 0 | 135 | 0 | 40 | 88 | 50 | 90 | 93 | 50 | 19 | 25 | 0 | 100 | 100 | 360 | 360 | 225 | 148 | 155 | 43 | 0 | 5 | 0 | 85 | 50 | 52 | 22 | 11 | 33 | 21 | 180 | 50 | 88 | 20 | 0 | 60 | 0 | 50 | 50 | 163 | 330 | 66 | 86 | 45 | 130 | 20 | 46 | 9 | 341 | 24 | 11 | 200 | 280 | 300 | 96 | 185 | 100 | 100 | 0 |  | 781 | 48 | 410 | 100 | 115 | 225 | 0 | 0 | 42 | 85 | 40 | 150 | 33 | 110 | 26 | 0 | 0 | 50 | 52 | 102 | 50 | 50 | 40 | 52 | 35 | 22 | 12 | 11 | 0 | 0 | 170 | 10 | 18 | 0 | 0 | 0 | 220 | 95 | 94 | 150
Forecast for Day | 74 | 0 | 0 | 120 | 365 | 45 | 20 | 412 | 355 | 55 | 0 | 450 | 0 | 80 | 81 | 55 | 0 | 0 | 100 | 100 | 100 | 102 | 149 | 100 | 60 | 50 | 35 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 41 | 0 | 118 | 30 | 0 | 120 | 16 | 221 | 0 | 0 | 60 | 0 | 40 | 0 | 44 | 90 | 93 | 47 | 19 | 10 | 0 | 100 | 100 | 360 | 360 | 225 | 148 | 155 | 43 | 0 | 5 | 0 | 85 | 0 | 52 | 22 | 8 | 33 | 21 | 128 | 45 | 88 | 20 | 2 | 60 | 0 | 50 | 40 | 163 | 330 | 66 | 86 | 45 | 130 | 20 | 46 | 9 | 300 | 24 | 11 | 100 | 200 | 150 | 96 | 185 | 50 | 100 | 20 |  | 781 | 0 | 410 | 100 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 150 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 30 | 52 | 0 | 22 | 12 | 11 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 220 | 95 | 94 | 150
Generation at 08:00(Today) | 74 | 0 | 0 | 120 | 300 | 0 | 0 | 360 | 355 | 0 | 0 | 400 | 0 | 7 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 48 | 10 | 21 | 10 | 33 | 18 | 31 | 36 | 0 | 25 | 24 | 33 | 33 | 11 | 0 | 118 | 30 | 0 | 120 | 8 | 231 | 0 | 0 | 60 | 0 | 40 | 8 | 16 | 90 | 59 | 42 | 19 | 14 | 0 | 100 | 90 | 360 | 298 | 193 | 68 | 155 | 30 | 5 | 5 | 0 | 80 | 0 | 0 | 22 | 5 | 14 | 21 | 110 | 45 | 7 | 20 | 1.2 | 29 | 0 | 50 | 30 | 130 | 303 | 64 | 40 | 45 | 77 | 19 | 44 | 9 | 275 | 25 | 11 | 0 | 195 | 0 | 0 | 180 | 0 | 93 | 9.9 | 0 | 770 | 0 | 360 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 150 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 30 | 8 | 0 | 22 | 12 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 96 | 0 | 151 | 0 | 0 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [65 empty] | 199
| Minimum Generation |  | 8109.8 | 8:00
| Highest Generation |  | 11432 | 20:00
| Day Peak Generation |  | 9167 | 12:00
| Evening Peak Generation |  | 11432 | 20:00
| HVDC Max Flow |  | 776 | 3:00
| HVDC EvPeak Flow |  | 768 | 20:00
| Load factor L.F |  | 85.18%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-09-24
Till now the maximum generation is : - |  |  | 11623 | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-09-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9167 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8374.2 | MW
Evening Peak Generation : |  | 11432 | MW Hour : | 20:00 | Available Max Generation : |  | 12990 | MW
E.P. Demand (at gen end) : |  | 11432 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 11432 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1290 | MW
Total Gen. (MKWH) : |  | 233.7046 | System Load Factor : | 85.18% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -400 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-09-24
Actual : | 103.99 | Ft.(MSL) , | Rule curve : | 104.32 | Ft.( MSL )
Gas Consumed : | Total = | 1153.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 96415779.526
|  | Coal : | 15079862 | Oil : | 641665441.13 | Total : | 753161082.656
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4124.839 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1403.9561 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1258.1266 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1136.9047 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1027.3595 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 829.046 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 461.9114 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 213.4134 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 639.4094 |  |  | 0 | 0%
Total | 0 |  | 11094.966 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Kaptai #5
|  |  |  | 3) Ghorasal Unit-3,4 |  | 12)Siddhirganj CCPP-335 MW
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-2
7) Baghabari-71 MW
8) Ashuganj Unit-3
9) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 08:42 to 17:22 for D/W.
b) Tongi-Uttara 3rd phase was under shut down from 08:58 to 16:39 for D/W.
c) Bhola CCPP GT-1 was synchronized at 10:28.
d) Raozan Unit-1 tripped at 10:20 due to tripping of auxiliary transformer and was synchronized at 12:38.
e) Cumilla(N)-Feni 132 kV Ckt-2 was under shut down from 08:15 to 10:34 for red hot maintenance at B-phase
isolator of Feni end.
f) Rangpur 132/33 kV T2 transformer was under shut down from 08:25 to 08:52 for ret hot maintenance at |  |  |  | About 20 MW power interruption occurred under Rangpur S/S area
33 kV breaker. |  |  |  | from 08:25 to 08:52.
g) Bheramara HVDC-Khulna(S) 230 kV Ckt-1 was under shut down from 10:34 to 18:30 for D/W.
h) Aminbazar-Kaliakoir 230 kV Ckt-1 tripped at 12:21 from Kaliakoir end showing gen trip, 67N and
was switched on at 12:59.
i) Mirpur- Uttara 3rd phase was switched on at 16:01.
j) Khulshi-Halisahar 132kV Ckt-1 tripped at 15:32 from khulshi end showing dist, Z1 CN and was switched on at 15:47. |  |  |  | About 130 MW power interruption occurred under Halishahar S/S
Khulshi-Halisahar 132 kV Ckt-2 was under maintenance since 14/09/2018 for D/W. |  |  |  | areas from 15:32 to 15:47.
k) Halishahar- Juldah 132 kV Ckt tripped at 15:32 from both end showing dist, CN at Halishahar end &
O/C, E/F at Juldah end and was switched on at 15:47.
l) Raozan unit-2 was synchronized at 18:00.
m) Dohazari 132/33 kV T1 transformer was under shut down from 19:52 to 21:08 for red hot maintenance.
n) Noapara 132 kV bus-A was shut down at 07:20 (24/09/2018) for C/M.
o) Feni 132/33 kV T2 transformer was shut down at 07:41(24/09/2018) for C/M.
p) Raozan unit-1 was shut down at 00:14(24/09/2018) due to gas pressure low.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-09-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 74 | 1685000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2835000 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7807900 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 765272 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9095240 | Gas shortage
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 50 | 498200 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 353 | 8253000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8291100
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1905600
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 81 | 1669464 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1213301
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1401752
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 355824
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 103 | 2315000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 768000
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 82 | 1652160
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 444757
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1617120
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 782400 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 597600
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1874880
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1201634
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1133770
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 57 | 1285440 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1158360 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 814700
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 811100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 41 | 734760 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 253 | 5439707 | Machine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 53 | 253935 | Low demand
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 50 | 275735 | Low demand
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 354921 | Low demand
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 102 | 2160000 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3617 | 71452632
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 80 | 2400000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 30 | 400000 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 524880
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 131180
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 48 | 986880
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 141 | 3295575 | Unit # 05 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 230 | 5042384
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2614583
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 937920 | Engine problem
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 81 | 1113640
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 46 | 927633
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2124360
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 450960
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 504000
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 93 | 2162880 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 1079 | 23616875
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 930130 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2764968 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 170 | 4654000 | Gas shortage
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8967600
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 5979000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 30 | 817992
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 150240 | Gas shortage
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 190000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 2726545 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Development work
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1669464
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 313928
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 157 | 3677290
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 489852
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216900
** | Tripura |  | Imported power | 0 | 160 | 180 | 3557760
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 826500
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 92294 | Feni-Comilla (N) L/O
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 520320
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 80 | 238080 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1797 | 38782863
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 45 | 976720 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 459324
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 88 | 1309440
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 13900
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 184 | 4056000
| Mymensingh Area Total |  |  |  | 522 | 337 | 6815384
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 28 | 657000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3492278
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 314 | 6873117 | FGMO.
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 1123800
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1093000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 242976
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 65 | 1488000
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1954560
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 991800
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 110 | 2377310
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 458000
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 1067940
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 584136
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 270 | 7370000 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 216540
| Sylhet Area Total |  |  |  | 1549 | 1290 | 29990457
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 768 | 18469818
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 89 | 1322400 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 107 | 1775040 | Engine problem
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 39 | 397440
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 236 | 3844800
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 80 | 625152
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 414 | 9475872
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 694125
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 94 | 521280 | Engine problem
| Khulna Area Total |  |  |  | 2214 | 1867 | 37125927
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2505024
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 26 | 142903
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 38 | 703572
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 148 | 2379244 | ST Under maint.
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 2284913
| Barisal Area Total |  |  |  | 462 | 418 | 8015656
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 307304
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 51 | 371135
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1137300
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 860192
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 40 | 379995
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Shut down
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | FGMO.
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 150 | 3422400 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | On test
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 32 | 222408
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 508320
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 12 | 280260 | Engine problem
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 9 | 231408
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 737280
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1050352
| Rajshahi Area Total |  |  |  | 1264 | 840 | 9508354
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 159 | 3906700 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 10 | 103000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 198000
| Rangpur Area Total |  |  |  | 484 | 187 | 4207700
| Total |  |  |  | 16445 | 11432 | 229515848
| Eastern Grid Total |  |  |  | 12021 | 8120 | 170658211
| Western Grid Total |  |  |  | 4424 | 3312 | 58857637
| National Grid Total |  |  |  | 16445 | 11432 | 229515848
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-09-23 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7403 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3426 | MW
i) Dhaka area |  |  | 4044 | MW | i) Khulna area |  |  | 1353 | MW
ii) Chittagong area |  |  | 1078 | MW | ii) Rajshahi area |  |  | 1159 | MW
iii) Comilla area |  |  | 1045 | MW | iii) Barisal area |  |  | 258 | MW
iv) Mymensingh area |  |  | 769 | MW | iv) Rangpur area |  |  | 656 | MW
v) Sylhet area |  |  | 467 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10829 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 1500 | Netrokona | 75 | 1830 | Central s/s | 96 | 2000
Munsiganj | 115 | 2100 | Jamalpur | 124 | 1900 | Noapara | 90 | 1830
Sonargaon | 45 | 1830 | Sherpur | 86 | 1930 | Jessore | 154 | 1900
Shyampur | 190 | 1200 | Srimongal | 35 | 1900 | Jhenida | 91 | 2000
Bhulta | 175 | 1700 | Shahjibazar | 108 | 1930 | Bottail | 126 | 2000
Madanganj | 59 | 2100 | Fenchuganj | 48 | 1900 | G.K Project | 58 | 2100
Shitalakhya | 115 | 1500 | Kulawara | 41 | 2000 | Faridpur | 160 | 1930
Rahim steel | 13 | 1100 | Sylhet | 140 | 1800 | Madaripur | 148 | 2100
Matuail | 98 | 900 | Chatak | 28 | 2000 | Gopalganj | 86 | 2000
Ghorasal | 82 | 2000 | Sunamganj | 35 | 1900 | Bagerhat | 79 | 1930
Narsingdi | 127 | 2000 | Biani Bazar | 42 | 2000 | Mongla | 36 | 1100
Haripur (SBU) | 106 | 1200 | Comilla (S) | 180 | 2000 | Satkhira | 92 | 2100
Ullon | 96 | 1830 | Comilla(N) | 97 | 2000 | Gallamari | 43 | 2000
Hasnabad | 214 | 2000 | Chandpur | 124 | 1930 | Magura | 54 | 1900
Magbazar | 139 | 1300 | Feni | 134 | 2100 | Chuadanga | 80 | 2000
Maniknagar | 110 | 1200 | Chowmuhani | 192 | 2200 | Barisal | 118 | 2100
Bangabhaban | 42 | 1300 | Ashuganj | 62 | 2300 | Patuakhali | 94 | 2100
Narinda | 90 | 1300 | Daudkandi | 106 | 1830 | Bhandaria | 47 | 2000
Dhanmondi | 141 | 1200 | B.Baria | 133 | 2000 | Ishurdi | 56 | 1830
Lalbag | 92 | 1800 | Ramganj | 36 | 2100 | Ruppur Paromanobik | 2 | 1500
Madartek | 51 | 2100 | Madunaghat | 63.5 | 1830 | Natore | 112 | 2100
Mirpur | 108 | 1830 | Hathazari | 91 | 2100 | Bogra | 133 | 2000
Kalyanpur | 123 | 1830 | Khulshi | 174 | 1600 | Noagaon | 101 | 1930
Gulshan | 140 | 1500 | Halishahar | 139 | 1500 | Rajshahi | 142 | 2100
Uttara | 92 | 1500 | Baraulia | 157 | 1500 | C.Nawabganj | 69 | 2100
Uttara(New) | 3 | 300 | Sikalbaha | 39 | 2000 | Amnura | 45 | 2100
Kamrangirchar | 83 | 1000 | Dohazari | 92 | 1830 | Pabna | 118 | 1930
Savar | 126 | 1830 | Cox'sbazar | 79 | 2100 | Shahjadpur | 98 | 1900
Bhasantec | 165 | 1830 | Chandraghona | 34 | 1830 | Serajganj | 104 | 2000
Agargaon | 48 | 1500 | Kaptai | 7.2 | 1830 | Niyamatpur | 53 | 1930
Satmosjid | 101 | 1830 | A. Khaer Stl. | 12 | 300 | Joypurhat | 46 | 1900
Tongi | 138 | 1800 | Bakulia | 107 | 1830 | Rangpur | 124 | 2100
Kabirpur | 204 | 1500 | Julda | 20 | 800 | Lalmonirhat | 87 | 1830
Basundhara | 129 | 1300 | TK chemical | 4.4 | 1100 | Saidpur | 116 | 1830
Manikganj | 105 | 2100 | Modern Steel | 13 | 500 | Purbasadipur | 87 | 1900
Joydevpur | 230 | 2100 | Shahmirpur | 27 | 300 | Thakurgaon | 69 | 1930
New Tongi | 106 | 1800 | Khagrachhari | 20 | 2000 | Palashbari | 100 | 1930
Korda | 271 | 1830 | Matarbari | 25 | 1900 | Barapukuria | 54 | 2000
Dhamrai | 42 | 2100 | Baroiar Hat | 11 | 1830 | Panchagar | 40 | 1830
Tangail | 156 | 1900 | Abul Khair 230 | 180 | 2400
Mymensing | 245 | 1930 | BSRM | 115 | 2300
Kishorganj | 104 | 2000 | Goalpara | 39 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-09-23
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 391 | 13:00 | 380 | 18:30 | Kaliakoir | 371 | 5:00 | 357 | 18:30
Bheramara | 404 | 7:00 | 395 | 19:00 | Bhulta | 382 | 6:00 | 372 | 11:00
Ashuganj(N) | 390 | 3:00 | 377 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 233 | 24:00 | 225 | 19:00 | Hathazari | 218 | 4:00 | 208 | 11:00
Ishurdi | 221 | 3:00 | 213 | 11:00 | Megnaghat | 220 | 4:00 | 211 | 11:00
Ashuganj | 220 | 19:00 | 212 | 11:00 | Fenchuganj | 234 | 6:00 | 227 | 11:00
Serajganj | 225 | 5:00 | 213 | 12:00 | Siddhirganj | 224 | 4:00 | 213 | 11:00
Baghabari | 223 | 4:00 | 213 | 12:00 | Maniknagar | 232 | 6:00 | 227 | 15:00
Barapukuria | 220 | 4:00 | 210 | 11:00 | Old Airport | 228 | 6:00 | 216 | 8:00
Bogra | 227 | 3:00 | 221 | 12:00 | Barisal | 409 | 18:00 | 397 | 1:00
Khulna South | 218 | 5:00 | 212 | 11:00 | AKSML | 391 | 4:00 | 380 | 8:00
Rampura | 223 | 6:00 | 216 | 8:00 | BSRM | 380 | 3:00 | 368 | 15:00
Haripur | 237 | 6:00 | 230 | 14:00 | Bibiyana | 388 | 5:00 | 376 | 15:00
Hasnabad | 220 | 1:00 | 214 | 12:00 | Bhulta | 370 | 6:00 | 356 | 8:00
Aminbazar | 220 | 4:00 | 212 | 11:00 | Ashuganj (S) | 235 | 6:00 | 224 | 11:00
Tongi | 223 | 4:00 | 211 | 11:00 | Kaliakoir | 227 | 2:00 | 220 | 8:00
Comilla (N) | 223 | 17:00 | 213 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 200 | 129 | 1100 | Ramganj | 130 | 800 | 112 | 1900
Munsiganj | 135 | 1800 | 130 | 800 | Madanhat | 130 | 100 | 126 | 1300
Megnaghat | 134 | 1830 | 128 | 700 | Hathazari | 128 | 300 | 126 | 800
Shyampur | 132 | 2000 | 122 | 1100 | Khulshi | 127 | 400 | 123 | 1000
Bhulta | 130 | 100 | 125 | 800 | Halishahar | 131 | 700 | 125 | 1100
Madanganj | 137 | 100 | 127 | 800 | Baraulia | 127 | 300 | 123 | 1500
Shitalakhya | 138 | 100 | 127 | 800 | Sikalbaha | 130 | 500 | 125 | 1300
Rahim steal | 135 | 100 | 129 | 1100 | Dohazari | 126 | 400 | 122 | 1000
Matuail | 134 | 1830 | 128 | 800 | Cox'sbazar | 122 | 500 | 112 | 1830
Ghorasal | 136 | 100 | 133 | 800 | Chandraghona | 130 | 400 | 127 | 1000
Narsinghdi | 130 | 1830 | 121 | 1100 | Kaptai | 129 | 2100 | 125 | 300
Haripur (SBU) | 134 | 1900 | 129 | 1100 | A. Khaer Stl. | 125 | 100 | 124 | 300
Ullon | 134 | 600 | 125 | 1100 | Bakulia | 128 | 400 | 124 | 900
Hasnabad | 134 | 1830 | 126 | 1100 | Julda | 129 | 300 | 125 | 900
Magbazar | 134 | 800 | 123 | 1100 | TK Chemical | 130 | 2100 | 125 | 500
Maniknagar | 130 | 600 | 125 | 1200 | Modern Steel | 127 | 100 | 124 | 1600
Bangabhaban | 130 | 600 | 125 | 1200 | Shahmirpur | 129 | 700 | 125 | 1500
Narinda | 130 | 600 | 125 | 1200 | Khagrachhari | 130 | 500 | 126 | 1000
Dhanmondi | 134 | 600 | 125 | 1100 | Matarbari | 124 | 700 | 115 | 1830
Lalbag | 134 | 100 | 121 | 1200 | Baroiar Hat | 125 | 600 | 120 | 2000
Madartek | 134 | 400 | 125 | 1100 | Goalpara | 137 | 1400 | 134 | 600
Mirpur | 135 | 400 | 127 | 1200 | Central s/s | 137 | 1700 | 134 | 1100
Kalyanpur | 134 | 400 | 127 | 1100 | Noapara | 135 | 1400 | 130 | 1830
Gulshan | 133 | 600 | 124 | 1500 | Jessore | 129 | 100 | 121 | 1900
Uttara | 130 | 200 | 122 | 1200 | Jhenida | 130 | 400 | 118 | 1900
Uttara(New) | 132 | 400 | 125 | 700 | Bottail | 196 | 600 | 126 | 2000
Kamrangirchar | 135 | 100 | 124 | 1100 | G.K.Project | 140 | 700 | 134 | 1900
Savar | 133 | 400 | 124 | 1200 | Faridpur | 132 | 900 | 122 | 1900
Bhasantec | 135 | 400 | 126 | 1200 | Madaripur | 135 | 900 | 125 | 1500
Agargaon | 134 | 200 | 127 | 1100 | Gopalganj | 134 | 900 | 124 | 1830
Satmosjid | 135 | 400 | 126 | 1200 | Bagerhat | 134 | 100 | 129 | 2100
Tongi | 132 | 400 | 125 | 1800 | Mongla | 135 | 1000 | 127 | 1900
Kabirpur | 135 | 500 | 124 | 2100 | Satkhira | 134 | 900 | 130 | 1900
Basundhara | 130 | 500 | 120 | 1600 | Gallamari | 137 | 1800 | 133 | 1900
Manikganj | 134 | 500 | 124 | 1830 | Magura | 130 | 600 | 115 | 1830
Joydevpur | 138 | 1700 | 128 | 800 | Chuadanga | 127 | 600 | 110 | 1900
New Tongi | 133 | 400 | 124 | 1500 | Barisal | 139 | 1700 | 134 | 1900
Kodda | 136 | 1300 | 128 | 800 | Patuakhali | 135 | 1200 | 127 | 2100
Dhamrai | 131 | 700 | 123 | 1830 | Bhandaria | 135 | 700 | 130 | 1600
Tangail | 130 | 1000 | 119 | 1830 | Ishurdi | 140 | 300 | 130 | 1900
Mymensing | 130 | 1400 | 116 | 800 | Ruppur Paromanobik | 139 | 600 | 132 | 1900
Kishorganj | 127 | 1700 | 118 | 1830 | Natore | 137 | 1800 | 124 | 2000
Netrokona | 129 | 1700 | 105 | 1830 | Bogra | 129 | 600 | 114 | 1830
Jamalpur | 136 | 1700 | 115 | 800 | Noagaon | 127 | 600 | 110 | 1900
Sherpur | 135 | 1600 | 114 | 800 | Rajshahi | 134 | 1800 | 122 | 1900
Srimongal | 138 | 500 | 133 | 1900 | C.Nawabganj | 132 | 1800 | 123 | 1900
Shahjibazar | 136 | 600 | 132 | 2000 | Amnura | 134 | 300 | 123 | 1200
Fenchuganj | 137 | 700 | 132 | 1800 | Pabna | 132 | 1800 | 124 | 2100
Khulawara | 135 | 400 | 131 | 1830 | Shahjadpur | 138 | 600 | 131 | 1900
Sylhet | 135 | 500 | 131 | 1830 | Serajganj | 131 | 600 | 120 | 1930
Chatak | 135 | 600 | 129 | 2000 | Niyamatpur | 124 | 600 | 107 | 2000
Sunamganj | 133 | 400 | 128 | 1900 | Joypurhat | 125 | 600 | 108 | 2000
Biani Bazar | 134 | 500 | 128 | 1900 | Rangpur | 123 | 600 | 100 | 1900
Comilla(s) | 127 | 700 | 121 | 1830 | Lalmonirhat | 120 | 600 | 88 | 2000
Comilla(n) | 135 | 700 | 131 | 1200 | Saidpur | 122 | 600 | 97 | 1900
Chandpur | 125 | 100 | 125 | 200 | Purbasadipur | 130 | 600 | 110 | 1900
Feni | 120 | 700 | 112 | 200 | Thakurgaon | 122 | 600 | 98 | 1830
Chowmuhani | 122 | 700 | 112 | 2000 | Palashbari | 122 | 900 | 100 | 2000
Ashuganj | 137 | 1700 | 133 | 2300 | Barapukuria | 135 | 600 | 116 | 2000
Daudkandi | 134 | 1830 | 126 | 1100 | Panchagar | 119 | 600 | 97 | 2000
B.Baria | 136 | 500 | 130 | 2000

## L-Curve
Date | 2018-09-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 280 | 7822 | 3209 | 11031 |  |  |  | QF-LDC-12
0:30 | 260 | 7541 | 3067 | 10608 | Date: | 2018-09-23
1:00 | 240 | 7260 | 2925 | 10185
1:30 | 252 | 7188.5 | 2868.5 | 10057
2:00 | 264 | 7117 | 2812 | 9929
2:30 | 292 | 7015 | 2720 | 9735 | [5 empty] | Gen. at Eve. Peak | 11432 | 11432 MW (20:00 )
3:00 | 320 | 6913 | 2628 | 9541 | [6 empty] | 20:00
3:30 | 330 | 6894.5 | 2581 | 9475.5 | [5 empty] | Gen. at Day Peak | 9167 | 9167 MW (12:00 )
4:00 | 340 | 6876 | 2534 | 9410 | [6 empty] | 12:00
4:30 | 320 | 6805.5 | 2431.5 | 9237 | [5 empty] | Highest Generation | 11432
5:00 | 300 | 6735 | 2329 | 9064 | [6 empty] | 20:00
5:30 | 240 | 6544.8 | 2295.5 | 8840.3
6:00 | 180 | 6354.6 | 2262 | 8616.6
6:30 | 190 | 6220.85 | 2216 | 8436.85
7:00 | 200 | 6087.1 | 2170 | 8257.1
7:30 | 220 | 6026.45 | 2157 | 8183.45
8:00 | 240 | 5965.8 | 2144 | 8109.8
8:30 | 145 | 6170.4 | 2169.5 | 8339.9
9:00 | 50 | 6375 | 2195 | 8570
9:30 | 60 | 6495.05 | 2166.5 | 8661.55
10:00 | 70 | 6615.1 | 2138 | 8753.1
10:30 | 60 | 6723.55 | 2175 | 8898.55
11:00 | 50 | 6832 | 2212 | 9044
11:30 | 75 | 6838 | 2267.5 | 9105.5
12:00 | 100 | 6844 | 2323 | 9167
12:30 | 165 | 6939.55 | 2320 | 9259.55
13:00 | 230 | 7035.1 | 2317 | 9352.1
13:30 | 250 | 7016.25 | 2320.5 | 9336.75
14:00 | 270 | 6997.4 | 2324 | 9321.4
14:30 | 260 | 7108.6 | 2377.5 | 9486.1
15:00 | 250 | 7219.8 | 2431 | 9650.8
15:30 | 240 | 7174.45 | 2426 | 9600.45
16:00 | 230 | 7129.1 | 2421 | 9550.1
16:30 | 120 | 6996.4 | 2396 | 9392.4
17:00 | 10 | 6863.7 | 2371 | 9234.7
17:30 | 50 | 6931.85 | 2489 | 9420.85
18:00 | 90 | 7000 | 2607 | 9607
18:30 | 245 | 7568.5 | 2921.5 | 10490
19:00 | 400 | 8137 | 3236 | 11373
19:30 | 370 | 8058 | 3314 | 11372
20:00 | 370 | 8120 | 3312 | 11432 |  |  |  | Executive Engineer
20:30 | 375 | 8082 | 3317 | 11399 |  |  |  | Network Operation Division
21:00 | 380 | 8044 | 3322 | 11366
21:30 | 360 | 8000 | 3319.5 | 11319.5
22:00 | 340 | 7956 | 3317 | 11273 |  |  |  |  | Page 6 of 7
22:30 | 310 | 7936.5 | 3314 | 11250.5
23:00 | 280 | 7917 | 3311 | 11228
23:30 | 280 | 7869.5 | 3260 | 11129.5
24:00 | 280 | 7822 | 3209 | 11031
11432 MW (20:00 )
9167 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-09-23 |  | Energy | 233704629
[10 empty] | 2018-09-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4119 | 768 | 1898 | 2458 | 160 | 142 | 1324 | 0 | 162
0:30 | 3952 | 771.5 | 1866.5 | 2331.5 | 160 | 142 | 1224.5 | 0 | 160 | Date: | 2018-09-23
1:00 | 3785 | 775 | 1835 | 2205 | 160 | 142 | 1125 | 0 | 158
1:30 | 3782.5 | 775 | 1843.5 | 2152 | 160 | 142 | 1045 | 0 | 157 | [7 empty] | Total Energy | 233.7046 | Total Energy Gen 233.705 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 233.705 MKWHr
2:00 | 3780 | 775 | 1852 | 2099 | 160 | 142 | 965 | 0 | 156 | [7 empty] | Energy not Served | 0
2:30 | 3736 | 775.5 | 1865.5 | 1997 | 160 | 142 | 906 | 0 | 153 | [7 empty] | Energy Requirement | 233.7046
3:00 | 3692 | 776 | 1879 | 1895 | 160 | 142 | 847 | 0 | 150
3:30 | 3699 | 775.5 | 1875 | 1849.5 | 160 | 142 | 824.5 | 0 | 150 | [6 empty] | Shortage
4:00 | 3706 | 775 | 1871 | 1804 | 160 | 142 | 802 | 0 | 150
4:30 | 3708 | 775 | 1875.5 | 1685.5 | 160 | 142 | 746 | 0 | 145
5:00 | 3710 | 775 | 1880 | 1567 | 160 | 142 | 690 | 0 | 140
5:30 | 3697 | 775.5 | 1876.5 | 1446.5 | 159.5 | 142 | 608 | 0 | 135
6:00 | 3684 | 776 | 1873 | 1326 | 159 | 142 | 526 | 0 | 130
6:30 | 3800 | 775.5 | 1864.5 | 1143.5 | 159.5 | 141.5 | 431.5 | 0 | 118 |  |  |  |  | Coal
7:00 | 3916 | 775 | 1856 | 961 | 160 | 141 | 337 | 0 | 106
7:30 | 4017 | 772 | 1783 | 831.5 | 160 | 141 | 360.5 | 0 | 110 |  |  |  | Oil |  |  |  | ,
8:00 | 4118 | 769 | 1710 | 702 | 160 | 141 | 384 | 0 | 114
8:30 | 4045.5 | 769 | 1802 | 886 | 160 | 142.5 | 401.5 | 0 | 119
9:00 | 3973 | 769 | 1894 | 1070 | 160 | 144 | 419 | 0 | 124
9:30 | 3866 | 769 | 1871.5 | 1279 | 160 | 143 | 426.5 | 0 | 127
10:00 | 3759 | 769 | 1849 | 1488 | 160 | 142 | 434 | 0 | 130
10:30 | 3817 | 769 | 1869.5 | 1552 | 160 | 142 | 436 | 0 | 131
11:00 | 3875 | 769 | 1890 | 1616 | 160 | 142 | 438 | 0 | 132
11:30 | 3815 | 769.5 | 1883 | 1703.5 | 160 | 141 | 476.5 | 0 | 135
12:00 | 3755 | 770 | 1876 | 1791 | 160 | 140 | 515 | 0 | 138
12:30 | 3759 | 770 | 1869.5 | 1889.5 | 160 | 139.5 | 510.5 | 0 | 140
13:00 | 3763 | 770 | 1863 | 1988 | 160 | 139 | 506 | 0 | 142
13:30 | 3763 | 770 | 1863 | 1988 | 160 | 139 | 506 | 0 | 142
14:00 | 3763 | 770 | 1863 | 1988 | 160 | 139 | 506 | 0 | 142
14:30 | 3849.5 | 769.5 | 1850.5 | 2042 | 159 | 139.5 | 532.5 | 0 | 140.5
15:00 | 3936 | 769 | 1838 | 2096 | 158 | 140 | 559 | 0 | 139
15:30 | 3940 | 769 | 1759 | 2119 | 158.5 | 140 | 562 | 0 | 140.5
16:00 | 3944 | 769 | 1680 | 2142 | 159 | 140 | 565 | 0 | 142
16:30 | 3914.5 | 769 | 1635 | 2058 | 159 | 140 | 570 | 0 | 141
17:00 | 3885 | 769 | 1590 | 1974 | 159 | 140 | 575 | 0 | 140
17:30 | 3877.5 | 768.5 | 1531.5 | 2057 | 159 | 140 | 741 | 0 | 145
18:00 | 3870 | 768 | 1473 | 2140 | 159 | 140 | 907 | 0 | 150
18:30 | 3983 | 768.5 | 1665 | 2508.5 | 159 | 140.5 | 1104.5 | 0 | 161
19:00 | 4096 | 769 | 1857 | 2877 | 159 | 141 | 1302 | 0 | 172
19:30 | 4158 | 769 | 1870 | 2730 | 159 | 141 | 1371 | 0 | 174
20:00 | 4175 | 768 | 1882 | 2763 | 159 | 141 | 1364 | 0 | 180
20:30 | 4136 | 768.5 | 1895 | 2752 | 159 | 141.5 | 1368 | 0 | 179
21:00 | 4097 | 769 | 1908 | 2741 | 159 | 142 | 1372 | 0 | 178
21:30 | 4112 | 769 | 1891 | 2707 | 159 | 142 | 1362.5 | 0 | 177
22:00 | 4127 | 769 | 1874 | 2673 | 159 | 142 | 1353 | 0 | 176
22:30 | 4129.5 | 769 | 1886 | 2648.5 | 159.5 | 142 | 1342 | 0 | 174
23:00 | 4132 | 769 | 1898 | 2624 | 160 | 142 | 1331 | 0 | 172
23:30 | 4125.5 | 768.5 | 1898 | 2541 | 160 | 142 | 1327.5 | 0 | 167 | Max Temp. in Dhaka |  | 33.9° C
24:00 | 4119 | 768 | 1898 | 2458 | 160 | 142 | 1324 | 0 | 162
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 233.705 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 233.705 MKWHr
Note on W13: Author:

## Generation
2018-09-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 111 | 114 | 112 | 112 | 110 | 109 | 110 | 110 | 110 | 110 | 110 |  | 111 | 111 | 111 | 112 | 112 | 112 | 112 | 2573575
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 722000
3 | Chittagong ST-1 (Raozan) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 70 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 53 | 2400000
4 | Chittgong ST-2 (Raozan) | [17 empty] | 0 |  | 10 | 27 | 30 | 60 | 70 | 90 | 100 | 400000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 524880
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.6 | 4.7 | 11 | 15.7 | 20 | 20 | 20 | 20 | 19.4 | 14.5 | 8.2 | 2.5 | 0 | [8 empty] | 131180
6 | Sikalbaha 225MW (Gas) | [6 empty] | 204 | 221 | 198 | 204 | 215 | 204 | 204 | 204 | 205 | 203 | 203 | 203 |  | 231 | 231 | 230 | 232 | 232 | 232 | 231 | 3850473
7 | Sikalbaha 225MW (Oil) | 229 | 229 | 229 | 229 | 203 | 165 | 0 | [19 empty] | 1191911
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 135 | 135 | 135 | 135 | 100 | 60 | 60
10 | Sikalbaha GT 150MW (Oil) | 48 | 48 | 48 | 48 | 48 | 34 | 32 | 60 | 80 | 100 | 100 | 140 | 100 | 70 | 135 | 100 | 80 | 60 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2614583
| Dohazari Peaking | [7 empty] | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 45 |  | 41 | 46 | 46 | 47 | 47 | 33 | 47 | 927633
12 | Hathazari peaking | 80 | 80 | 72 | 72 | 72 | 0 | [6 empty] | 40 | 39 | 42 | 41 | 41 | 80 |  | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 1113640
| Daudkandi bangla trak | [17 empty] | 0 |  | 100 | 100 | 80 | 50 | 0 |  |  | 238080
14 | Daudkandi Peaking 52MW | 0 | [15 empty] | 0 | 50 |  | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 313928
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 106 | 105 | 105 | 107 | 107 | 106 | 107 | 103 | 65 | 39 | 39 | 104 | 85 | 64 | 100 | 62 | 103 | 101 |  | 105 | 102 | 103 | 104 | 87 | 87 | 104 | 2315000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 253 | 265 | 220 | 273 | 270 | 270 | 218 | 70 | 72 | 145 | 223 | 230 | 235 | 253 | 202 | 203 | 200 | 203 |  | 241 | 213 | 253 | 255 | 273 | 273 | 270 | 5439707
19 | Ashuganj 195MW Modular | 120 | 152 | 152 | 152 | 152 | 152 | 148 | 148 | 148 | 140 | 140 | 140 | 140 | 140 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 2726545
20 | Ghorasal ST: Unit-1,2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1685000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4 | [14 empty] | 0 | 25 | 25 | 0
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2835000
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7807900
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | [14 empty] | 0 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 930130
30 | Ashuganj ST: Unit- 5 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 120 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 2764968
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 40 | 40 | 40 | 40 | 35 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 817992
33 | Ashuganj CCPP 225 MW | 211 | 210 | 210 | 210 | 210 | 210 | 210 | 211 | 216 | 181 | 198 | 180 | 153 | 149 | 199 | 199 | 190 | 191 |  | 185 | 185 | 170 | 181 | 183 | 177 | 180 | 4654000
34 | Ashuganj CCPP(South) | 70 | 70 | 18 | 30 | 33 | 85 | 147 | 334 | 301 | 298 | 334 | 301 | 301 | 295 | 327 | 301 | 301 | 301 |  | 301 | 301 | 320 | 301 | 327 | 305 | 301 | 5979000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8967600
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 150240
36 | Chandpur CCPP | 146 | 149 | 151 | 155 | 155 | 156 | 154 | 156 | 155 | 157 | 156 | 156 | 156 | 153 | 155 | 147 | 149 | 156 |  | 151 | 155 | 157 | 149 | 155 | 155 | 155 | 3677290
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 390 | 373 | 347 | 348 | 350 | 360 | 345 | 360 | 395 | 380 | 380 | 380 | 415 | 380 | 380 | 410 | 380 | 350 |  | 414 | 414 | 400 | 345 | 345 | 350 | 345 | 9095240
40 | Meghnaghat CCPP 450MW | 225 | 225 | 225 | 225 | 240 | 240 | 260 | 260 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 330 |  | 430 | 450 | 450 | 450 | 450 | 450 | 450 | 8291100
41 | Haripur Power CCPP 360MW | 352 | 356 | 355 | 356 | 355 | 360 | 358 | 351 | 353 | 351 | 342 | 316 | 332 | 350 | 344 | 321 | 303 | 330 |  | 357 | 355 | 353 | 354 | 350 | 353 | 352 | 8253000
42 | Mymensingh RPCL 210MW | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 30 | 30 | 30 | 29 | 30 | 29 | 30 | 45 | 44 | 45 | 44 |  | 46 | 45 | 45 | 46 | 45 | 45 | 46 | 976720
43 | Haripur NEPC 110MW | [11 empty] | 13 | 13 | 13 | 40 | 55 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 498200
44 | Fenchugonj CCPP-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 |  | 27 | 28 | 28 | 27 | 28 | 29 | 29 | 657000
45 | Fenchugonj CCPP-2
46 | Shajibazar 330 MW | 300 | 312 | 302 | 300 | 331 | 298 | 300 | 330 | 303 | 306 | 315 | 300 | 303 | 306 | 315 | 305 | 302 | 301 |  | 301 | 300 | 314 | 300 | 308 | 310 | 304 | 6873117
47 | Shahjibazar GT: Unit- 8, 9 | 67 | 66 | 66 | 66 | 67 | 67 | 67 | 62 | 53 | 65 | 65 | 64 | 59 | 63 | 65 | 63 | 50 | 65 |  | 40 | 61 | 65 | 48 | 65 | 64 | 65 | 1488000
48 | Shahjibazar 86MW | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 10 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 50 | 50 | 30 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1954560
49 | Shahjibazar (EPL) 50MW | 45 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 42 | 43 | 43 | 44 | 44 | 44 | 10 | 10 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 991800
50 | Sylhet GT 150 MW | 100 | 98 | 98 | 98 | 98 | 78 | 78 | 130 | 87 | 77 | 78 | 95 | 78 | 97 | 130 | 110 | 78 | 98 |  | 108 | 108 | 110 | 110 | 88 | 87 | 86 | 2377310
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 458000
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 46 | 45 | 45 | 44 | 44 | 46 | 46 | 46 | 46 | 44 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1067940
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 216540
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242976
55 | Fenchugonj (Barakatullah) 51MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1123800
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 17 | 24 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 584136
57 | Summit Bibiana- 2 | 300 | 290 | 310 | 300 | 300 | 290 | 290 | 285 | 260 | 260 | 315 | 290 | 270 | 265 | 300 | 265 | 270 | 265 |  | 270 | 290 | 270 | 290 | 290 | 310 | 310 | 7370000
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 36 | 17 | 17 | 36 | 55 | 55 | 36 | 36 | 36 | 48 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1133770
59 | Sikalbaha (Energis) | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 32 | 40 | 40 | 40 | 40 | 32 | 40 | 40 | 40 | 40 | 40 |  | 32 | 32 | 32 | 40 | 40 | 40 | 40 | 937920
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450960
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 19 | 22 | 0 | 5 | 22 | 22 | 0 | 0 | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 355824
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 |  | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 459324
63 | Tripura | 158 | 156 | 150 | 150 | 140 | 130 | 106 | 114 | 124 | 130 | 132 | 138 | 142 | 142 | 139 | 142 | 140 | 150 |  | 172 | 174 | 180 | 178 | 176 | 172 | 162 | 3557760
64 | Malancha, Ctg. EPZ (United) | 38 | 30 | 38 | 39 | 39 | 39 | 13 | 8 | 12 | 5 | 3 | 6 | 7 | 5 | 4 | 4 | 10 | 6 |  | 20 | 20 | 29 | 35 | 38 | 38 | 39 | 504000
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 21 | 21 | 21 | 12 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 489852
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 0 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 216900
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826500
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520320
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 558360
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 814700
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811100
73 | Ghorashal (Regent) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 44 | 0 | [17 empty] | 765272
76 | Siddhirganj (Desh) | [11 empty] | 0 | 17 | 17 | 20 | 35 | 35 | 35 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 768000
77 | Siddhirganj (Dutch Bangla) | 96 | 92 | 92 | 92 | 50 | 7 | 7 | 7 | 8 | 40 | 50 | 50 | 70 | 85 | 80 | 80 | 60 | 60 |  | 70 | 82 | 82 | 82 | 82 | 82 | 82 | 1652160
78 | Gazipur (RPCL) | 42 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 24 | 33 | 33 | 33 | 33 | 34 | 40 | 41 | 36 | 41 |  | 41 | 41 | 41 | 36 | 42 | 42 | 42 | 734760
79 | Kodda 149 MW | 82 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 30 | 48 | 48 | 64 | 84 | 84 | 84 | 133 | 105 | 98 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 1874880
80 | Jamalpur 95MW | 88 | 56 | 40 | 40 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 50 | 64 | 64 | 78 | 79 | 80 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1309440
81 | Lakdhanvi 52 MW | [13 empty] | 0 | 1 | 22 | 25 | 25 |  | 0 | [6 empty] | 92294
82 | Madanganj 102MW | 81 | 81 | 81 | 81 | 81 | 70 | 15 | 15 | 18 | 55 | 65 | 65 | 65 | 70 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1669464
83 | Pagla (DPA ) | [9 empty] | 0 | 11 | 21 | 20 | 22 | 21 | 21 | 20 | 11 |  | 50 | 50 | 51 | 51 | 51 | 50 | 50 | 444757
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 60 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1669464
85 | Keraniganj (Powerpac) 100MW | 75 | 63 | 63 | 20 | 10 | 10 | 10 | 10 | 35 | 50 | 50 | 50 | 60 | 60 | 50 | 74 | 50 | 70 |  | 87 | 87 | 100 | 100 | 100 | 100 | 100 | 1401752
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 100 | 70 | 30 | 8 | 8 | 22 | 56 | 56 | 69 | 98 | 100 | 100 | 100 | 75 | 74 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1905600
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 20 | 10 | 10 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 190000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2124360
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 28 | 28 | 28 | 28 | 31 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1093000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 102 | 102 | 40 | 7 | 7 | 7 | 7 | 7 | 16 | 32 | 32 | 48 | 84 | 102 | 102 | 102 | 64 | 70 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1617120
95 | Patenga 50MW | 43 | 43 | 43 | 43 | 43 | 39 | 36 | 37 | 39 | 44 | 42 | 46 | 47 | 46 | 46 | 0 | 6 | 31 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 986880
96 | Chittagong ECPV 108 MW | 92 | 92 | 92 | 85 | 92 | 70 | 92 | 81 | 86 | 86 | 79 | 85 | 92 | 92 | 92 | 92 | 92 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2162880
97 | Katpotti 51 MW | 33 | 33 | 32 | 33 | 26 | 25 | 31 | 12 | 18 | 33 | 33 | 33 | 33 | 33 | 33 | 35 | 37 | 33 |  | 38 | 40 | 40 | 40 | 39 | 29 | 26 | 782400
98 | Bosila 108MW | 49 | 64 | 57 | 57 | 57 | 57 | 37 | 8 | 58 | 58 | 58 | 58 | 57 | 56 | 56 | 56 | 56 | 56 |  | 59 | 57 | 57 | 57 | 57 | 57 | 57 | 1285440
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1213301
100 | Northern 55 MW | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 18 | 36 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 56 | 55 | 1201634
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 130 | 130 | 100 | 163 | 100 | 100 | 100 |  | 163 | 140 | 163 | 163 | 130 | 130 | 130 | 3492278
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.4 | 0.8 | 1.3 | 2.1 | 2 | 2 | 1.1 | 1 | 1.3 | 0.9 | 0.2 | 0 | [8 empty] | 13900
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 54 | 18 | 18 | 597600
104 | APR Energy , Keranigonj | [16 empty] | 0 | 11 |  | 154 | 60 | 53 | 52 | 0 |  |  | 253935
105 | Bramhangoan 100 MW (Aggreko) | [16 empty] | 0 | 20 |  | 70 | 50 | 50 | 50 | 50 | 50 | 10 | 275735
106 | United Mymensingh PPL | 178 | 178 | 178 | 178 | 175 | 182 | 106 | 56 | 178 | 178 | 180 | 178 | 170 | 180 | 180 | 178 | 178 | 180 |  | 180 | 180 | 184 | 180 | 180 | 180 | 180 | 4056000
112 | Aggreko Aurahati 100MW | 51 | 0 | [14 empty] | 0 | 17 |  | 99 | 50 | 50 | 51 | 51 | 51 | 11 | 354921
114 | Summit Gazipur-1 150MW | 92 | 96 | 96 | 96 | 96 | 95 | 30 | 30 | 46 | 84 | 93 | 95 | 92 | 90 | 92 | 92 | 93 | 93 |  | 93 | 103 | 102 | 106 | 103 | 105 | 105 | 2160000
115
116
117
118
120 | Eastern Zone Total | 7260 | 7117 | 6913 | 6876 | 6735 | 6354.6 | 6087.1 | 5965.8 | 6375 | 6615.1 | 6832 | 6844 | 7035.1 | 6997.4 | 7219.8 | 7129.1 | 6863.7 | 7000 |  | 8137 | 8058 | 8120 | 8044 | 7956 | 7917 | 7822 | 170658211
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 98 | 95 | 51 | 27 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 66 | 83 | 83 | 75 | 83 | 51 | 59 |  | 93 | 88 | 89 | 92 | 97 | 91 | 91 | 1322400
125 | Khulna (KPCL-2) | 99 | 99 | 70 | 49 | 16 | 16 | 16 | 16 | 30 | 49 | 49 | 58 | 83 | 83 | 99 | 98 | 102 | 103 |  | 107 | 107 | 107 | 106 | 115 | 115 | 115 | 1775040
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 40 | 40 | 40 | 40 | 12 | 0 | [10 empty] | 0 | 11 |  | 38 | 38 | 39 | 39 | 37 | 34 | 34 | 397440
129 | Khulna CCPP 225MW | 241 | 180 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 |  | 210 | 236 | 236 | 238 | 238 | 238 | 239 | 3844800
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 80 | 48 | 48 | 64 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2505024
136 | Barisal GT: Unit-1, 2 | [17 empty] | 0 |  | 24 | 26 | 26 | 26 | 26 | 26 | 14 | 142903
137 | Bhola Aggreko 95MW | 97 | 97 | 97 | 97 | 96 | 96 | 96 | 95 | 95 | 96 | 96 | 96 | 96 | 95 | 96 | 96 | 96 | 65 |  | 97 | 96 | 96 | 95 | 95 | 96 | 96 | 2284913
| Bhola CCPP 194MW | 69 | 69 | 69 | 66 | 69 | 70 | 68 | 68 | 60 | 66 | 117 | 114 | 77 | 79 | 77 | 77 | 63 | 103 |  | 137 | 142 | 148 | 146 | 147 | 147 | 147 | 2379244
140 | Bhola (Venture) 33MW | 32 | 32 | 32 | 32 | 28 | 26 | 23 | 22 | 22 | 23 | 23 | 25 | 25 | 26 | 27 | 26 | 25 | 30 |  | 37 | 36 | 38 | 38 | 38 | 38 | 38 | 703572
141 | Bangla Trak Noapara | [16 empty] | 0 | 10 |  | 94 | 94 | 94 | 94 | 94 | 94 | 15 | 521280
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 0 |  |  |  | 32 | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 694125
143 | Gopalganj Peaking | 30 | 30 | 28 | 28 | 0 | [9 empty] | 0 | 6 | 22 | 43 |  | 70 | 91 | 80 | 88 | 76 | 74 | 68 | 625152
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 775 | 775 | 776 | 775 | 775 | 776 | 775 | 769 | 769 | 769 | 769 | 770 | 770 | 769 | 769 | 769 | 769 | 768 |  | 769 | 769 | 768 | 769 | 769 | 769 | 768 | 18469818
147 | Bheramara 360 MW | 422 | 423 | 421 | 421 | 420 | 424 | 425 | 417 | 422 | 350 | 350 | 350 | 350 | 350 | 410 | 410 | 380 | 320 |  | 416 | 419 | 414 | 417 | 416 | 417 | 417 | 9475872
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 158 | 159 | 159 | 159 |  | 159 | 159 | 159 | 159 | 159 | 160 | 160 | 3906700
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [16 empty] | 0 | 26 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 307304
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 220 | 187 | 146 | 149 | 147 | 153 | 144 | 156 | 157 | 134 | 139 | 160 | 131 | 131 | 147 | 134 | 130 | 136 |  | 204 | 220 | 220 | 220 | 220 | 220 | 220 | 4188781
159 | Sirajgonj Unit-3 225 MW(Gas) | 150 | 151 | 151 | 151 | 151 | 151 | 153 | 152 | 153 | 118 | 120 | 127 | 119 | 118 | 131 | 121 | 118 | 119 |  | 142 | 150 | 150 | 150 | 150 | 153 | 152 | 3422400
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [15 empty] | 0 | 46 | 51 |  | 50 | 50 | 51 | 50 | 45 | 45 | 45 | 371135
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 20 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508320
163 | Bogra (EPL) | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 280260
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 8 | 9 | 9 | 9 | 11 | 11 | 231408
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1137300
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 25 | 25 | 43 | 43 | 43 | 43 | 43 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 860192
167 | Katakhali Peaking | 30 | 30 | 30 | 30 | 30 | 13 | 0 | [9 empty] | 0 | 24 |  | 39 | 39 | 40 | 37 | 37 | 37 | 36 | 379995
168 | Santahar Peaking | [16 empty] | 0 | 30 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 222408
169 | Rajlanka 52 MW | 52 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 34 | 34 | 34 | 34 |  | 43 | 50 | 52 | 52 | 52 | 52 | 52 | 737280
170 | Chapainawabganj-100 MW | 97 | 97 | 75 | 42 | 42 | 25 | 25 | 0 | [8 empty] | 0 | 83 |  | 102 | 102 | 102 | 102 | 102 | 100 | 97 | 1050352
171
172
173 | Rangpur GT | 10 | 10 | 10 | 10 | 0 | [11 empty] | 0 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 103000
175 | Saidpur GT | 18 | 18 | 18 | 18 | 0 | [11 empty] | 0 | 18 |  | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 198000
176
177
178
178 | Western Zone Total | 2925 | 2812 | 2628 | 2534 | 2329 | 2262 | 2170 | 2144 | 2195 | 2138 | 2212 | 2323 | 2317 | 2324 | 2431 | 2421 | 2371 | 2607 | 0 | 3236 | 3314 | 3312 | 3322 | 3317 | 3311 | 3209 | 63046418