## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-09-19 | Wednesday
|  | Date (day): | 2018-09-19 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11307 | MW |  |  | (b) At Evening Peak Hour : |  | 12459 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-09-18 | 2018-09-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 74 | 74 | 74 | 74 | 11 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120 | 70 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 58 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 304 | 330 | 350 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 55 | 103 | 98 | 105 |  |  | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 241 | 350 | 350
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 260 | 225 | 225 |  | 225 | GT 2 Under Maint.,
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 81 | 81 | 81 | 81 |  | 19 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 17 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 96 | 97 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 150 | 150 | 0 | 0 |  | 217 | Under maint.
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 10 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 33 | 26 | 35 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 65 | 133 | 132 | 132
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 61 | 70 | 71 | 71 |  | 37 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 50 | 50 | 50 |  | 30 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 41 | 41 | 41 |  | 11 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 190 | 260 | 210 | 260 |  | 40 | Machine problem
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 73 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 97 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 108 | 108 | 110 | 110 |  | 34 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 3155 | 3548 | 3580 | 4109 | 467 | 1194
38 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 16.2 | 0 | 0 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 34 | 45 | 45 |  | 5 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 142 | 150 | 144 | 144 |  |  | #5 Under maint.
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 41 | 192 | 215 | 215 |  |  | ST Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 135 | 135 | 135
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 72 | 70 | 70
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 14 | 44 | 45 | 45
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 78 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 15 | 10 | 15
50 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 90 | 92 | 92 |  | 16 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 768.2 | 1027 | 1051 | 1056 | 230 | 91
51 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 95 | 120 | 130 | 120
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 | 34 |  | Gas shortage
52 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 209 | 225 | 225
53 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
54 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 301 | 360 | 360 |  |  | FGMO
55 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 42 | 40 | 40
56 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
57 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas shortage
58 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 68 | 68 | 68 | 127 |  | Gas shortage
59 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | line problem
60 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
61 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
62 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 152 | 100 | 100 | 100
63 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 0 | 22 | 22
64 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 98 | 150 | 129 | 175
65 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
66 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 0 | 52 | 52
67 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 18 | 21 | 21
68 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 130 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1571 | 1845 | 1873 | 2029 | 394 | 51
69 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 65 | 65 | 65 | 137 |  | Gas shortage
70 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
71 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 64 | 87 | 88 | 88
72 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.9 | 0 | 2 | 0
73 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 163 | 178 | 180 | 185 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 275.9 | 352 | 357 | 360 | 137 | 0
74 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 58 | 58 | 58
75 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60
76 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
77 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 317 | 301 | 330 | 330
78 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 47 | 47
79 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 47 | 47
80 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
81 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 56 | 66 | 66
82 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86
83 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 46 | 45 | 45
84 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 76 | 100 | 130 | 130
85 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
86 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 44 | 44 | 44
87 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 21 | 21 | 21 |  | 13 | Engine problem
88 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 341 | 341 |  |  | FGMO
89 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1271 | 1274 | 1478 | 1478 | 0 | 13
90 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 779 | 769 | 781 | 781
91 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 27 | 88 | 100 | 100 |  | 10 | Engine problem
92 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 115 | 115
93 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 0 | 42
94 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 241 | 225 | 225
95 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 0 | 85
96 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 410 | 410 | 410
97 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
98 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 94 | 94 | 94
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 1379 | 1837 | 1765 | 1940 | 0 | 10
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 112 | 110 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 24 | 0 | 26
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 38 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 118 | 120 | 120 |  | 74 | Machine problem
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 348 | 387 | 358 | 384 | 0 | 74
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 49 | 0 | 48
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 50 | 40 | 40 | 10 |  | Engine problem
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 38
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 175 | 215 | 220 | 220
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 163 | 220 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 0 | 0 | 0 | 0 |  | 141 | Under Shut down
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | 0 | 0 | 0
113 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
114 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
115 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 10 | 10 | 10
116 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
117 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
118 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 102 | 50 | 102
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 502 | 896 | 675 | 898 | 81 | 241
119 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
120 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 | 104 |  | Coal shortage
121 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 9 | 0 | 17
122 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 170 | 197 | 170 | 205 | 189 | 85
| Total |  |  |  |  | 17043 | 16445 | 9440.1 | 11363 | 11307 | 12459 | 1498 | 1759
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8919.2039 | 10736 | 10683.09 | 11771.5237
A. |  | 2018-09-18 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11363 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 8753.2 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11363 | MW
3 | Day peak Generation : |  |  | 9440.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10736 | MW
4 | Evening peak Generation : |  |  | 11363 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 243.1927 | MKWHr | By Solar | 0.1308 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 142.779 | MKWHr |  | By Oil: | 70.9879 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.1436 | MKWHr |  | By Hydro: | 3.3255 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1498 | MW | Dhaka | 4096 | 4096 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1759 | MW | Chittagong | 1034 | 1034 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3257 | MW | Khulna | 1369 | 1369 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1187.53 | MMCFD |  |  | Rajshahi | 1223 | 1223 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104337755.602 | ii) Oil : | Taka | 650552666.69 | Comilla | 924 | 924 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15994296 | Total | Taka | 770884718.292 | Mymensingh | 742 | 742 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 3.259 | MKWHr. | Sylhet | 477 | 477 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -430 | MW at | 20:00 | hrs | Barisal | 299 | 299 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -490 | MW at | 4:00 | hrs | Rangpur | 572 | 572 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.2° C |  |  | Total | 10736 | 10736 |  | 0
B. |  | 2018-09-19 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12459 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 959 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 246.1248 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8905.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.7491 | MKWHr. | ii) HVDC Flow at Peak Time |  | 769 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0768 | MKWHr. | iii) Maximum HVDC Flow : |  | 780 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.4 |  | (b) Today: | 104.29 |  | (c) Rule Curve: |  | 103.14
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-09-18
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 244 | 340 | 96 | 0 | 440 | 0 | 100 | 81 | 55 | 207 | 0 | 0 | 100 | 100 | 102 | 117 | 100 | 71 | 51 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 100 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 63 | 44 | 90 | 91 | 44 | 19 | 30 | 0 | 100 | 100 | 360 | 300 | 175 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 150 | 46 | 87 | 17 | 0 | 53 | 60 | 50 | 47 | 130 | 302 | 47 | 86 | 45 | 100 | 19 | 46 | 9 | 290 | 21 | 11 | 50 | 205 | 0 | 0 | 187 | 50 | 100 | 0 |  | 779 | 0 | 415 | 87 | 115 | 244 | 0 | 0 | 36 | 54 | 40 | 100 | 32 | 111 | 24 | 0 | 0 | 50 | 48 | 85 | 40 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 10 | 16 | 188 | 0 | 0 | 150 | 96 | 91 | 0 | 0 | 0 |  | 7854 | 3186 | 11040 | 4254 | 779 | 1848 | 2647 | 169 | 142 | 1051 | 150 | 0 | 0 | 104.4
2:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 256 | 350 | 96 | 0 | 440 | 0 | 100 | 81 | 55 | 206 | 0 | 0 | 50 | 100 | 102 | 117 | 100 | 71 | 10 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 130 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 63 | 44 | 90 | 91 | 44 | 19 | 31 | 0 | 100 | 100 | 360 | 300 | 180 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 146 | 46 | 87 | 17 | 0 | 59 | 60 | 50 | 47 | 163 | 302 | 54 | 86 | 45 | 100 | 19 | 46 | 9 | 285 | 21 | 11 | 0 | 158 | 0 | 0 | 187 | 0 | 100 | 0 |  | 779 | 0 | 411 | 87 | 115 | 243 | 0 | 0 | 12 | 52 | 40 | 112 | 32 | 111 | 0 | 0 | 0 | 50 | 44 | 85 | 40 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 8 | 16 | 182 | 0 | 0 | 33 | 96 | 0 | 0 | 0 | 0 |  | 7661 | 2923 | 10584 | 4315 | 779 | 1887 | 2318 | 169 | 142 | 828 | 146 | 0 | 0 | 104.4
3:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 262 | 351 | 96 | 0 | 450 | 0 | 100 | 81 | 55 | 207 | 0 | 0 | 0 | 100 | 102 | 117 | 100 | 71 | 11 | 40 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 130 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 63 | 48 | 90 | 91 | 46 | 19 | 32 | 0 | 100 | 100 | 360 | 300 | 181 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 142 | 47 | 87 | 17 | 0 | 59 | 60 | 50 | 47 | 163 | 307 | 50 | 86 | 45 | 100 | 19 | 46 | 9 | 305 | 22 | 11 | 0 | 158 | 0 | 0 | 190 | 0 | 90 | 0 |  | 779 | 0 | 413 | 87 | 115 | 150 | 0 | 0 | 32 | 39 | 40 | 118 | 31 | 111 | 0 | 0 | 0 | 0 | 15 | 85 | 40 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 8 | 16 | 188 | 0 | 0 | 28 | 96 | 0 | 0 | 0 | 0 |  | 7651 | 2766 | 10417 | 4340 | 779 | 1918 | 2265 | 169 | 142 | 662 | 142 | 0 | 0 | 104.4
4:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 262 | 351 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 208 | 0 | 0 | 0 | 99 | 102 | 55 | 100 | 71 | 11 | 40 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 112 | 30 | 130 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 63 | 48 | 90 | 91 | 45 | 19 | 32 | 0 | 100 | 100 | 360 | 300 | 180 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 140 | 47 | 72 | 17 | 0 | 59 | 60 | 50 | 47 | 163 | 303 | 50 | 86 | 45 | 100 | 19 | 46 | 9 | 280 | 22 | 11 | 0 | 158 | 0 | 0 | 190 | 0 | 96 | 0 |  | 780 | 0 | 415 | 87 | 115 | 120 | 0 | 0 | 30 | 39 | 40 | 104 | 29 | 111 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 50 | 25 | 52 | 14 | 22 | 10 | 11 | 0 | 0 | 169 | 8 | 16 | 190 | 0 | 0 | 71 | 96 | 0 | 0 | 0 | 0 |  | 7451 | 2729 | 10180 | 4326 | 780 | 1891 | 2158 | 169 | 142 | 574 | 140 | 0 | 0 | 104.4
5:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 262 | 351 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 210 | 0 | 0 | 0 | 99 | 102 | 16 | 100 | 71 | 11 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 16 | 0 | 112 | 30 | 130 | 0 | 0 | 151 | 0 | 135 | 0 | 0 | 40 | 8 | 24 | 90 | 84 | 45 | 19 | 32 | 0 | 100 | 100 | 360 | 334 | 190 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 132 | 47 | 48 | 17 | 0 | 59 | 60 | 47 | 44 | 163 | 310 | 50 | 86 | 45 | 100 | 19 | 46 | 9 | 290 | 0 | 11 | 0 | 160 | 0 | 0 | 190 | 0 | 93 | 0 |  | 779 | 0 | 412 | 84 | 99 | 120 | 0 | 0 | 30 | 0 | 40 | 119 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 169 | 0 | 16 | 190 | 0 | 0 | 87 | 95 | 0 | 0 | 0 | 0 |  | 7286 | 2652 | 9938 | 4369 | 779 | 1897 | 2064 | 169 | 142 | 386 | 132 | 0 | 0 | 104.4
6:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 241 | 351 | 0 | 0 | 450 | 0 | 80 | 48 | 15 | 210 | 0 | 0 | 0 | 50 | 30 | 16 | 50 | 8 | 10 | 40 | 35 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 16 | 0 | 112 | 30 | 130 | 0 | 0 | 151 | 0 | 130 | 0 | 0 | 40 | 8 | 17 | 90 | 84 | 45 | 19 | 32 | 0 | 100 | 100 | 360 | 327 | 181 | 68 | 154 | 30 | 5 | 5 | 0 | 50 | 0 | 0 | 22 | 8 | 33 | 21 | 124 | 47 | 48 | 17 | 0 | 59 | 60 | 47 | 47 | 130 | 312 | 51 | 50 | 45 | 80 | 19 | 46 | 9 | 270 | 11 | 11 | 0 | 150 | 0 | 0 | 98 | 0 | 93 | 0.25 |  | 779 | 0 | 414 | 10 | 49 | 120 | 0 | 0 | 8 | 0 | 40 | 120 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 195 | 0 | 0 | 129 | 95 | 0 | 0 | 0 | 0 |  | 6641.25 | 2534 | 9175.25 | 4314 | 779 | 1772 | 1491 | 170 | 142 | 383 | 124 | 0.25 | 0 | 104.4
7:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 60 | 351 | 0 | 0 | 450 | 0 | 50 | 48 | 15 | 209 | 0 | 0 | 0 | 50 | 32 | 16 | 50 | 8 | 11 | 6 | 18 | 37 | 55 | 19 | 25 | 24 | 33 | 33 | 16 | 0 | 112 | 30 | 130 | 0 | 0 | 90 | 0 | 135 | 0 | 0 | 40 | 8 | 17 | 90 | 84 | 44 | 19 | 23 | 0 | 100 | 100 | 360 | 300 | 183 | 68 | 154 | 30 | 5 | 5 | 0 | 51 | 0 | 0 | 22 | 8 | 33 | 21 | 116 | 45 | 48 | 17 | 0.4 | 53 | 60 | 47 | 44 | 163 | 302 | 51 | 50 | 45 | 130 | 19 | 44 | 9 | 300 | 0 | 11 | 0 | 158 | 0 | 0 | 98 | 0 | 92 | 3 |  | 779 | 0 | 416 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 100 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 194 | 0 | 0 | 205 | 95 | 0 | 0 | 0 | 0 |  | 6354.4 | 2547 | 8901.4 | 4053 | 779 | 1821 | 1401 | 170 | 142 | 416 | 116 | 3.4 | 0 | 104.39
8:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 60 | 353 | 0 | 0 | 450 | 0 | 50 | 49 | 15 | 208 | 0 | 0 | 0 | 50 | 32 | 16 | 50 | 8 | 10 | 6 | 18 | 37 | 55 | 0 | 25 | 24 | 33 | 33 | 16 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 17 | 90 | 84 | 44 | 19 | 9 | 0 | 100 | 100 | 360 | 300 | 173 | 68 | 154 | 30 | 5 | 5 | 0 | 51 | 0 | 0 | 22 | 8 | 25 | 21 | 118 | 44 | 48 | 17 | 1 | 52 | 60 | 47 | 41 | 163 | 300 | 60 | 50 | 45 | 130 | 19 | 44 | 9 | 280 | 8 | 11 | 0 | 155 | 0 | 0 | 98 | 0 | 90 | 9.2 |  | 779 | 0 | 417 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 100 | 18 | 100 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 169 | 0 | 0 | 182 | 0 | 0 | 180 | 92 | 0 | 0 | 0 | 0 |  | 6265.2 | 2488 | 8753.2 | 3968 | 779 | 1774 | 1402 | 169 | 142 | 391 | 118 | 10.2 | 0 | 104.39
9:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 76 | 348 | 0 | 0 | 450 | 0 | 50 | 48 | 20 | 204 | 0 | 0 | 0 | 50 | 32 | 98 | 50 | 41 | 10 | 11 | 25 | 55 | 55 | 0 | 25 | 24 | 25 | 33 | 30 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 16 | 90 | 84 | 44 | 19 | 2 | 0 | 100 | 90 | 360 | 300 | 170 | 68 | 154 | 30 | 5 | 5 | 0 | 82 | 0 | 0 | 22 | 8 | 25 | 21 | 124 | 41 | 48 | 17 | 1.5 | 56 | 60 | 44 | 44 | 163 | 305 | 61 | 84 | 45 | 128 | 19 | 42 | 9 | 290 | 15 | 11 | 0 | 158 | 0 | 0 | 98 | 0 | 86 | 13.4 |  | 779 | 0 | 410 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 112 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 169 | 0 | 0 | 214 | 0 | 0 | 171 | 90 | 0 | 0 | 0 | 0 |  | 6500.9 | 2507 | 9007.9 | 4011 | 779 | 1838 | 1492 | 169 | 142 | 438 | 124 | 14.9 | 0 | 104.39
10:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 55 | 345 | 13 | 0 | 450 | 0 | 75 | 70 | 40 | 201 | 0 | 0 | 0 | 75 | 32 | 98 | 70 | 61 | 11 | 38 | 54 | 56 | 55 | 19 | 25 | 24 | 25 | 33 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 15 | 78 | 84 | 44 | 19 | 3 | 0 | 100 | 90 | 360 | 300 | 157 | 68 | 153 | 30 | 5 | 5 | 0 | 85 | 0 | 1 | 22 | 8 | 33 | 21 | 110 | 28 | 50 | 17 | 2.1 | 56 | 58 | 44 | 44 | 163 | 300 | 60 | 83 | 45 | 128 | 19 | 44 | 9 | 300 | 24 | 11 | 0 | 228 | 0 | 0 | 106 | 0 | 94 | 16.4 |  | 780 | 0 | 410 | 44 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 25 | 0 | 22 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 174 | 92 | 0 | 0 | 0 | 0 |  | 6761.5 | 2500 | 9261.5 | 3967 | 780 | 1852 | 1782 | 170 | 142 | 440 | 110 | 18.5 | 0 | 104.39
11:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 130 | 343 | 55 | 0 | 450 | 0 | 94 | 81 | 40 | 150 | 0 | 0 | 10 | 98 | 92 | 65 | 100 | 61 | 10 | 36 | 54 | 56 | 55 | 19 | 25 | 9 | 27 | 25 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 15 | 78 | 84 | 44 | 19 | 2 | 0 | 95 | 80 | 360 | 300 | 181 | 68 | 153 | 20 | 5 | 5 | 0 | 85 | 0 | 8 | 22 | 8 | 33 | 20 | 92 | 28 | 64 | 20 | 2.2 | 56 | 60 | 47 | 44 | 100 | 303 | 40 | 83 | 45 | 78 | 18 | 42 | 9 | 255 | 24 | 11 | 0 | 185 | 0 | 0 | 154 | 0 | 94 | 8.7 |  | 779 | 0 | 330 | 51 | 77 | 120 | 0 | 0 | 0 | 0 | 40 | 100 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 25 | 0 | 22 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 164 | 90 | 0 | 0 | 0 | 0 |  | 6748.9 | 2409 | 9157.9 | 3794 | 779 | 1738 | 2035 | 170 | 142 | 397 | 92 | 10.9 | 0 | 104.38
12:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 304 | 331 | 55 | 0 | 430 | 0 | 100 | 81 | 42 | 150 | 0 | 0 | 17 | 96 | 102 | 65 | 100 | 61 | 10 | 33 | 54 | 56 | 55 | 19 | 25 | 9 | 33 | 25 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 14 | 78 | 83 | 43 | 19 | 3 | 0 | 95 | 80 | 360 | 320 | 193 | 68 | 152 | 20 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 20 | 98 | 28 | 64 | 20 | 0.9 | 56 | 60 | 47 | 44 | 100 | 317 | 62 | 82 | 43 | 76 | 18 | 42 | 9 | 280 | 24 | 11 | 0 | 190 | 0 | 0 | 163 | 0 | 108 | 16.2 |  | 779 | 0 | 330 | 27 | 83 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 112 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 8 | 0 | 22 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 175 | 0 | 0 | 163 | 90 | 0 | 0 | 0 | 0 |  | 7041.1 | 2399 | 9440.1 | 4059 | 779 | 1732 | 2048 | 170 | 142 | 395 | 98 | 17.1 | 0 | 104.38
13:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 334 | 310 | 50 | 0 | 420 | 0 | 100 | 81 | 42 | 195 | 0 | 0 | 17 | 95 | 102 | 65 | 90 | 54 | 10 | 36 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 25 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 14 | 78 | 83 | 43 | 19 | 6 | 0 | 100 | 100 | 360 | 300 | 215 | 68 | 153 | 38 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 20 | 96 | 10 | 64 | 20 | 1.6 | 56 | 60 | 47 | 44 | 163 | 304 | 61 | 84 | 43 | 76 | 18 | 42 | 9 | 270 | 8 | 11 | 0 | 188 | 0 | 0 | 170 | 0 | 108 | 17.3 |  | 779 | 0 | 410 | 27 | 98 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 10 | 0 | 18 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 188 | 0 | 0 | 181 | 92 | 0 | 0 | 0 | 0 |  | 7139.9 | 2498 | 9637.9 | 4239 | 779 | 1757 | 2048 | 170 | 142 | 388 | 96 | 18.9 | 0 | 104.39
14:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 325 | 295 | 61 | 0 | 410 | 0 | 100 | 80 | 40 | 195 | 0 | 0 | 20 | 94 | 102 | 82 | 85 | 64 | 49 | 36 | 54 | 55 | 17 | 19 | 25 | 23 | 33 | 33 | 33 | 0 | 108 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 16 | 14 | 90 | 83 | 42 | 19 | 7 | 0 | 150 | 100 | 360 | 300 | 215 | 68 | 153 | 42 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 20 | 96 | 10 | 74 | 20 | 1.9 | 55 | 60 | 47 | 49 | 163 | 302 | 60 | 84 | 43 | 128 | 18 | 42 | 9 | 270 | 8 | 11 | 30 | 188 | 32 | 30 | 170 | 30 | 108 | 15.6 |  | 779 | 0 | 410 | 86 | 97 | 120 | 0 | 0 | 0 | 0 | 32 | 120 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 44 | 0 | 18 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 147 | 90 | 30 | 0 | 0 | 0 |  | 7399.5 | 2573 | 9972.5 | 4342 | 779 | 1731 | 2320 | 170 | 138 | 379 | 96 | 17.5 | 0 | 104.39
15:00 | 74 | 0 | 0 | 120 | 366 | 11 | 0 | 315 | 296 | 70 | 0 | 400 | 0 | 100 | 80 | 42 | 194 | 0 | 0 | 60 | 94 | 102 | 117 | 90 | 69 | 49 | 35 | 54 | 55 | 40 | 19 | 25 | 25 | 33 | 33 | 33 | 0 | 107 | 30 | 130 | 0 | 16 | 51 | 0 | 135 | 0 | 0 | 32 | 46 | 27 | 90 | 82 | 38 | 19 | 2 | 0 | 150 | 100 | 360 | 320 | 215 | 68 | 152 | 42 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 20 | 98 | 29 | 88 | 20 | 1.4 | 55 | 58 | 44 | 49 | 163 | 310 | 61 | 84 | 43 | 130 | 18 | 41 | 9 | 300 | 24 | 11 | 100 | 188 | 33 | 88 | 170 | 97 | 108 | 11.5 |  | 779 | 0 | 410 | 86 | 96 | 120 | 0 | 0 | 0 | 0 | 40 | 60 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 52 | 0 | 18 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 139 | 91 | 30 | 0 | 0 | 0 |  | 7829.9 | 2520 | 10349.9 | 4341 | 779 | 1748 | 2615 | 170 | 137 | 449 | 98 | 12.9 | 0 | 104.39
16:00 | 74 | 0 | 0 | 120 | 365 | 11 | 0 | 300 | 285 | 74 | 0 | 360 | 0 | 100 | 81 | 42 | 195 | 0 | 0 | 80 | 94 | 102 | 117 | 90 | 69 | 48 | 35 | 54 | 55 | 48 | 19 | 25 | 25 | 33 | 33 | 36 | 0 | 107 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 32 | 64 | 26 | 90 | 82 | 38 | 19 | 6 | 0 | 150 | 100 | 360 | 301 | 191 | 68 | 151 | 42 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 16 | 0 | 70 | 43 | 88 | 17 | 0.8 | 59 | 59 | 41 | 43 | 130 | 317 | 56 | 84 | 44 | 115 | 18 | 41 | 9 | 280 | 23 | 11 | 100 | 175 | 0 | 52 | 170 | 67 | 108 | 7 |  | 779 | 0 | 410 | 88 | 96 | 120 | 0 | 0 | 0 | 3 | 40 | 50 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 52 | 0 | 22 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 0 | 131 | 92 | 0 | 0 | 0 | 0 |  | 7524.8 | 2482 | 10006.8 | 4219 | 779 | 1643 | 2520 | 170 | 137 | 461 | 70 | 7.8 | 0 | 104.39
17:00 | 74 | 0 | 0 | 120 | 300 | 11 | 0 | 285 | 266 | 95 | 0 | 330 | 0 | 70 | 81 | 42 | 196 | 0 | 0 | 100 | 50 | 48 | 117 | 50 | 69 | 10 | 30 | 54 | 55 | 54 | 19 | 25 | 25 | 33 | 33 | 40 | 0 | 111 | 30 | 130 | 0 | 16 | 49 | 0 | 125 | 0 | 0 | 32 | 72 | 39 | 90 | 82 | 36 | 19 | 7 | 0 | 150 | 100 | 360 | 301 | 191 | 68 | 150 | 42 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 0 | 88 | 43 | 87 | 21 | 0.3 | 59 | 59 | 42 | 46 | 130 | 303 | 41 | 84 | 10 | 110 | 18 | 42 | 9 | 270 | 23 | 11 | 10 | 185 | 0 | 0 | 170 | 0 | 108 | 1 |  | 779 | 0 | 380 | 88 | 96 | 120 | 0 | 0 | 8 | 18 | 40 | 50 | 26 | 110 | 0 | 0 | 0 | 0 | 5 | 0 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 170 | 0 | 18 | 176 | 0 | 0 | 141 | 93 | 0 | 0 | 0 | 0 |  | 7017.3 | 2503 | 9520.3 | 4094 | 779 | 1561 | 2148 | 170 | 141 | 538 | 88 | 1.3 | 0 | 104.39
18:00 | 74 | 0 | 0 | 120 | 300 | 11 | 0 | 300 | 261 | 97 | 0 | 310 | 0 | 72 | 80 | 42 | 170 | 0 | 0 | 100 | 52 | 48 | 117 | 40 | 69 | 45 | 20 | 54 | 55 | 54 | 19 | 25 | 25 | 33 | 33 | 40 | 0 | 111 | 30 | 130 | 0 | 16 | 65 | 0 | 125 | 0 | 0 | 32 | 72 | 40 | 90 | 89 | 33 | 19 | 11 | 0 | 120 | 100 | 360 | 301 | 202 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 8 | 21 | 8 | 33 | 20 | 98 | 50 | 87 | 20 | 0 | 59 | 59 | 47 | 50 | 163 | 300 | 58 | 30 | 10 | 100 | 18 | 42 | 9 | 265 | 23 | 11 | 10 | 190 | 11 | 10 | 170 | 81 | 108 | 0 |  | 769 | 0 | 380 | 88 | 96 | 140 | 0 | 0 | 20 | 25 | 40 | 65 | 28 | 96 | 0 | 0 | 0 | 40 | 50 | 50 | 50 | 50 | 16 | 52 | 27 | 21 | 10 | 11 | 0 | 0 | 170 | 15 | 18 | 175 | 0 | 0 | 133 | 97 | 10 | 0 | 0 | 0 |  | 7135 | 2742 | 9877 | 4074 | 769 | 1528 | 2285 | 170 | 141 | 812 | 98 | 0 | 0 | 104.39
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 300 | 245 | 103 | 0 | 290 | 0 | 96 | 80 | 42 | 175 | 0 | 0 | 100 | 90 | 102 | 133 | 100 | 69 | 49 | 24 | 54 | 55 | 54 | 0 | 25 | 25 | 33 | 33 | 41 | 0 | 120 | 30 | 130 | 0 | 16 | 107 | 0 | 135 | 0 | 0 | 40 | 80 | 44 | 90 | 90 | 38 | 19 | 7 | 0 | 120 | 100 | 360 | 301 | 204 | 68 | 101 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 0 | 144 | 29 | 87 | 0 | 0 | 60 | 60 | 47 | 50 | 163 | 302 | 40 | 86 | 46 | 127 | 18 | 43 | 9 | 275 | 23 | 11 | 200 | 238 | 202 | 95 | 174 | 100 | 108 | 0 |  | 768 | 0 | 410 | 89 | 99 | 205 | 0 | 0 | 36 | 50 | 40 | 111 | 38 | 110 | 24 | 0 | 0 | 50 | 50 | 102 | 50 | 50 | 21 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 170 | 10 | 18 | 214 | 0 | 0 | 220 | 97 | 93 | 0 | 0 | 0 |  | 8075 | 3253 | 11328 | 4248 | 768 | 1603 | 3120 | 170 | 150 | 1125 | 144 | 0 | 0 | 104.37
19:30 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 320 | 248 | 103 | 0 | 290 | 0 | 100 | 81 | 42 | 150 | 0 | 0 | 100 | 90 | 102 | 133 | 100 | 70 | 50 | 24 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 33 | 41 | 0 | 120 | 30 | 130 | 0 | 16 | 139 | 0 | 135 | 0 | 0 | 32 | 72 | 44 | 90 | 91 | 38 | 19 | 12 | 0 | 120 | 100 | 360 | 301 | 210 | 68 | 98 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 0 | 128 | 20 | 87 | 0 | 0 | 58 | 60 | 47 | 47 | 100 | 300 | 58 | 86 | 46 | 100 | 18 | 43 | 9 | 290 | 21 | 11 | 200 | 238 | 200 | 96 | 174 | 100 | 108 | 0 |  | 769 | 0 | 410 | 89 | 99 | 237 | 0 | 0 | 41 | 50 | 40 | 110 | 35 | 110 | 24 | 0 | 0 | 50 | 50 | 102 | 50 | 50 | 23 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 169 | 10 | 18 | 216 | 0 | 0 | 220 | 97 | 94 | 0 | 0 | 0 |  | 8014 | 3291 | 11305 | 4255 | 769 | 1557 | 3121 | 169 | 150 | 1156 | 128 | 0 | 0 | 104.37
20:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 330 | 241 | 103 | 0 | 260 | 0 | 100 | 81 | 55 | 150 | 0 | 0 | 100 | 97 | 102 | 133 | 100 | 70 | 51 | 26 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 120 | 30 | 130 | 0 | 16 | 192 | 0 | 135 | 0 | 0 | 40 | 72 | 44 | 90 | 90 | 34 | 19 | 15 | 0 | 120 | 100 | 360 | 301 | 209 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 0 | 0 | 33 | 18 | 150 | 65 | 87 | 22 | 0 | 58 | 60 | 47 | 47 | 100 | 301 | 56 | 86 | 46 | 100 | 18 | 44 | 9 | 270 | 21 | 11 | 200 | 260 | 73 | 97 | 178 | 100 | 108 | 0 |  | 769 | 0 | 410 | 88 | 99 | 241 | 0 | 0 | 41 | 55 | 40 | 118 | 38 | 110 | 24 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 32 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 170 | 9 | 18 | 215 | 0 | 0 | 220 | 97 | 94 | 0 | 0 | 0 |  | 8046 | 3317 | 11363 | 4399 | 769 | 1507 | 3046 | 170 | 150 | 1172 | 150 | 0 | 0 | 104.37
21:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 336 | 238 | 103 | 0 | 240 | 0 | 100 | 81 | 55 | 150 | 0 | 0 | 100 | 97 | 102 | 133 | 100 | 70 | 51 | 25 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 119 | 30 | 130 | 0 | 16 | 211 | 0 | 135 | 0 | 0 | 32 | 72 | 35 | 90 | 94 | 35 | 19 | 24 | 0 | 120 | 100 | 360 | 301 | 209 | 68 | 98 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 21 | 8 | 33 | 21 | 160 | 60 | 88 | 22 | 0 | 57 | 60 | 47 | 47 | 100 | 300 | 65 | 86 | 46 | 70 | 18 | 45 | 9 | 265 | 23 | 11 | 120 | 268 | 0 | 99 | 185 | 100 | 108 | 0 |  | 769 | 0 | 410 | 93 | 115 | 241 | 0 | 0 | 41 | 78 | 40 | 110 | 39 | 110 | 26 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 170 | 9 | 18 | 214 | 0 | 0 | 220 | 97 | 94 | 0 | 0 | 0 |  | 7918 | 3351 | 11269 | 4419 | 769 | 1490 | 2928 | 170 | 149 | 1184 | 160 | 0 | 0 | 104.36
22:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 329 | 222 | 103 | 0 | 215 | 0 | 100 | 80 | 55 | 122 | 0 | 0 | 100 | 98 | 102 | 133 | 100 | 71 | 0 | 27 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 116 | 30 | 130 | 0 | 16 | 209 | 0 | 135 | 0 | 0 | 32 | 72 | 35 | 90 | 97 | 27 | 19 | 23 | 0 | 120 | 100 | 360 | 305 | 213 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 186 | 100 | 87 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 324 | 65 | 85 | 46 | 70 | 18 | 44 | 9 | 300 | 23 | 11 | 0 | 260 | 0 | 51 | 185 | 101 | 108 | 0 |  | 769 | 0 | 410 | 82 | 115 | 241 | 0 | 0 | 41 | 68 | 40 | 120 | 39 | 110 | 26 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 170 | 10 | 18 | 214 | 0 | 0 | 220 | 97 | 94 | 0 | 0 | 0 |  | 7770 | 3341 | 11111 | 4466 | 769 | 1511 | 2688 | 170 | 146 | 1175 | 186 | 0 | 0 | 104.48
23:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 337 | 233 | 103 | 0 | 215 | 0 | 100 | 80 | 55 | 120 | 0 | 0 | 100 | 98 | 102 | 133 | 100 | 71 | 49 | 32 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 116 | 30 | 130 | 0 | 16 | 210 | 0 | 135 | 0 | 0 | 32 | 63 | 33 | 90 | 95 | 30 | 19 | 12 | 0 | 120 | 90 | 360 | 334 | 203 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 188 | 98 | 87 | 22 | 0 | 56 | 60 | 47 | 50 | 130 | 312 | 65 | 86 | 46 | 70 | 19 | 44 | 9 | 290 | 23 | 11 | 135 | 255 | 38 | 95 | 185 | 99 | 108 | 0 |  | 769 | 0 | 410 | 88 | 115 | 240 | 0 | 0 | 39 | 72 | 40 | 120 | 37 | 110 | 14 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 10 | 18 | 204 | 0 | 0 | 205 | 97 | 94 | 0 | 0 | 0 |  | 8023 | 3308 | 11331 | 4459 | 769 | 1503 | 2959 | 169 | 146 | 1138 | 188 | 0 | 0 | 104.48
24:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 350 | 253 | 103 | 0 | 230 | 0 | 100 | 81 | 55 | 120 | 0 | 0 | 100 | 98 | 102 | 133 | 100 | 0 | 50 | 32 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 108 | 30 | 130 | 0 | 16 | 212 | 0 | 135 | 0 | 0 | 32 | 63 | 32 | 90 | 99 | 44 | 19 | 16 | 0 | 120 | 90 | 360 | 301 | 180 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 180 | 100 | 87 | 22 | 0 | 59 | 60 | 47 | 50 | 100 | 300 | 63 | 86 | 46 | 70 | 19 | 44 | 9 | 290 | 23 | 11 | 150 | 265 | 108 | 95 | 185 | 101 | 108 | 0 |  | 769 | 0 | 340 | 82 | 115 | 243 | 0 | 0 | 39 | 67 | 40 | 110 | 37 | 98 | 14 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 10 | 18 | 184 | 0 | 0 | 171 | 96 | 94 | 0 | 0 | 0 |  | 8011 | 3153 | 11164 | 4309 | 769 | 1511 | 2987 | 169 | 138 | 1101 | 180 | 0 | 0 | 104.48
KWH | 1689000 | 0 | 0 | 2835000 | 8661290 | 291681 | 0 | 6097570 | 7307000 | 1402800 | 0 | 8274812 | 0 | 2199360 | 1830120 | 1078597 | 4424365 | 0 | 0 | 1246080 | 2153280 | 2053584 | 2241120 | 2056920 | 1359360 | 612150 | 751104 | 1185480 | 1282136 | 1180517 | 364896 | 600000 | 525420 | 754800 | 788100 | 836112 | 0 | 2601138 | 724400 | 3000000 | 0 | 340380 | 2604473 | 0 | 3120355 | 0 | 0 | 918240 | 979600 | 715941 | 2076480 | 2087040 | 973440 | 454704 | 364320 | 0 | 2691400 | 2324176 | 8921500 | 7470000 | 4660000 | 1656000 | 3265460 | 868032 | 153120 | 120000 | 0 | 1830120 | 422040 | 71040 | 490284 | 185400 | 777200 | 446800 | 3076800 | 1097060 | 1788480 | 426204 | 14800 | 1339000 | 1440000 | 1132200 | 1109000 | 3486256 | 7002759 | 1341000 | 1911360 | 991080 | 2495440 | 444000 | 1038720 | 214200 | 7452950 | 436920 | 264000 | 936840 | 4684470 | 508497 | 666124 | 3852000 | 890150 | 2414880 | 116000 |  | 18749090 | 0 | 9785376 | 1510560 | 2157120 | 3927360 | 0 | 0 | 396000 | 597120 | 925500 | 2543000 | 693998 | 2640000 | 166869 | 0 | 0 | 426432 | 445529 | 1222792 | 1064360 | 1161984 | 275049 | 1088160 | 329490 | 500160 | 229752 | 249156 | 0 | 0 | 4143600 | 97000 | 218000 | 4869109 | 0 | 0 | 3807881 | 2269005 | 736320 | 0 | 0 | 0 |  | 175966927 | 67225772 | 243192699 | 101753249 | 18749090 | 41025734 | 54719665 | 4143600 | 3325538 | 16268223 | 3076800 | 130800 | 0
Fuel Cost | 1452540 | 0 | 0 | 2438100 | 5543225.6 | 236261.61 | 0 | 3719517.7 | 4457270 | 13480908 | 0 | 5544124.04 | 0 | 13811980.8 | 12225201.6 | 6590227.67 | 2875837.25 | 0 | 0 | 19389004.8 | 13458000 | 13533118.56 | 21671630.4 | 13102580.4 | 8142566.4 | 9788278.5 | 5009863.68 | 8452472.4 | 8013350 | 7401841.59 | 273672 | 450000 | 0 | 0 | 0 | 7909619.52 | 0 | 0 | 0 | 3300000 | 0 | 3223398.6 | 1718952.18 | 0 | 3588408.25 | 0 | 0 | 8071329.6 | 10550292 | 6966105.93 | 12853411.2 | 13482278.4 | 6366297.6 | 386498.4 | 0 | 0 | 2449174 | 2115000.16 | 5531330 | 5154300 | 3262000 | 1142640 | 3134841.6 | 581581.44 | 131683.2 | 110400 | 0 | 1738614 | 4574913.6 | 527116.8 | 377518.68 | 139050 | 598444 | 335100 | 21045312 | 822795 | 16436131.2 | 328177.08 | 0 | 1392560 | 1497600 | 1086912 | 998100 | 2719279.68 | 4901931.3 | 1528740 | 2045155.2 | 1090188 | 2844801.6 | 568320 | 966009.6 | 199206 | 4769888 | 327690 | 200640 | 16235437.2 | 34009252.2 | 8812253.01 | 11357414.2 | 27541800 | 15177057.5 | 0 | 0 |  | 95620359 | 0 | 6556201.92 | 12099585.6 | 17882524.8 | 63151948.8 | 0 | 0 | 4458960 | 7034073.6 | 7292940 | 1754670 | 687058.02 | 19536000 | 5620147.92 | 0 | 0 | 4882646.4 | 4776070.88 | 10956216.32 | 9206714 | 10341657.6 | 2929271.85 | 10794547.2 | 3878097.3 | 550176 | 215966.88 | 188611.092 | 0 | 0 | 15994296 | 3126310 | 5835860 | 3310994.12 | 0 | 0 | 55823535.46 | 0 | 12760425.6 | 0 | 0 | 0 |  | 490284522.93 | 397265866.362 | 887550389.292 | 75648823.372 | 95620359 | 28688932.23 | 434316586.23 | 15994296 | 0 | 216236080.46 | 21045312 | 0 | 0
Yesterday Day Peak | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 304 | 331 | 55 | 0 | 430 | 0 | 100 | 81 | 42 | 150 | 0 | 0 | 17 | 96 | 102 | 65 | 100 | 61 | 10 | 33 | 54 | 56 | 55 | 19 | 25 | 9 | 33 | 25 | 33 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 14 | 78 | 83 | 43 | 19 | 3 | 0 | 95 | 80 | 360 | 320 | 193 | 68 | 152 | 20 | 5 | 5 | 0 | 85 | 0 | 8 | 21 | 8 | 33 | 20 | 98 | 28 | 64 | 20 | 0.9 | 56 | 60 | 47 | 44 | 100 | 317 | 62 | 82 | 43 | 76 | 18 | 42 | 9 | 280 | 24 | 11 | 0 | 190 | 0 | 0 | 163 | 0 | 108 | 16.2 |  | 779 | 0 | 330 | 27 | 83 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 112 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 50 | 0 | 8 | 0 | 22 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 175 | 0 | 0 | 163 | 90 | 0 | 0 | 0 | 0 |  | 9440.1 | DayPeak
Yesterday Evening Peak | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 330 | 241 | 103 | 0 | 260 | 0 | 100 | 81 | 55 | 150 | 0 | 0 | 100 | 97 | 102 | 133 | 100 | 70 | 51 | 26 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 120 | 30 | 130 | 0 | 16 | 192 | 0 | 135 | 0 | 0 | 40 | 72 | 44 | 90 | 90 | 34 | 19 | 15 | 0 | 120 | 100 | 360 | 301 | 209 | 68 | 100 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 0 | 0 | 33 | 18 | 150 | 65 | 87 | 22 | 0 | 58 | 60 | 47 | 47 | 100 | 301 | 56 | 86 | 46 | 100 | 18 | 44 | 9 | 270 | 21 | 11 | 200 | 260 | 73 | 97 | 178 | 100 | 108 | 0 |  | 769 | 0 | 410 | 88 | 99 | 241 | 0 | 0 | 41 | 55 | 40 | 118 | 38 | 110 | 24 | 0 | 0 | 50 | 49 | 102 | 50 | 50 | 32 | 52 | 33 | 22 | 10 | 11 | 0 | 0 | 170 | 9 | 18 | 215 | 0 | 0 | 220 | 97 | 94 | 0 | 0 | 0 |  | 11363 | EvPeak
Forecast for Evening | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 412 | 350 | 105 | 0 | 225 | 305 | 100 | 81 | 55 | 0 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 71 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 114 | 30 | 130 | 0 | 16 | 215 | 0 | 135 | 0 | 0 | 40 | 70 | 45 | 90 | 92 | 45 | 19 | 15 | 0 | 120 | 100 | 360 | 360 | 225 | 68 | 100 | 40 | 5 | 5 | 0 | 85 | 50 | 52 | 22 | 8 | 33 | 21 | 175 | 65 | 88 | 22 | 0 | 58 | 60 | 47 | 47 | 163 | 330 | 66 | 86 | 45 | 130 | 20 | 44 | 9 | 341 | 21 | 11 | 200 | 260 | 300 | 100 | 185 | 100 | 110 |  |  | 781 | 48 | 410 | 100 | 115 | 225 | 0 | 0 | 42 | 85 | 40 | 120 | 33 | 110 | 26 | 0 | 0 | 50 | 48 | 102 | 40 | 50 | 38 | 52 | 35 | 22 | 10 | 11 | 0 | 0 | 170 | 17 | 18 | 220 | 0 | 0 | 220 | 95 | 94 | 0
Forecast for Day | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 350 | 350 | 98 | 0 | 225 | 0 | 100 | 81 | 55 | 0 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 71 | 50 | 35 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 114 | 30 | 130 | 0 | 16 | 215 | 0 | 135 | 0 | 0 | 40 | 70 | 45 | 90 | 92 | 45 | 19 | 10 | 0 | 130 | 100 | 360 | 360 | 225 | 68 | 100 | 40 | 5 | 5 | 0 | 85 | 0 | 52 | 22 | 8 | 33 | 21 | 129 | 65 | 88 | 22 | 2 | 58 | 60 | 47 | 47 | 163 | 330 | 66 | 86 | 45 | 130 | 20 | 44 | 9 | 341 | 21 | 11 | 130 | 210 | 200 | 100 | 180 | 100 | 110 |  |  | 781 | 0 | 410 | 100 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 120 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 170 |  | 0 | 220 | 0 | 0 | 220 | 95 | 94 | 0
Generation at 08:00(Today) | 74 | 0 | 0 | 120 | 270 | 0 | 0 | 320 | 351 | 0 | 0 | 225 | 0 | 100 | 81 | 55 | 120 | 0 | 0 | 0 | 97 | 50 | 48 | 50 | 70 | 20 | 27 | 54 | 55 | 55 | 16 | 25 | 24 | 33 | 17 | 32 | 0 | 114 | 30 | 130 | 0 | 16 | 213 | 0 | 100 | 0 | 0 | 32 | 8 | 16 | 90 | 92 | 43 | 19 | 3 | 0 | 130 | 90 | 360 | 272 | 181 | 68 | 50 | 39 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 126 | 103 | 8 | 22 | 1 | 56 | 60 | 44 | 47 | 100 | 302 | 54 | 86 | 45 | 70 | 20 | 43 | 9 | 270 | 21 | 11 | 0 | 213 | 0 | 0 | 130 | 0 | 109 | 5.2 | 0 | 427 | 0 | 330 | 30 | 49 | 140 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 97 | 0 | 0 | 0 | 0 | 0 | 24 | 50 | 50 | 0 | 25 | 0 | 22 | 9 | 8 | 0 | 0 | 169 | 0 | 0 | 181 | 0 | 0 | 170 | 97 | 0 | 0 | 0 | 0 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [65 empty] | 199
| Minimum Generation |  | 8753.2 | 8:00
| Highest Generation |  | 11363 | 20:00
| Day Peak Generation |  | 9440.1 | 12:00
| Evening Peak Generation |  | 11363 | 20:00
| HVDC Max Flow |  | 780 | 4:00
| HVDC EvPeak Flow |  | 769 | 20:00
| Load factor L.F |  | 89.18%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-09-19
Till now the maximum generation is : - |  |  | 11534 | 19:00 | Hrs on | 2018-09-17
The Summary of Yesterday's |  | 2018-09-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9440.1 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8905.2 | MW
Evening Peak Generation : |  | 11363 | MW Hour : | 20:00 | Available Max Generation : |  | 12459 | MW
E.P. Demand (at gen end) : |  | 11363 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11363 | MW Hour : | 20:00 | Reserve(Generation end) |  | 959 | MW
Total Gen. (MKWH) : |  | 243.1927 | System Load Factor : | 89.18% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -490 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-09-19
Actual : | 104.29 | Ft.(MSL) , | Rule curve : | 103.14 | Ft.( MSL )
Gas Consumed : | Total = | 1187.53 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104337755.602
|  | Coal : | 15994296 | Oil : | 650552666.69 | Total : | 770884718.292
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4045.181 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1376.2904 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1233.2362 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1114.3775 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1007.0223 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 812.6331 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 453.4773 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 209.2072 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 626.7473 |  |  | 0 | 0%
Total | 0 |  | 10878.1723 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Siddhirganj 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Kaptai #5
|  |  |  | 3) Ghorasal Unit-3,4 |  | 12)Meghnaghat CCPP 450 MW GT 2
|  |  |  | 4) Baghabari 100 MW |  | 13)Siddhirganj CCPP-335 MW
5) Tongi GT
6) Chittagong Unit-2
7) Baghabari-71 MW
8) Ashuganj Unit-3
9) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bheramara HVDC-Khulna(S) 230 kV Ckt-2 was shut down at 10:11 for D/W.
b) Comilla(S) 132/33 kV T3 transformer was under shut down from 10:21 to 20:50 due to gas
pressure low of 33 kV breaker.
c) Manikganj 132/33 kV T3 transformer was under shut down from 10:26 to 11:12 for red hot
maintenance at 33 kV Y-phase isolator.
d) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 11:12 from both ends showing gen trip, Dist Z1 3-phase at
Ashuganj end & gen trip,Dist Z1 3-phase & Auto reclosure operated at Sirajganj end and was switched on at 11:42.
e) Sikalbaha 225 MW ST was synchronized at 14:14.
f) Bhola CCPP 225 MW GT-1 tripped at 14:21 due to bearing # 3 radial shaft displacement and was synchronized at 17:52.
g) Chandpur 225 MW CCPP ST tripped at 18:10 due to winding temperature high.
h) Tangail 132/33 kV T1,T2 & T3 transformers tripped at 18:47 showing O/C relay and were switched on at 19:05. |  |  |  | About 169 MW Power interruption occurred under Tangail S/S
area from 18:47 to 19:05.
i) Feni 132/33 kV T1 & T2 transformers tripped at 19:57 showing O/C and were switched on at 20:04 |  |  |  | About 130 MW Power interruption occurred under Feni S/S
& 20:08 respectively. |  |  |  | area from 19:57 to 20:04.
j) Satkhira 132/33 kV T1 & T2 transformers tripped at 21:15 due to 33 kV Satkhira feeder fault and were switched |  |  |  | About 94 MW Power interruption occurred under Satkhira S/S
on at 21:20. |  |  |  | area from 21:15 to 21:20.
k) Jamalpur 132/33 kV T2 transformer tripped at 20:53 showing L/O due to 33 kV feeder fault and was switched |  |  |  | About 48 MW Power interruption occurred under Jamalpur S/S
on at 21:10. |  |  |  | area from 20:53 to 21:10.
l) Aminbazar-Kallayanpur 132 kV Ckt-1,2 tripped at 23:20 from Kallyanpur end due to CVT fire of 132 kV main |  |  |  | About 132 MW Power interruption occurred under Kallyanpur S/S
bus and were switched on at 23:50. |  |  |  | area from 23:20 to 23:50.
m) Barisal 132/33 kV T2 (New) transformer was switched on at 23:40.
n) Meghnaghat 450 MW GT-2 was shut down at 00:13(19/09/2018) for maintenance.
o) Ghorasal P/S - Ghorasal Regent 230 kV Ckt was shut down at 03:20 (19/09/2018) due to sparking.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-09-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 74 | 1689000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2835000 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8661290
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 291681 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 6097570 | Gas shortage
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 103 | 1402800
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 241 | 7307000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 260 | 8274812 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2199360
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 81 | 1830120 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1078597
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 2056920
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 364896
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 1246080
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 97 | 2153280
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 150 | 4424365
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 612150
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 2053584
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 26 | 751104 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1185480
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 2241120 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1282136
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1180517
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 70 | 1359360 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1125420 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 754800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 788100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 41 | 836112 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 260 | 4684470 | Engine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 73 | 508497 | Low demand
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 97 | 666124
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 890150
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 108 | 2414880 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3548 | 75246775
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 130 | 3000000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 340380 | Engine problem
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 116000
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 34 | 973440 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 150 | 3325538 | unit # 05 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 192 | 2604473 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 3120355
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 918240 | Engine problem
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 72 | 979600
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 44 | 715941
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2076480 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 454704
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 364320
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 90 | 2087040 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 1027 | 21076511
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2691400 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2324176 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 209 | 4660000
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8921500
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 301 | 7470000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 868032 | Gas shortage
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 153120 | Gas shortage
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 1656000 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Development work
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1830120
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 422040
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 3265460
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 490284 | tripped at 19:55.
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 185400 | tripped at 19:55.
** | Tripura |  | Imported power | 0 | 160 | 150 | 3076800
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 777200
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 71040 | Line over load
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 446800
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 200 | 936840
| Comilla Area Total |  |  |  | 2541 | 1845 | 40366212
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 65 | 1097060 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 426204
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 87 | 1788480 | Engine problem
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14800
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 178 | 3852000 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 352 | 7178544
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1339000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1440000
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3486256
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 301 | 7002759 | FGMO.
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 47 | 1132200
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 1109000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 56 | 1341000 | Frequency control.
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1911360
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 991080
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 100 | 2495440
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 18 | 444000
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 44 | 1038720
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 21 | 436920 | Engine problem
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 270 | 7452950 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 214200
| Sylhet Area Total |  |  |  | 1549 | 1274 | 32098885
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 769 | 18749090
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 88 | 1510560 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2157120 | Engine problem
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 41 | 396000
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 241 | 3927360
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 55 | 597120
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9785376
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 925500
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 94 | 736320 | Engine problem
| Khulna Area Total |  |  |  | 2214 | 1837 | 38784446
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2640000
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 24 | 166869
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 38 | 693998
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 118 | 2543000
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2269005
| Barisal Area Total |  |  |  | 462 | 387 | 8312872
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 426432
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 49 | 445529
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1064360
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 1161984
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 32 | 275049
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 215 | 4869109 | FGMO
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 0
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | On test
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 33 | 329490
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 500160
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 229752 | Engine problem
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249156
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 1088160
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1222792
| Rajshahi Area Total |  |  |  | 1264 | 896 | 11861973
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 170 | 4143600 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 9 | 97000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 218000
| Rangpur Area Total |  |  |  | 484 | 197 | 4458600
| Total |  |  |  | 16445 | 11363 | 239384818
| Eastern Grid Total |  |  |  | 12021 | 8046 | 175966927
| Western Grid Total |  |  |  | 4424 | 3317 | 63417891
| National Grid Total |  |  |  | 16445 | 11363 | 239384818
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-09-18 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7273 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3463 | MW
i) Dhaka area |  |  | 4096 | MW | i) Khulna area |  |  | 1369 | MW
ii) Chittagong area |  |  | 1034 | MW | ii) Rajshahi area |  |  | 1223 | MW
iii) Comilla area |  |  | 924 | MW | iii) Barisal area |  |  | 299 | MW
iv) Mymensingh area |  |  | 742 | MW | iv) Rangpur area |  |  | 572 | MW
v) Sylhet area |  |  | 477 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10736 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 138 | 1500 | Netrokona | 87 | 2100 | Central s/s | 81 | 2200
Munsiganj | 116 | 2000 | Jamalpur | 123 | 1830 | Noapara | 95 | 1900
Sonargaon | 45 | 2100 | Sherpur | 80 | 100 | Jessore | 154 | 1830
Shyampur | 170 | 1100 | Srimongal | 40 | 1900 | Jhenida | 96 | 1830
Bhulta | 190 | 2100 | Shahjibazar | 112 | 2100 | Bottail | 124 | 1930
Madanganj | 58 | 1600 | Fenchuganj | 51 | 1830 | G.K Project | 56 | 1930
Shitalakhya | 114 | 1600 | Kulawara | 44 | 1930 | Faridpur | 160 | 2100
Rahim steel | 10 | 1300 | Sylhet | 151 | 1830 | Madaripur | 129 | 1930
Matuail | 88 | 1200 | Chatak | 29 | 1900 | Gopalganj | 90 | 2100
Ghorasal | 84 | 2100 | Sunamganj | 38 | 2000 | Bagerhat | 85 | 2200
Narsingdi | 124 | 2100 | Biani Bazar | 43 | 1930 | Mongla | 38 | 100
Haripur (SBU) | 99 | 1930 | Comilla (S) | 186 | 2200 | Satkhira | 97 | 1900
Ullon | 98 | 1900 | Comilla(N) | 137 | 1830 | Gallamari | 48 | 1400
Hasnabad | 217 | 2100 | Chandpur | 127 | 2200 | Magura | 49 | 2000
Magbazar | 139 | 1100 | Feni | 137 | 2200 | Chuadanga | 82 | 1900
Maniknagar | 110 | 1500 | Chowmuhani | 204 | 2000 | Barisal | 126 | 1900
Bangabhaban | 44 | 1100 | Ashuganj | 62 | 2300 | Patuakhali | 98 | 2100
Narinda | 88 | 1200 | Daudkandi | 118 | 1930 | Bhandaria | 50 | 2000
Dhanmondi | 145 | 1300 | B.Baria | 143 | 2100 | Ishurdi | 56 | 2100
Lalbag | 97 | 1600 | Ramganj | 38 | 2300 | Ruppur Paromanobik | 2 | 2100
Madartek | 54 | 2100 | Madunaghat | 56.5 | 2000 | Natore | 117 | 2000
Mirpur | 113 | 1830 | Hathazari | 97 | 1830 | Bogra | 252 | 1930
Kalyanpur | 129 | 1830 | Khulshi | 193 | 1600 | Noagaon | 109 | 2000
Gulshan | 162 | 1500 | Halishahar | 141 | 1500 | Rajshahi | 154 | 1930
Uttara | 100 | 1600 | Baraulia | 154 | 100 | C.Nawabganj | 70 | 2100
Uttara(New) | 7 | 1300 | Sikalbaha | 38 | 1830 | Amnura | 43 | 2000
Kamrangirchar | 81 | 1900 | Dohazari | 86 | 1830 | Pabna | 124 | 2000
Savar | 124 | 1900 | Cox'sbazar | 66 | 1800 | Shahjadpur | 92 | 1930
Bhasantec | 177 | 1500 | Chandraghona | 30 | 1800 | Serajganj | 100 | 2000
Agargaon | 54 | 1600 | Kaptai | 4.5 | 1900 | Niyamatpur | 62 | 2000
Satmosjid | 103 | 1900 | A. Khaer Stl. | 12 | 1100 | Joypurhat | 49 | 1900
Tongi | 139 | 2100 | Bakulia | 119 | 2000 | Rangpur | 124 | 2000
Kabirpur | 208 | 1200 | Julda | 22 | 100 | Lalmonirhat | 82 | 100
Basundhara | 130 | 1100 | TK chemical | 5.3 | 1000 | Saidpur | 100 | 100
Manikganj | 102 | 2000 | Modern Steel | 17 | 1000 | Purbasadipur | 82 | 100
Joydevpur | 232 | 1600 | Shahmirpur | 28.5 | 1930 | Thakurgaon | 56 | 1830
New Tongi | 104 | 900 | Khagrachhari | 20 | 1830 | Palashbari | 100 | 100
Korda | 269 | 1800 | Matarbari | 21 | 100 | Barapukuria | 49 | 1900
Dhamrai | 52 | 2100 | Baroiar Hat | 11 | 1830 | Panchagar | 38 | 2100
Tangail | 169 | 1830 | Abul Khair 230 | 171 | 1500
Mymensing | 251 | 2200 | BSRM | 117 | 500
Kishorganj | 104 | 1900 | Goalpara | 39 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-09-18
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 388 | 8:00 | 381 | 15:00 | Kaliakoir | 368 | 24:00 | 357 | 13:00
Bheramara | 400 | 7:00 | 390 | 19:30 | Bhulta | 382 | 20:00 | 371 | 12:00
Ashuganj(N) | 389 | 4:00 | 381 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 218 | 8:00 | 210 | 15:00
Ishurdi | 235 | 7:00 | 224 | 20:00 | Megnaghat | 226 | 4:00 | 219 | 15:00
Ashuganj | 235 | 4:00 | 230 | 9:00 | Fenchuganj | 236 | 8:00 | 230 | 13:00
Serajganj | 225 | 17:00 | 216 | 19:30 | Siddhirganj | 224 | 1:00 | 216 | 15:00
Baghabari | 226 | 17:00 | 215 | 20:00 | Maniknagar | 222 | 1:00 | 215 | 15:00
Barapukuria | 230 | 17:00 | 218 | 21:00 | Old Airport | 222 | 4:00 | 212 | 12:00
Bogra | 220 | 18:00 | 202 | 21:00 | Barisal | 216 | 12:00 | 211 | 20:00
Khulna South | 234 | 8:00 | 223 | 18:30 | AKSML | 220 | 10:00 | 205 | 15:00
Rampura | 221 | 1:00 | 216 | 12:00 | BSRM | 219 | 6:00 | 208 | 15:00
Haripur | 222 | 23:00 | 216 | 12:00 | Bibiyana | 232 | 8:00 | 229 | 1:00
Hasnabad | 222 | 3:00 | 215 | 10:00 | Bhulta | 224 | 3:00 | 216 | 11:00
Aminbazar | 223 | 3:00 | 213 | 14:00 | Ashuganj (S) | 232 | 6:00 | 228 | 13:00
Tongi | 221 | 24:00 | 211 | 15:00 | Kaliakoir | 226 | 24:00 | 218 | 16:00
Comilla (N) | 230 | 4:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 130 | 900 | Ramganj | 122 | 900 | 112 | 2300
Munsiganj | 135 | 1800 | 132 | 500 | Madanhat | 130 | 100 | 124 | 1600
Megnaghat | 133 | 100 | 128 | 1200 | Hathazari | 129 | 800 | 124 | 1500
Shyampur | 133 | 100 | 124 | 900 | Khulshi | 126 | 400 | 120 | 1400
Bhulta | 130 | 200 | 126 | 1200 | Halishahar | 130 | 2100 | 122 | 1800
Madanganj | 137 | 100 | 130 | 1300 | Baraulia | 128 | 700 | 121 | 1500
Shitalakhya | 137 | 100 | 130 | 900 | Sikalbaha | 129 | 2100 | 122 | 1400
Rahim steal | 134 | 1830 | 130 | 1000 | Dohazari | 129 | 2100 | 122 | 1400
Matuail | 134 | 1900 | 128 | 900 | Cox'sbazar | 123 | 500 | 111 | 1800
Ghorasal | 134 | 100 | 134 | 200 | Chandraghona | 130 | 2100 | 125 | 1400
Narsinghdi | 129 | 1800 | 122 | 900 | Kaptai | 130 | 800 | 127 | 300
Haripur (SBU) | 134 | 100 | 129 | 900 | A. Khaer Stl. | 127 | 700 | 122 | 1400
Ullon | 133 | 400 | 126 | 1300 | Bakulia | 127 | 500 | 121 | 1300
Hasnabad | 135 | 300 | 128 | 1700 | Julda | 129 | 2100 | 122 | 1600
Magbazar | 133 | 300 | 123 | 1100 | TK Chemical | 129 | 100 | 116 | 2400
Maniknagar | 131 | 300 | 125 | 1200 | Modern Steel | 128 | 500 | 121 | 1600
Bangabhaban | 131 | 300 | 125 | 1200 | Shahmirpur | 128 | 2100 | 122 | 1500
Narinda | 131 | 300 | 125 | 1200 | Khagrachhari | 130 | 400 | 123 | 1500
Dhanmondi | 133 | 400 | 126 | 1300 | Matarbari | 125 | 2000 | 116 | 1800
Lalbag | 134 | 400 | 123 | 1200 | Baroiar Hat | 126 | 800 | 118 | 1300
Madartek | 133 | 300 | 126 | 1300 | Goalpara | 137 | 100 | 132 | 1830
Mirpur | 134 | 500 | 126 | 1200 | Central s/s | 137 | 1700 | 132 | 1300
Kalyanpur | 134 | 400 | 128 | 1200 | Noapara | 135 | 1800 | 128 | 1930
Gulshan | 132 | 400 | 125 | 1200 | Jessore | 129 | 1800 | 119 | 1830
Uttara | 130 | 600 | 122 | 1200 | Jhenida | 128 | 700 | 115 | 2000
Uttara(New) | 131 | 500 | 126 | 1200 | Bottail | 135 | 700 | 125 | 1830
Kamrangirchar | 134 | 300 | 127 | 1300 | G.K.Project | 143 | 1800 | 135 | 1930
Savar | 132 | 500 | 125 | 1200 | Faridpur | 135 | 1800 | 123 | 1900
Bhasantec | 134 | 400 | 126 | 1200 | Madaripur | 136 | 1800 | 123 | 2000
Agargaon | 135 | 400 | 127 | 1200 | Gopalganj | 136 | 1800 | 119 | 1830
Satmosjid | 135 | 400 | 127 | 1200 | Bagerhat | 136 | 1800 | 127 | 1930
Tongi | 132 | 800 | 124 | 1600 | Mongla | 131 | 700 | 125 | 1830
Kabirpur | 136 | 1300 | 128 | 1930 | Satkhira | 135 | 1800 | 127 | 1900
Basundhara | 128 | 1200 | 122 | 1600 | Gallamari | 138 | 1800 | 131 | 2000
Manikganj | 132 | 400 | 124 | 1500 | Magura | 128 | 1800 | 112 | 2000
Joydevpur | 140 | 1000 | 130 | 800 | Chuadanga | 124 | 1800 | 108 | 1900
New Tongi | 131 | 400 | 124 | 1400 | Barisal | 140 | 600 | 132 | 1900
Kodda | 138 | 1930 | 130 | 2200 | Patuakhali | 135 | 600 | 125 | 2000
Dhamrai | 133 | 1900 | 128 | 1930 | Bhandaria | 135 | 500 | 127 | 2000
Tangail | 132 | 1800 | 121 | 1930 | Ishurdi | 140 | 600 | 132 | 2000
Mymensing | 127 | 1100 | 110 | 1930 | Ruppur Paromanobik | 141 | 1800 | 133 | 1930
Kishorganj | 126 | 900 | 114 | 1900 | Natore | 137 | 1800 | 125 | 2000
Netrokona | 130 | 1900 | 113 | 1930 | Bogra | 130 | 1800 | 115 | 2100
Jamalpur | 132 | 1000 | 121 | 1830 | Noagaon | 127 | 1800 | 109 | 2100
Sherpur | 132 | 1500 | 116 | 1930 | Rajshahi | 135 | 1800 | 124 | 2100
Srimongal | 136 | 700 | 132 | 1930 | C.Nawabganj | 132 | 1800 | 123 | 1900
Shahjibazar | 136 | 900 | 130 | 1900 | Amnura | 136 | 1800 | 125 | 1900
Fenchuganj | 135 | 600 | 132 | 2000 | Pabna | 132 | 1800 | 124 | 2000
Khulawara | 134 | 100 | 132 | 1500 | Shahjadpur | 138 | 1800 | 130 | 2000
Sylhet | 136 | 1400 | 131 | 1830 | Serajganj | 132 | 1800 | 121 | 2100
Chatak | 133 | 200 | 129 | 1830 | Niyamatpur | 127 | 1800 | 106 | 2000
Sunamganj | 133 | 600 | 127 | 2000 | Joypurhat | 126 | 1800 | 108 | 2100
Biani Bazar | 134 | 700 | 129 | 1830 | Rangpur | 121 | 1800 | 103 | 2100
Comilla(s) | 127 | 600 | 120 | 2200 | Lalmonirhat | 120 | 1700 | 95 | 2100
Comilla(n) | 135 | 700 | 131 | 2200 | Saidpur | 120 | 1700 | 102 | 2100
Chandpur | 126 | 800 | 120 | 2200 | Purbasadipur | 126 | 700 | 114 | 2100
Feni | 120 | 800 | 111 | 2200 | Thakurgaon | 120 | 700 | 102 | 100
Chowmuhani | 122 | 600 | 109 | 2200 | Palashbari | 121 | 1700 | 105 | 1930
Ashuganj | 137 | 1100 | 131 | 2000 | Barapukuria | 130 | 1700 | 118 | 2100
Daudkandi | 136 | 1900 | 127 | 900 | Panchagar | 118 | 700 | 100 | 2100
B.Baria | 135 | 1000 | 128 | 1900

## L-Curve
Date | 2018-09-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 410 | 8011 | 3153 | 11164 |  |  |  | QF-LDC-12
0:30 | 400 | 7932.5 | 3169.5 | 11102 | Date: | 2018-09-18
1:00 | 390 | 7854 | 3186 | 11040
1:30 | 395 | 7757.5 | 3054.5 | 10812
2:00 | 400 | 7661 | 2923 | 10584
2:30 | 440 | 7656 | 2844.5 | 10500.5 | [5 empty] | Gen. at Eve. Peak | 11363 | 11363 MW (20:00 )
3:00 | 480 | 7651 | 2766 | 10417 | [6 empty] | 20:00
3:30 | 485 | 7551 | 2747.5 | 10298.5 | [5 empty] | Gen. at Day Peak | 9440.1 | 9440.1 MW (12:00 )
4:00 | 490 | 7451 | 2729 | 10180 | [6 empty] | 12:00
4:30 | 460 | 7368.5 | 2690.5 | 10059 | [5 empty] | Highest Generation | 11363
5:00 | 430 | 7286 | 2652 | 9938 | [6 empty] | 20:00
5:30 | 360 | 6963.625 | 2593 | 9556.625
6:00 | 290 | 6641.25 | 2534 | 9175.25
6:30 | 175 | 6497.825 | 2540.5 | 9038.325
7:00 | 60 | 6354.4 | 2547 | 8901.4
7:30 | 55 | 6309.8 | 2517.5 | 8827.3
8:00 | 50 | 6265.2 | 2488 | 8753.2
8:30 | 80 | 6383.05 | 2497.5 | 8880.55
9:00 | 110 | 6500.9 | 2507 | 9007.9
9:30 | 65 | 6631.2 | 2503.5 | 9134.7
10:00 | 20 | 6761.5 | 2500 | 9261.5
10:30 | 38 | 6755.2 | 2454.5 | 9209.7
11:00 | 56 | 6748.9 | 2409 | 9157.9
11:30 | 133 | 6895 | 2404 | 9299
12:00 | 210 | 7041.1 | 2399 | 9440.1
12:30 | 220 | 7090.5 | 2448.5 | 9539
13:00 | 230 | 7139.9 | 2498 | 9637.9
13:30 | 225 | 7269.7 | 2535.5 | 9805.2
14:00 | 220 | 7399.5 | 2573 | 9972.5
14:30 | 260 | 7614.7 | 2546.5 | 10161.2
15:00 | 300 | 7829.9 | 2520 | 10349.9
15:30 | 300 | 7677.35 | 2501 | 10178.35
16:00 | 300 | 7524.8 | 2482 | 10006.8
16:30 | 170 | 7271.05 | 2492.5 | 9763.55
17:00 | 40 | 7017.3 | 2503 | 9520.3
17:30 | 65 | 7076.15 | 2622.5 | 9698.65
18:00 | 90 | 7135 | 2742 | 9877
18:30 | 245 | 7605 | 2997.5 | 10602.5
19:00 | 400 | 8075 | 3253 | 11328
19:30 | 400 | 8014 | 3291 | 11305
20:00 | 430 | 8046 | 3317 | 11363 |  |  |  | Executive Engineer
20:30 | 415 | 7982 | 3334 | 11316 |  |  |  | Network Operation Division
21:00 | 400 | 7918 | 3351 | 11269
21:30 | 310 | 7844 | 3346 | 11190
22:00 | 220 | 7770 | 3341 | 11111 |  |  |  |  | Page 6 of 7
22:30 | 270 | 7896.5 | 3324.5 | 11221
23:00 | 320 | 8023 | 3308 | 11331
23:30 | 365 | 8017 | 3230.5 | 11247.5
24:00 | 410 | 8011 | 3153 | 11164
11363 MW (20:00 )
9440.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-09-18 |  | Energy | 243192699
[10 empty] | 2018-09-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4309 | 769 | 1511 | 2987 | 169 | 138 | 1101 | 0 | 180
0:30 | 4281.5 | 774 | 1679.5 | 2817 | 169 | 140 | 1076 | 0 | 165 | Date: | 2018-09-18
1:00 | 4254 | 779 | 1848 | 2647 | 169 | 142 | 1051 | 0 | 150
1:30 | 4284.5 | 779 | 1867.5 | 2482.5 | 169 | 142 | 939.5 | 0 | 148 | [7 empty] | Total Energy | 243.1927 | Total Energy Gen 243.193 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.193 MKWHr
2:00 | 4315 | 779 | 1887 | 2318 | 169 | 142 | 828 | 0 | 146 | [7 empty] | Energy not Served | 0
2:30 | 4327.5 | 779 | 1902.5 | 2291.5 | 169 | 142 | 745 | 0 | 144 | [7 empty] | Energy Requirement | 243.1927
3:00 | 4340 | 779 | 1918 | 2265 | 169 | 142 | 662 | 0 | 142
3:30 | 4333 | 779.5 | 1904.5 | 2211.5 | 169 | 142 | 618 | 0 | 141 | [6 empty] | Shortage
4:00 | 4326 | 780 | 1891 | 2158 | 169 | 142 | 574 | 0 | 140
4:30 | 4347.5 | 779.5 | 1894 | 2111 | 169 | 142 | 480 | 0 | 136
5:00 | 4369 | 779 | 1897 | 2064 | 169 | 142 | 386 | 0 | 132
5:30 | 4341.5 | 779 | 1834.5 | 1777.5 | 169.5 | 142 | 384.5 | 0 | 128
6:00 | 4314 | 779 | 1772 | 1491 | 170 | 142 | 383 | 0 | 124
6:30 | 4183.5 | 779 | 1796.5 | 1446 | 170 | 142 | 399.5 | 0 | 120 |  |  |  |  | Coal
7:00 | 4053 | 779 | 1821 | 1401 | 170 | 142 | 416 | 0 | 116
7:30 | 4010.5 | 779 | 1797.5 | 1401.5 | 169.5 | 142 | 403.5 | 0 | 117 |  |  |  | Oil |  |  |  | ,
8:00 | 3968 | 779 | 1774 | 1402 | 169 | 142 | 391 | 0 | 118
8:30 | 3989.5 | 779 | 1806 | 1447 | 169 | 142 | 414.5 | 0 | 121
9:00 | 4011 | 779 | 1838 | 1492 | 169 | 142 | 438 | 0 | 124
9:30 | 3989 | 779.5 | 1845 | 1637 | 169.5 | 142 | 439 | 0 | 117
10:00 | 3967 | 780 | 1852 | 1782 | 170 | 142 | 440 | 0 | 110
10:30 | 3880.5 | 779.5 | 1795 | 1908.5 | 170 | 142 | 418.5 | 0 | 101
11:00 | 3794 | 779 | 1738 | 2035 | 170 | 142 | 397 | 0 | 92
11:30 | 3926.5 | 779 | 1735 | 2041.5 | 170 | 142 | 396 | 0 | 95
12:00 | 4059 | 779 | 1732 | 2048 | 170 | 142 | 395 | 0 | 98
12:30 | 4149 | 779 | 1744.5 | 2048 | 170 | 142 | 391.5 | 0 | 97
13:00 | 4239 | 779 | 1757 | 2048 | 170 | 142 | 388 | 0 | 96
13:30 | 4239 | 779 | 1757 | 2048 | 170 | 142 | 388 | 0 | 96
14:00 | 4239 | 779 | 1757 | 2048 | 170 | 142 | 388 | 0 | 96
14:30 | 4290 | 779 | 1752.5 | 2331.5 | 170 | 139.5 | 418.5 | 0 | 97
15:00 | 4341 | 779 | 1748 | 2615 | 170 | 137 | 449 | 0 | 98
15:30 | 4280 | 779 | 1695.5 | 2567.5 | 170 | 137 | 455 | 0 | 84
16:00 | 4219 | 779 | 1643 | 2520 | 170 | 137 | 461 | 0 | 70
16:30 | 4156.5 | 779 | 1602 | 2334 | 170 | 139 | 499.5 | 0 | 79
17:00 | 4094 | 779 | 1561 | 2148 | 170 | 141 | 538 | 0 | 88
17:30 | 4084 | 774 | 1544.5 | 2216.5 | 170 | 141 | 675 | 0 | 93
18:00 | 4074 | 769 | 1528 | 2285 | 170 | 141 | 812 | 0 | 98
18:30 | 4161 | 768.5 | 1565.5 | 2702.5 | 170 | 145.5 | 968.5 | 0 | 121
19:00 | 4248 | 768 | 1603 | 3120 | 170 | 150 | 1125 | 0 | 144
19:30 | 4255 | 769 | 1557 | 3121 | 169 | 150 | 1156 | 0 | 128
20:00 | 4399 | 769 | 1507 | 3046 | 170 | 150 | 1172 | 0 | 150
20:30 | 4409 | 769 | 1498.5 | 2987 | 170 | 149.5 | 1178 | 0 | 155
21:00 | 4419 | 769 | 1490 | 2928 | 170 | 149 | 1184 | 0 | 160
21:30 | 4442.5 | 769 | 1500.5 | 2808 | 170 | 147.5 | 1179.5 | 0 | 173
22:00 | 4466 | 769 | 1511 | 2688 | 170 | 146 | 1175 | 0 | 186
22:30 | 4462.5 | 769 | 1507 | 2823.5 | 169.5 | 146 | 1156.5 | 0 | 187
23:00 | 4459 | 769 | 1503 | 2959 | 169 | 146 | 1138 | 0 | 188
23:30 | 4384 | 769 | 1507 | 2973 | 169 | 142 | 1119.5 | 0 | 184 | Max Temp. in Dhaka |  | 36.2° C
24:00 | 4309 | 769 | 1511 | 2987 | 169 | 138 | 1101 | 0 | 180
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 243.193 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.193 MKWHr
Note on W13: Author:

## Generation
2018-09-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 108 | 107 | 107 | 111 | 111 |  | 120 | 120 | 120 | 119 | 116 | 116 | 108 | 2601138
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 724400
3 | Chittagong ST-1 (Raozan) | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3000000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 0 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 340380
| Teknaf Solartech 20MW | [5 empty] | 0.25 | 3 | 9.2 | 13.4 | 16.4 | 8.7 | 16.2 | 17.3 | 15.6 | 11.5 | 7 | 1 | 0 | [8 empty] | 116000
6 | Sikalbaha 225MW (Gas) | 151 | 151 | 151 | 151 | 151 | 151 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 51 | 41 | 49 | 65 |  | 107 | 139 | 192 | 211 | 209 | 210 | 212 | 2604473
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 135 | 135 | 135 | 135 | 135 | 130 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 125 | 125 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3120355
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 44 | 44 | 48 | 48 | 24 | 17 | 17 | 17 | 16 | 15 | 15 | 14 | 14 | 14 | 27 | 26 | 39 | 40 |  | 44 | 44 | 44 | 35 | 35 | 33 | 32 | 715941
12 | Hathazari peaking | 63 | 63 | 63 | 63 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 46 | 64 | 72 | 72 |  | 80 | 72 | 72 | 72 | 72 | 63 | 63 | 979600
| Daudkandi bangla trak | 50 | 0 | [10 empty] | 0 | 30 | 100 | 100 | 10 | 10 |  | 200 | 200 | 200 | 120 | 0 | 135 | 150 | 936840
14 | Daudkandi Peaking 52MW | 49 | 0 | [14 empty] | 0 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 422040
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 207 | 206 | 207 | 208 | 210 | 210 | 209 | 208 | 204 | 201 | 150 | 150 | 195 | 195 | 194 | 195 | 196 | 170 |  | 175 | 150 | 150 | 150 | 122 | 120 | 120 | 4424365
18 | Summit Gazipur | 205 | 158 | 158 | 158 | 160 | 150 | 158 | 155 | 158 | 228 | 185 | 190 | 188 | 188 | 188 | 175 | 185 | 190 |  | 238 | 238 | 260 | 268 | 260 | 255 | 265 | 4684470
19 | Ashuganj 195MW Modular | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1656000
20 | Ghorasal ST: Unit-1,2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1689000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2835000
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 366 | 365 | 300 | 300 |  | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 8661290
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 150 | 150 | 150 | 150 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2691400
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 2324176
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 42 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 38 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 868032
33 | Ashuganj CCPP 225 MW | 175 | 180 | 181 | 180 | 190 | 181 | 183 | 173 | 170 | 157 | 181 | 193 | 215 | 215 | 215 | 191 | 191 | 202 |  | 204 | 210 | 209 | 209 | 213 | 203 | 180 | 4660000
34 | Ashuganj CCPP(South) | 300 | 300 | 300 | 300 | 334 | 327 | 300 | 300 | 300 | 300 | 300 | 320 | 300 | 300 | 320 | 301 | 301 | 301 |  | 301 | 301 | 301 | 301 | 305 | 334 | 301 | 7470000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8921500
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 153120
36 | Chandpur CCPP | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 153 | 153 | 152 | 153 | 153 | 152 | 151 | 150 | 100 |  | 101 | 98 | 100 | 98 | 100 | 100 | 100 | 3265460
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 244 | 256 | 262 | 262 | 262 | 241 | 60 | 60 | 76 | 55 | 130 | 304 | 334 | 325 | 315 | 300 | 285 | 300 |  | 300 | 320 | 330 | 336 | 329 | 337 | 350 | 6097570
40 | Meghnaghat CCPP 450MW | 440 | 440 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 430 | 420 | 410 | 400 | 360 | 330 | 310 |  | 290 | 290 | 260 | 240 | 215 | 215 | 230 | 8274812
41 | Haripur Power CCPP 360MW | 340 | 350 | 351 | 351 | 351 | 351 | 351 | 353 | 348 | 345 | 343 | 331 | 310 | 295 | 296 | 285 | 266 | 261 |  | 245 | 248 | 241 | 238 | 222 | 233 | 253 | 7307000
42 | Mymensingh RPCL 210MW | 46 | 46 | 47 | 47 | 47 | 47 | 45 | 44 | 41 | 28 | 28 | 28 | 10 | 10 | 29 | 43 | 43 | 50 |  | 29 | 20 | 65 | 60 | 100 | 98 | 100 | 1097060
43 | Haripur NEPC 110MW | 96 | 96 | 96 | 0 | [5 empty] | 13 | 55 | 55 | 50 | 61 | 70 | 74 | 95 | 97 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 1402800
44 | Fenchugonj CCPP-1 | 53 | 59 | 59 | 59 | 59 | 59 | 53 | 52 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 59 | 59 | 59 |  | 60 | 58 | 58 | 57 | 58 | 56 | 59 | 1339000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 58 | 59 | 59 | 59 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440000
46 | Shajibazar 330 MW | 302 | 302 | 307 | 303 | 310 | 312 | 302 | 300 | 305 | 300 | 303 | 317 | 304 | 302 | 310 | 317 | 303 | 300 |  | 302 | 300 | 301 | 300 | 324 | 312 | 300 | 7002759
47 | Shahjibazar GT: Unit- 8, 9 | 47 | 54 | 50 | 50 | 50 | 51 | 51 | 60 | 61 | 60 | 40 | 62 | 61 | 60 | 61 | 56 | 41 | 58 |  | 40 | 58 | 56 | 65 | 65 | 65 | 63 | 1341000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 50 | 50 | 50 | 84 | 83 | 83 | 82 | 84 | 84 | 84 | 84 | 84 | 30 |  | 86 | 86 | 86 | 86 | 85 | 86 | 86 | 1911360
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 43 | 43 | 43 | 43 | 44 | 10 | 10 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 991080
50 | Sylhet GT 150 MW | 100 | 100 | 100 | 100 | 100 | 80 | 130 | 130 | 128 | 128 | 78 | 76 | 76 | 128 | 130 | 115 | 110 | 100 |  | 127 | 100 | 100 | 70 | 70 | 70 | 70 | 2495440
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 444000
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 42 | 44 | 42 | 42 | 42 | 42 | 41 | 41 | 42 | 42 |  | 43 | 43 | 44 | 45 | 44 | 44 | 44 | 1038720
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 214200
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 47 | 47 | 47 | 44 | 41 | 42 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1132200
56 | Shahjahanulla 25 MW | 21 | 21 | 22 | 22 | 0 | 11 | 0 | 8 | 15 | 24 | 24 | 24 | 8 | 8 | 24 | 23 | 23 | 23 |  | 23 | 21 | 21 | 23 | 23 | 23 | 23 | 436920
57 | Summit Bibiana- 2 | 290 | 285 | 305 | 280 | 290 | 270 | 300 | 280 | 290 | 300 | 255 | 280 | 270 | 270 | 300 | 280 | 270 | 265 |  | 275 | 290 | 270 | 265 | 300 | 290 | 290 | 7452950
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 40 | 48 | 54 | 54 |  | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 1180517
59 | Sikalbaha (Energis) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 |  | 40 | 32 | 40 | 32 | 32 | 32 | 32 | 918240
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 454704
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 364896
62 | Tangail (Doreen) 22MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 17 | 21 | 20 |  | 0 | 0 | 22 | 22 | 20 | 22 | 22 | 426204
63 | Tripura | 150 | 146 | 142 | 140 | 132 | 124 | 116 | 118 | 124 | 110 | 92 | 98 | 96 | 96 | 98 | 70 | 88 | 98 |  | 144 | 128 | 150 | 160 | 186 | 188 | 180 | 3076800
64 | Malancha, Ctg. EPZ (United) | 30 | 31 | 32 | 32 | 32 | 32 | 23 | 9 | 2 | 3 | 2 | 3 | 6 | 7 | 2 | 6 | 7 | 11 |  | 7 | 12 | 15 | 24 | 23 | 12 | 16 | 364320
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 0 | 21 | 22 | 22 | 22 | 490284
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 185400
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 777200
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 20 |  | 0 | 0 | 18 | 21 | 21 | 21 | 21 | 446800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 9 | 9 | 23 | 23 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 525420
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 27 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788100
73 | Ghorashal (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 291681
76 | Siddhirganj (Desh) | 100 | 50 | 0 | [6 empty] | 0 | 10 | 17 | 17 | 20 | 60 | 80 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1246080
77 | Siddhirganj (Dutch Bangla) | 100 | 100 | 100 | 99 | 99 | 50 | 50 | 50 | 50 | 75 | 98 | 96 | 95 | 94 | 94 | 94 | 50 | 52 |  | 90 | 90 | 97 | 97 | 98 | 98 | 98 | 2153280
78 | Gazipur (RPCL) | 41 | 41 | 41 | 41 | 16 | 16 | 16 | 16 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 36 | 40 | 40 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 836112
79 | Kodda 149 MW | 117 | 117 | 117 | 55 | 16 | 16 | 16 | 16 | 98 | 98 | 65 | 65 | 65 | 82 | 117 | 117 | 117 | 117 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 2241120
80 | Jamalpur 95MW | 87 | 87 | 87 | 72 | 48 | 48 | 48 | 48 | 48 | 50 | 64 | 64 | 64 | 74 | 88 | 88 | 87 | 87 |  | 87 | 87 | 87 | 88 | 87 | 87 | 87 | 1788480
81 | Lakdhanvi 52 MW | [9 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | [6 empty] | 71040
82 | Madanganj 102MW | 81 | 81 | 81 | 81 | 81 | 48 | 48 | 49 | 48 | 70 | 81 | 81 | 81 | 80 | 80 | 81 | 81 | 80 |  | 80 | 81 | 81 | 81 | 80 | 80 | 81 | 1830120
83 | Pagla (DPA ) | 51 | 10 | 11 | 11 | 11 | 10 | 11 | 10 | 10 | 11 | 10 | 10 | 10 | 49 | 49 | 48 | 10 | 45 |  | 49 | 50 | 51 | 51 | 0 | 49 | 50 | 612150
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 50 | 51 | 51 | 82 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1830120
85 | Keraniganj (Powerpac) 100MW | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 70 | 100 | 100 | 90 | 85 | 90 | 90 | 50 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2056920
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 100 | 100 | 80 | 50 | 50 | 50 | 75 | 94 | 100 | 100 | 100 | 100 | 100 | 70 | 72 |  | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 2199360
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 78 | 78 | 78 | 78 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2076480
92 | Fenchuganj (EPL) 44MW | 47 | 47 | 47 | 47 | 44 | 47 | 44 | 41 | 44 | 44 | 44 | 44 | 44 | 49 | 49 | 43 | 46 | 50 |  | 50 | 47 | 47 | 47 | 47 | 50 | 50 | 1109000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 102 | 102 | 102 | 102 | 102 | 30 | 32 | 32 | 32 | 32 | 92 | 102 | 102 | 102 | 102 | 102 | 48 | 48 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2053584
95 | Patenga 50MW | 44 | 44 | 46 | 45 | 45 | 45 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 38 | 38 | 36 | 33 |  | 38 | 38 | 34 | 35 | 27 | 30 | 44 | 973440
96 | Chittagong ECPV 108 MW | 91 | 91 | 91 | 91 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 83 | 83 | 82 | 82 | 82 | 89 |  | 90 | 91 | 90 | 94 | 97 | 95 | 99 | 2087040
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 40 | 40 | 6 | 6 | 11 | 38 | 36 | 33 | 36 | 36 | 35 | 35 | 30 | 20 |  | 24 | 24 | 26 | 25 | 27 | 32 | 32 | 751104
98 | Bosila 108MW | 71 | 71 | 71 | 71 | 71 | 8 | 8 | 8 | 41 | 61 | 61 | 61 | 54 | 64 | 69 | 69 | 69 | 69 |  | 69 | 70 | 70 | 70 | 71 | 71 | 0 | 1359360
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 20 | 40 | 40 | 42 | 42 | 40 | 42 | 42 | 42 | 42 |  | 42 | 42 | 55 | 55 | 55 | 55 | 55 | 1078597
100 | Northern 55 MW | 55 | 55 | 56 | 56 | 55 | 55 | 37 | 37 | 55 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1282136
101 | Kushiara 163 MW CCPP GT | 130 | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 163 | 163 | 100 | 100 | 163 | 163 | 163 | 130 | 130 | 163 |  | 163 | 100 | 100 | 100 | 130 | 130 | 100 | 3486256
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.4 | 1 | 1.5 | 2.1 | 2.2 | 0.9 | 1.6 | 1.9 | 1.4 | 0.8 | 0.3 | 0 | [8 empty] | 14800
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 35 | 18 | 18 | 25 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1185480
104 | APR Energy , Keranigonj | [13 empty] | 32 | 33 | 0 | 0 | 11 |  | 202 | 200 | 73 | 0 | 0 | 38 | 108 | 508497
105 | Bramhangoan 100 MW (Aggreko) | [13 empty] | 30 | 88 | 52 | 0 | 10 |  | 95 | 96 | 97 | 99 | 51 | 95 | 95 | 666124
106 | United Mymensingh PPL | 187 | 187 | 190 | 190 | 190 | 98 | 98 | 98 | 98 | 106 | 154 | 163 | 170 | 170 | 170 | 170 | 170 | 170 |  | 174 | 174 | 178 | 185 | 185 | 185 | 185 | 3852000
112 | Aggreko Aurahati 100MW | 50 | 0 | [11 empty] | 30 | 97 | 67 | 0 | 81 |  | 100 | 100 | 100 | 100 | 101 | 99 | 101 | 890150
114 | Summit Gazipur-1 150MW | 100 | 100 | 90 | 96 | 93 | 93 | 92 | 90 | 86 | 94 | 94 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2414880
115
116
117
118
120 | Eastern Zone Total | 7854 | 7661 | 7651 | 7451 | 7286 | 6641.25 | 6354.4 | 6265.2 | 6500.9 | 6761.5 | 6748.9 | 7041.1 | 7139.9 | 7399.5 | 7829.9 | 7524.8 | 7017.3 | 7135 |  | 8075 | 8014 | 8046 | 7918 | 7770 | 8023 | 8011 | 175966927
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 87 | 87 | 87 | 87 | 84 | 10 | 10 | 10 | 10 | 44 | 51 | 27 | 27 | 86 | 86 | 88 | 88 | 88 |  | 89 | 89 | 88 | 93 | 82 | 88 | 82 | 1510560
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 99 | 49 | 49 | 49 | 49 | 49 | 77 | 83 | 98 | 97 | 96 | 96 | 96 | 96 |  | 99 | 99 | 99 | 115 | 115 | 115 | 115 | 2157120
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 36 | 12 | 32 | 30 | 30 | 8 | [9 empty] | 0 | 8 | 20 |  | 36 | 41 | 41 | 41 | 41 | 39 | 39 | 396000
129 | Khulna CCPP 225MW | 244 | 243 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 |  | 205 | 237 | 241 | 241 | 241 | 240 | 243 | 3927360
130
131
132
133
| Summit Barisal 110 MW | 111 | 111 | 111 | 111 | 110 | 110 | 110 | 100 | 110 | 110 | 110 | 112 | 110 | 110 | 110 | 110 | 110 | 96 |  | 110 | 110 | 110 | 110 | 110 | 110 | 98 | 2640000
136 | Barisal GT: Unit-1, 2 | 24 | [18 empty] | 24 | 24 | 24 | 26 | 26 | 14 | 14 | 166869
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 96 | 95 | 95 | 95 | 92 | 90 | 92 | 90 | 90 | 92 | 90 | 91 | 92 | 93 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 2269005
| Bhola CCPP 194MW | 100 | 112 | 118 | 104 | 119 | 120 | 100 | 100 | 112 | 120 | 100 | 120 | 120 | 120 | 60 | 50 | 50 | 65 |  | 111 | 110 | 118 | 110 | 120 | 120 | 110 | 2543000
140 | Bhola (Venture) 33MW | 32 | 32 | 31 | 29 | 32 | 28 | 27 | 18 | 23 | 25 | 23 | 26 | 26 | 21 | 26 | 24 | 26 | 28 |  | 38 | 35 | 38 | 39 | 39 | 37 | 37 | 693998
141 | Bangla Trak Noapara | 91 | [12 empty] | 30 | 30 | 0 | 0 | 10 |  | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 736320
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 925500
143 | Gopalganj Peaking | 54 | 52 | 39 | 39 | [10 empty] | 0 | 3 | 18 | 25 |  | 50 | 50 | 55 | 78 | 68 | 72 | 67 | 597120
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 779 | 779 | 779 | 780 | 779 | 779 | 779 | 779 | 779 | 780 | 779 | 779 | 779 | 779 | 779 | 779 | 779 | 769 |  | 768 | 769 | 769 | 769 | 769 | 769 | 769 | 18749090
147 | Bheramara 360 MW | 415 | 411 | 413 | 415 | 412 | 414 | 416 | 417 | 410 | 410 | 330 | 330 | 410 | 410 | 410 | 410 | 380 | 380 |  | 410 | 410 | 410 | 410 | 410 | 410 | 340 | 9785376
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 169 | 169 | 169 | 169 | 169 | 170 | 170 | 169 | 169 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 169 | 170 | 170 | 170 | 169 | 169 | 4143600
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 0 | [13 empty] | 0 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 426432
157 | Sirajgonj Unit-1 225MW (Gas) | 188 | 182 | 188 | 190 | 190 | 195 | 194 | 182 | 214 | 185 | 174 | 175 | 188 | 190 | 184 | 176 | 176 | 175 |  | 214 | 216 | 215 | 214 | 214 | 204 | 184 | 4869109
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 150 | 33 | 28 | 71 | 87 | 129 | 205 | 180 | 171 | 174 | 164 | 163 | 181 | 147 | 139 | 131 | 141 | 133 |  | 220 | 220 | 220 | 220 | 220 | 205 | 171 | 3807881
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | 48 | 44 | 15 | 0 | [11 empty] | 0 | 5 | 50 |  | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 445529
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500160
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 229752
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249156
165 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 40 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1064360
166 | Katakhali (Northern) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1161984
167 | Katakhali Peaking | 29 | 29 | 29 | 25 | 0 | [11 empty] | 0 | 16 |  | 21 | 23 | 32 | 29 | 29 | 29 | 29 | 275049
168 | Santahar Peaking | 32 | 32 | 32 | 14 | 0 | 0 | [10 empty] | 0 | 27 |  | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 329490
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 8 | 10 | 44 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1088160
170 | Chapainawabganj-100 MW | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 50 | 25 | 25 | 25 | 25 | 0 |  |  |  | 0 | 50 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1222792
171
172
173 | Rangpur GT | 10 | 8 | 8 | 8 | 0 | [11 empty] | 0 | 15 |  | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 97000
175 | Saidpur GT | 16 | 16 | 16 | 16 | 16 | 0 | [9 empty] | 0 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 218000
176
177
178
178 | Western Zone Total | 3186 | 2923 | 2766 | 2729 | 2652 | 2534 | 2547 | 2488 | 2507 | 2500 | 2409 | 2399 | 2498 | 2573 | 2520 | 2482 | 2503 | 2742 | 0 | 3253 | 3291 | 3317 | 3351 | 3341 | 3308 | 3153 | 67225772