## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-09-18 | Tuesday
|  | Date (day): | 2018-09-18 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11557 | MW |  |  | (b) At Evening Peak Hour : |  | 12759 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-09-17 | 2018-09-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 74 | 74 | 74 | 74 | 11 |  | Gas shortage
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120 | 70 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 58 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 309 | 356 | 350 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 96 | 105 | 105
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 332 | 350 | 350
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 92 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 81 | 81 | 81 |  | 19 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 86 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 96 | 80 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 200 | 204 | 216 | 216
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 50 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 90 | 117 | 115 | 115
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 53 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 71 | 70 | 71 | 71 |  | 37 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 48 | 49 | 49 |  | 31 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 220 | 200 | 200 | 273 |  | 27 | Machine problem
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 300 | 300 | 0 | 215 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 98 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 92 | 108 | 92 | 92 |  | 34 | Engine problem
| Dhaka area Total |  |  |  |  | 6084 | 5848 | 3213 | 3936 | 3987 | 4527 | 467 | 740
38 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 0 | 130 | 130 | 50 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 18 | 0 | 0 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 36 | 43 | 45 | 45 |  | 5 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 142 | 143 | 143 |  |  | #5 Under maint.
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 136 | 150 | 151 | 151 |  |  | ST Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 130 | 135 | 135
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 71 | 70 | 70
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 42 | 45 | 45
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 9 | 10 | 10
50 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 90 | 92 | 92 |  | 16 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 776 | 842 | 986 | 986 | 230 | 91
51 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 130 | 100 | 100 | 100
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 90 | 90 | 100 | 100 | 34 |  | Gas shortage
52 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 207 | 217 | 217
53 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
54 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 272 | 360 | 360 |  |  | FGMO
55 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 42 | 40 | 40
56 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
57 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas shortage
58 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 70 | 68 | 68 | 68 | 127 |  | Gas shortage
59 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | line problem
60 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
61 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
62 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 150 | 150 | 150 | 150
63 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
64 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 106 | 164 | 125 | 173
65 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
66 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 20 | 52
67 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
68 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 130 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1601 | 1881 | 1849 | 2049 | 394 | 51
69 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 41 | 43 | 44 | 44 | 158 |  | Gas shortage
70 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
71 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 80 | 80 | 89 | 89
72 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 2 | 0
73 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 180 | 187 | 180 | 185 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 323.4 | 330 | 335 | 338 | 158 | 0
74 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 57 | 58 | 58
75 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 59 | 59 | 60 | 60
76 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
77 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 303 | 300 | 330 | 330
78 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 49 | 47 | 47
79 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 47 | 47
80 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
81 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 46 | 66 | 66
82 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 86 | 86
83 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 45 | 45 | 45
84 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 118 | 130 | 130 | 130
85 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
86 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 45 | 47 | 47
87 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 11 | 12 | 12 | 12 |  | 13 | Engine problem
88 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 |  |  | FGMO
89 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1358 | 1362 | 1471 | 1471 | 0 | 13
90 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 777 | 782 | 788 | 788
91 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 85 | 92 | 100 | 100 |  | 10 | Engine problem
92 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 97 | 99 | 115 | 115
93 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 42
94 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 233 | 225 | 225
95 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 0 | 85
96 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 410 | 410 | 410
97 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
98 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 94 | 94 | 94
| Khulna Area Total |  |  |  |  | 2283 | 2214 | 1529 | 1845 | 1772 | 1947 | 0 | 10
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 22 | 0 | 26
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 32 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 110 | 100 | 120 | 120 |  | 74 | Machine problem
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 55 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 300 | 360 | 358 | 384 | 0 | 74
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 52 | 0 | 48
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 | 10 |  | Engine problem
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 38
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 182 | 188 | 214 | 214
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 150 | 180 | 180
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 141 | 141 | 0 | 0 | 0 | 0 |  | 141 | Under Shut down
| Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | 0 | 0 | 0
113 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
114 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
115 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 10 | 10
116 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
117 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 52 | 52
118 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 99 | 50 | 102
| Rajshahi Area Total |  |  |  |  | 1274 | 1264 | 356 | 778 | 629 | 852 | 81 | 241
119 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
120 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 169 | 170 | 170 | 170 | 104 |  | Coal shortage
121 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 12 | 0 | 17
122 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 169 | 200 | 170 | 205 | 189 | 85
| Total |  |  |  |  | 17043 | 16445 | 9625.4 | 11534 | 11557 | 12759 | 1519 | 1305
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9077.1177 | 10877 | 10898.6899 | 12032.2215
A. |  | 2018-09-17 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11534 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8655.4 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11534 | MW
3 | Day peak Generation : |  |  | 9625.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10877 | MW
4 | Evening peak Generation : |  |  | 11534 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 238.8264 | MKWHr | By Solar | 0.1205 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 143.12 | MKWHr |  | By Oil: | 70.0065 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 0.41436 | MKWHr |  | By Hydro: | 3.2369 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1519 | MW | Dhaka | 4143 | 4143 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1305 | MW | Chittagong | 1129 | 1129 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2824 | MW | Khulna | 1339 | 1339 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1220.58 | MMCFD |  |  | Rajshahi | 1131 | 1131 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104315505.646 | ii) Oil : | Taka | 622434940.68 | Comilla | 1033 | 1033 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 1599429.6 | Total | Taka | 728349875.926 | Mymensingh | 794 | 794 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 4.7305 | MKWHr. | Sylhet | 482 | 482 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -410 | MW at | 19:00 | hrs | Barisal | 272 | 272 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -600 | MW at | 2:00 | hrs | Rangpur | 554 | 554 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 10877 | 10877 |  | 0
B. |  | 2018-09-18 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12759 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 959 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 244.3343 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8753.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.6633 | MKWHr. | ii) HVDC Flow at Peak Time |  | 782 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.265 | MKWHr. | iii) Maximum HVDC Flow : |  | 783 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.45 |  | (b) Today: | 104.4 |  | (c) Rule Curve: |  | 102.91
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-09-17
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 255 | 326 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 209 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 70 | 21 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 111 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 45 | 90 | 91 | 44 | 19 | 30 | 0 | 100 | 90 | 360 | 276 | 185 | 68 | 152 | 40 | 5 | 5 | 0 | 85 | 41 | 0 | 22 | 8 | 33 | 21 | 160 | 47 | 88 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 300 | 61 | 86 | 45 | 107 | 19 | 46 | 9 | 295 | 12 | 11 | 0 | 265 | 0 | 0 | 187 | 0 | 92 | 0 |  | 778 | 0 | 410 | 90 | 115 | 140 | 0 | 0 | 44 | 40 | 40 | 118 | 37 | 110 | 22 | 0 | 0 | 50 | 42 | 90 | 40 | 50 | 35 | 43 | 32 | 22 | 10 | 11 | 0 | 0 | 170 | 8 | 12 | 200 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 7776 | 2809 | 10585 | 4281 | 778 | 1785 | 2464 | 170 | 141 | 806 | 160 | 0 | 0 | 104.47
2:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 262 | 340 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 209 | 0 | 0 | 0 | 100 | 102 | 133 | 88 | 70 | 10 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 111 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 45 | 90 | 86 | 44 | 19 | 30 | 0 | 100 | 90 | 360 | 276 | 182 | 68 | 155 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 160 | 47 | 88 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 307 | 61 | 86 | 45 | 107 | 19 | 46 | 9 | 300 | 12 | 11 | 0 | 265 | 0 | 0 | 190 | 0 | 92 | 0 |  | 779 | 0 | 410 | 90 | 115 | 120 | 0 | 0 | 44 | 40 | 40 | 120 | 31 | 110 | 22 | 0 | 0 | 0 | 42 | 81 | 40 | 50 | 35 | 43 | 32 | 22 | 10 | 11 | 0 | 0 | 170 | 8 | 12 | 199 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 7643 | 2726 | 10369 | 4296 | 779 | 1798 | 2339 | 170 | 141 | 686 | 160 | 0 | 0 | 104.47
3:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 268 | 346 | 24 | 0 | 450 | 0 | 100 | 81 | 55 | 211 | 0 | 0 | 0 | 100 | 102 | 125 | 88 | 70 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 42 | 0 | 111 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 45 | 90 | 91 | 39 | 19 | 30 | 0 | 100 | 90 | 360 | 276 | 182 | 68 | 153 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 156 | 47 | 88 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 301 | 63 | 86 | 45 | 107 | 19 | 46 | 9 | 290 | 12 | 11 | 0 | 265 | 0 | 0 | 192 | 0 | 92 | 0 |  | 778 | 0 | 410 | 90 | 115 | 120 | 0 | 0 | 44 | 35 | 40 | 118 | 32 | 110 | 22 | 0 | 0 | 0 | 0 | 81 | 40 | 50 | 35 | 43 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 8 | 12 | 199 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 |  | 7569 | 2673 | 10242 | 4296 | 778 | 1812 | 2259 | 169 | 141 | 631 | 156 | 0 | 0 | 104.46
4:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 273 | 351 | 13 | 0 | 450 | 0 | 100 | 81 | 55 | 212 | 0 | 0 | 0 | 100 | 48 | 40 | 86 | 71 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 111 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 45 | 90 | 91 | 44 | 19 | 31 | 0 | 100 | 90 | 360 | 272 | 182 | 68 | 154 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 154 | 47 | 72 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 302 | 56 | 86 | 45 | 107 | 19 | 46 | 9 | 280 | 12 | 11 | 0 | 270 | 0 | 0 | 190 | 0 | 92 | 0 |  | 779 | 0 | 415 | 51 | 115 | 120 | 0 | 0 | 44 | 30 | 40 | 100 | 33 | 110 | 12 | 0 | 0 | 0 | 0 | 81 | 40 | 50 | 35 | 43 | 32 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 |  | 7384 | 2578 | 9962 | 4262 | 779 | 1816 | 2129 | 170 | 141 | 511 | 154 | 0 | 0 | 104.46
5:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 275 | 352 | 0 | 0 | 450 | 0 | 100 | 81 | 55 | 201 | 0 | 0 | 0 | 100 | 7 | 16 | 86 | 71 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 111 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 45 | 90 | 91 | 39 | 19 | 31 | 0 | 100 | 90 | 360 | 276 | 182 | 68 | 150 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 154 | 47 | 72 | 20 | 0 | 58 | 60 | 47 | 47 | 130 | 304 | 56 | 86 | 45 | 107 | 19 | 46 | 9 | 290 | 12 | 11 | 0 | 270 | 0 | 0 | 190 | 0 | 92 | 0 |  | 779 | 0 | 413 | 10 | 49 | 120 | 0 | 0 | 44 | 10 | 33 | 100 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 81 | 40 | 50 | 35 | 43 | 32 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 182 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 7304 | 2429 | 9733 | 4251 | 779 | 1828 | 1955 | 170 | 141 | 455 | 154 | 0 | 0 | 104.45
6:00 | 74 | 0 | 0 | 120 | 340 | 12 | 0 | 247 | 301 | 0 | 0 | 380 | 0 | 60 | 81 | 55 | 212 | 0 | 0 | 0 | 100 | 7 | 16 | 10 | 71 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 112 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 72 | 31 | 90 | 91 | 44 | 19 | 30 | 0 | 100 | 90 | 360 | 256 | 182 | 68 | 154 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 136 | 48 | 8 | 20 | 0 | 58 | 60 | 44 | 47 | 100 | 311 | 65 | 86 | 45 | 77 | 19 | 47 | 9 | 260 | 8 | 11 | 0 | 270 | 0 | 0 | 190 | 0 | 92 | 0 |  | 778 | 0 | 416 | 10 | 16 | 120 | 0 | 0 | 23 | 10 | 8 | 100 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 0 | 171 | 0 | 0 | 181 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 6839 | 2249 | 9088 | 4178 | 778 | 1639 | 1722 | 171 | 142 | 322 | 136 | 0 | 0 | 104.45
7:00 | 74 | 0 | 0 | 120 | 340 | 12 | 0 | 36 | 301 | 0 | 0 | 380 | 0 | 7 | 81 | 55 | 210 | 0 | 0 | 0 | 100 | 7 | 16 | 10 | 70 | 10 | 40 | 54 | 0 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 114 | 30 | 120 | 0 | 16 | 151 | 0 | 110 | 0 | 0 | 32 | 8 | 16 | 90 | 91 | 44 | 19 | 21 | 0 | 100 | 90 | 360 | 257 | 184 | 68 | 156 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 122 | 46 | 8 | 20 | 0.4 | 58 | 60 | 44 | 47 | 100 | 304 | 63 | 86 | 45 | 79 | 19 | 45 | 9 | 300 | 8 | 11 | 0 | 270 | 0 | 0 | 189 | 0 | 92 | 0 |  | 779 | 0 | 416 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 100 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 5 | 0 | 0 | 170 | 0 | 0 | 189 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 |  | 6461.4 | 2194 | 8655.4 | 3966 | 779 | 1667 | 1623 | 170 | 144 | 184 | 122 | 0.4 | 0 | 104.44
8:00 | 74 | 0 | 0 | 120 | 340 | 12 | 0 | 69 | 301 | 0 | 0 | 380 | 0 | 7 | 81 | 55 | 208 | 0 | 0 | 0 | 100 | 7 | 16 | 10 | 71 | 11 | 40 | 54 | 29 | 55 | 22 | 25 | 24 | 33 | 33 | 25 | 0 | 113 | 30 | 120 | 0 | 8 | 151 | 0 | 110 | 0 | 0 | 32 | 8 | 16 | 90 | 88 | 43 | 19 | 8 | 0 | 100 | 90 | 360 | 264 | 188 | 68 | 156 | 34 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 122 | 44 | 8 | 20 | 1.1 | 58 | 60 | 44 | 47 | 100 | 310 | 63 | 86 | 45 | 79 | 19 | 45 | 9 | 300 | 8 | 11 | 0 | 271 | 0 | 0 | 190 | 0 | 92 | 0 |  | 777 | 0 | 411 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 182 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 6509.1 | 2193 | 8702.1 | 4017 | 777 | 1652 | 1636 | 170 | 143 | 184 | 122 | 1.1 | 0 | 0
9:00 | 74 | 0 | 0 | 120 | 340 | 12 | 0 | 138 | 353 | 0 | 0 | 380 | 0 | 35 | 81 | 48 | 209 | 0 | 0 | 0 | 100 | 24 | 98 | 50 | 71 | 11 | 40 | 54 | 49 | 55 | 19 | 25 | 24 | 33 | 33 | 37 | 0 | 113 | 30 | 110 | 0 | 8 | 151 | 0 | 100 | 0 | 0 | 32 | 8 | 15 | 90 | 91 | 43 | 19 | 2 | 0 | 100 | 90 | 360 | 257 | 182 | 68 | 155 | 34 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 90 | 41 | 8 | 20 | 1.6 | 57 | 60 | 44 | 47 | 100 | 302 | 36 | 84 | 45 | 79 | 19 | 44 | 9 | 275 | 8 | 11 | 0 | 270 | 0 | 0 | 190 | 0 | 92 | 0 |  | 777 | 0 | 412 | 51 | 60 | 120 | 0 | 0 | 0 | 0 | 0 | 100 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 0 | 170 | 0 | 0 | 187 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 6682.6 | 2264 | 8946.6 | 3997 | 777 | 1670 | 1833 | 170 | 143 | 265 | 90 | 1.6 | 0 | 104.44
10:00 | 74 | 0 | 0 | 120 | 300 | 12 | 0 | 261 | 347 | 0 | 0 | 430 | 0 | 92 | 75 | 55 | 205 | 0 | 0 | 0 | 98 | 48 | 82 | 73 | 71 | 21 | 40 | 54 | 51 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 113 | 0 | 110 | 0 | 16 | 151 | 0 | 100 | 0 | 0 | 32 | 8 | 15 | 80 | 84 | 36 | 19 | 2 | 0 | 100 | 90 | 360 | 316 | 194 | 68 | 155 | 34 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 100 | 41 | 8 | 20 | 2.2 | 57 | 60 | 42 | 44 | 130 | 312 | 63 | 86 | 43 | 100 | 19 | 44 | 9 | 290 | 8 | 11 | 0 | 225 | 0 | 0 | 185 | 0 | 92 | 0 |  | 777 | 0 | 380 | 69 | 65 | 120 | 0 | 0 | 0 | 0 | 27 | 120 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 0 | 169 | 0 | 0 | 190 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 6992.2 | 2280 | 9272.2 | 4196 | 777 | 1754 | 1936 | 169 | 113 | 225 | 100 | 2.2 | 0 | 104.42
11:00 | 74 | 0 | 0 | 120 | 377 | 12 | 0 | 326 | 345 | 13 | 0 | 430 | 0 | 100 | 50 | 52 | 201 | 0 | 0 | 0 | 98 | 70 | 82 | 86 | 71 | 21 | 40 | 54 | 54 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 95 | 0 | 110 | 0 | 16 | 136 | 0 | 100 | 0 | 0 | 40 | 8 | 15 | 68 | 78 | 36 | 19 | 3 | 0 | 100 | 90 | 360 | 300 | 182 | 68 | 155 | 32 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 8 | 33 | 21 | 112 | 41 | 56 | 20 | 2.4 | 57 | 60 | 44 | 44 | 130 | 300 | 59 | 86 | 43 | 98 | 18 | 44 | 7 | 290 | 8 | 11 | 0 | 223 | 0 | 0 | 187 | 0 | 92 | 15 |  | 778 | 0 | 380 | 82 | 98 | 120 | 0 | 0 | 0 | 0 | 32 | 104 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 22 | 10 | 11 | 0 | 0 | 169 | 0 | 0 | 186 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 7143.4 | 2314 | 9457.4 | 4253 | 778 | 1752 | 2056 | 169 | 95 | 225 | 112 | 17.4 | 0 | 104.43
12:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 309 | 335 | 13 | 0 | 430 | 0 | 100 | 64 | 55 | 200 | 0 | 0 | 0 | 96 | 84 | 90 | 86 | 71 | 21 | 40 | 54 | 53 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 95 | 30 | 110 | 0 | 16 | 136 | 0 | 100 | 0 | 0 | 40 | 8 | 15 | 68 | 83 | 36 | 19 | 2 | 0 | 130 | 90 | 360 | 300 | 182 | 70 | 150 | 37 | 5 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 41 | 80 | 20 | 2.4 | 57 | 59 | 44 | 44 | 163 | 303 | 62 | 82 | 43 | 118 | 18 | 44 | 9 | 290 | 11 | 11 | 0 | 220 | 0 | 0 | 180 | 0 | 92 | 18 |  | 777 | 0 | 410 | 85 | 97 | 120 | 0 | 0 | 0 | 0 | 40 | 110 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 22 | 8 | 11 | 0 | 0 | 169 | 0 | 0 | 182 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 7271.4 | 2354 | 9625.4 | 4309 | 777 | 1773 | 2113 | 169 | 125 | 233 | 106 | 20.4 | 0 | 104.43
13:00 | 74 | 0 | 0 | 120 | 310 | 12 | 0 | 304 | 332 | 77 | 0 | 430 | 0 | 100 | 64 | 55 | 200 | 0 | 0 | 5 | 96 | 102 | 117 | 100 | 65 | 21 | 40 | 54 | 53 | 55 | 0 | 25 | 23 | 33 | 33 | 41 | 0 | 95 | 30 | 110 | 0 | 16 | 127 | 0 | 100 | 0 | 0 | 40 | 31 | 24 | 68 | 82 | 35 | 19 | 2 | 0 | 150 | 100 | 360 | 301 | 183 | 70 | 152 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 21 | 8 | 33 | 21 | 102 | 41 | 0 | 20 | 2.2 | 57 | 59 | 47 | 47 | 163 | 305 | 40 | 86 | 43 | 99 | 18 | 44 | 9 | 280 | 11 | 11 | 0 | 203 | 0 | 0 | 180 | 0 | 92 | 17 |  | 777 | 0 | 400 | 85 | 97 | 120 | 0 | 0 | 0 | 0 | 40 | 100 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 21 | 8 | 11 | 0 | 0 | 169 | 0 | 0 | 181 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 |  | 7230.2 | 2329 | 9559.2 | 4200 | 777 | 1766 | 2109 | 169 | 125 | 292 | 102 | 19.2 | 0 | 104.43
14:00 | 74 | 0 | 0 | 120 | 310 | 12 | 0 | 300 | 336 | 80 | 0 | 430 | 0 | 100 | 80 | 55 | 180 | 0 | 0 | 50 | 94 | 102 | 117 | 100 | 61 | 50 | 40 | 54 | 55 | 55 | 0 | 25 | 23 | 33 | 33 | 41 | 0 | 111 | 30 | 110 | 0 | 16 | 137 | 0 | 100 | 0 | 0 | 40 | 30 | 39 | 68 | 88 | 35 | 19 | 2 | 0 | 150 | 120 | 360 | 301 | 186 | 78 | 141 | 42 | 5 | 5 | 0 | 82 | 0 | 0 | 21 | 8 | 33 | 20 | 108 | 41 | 8 | 20 | 1.2 | 57 | 59 | 47 | 47 | 163 | 305 | 63 | 83 | 43 | 128 | 18 | 44 | 9 | 270 | 12 | 11 | 11 | 190 | 0 | 10 | 189 | 10 | 92 | 4.2 |  | 777 | 0 | 410 | 84 | 97 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 21 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 191 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 |  | 7430.4 | 2371 | 9801.4 | 4292 | 777 | 1764 | 2238 | 170 | 141 | 306 | 108 | 5.4 | 0 | 104.46
15:00 | 74 | 0 | 0 | 120 | 310 | 12 | 0 | 315 | 327 | 96 | 0 | 430 | 0 | 100 | 80 | 55 | 196 | 0 | 0 | 80 | 94 | 102 | 117 | 100 | 60 | 50 | 40 | 54 | 56 | 55 | 0 | 25 | 23 | 33 | 33 | 41 | 0 | 102 | 30 | 110 | 0 | 16 | 135 | 0 | 100 | 0 | 0 | 40 | 31 | 40 | 80 | 88 | 35 | 19 | 2 | 0 | 100 | 120 | 360 | 301 | 170 | 78 | 150 | 42 | 5 | 5 | 0 | 82 | 0 | 0 | 21 | 8 | 33 | 20 | 106 | 42 | 24 | 20 | 1 | 57 | 59 | 47 | 47 | 130 | 302 | 52 | 84 | 43 | 78 | 18 | 44 | 9 | 280 | 12 | 11 | 100 | 190 | 0 | 94 | 185 | 100 | 92 | 5.8 |  | 777 | 0 | 410 | 84 | 78 | 160 | 0 | 0 | 0 | 0 | 40 | 100 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 21 | 8 | 11 | 0 | 0 | 170 | 0 | 0 | 194 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 |  | 7633.8 | 2405 | 10038.8 | 4184 | 777 | 1763 | 2552 | 170 | 132 | 348 | 106 | 6.8 | 0 | 104.47
16:00 | 74 | 0 | 0 | 120 | 310 | 12 | 0 | 342 | 326 | 96 | 0 | 430 | 0 | 100 | 80 | 55 | 200 | 0 | 0 | 100 | 90 | 102 | 117 | 100 | 69 | 50 | 34 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 107 | 30 | 110 | 0 | 16 | 135 | 0 | 100 | 0 | 0 | 32 | 70 | 40 | 68 | 88 | 37 | 19 | 2 | 0 | 100 | 90 | 360 | 272 | 175 | 78 | 150 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 21 | 8 | 33 | 20 | 106 | 42 | 48 | 20 | 0.6 | 57 | 59 | 47 | 47 | 130 | 301 | 52 | 80 | 44 | 78 | 18 | 46 | 9 | 270 | 11 | 11 | 100 | 190 | 0 | 98 | 185 | 100 | 92 | 6.5 |  | 777 | 0 | 370 | 82 | 82 | 160 | 0 | 0 | 0 | 0 | 40 | 100 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 21 | 9 | 11 | 0 | 0 | 170 | 0 | 0 | 187 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 |  | 7691.1 | 2364 | 10055.1 | 4131 | 777 | 1758 | 2582 | 170 | 137 | 387 | 106 | 7.1 | 0 | 104.48
17:00 | 74 | 0 | 0 | 120 | 310 | 12 | 0 | 335 | 326 | 96 | 0 | 430 | 0 | 100 | 80 | 55 | 199 | 0 | 0 | 100 | 95 | 102 | 117 | 100 | 60 | 11 | 28 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 107 | 30 | 110 | 0 | 16 | 135 | 0 | 100 | 0 | 0 | 40 | 65 | 40 | 80 | 88 | 37 | 19 | 6 | 0 | 100 | 90 | 360 | 272 | 200 | 69 | 150 | 42 | 5 | 5 | 0 | 85 | 0 | 0 | 21 | 8 | 33 | 20 | 136 | 43 | 48 | 20 | 0.3 | 57 | 59 | 47 | 47 | 100 | 300 | 40 | 40 | 20 | 78 | 18 | 46 | 9 | 265 | 12 | 11 | 10 | 170 | 0 | 10 | 185 | 11 | 108 | 3.5 |  | 777 | 0 | 370 | 82 | 95 | 160 | 0 | 0 | 0 | 20 | 40 | 100 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 7 | 22 | 9 | 11 | 0 | 0 | 170 | 0 | 0 | 183 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 7314.8 | 2404 | 9718.8 | 4133 | 777 | 1658 | 2295 | 170 | 137 | 409 | 136 | 3.8 | 0 | 104.48
18:00 | 74 | 0 | 0 | 120 | 250 | 12 | 0 | 300 | 326 | 96 | 0 | 330 | 0 | 65 | 80 | 55 | 120 | 0 | 0 | 100 | 60 | 102 | 117 | 70 | 65 | 11 | 40 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 113 | 30 | 110 | 0 | 16 | 150 | 0 | 70 | 0 | 0 | 40 | 65 | 41 | 90 | 88 | 43 | 19 | 5 | 0 | 100 | 90 | 360 | 290 | 205 | 69 | 153 | 42 | 5 | 5 | 0 | 21 | 49 | 0 | 21 | 8 | 33 | 20 | 150 | 42 | 83 | 20 | 0 | 57 | 59 | 23 | 25 | 100 | 308 | 63 | 20 | 20 | 80 | 18 | 46 | 9 | 265 | 12 | 11 | 10 | 173 | 12 | 10 | 187 | 11 | 108 | 0 |  | 777 | 0 | 300 | 85 | 98 | 175 | 0 | 0 | 15 | 46 | 40 | 120 | 23 | 110 | 0 | 0 | 0 | 40 | 26 | 10 | 40 | 50 | 24 | 43 | 31 | 22 | 9 | 11 | 0 | 0 | 170 | 17 | 0 | 181 | 0 | 0 | 80 | 96 | 10 | 0 | 0 | 0 |  | 7004 | 2649 | 9653 | 3950 | 777 | 1431 | 2296 | 170 | 143 | 736 | 150 | 0 | 0 | 104.48
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 356 | 332 | 96 | 0 | 430 | 0 | 92 | 81 | 55 | 204 | 0 | 0 | 100 | 80 | 102 | 117 | 100 | 70 | 50 | 40 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 112 | 30 | 0 | 0 | 16 | 150 | 0 | 130 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 9 | 0 | 100 | 90 | 360 | 272 | 207 | 68 | 150 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 164 | 43 | 80 | 20 | 0 | 57 | 59 | 49 | 47 | 163 | 300 | 46 | 85 | 45 | 130 | 19 | 45 | 9 | 285 | 12 | 11 | 200 | 200 | 215 | 98 | 187 | 100 | 108 | 0 |  | 782 | 0 | 410 | 92 | 99 | 233 | 0 | 0 | 40 | 55 | 40 | 100 | 32 | 110 | 22 | 0 | 0 | 50 | 52 | 99 | 40 | 50 | 29 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 170 | 12 | 18 | 188 | 0 | 0 | 150 | 96 | 94 | 0 | 0 | 0 |  | 8351 | 3183 | 11534 | 4262 | 782 | 1835 | 3107 | 170 | 142 | 1072 | 164 | 0 | 0 | 104.48
19:30 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 351 | 332 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 204 | 0 | 0 | 100 | 96 | 102 | 117 | 100 | 70 | 51 | 40 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 112 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 15 | 0 | 100 | 90 | 360 | 279 | 214 | 68 | 150 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 168 | 43 | 80 | 20 | 0 | 60 | 59 | 49 | 47 | 100 | 301 | 55 | 85 | 45 | 90 | 19 | 46 | 9 | 305 | 12 | 11 | 200 | 200 | 158 | 97 | 187 | 100 | 108 | 0 |  | 782 | 0 | 410 | 92 | 105 | 240 | 0 | 0 | 41 | 64 | 40 | 101 | 30 | 110 | 22 | 0 | 0 | 50 | 51 | 102 | 40 | 50 | 30 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 170 | 8 | 18 | 181 | 0 | 0 | 150 | 97 | 94 | 0 | 0 | 0 |  | 8274 | 3198 | 11472 | 4244 | 782 | 1798 | 3080 | 170 | 142 | 1088 | 168 | 0 | 0 | 0
20:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 352 | 332 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 204 | 0 | 0 | 100 | 98 | 102 | 117 | 100 | 70 | 51 | 40 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 112 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 19 | 0 | 100 | 90 | 360 | 276 | 184 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 170 | 43 | 80 | 20 | 0 | 60 | 59 | 49 | 47 | 100 | 309 | 64 | 86 | 45 | 87 | 19 | 46 | 9 | 280 | 12 | 11 | 200 | 255 | 104 | 97 | 187 | 101 | 108 | 0 |  | 783 | 0 | 410 | 86 | 105 | 240 | 0 | 0 | 41 | 82 | 40 | 120 | 32 | 110 | 24 | 0 | 0 | 50 | 51 | 102 | 40 | 50 | 32 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 170 | 8 | 18 | 183 | 0 | 0 | 150 | 97 | 94 | 0 | 0 | 0 |  | 8245 | 3238 | 11483 | 4251 | 783 | 1780 | 3077 | 170 | 142 | 1110 | 170 | 0 | 0 | 104.48
21:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 351 | 332 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 206 | 0 | 0 | 100 | 98 | 102 | 117 | 100 | 70 | 50 | 35 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 113 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 25 | 0 | 100 | 100 | 360 | 301 | 178 | 68 | 153 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 164 | 43 | 87 | 20 | 0 | 60 | 59 | 49 | 47 | 100 | 301 | 59 | 86 | 46 | 97 | 19 | 46 | 9 | 300 | 12 | 11 | 200 | 270 | 51 | 96 | 187 | 100 | 108 | 0 |  | 782 | 0 | 412 | 87 | 108 | 241 | 0 | 0 | 36 | 67 | 40 | 105 | 15 | 110 | 24 | 0 | 0 | 50 | 51 | 102 | 40 | 50 | 29 | 52 | 32 | 22 | 11 | 11 | 0 | 0 | 170 | 10 | 16 | 190 | 0 | 0 | 151 | 97 | 91 | 0 | 0 | 0 |  | 8254 | 3202 | 11456 | 4271 | 782 | 1790 | 3048 | 170 | 143 | 1088 | 164 | 0 | 0 | 104.48
22:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 244 | 322 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 205 | 0 | 0 | 100 | 100 | 102 | 117 | 100 | 71 | 51 | 32 | 54 | 56 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 113 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 28 | 0 | 100 | 100 | 360 | 331 | 195 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 164 | 43 | 88 | 20 | 0 | 59 | 59 | 49 | 47 | 130 | 313 | 64 | 84 | 45 | 117 | 19 | 47 | 9 | 310 | 12 | 11 | 150 | 270 | 51 | 52 | 187 | 100 | 108 | 0 |  | 782 | 0 | 410 | 85 | 109 | 240 | 0 | 0 | 39 | 75 | 40 | 118 | 32 | 110 | 24 | 0 | 0 | 50 | 50 | 102 | 40 | 43 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 170 | 10 | 16 | 194 | 0 | 0 | 151 | 97 | 91 | 0 | 0 | 0 |  | 8172 | 3234 | 11406 | 4264 | 782 | 1837 | 2949 | 170 | 143 | 1097 | 164 | 0 | 0 | 104.48
23:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 238 | 322 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 206 | 0 | 0 | 100 | 100 | 102 | 117 | 100 | 71 | 51 | 40 | 54 | 56 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 113 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 71 | 44 | 90 | 90 | 43 | 19 | 32 | 0 | 100 | 100 | 360 | 320 | 187 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 164 | 43 | 88 | 20 | 0 | 59 | 60 | 49 | 47 | 163 | 312 | 65 | 86 | 45 | 130 | 19 | 46 | 9 | 300 | 12 | 11 | 150 | 270 | 51 | 52 | 187 | 99 | 108 | 0 |  | 782 | 0 | 410 | 85 | 115 | 241 | 0 | 0 | 39 | 67 | 40 | 120 | 33 | 110 | 24 | 0 | 0 | 50 | 50 | 96 | 40 | 43 | 29 | 52 | 32 | 22 | 10 | 11 | 0 | 0 | 169 | 10 | 16 | 193 | 0 | 0 | 151 | 97 | 91 | 0 | 0 | 0 |  | 8199 | 3228 | 11427 | 4255 | 782 | 1866 | 2962 | 169 | 143 | 1086 | 164 | 0 | 0 | 104.48
24:00 | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 239 | 326 | 96 | 0 | 430 | 0 | 100 | 81 | 55 | 207 | 0 | 0 | 100 | 100 | 102 | 117 | 100 | 71 | 51 | 39 | 54 | 56 | 55 | 19 | 25 | 25 | 33 | 33 | 41 | 0 | 113 | 30 | 0 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 63 | 44 | 90 | 91 | 44 | 19 | 31 | 0 | 100 | 100 | 360 | 300 | 181 | 68 | 154 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 154 | 44 | 87 | 20 | 0 | 59 | 60 | 50 | 47 | 130 | 302 | 55 | 86 | 45 | 100 | 19 | 46 | 9 | 280 | 12 | 11 | 150 | 263 | 0 | 52 | 187 | 100 | 106 | 0 |  | 782 | 0 | 414 | 87 | 115 | 241 | 0 | 0 | 39 | 56 | 40 | 102 | 33 | 110 | 24 | 0 | 0 | 50 | 50 | 90 | 40 | 43 | 29 | 52 | 32 | 22 | 10 | 10 | 0 | 0 | 169 | 10 | 16 | 188 | 0 | 0 | 150 | 95 | 91 | 0 | 0 | 0 |  | 8000 | 3190 | 11190 | 4162 | 782 | 1815 | 2905 | 169 | 143 | 1060 | 154 | 0 | 0 | 104.48
KWH | 1689000 | 0 | 0 | 2828700 | 8141090 | 296386 | 0 | 6533220 | 7902000 | 1284100 | 0 | 9326312 | 0 | 2111040 | 1881552 | 1317612 | 4894820 | 0 | 0 | 1209600 | 2339520 | 1922544 | 2257440 | 1957038 | 1640640 | 643910 | 931680 | 1299960 | 1236346 | 1253000 | 403236 | 600000 | 559260 | 793800 | 792800 | 908832 | 0 | 2582676 | 654200 | 2200000 | 0 | 352080 | 3464276 | 0 | 2684376 | 0 | 0 | 891840 | 1160104 | 831109 | 1962120 | 2108160 | 993600 | 449568 | 348480 | 0 | 2513330 | 2274086 | 8977400 | 6929000 | 4542000 | 1672727 | 3604540 | 906264 | 152160 | 120000 | 0 | 1881552 | 399952 | 0 | 505008 | 183060 | 821900 | 505870 | 3264960 | 1052160 | 1381440 | 446256 | 15700 | 1336000 | 1407880 | 1090200 | 1097000 | 3245571 | 6883572 | 1402000 | 1962240 | 1011960 | 2415270 | 450000 | 1084280 | 214740 | 7397300 | 248616 | 255744 | 1259520 | 5780940 | 529709 | 637332 | 4466400 | 857350 | 2355840 | 104800 |  | 18663273 | 0 | 9842976 | 1611840 | 2046720 | 3867360 | 0 | 0 | 467040 | 580224 | 770250 | 2678000 | 663414 | 2674560 | 219868 | 0 | 0 | 388776 | 396373 | 1049720 | 1010620 | 1155936 | 373998 | 1064160 | 398516 | 509280 | 226476 | 237528 | 0 | 0 | 414360 | 91000 | 138000 | 4791300 | 0 | 0 | 942092 | 1674000 | 597120 | 0 | 0 | 0 |  | 179281656 | 59544780 | 238826436 | 101243906 | 18663273 | 41876078 | 56444911 | 414360 | 3236876 | 13561572 | 3264960 | 120500 | 0
Fuel Cost | 1452540 | 0 | 0 | 2432682 | 5210297.6 | 240072.66 | 0 | 3985264.2 | 4820220 | 12340201 | 0 | 6248629.04 | 0 | 13257331.2 | 12568767.36 | 8050609.32 | 3181633 | 0 | 0 | 18821376 | 14622000 | 12669564.96 | 21829444.8 | 12466332.06 | 9827433.6 | 10296120.9 | 6214305.6 | 9268714.8 | 7727162.5 | 7856310 | 302427 | 450000 | 0 | 0 | 0 | 8597550.72 | 0 | 0 | 0 | 2420000 | 0 | 3334197.6 | 2286422.16 | 0 | 3087032.4 | 0 | 0 | 7839273.6 | 12494320.08 | 8086690.57 | 12145522.8 | 13618713.6 | 6498144 | 382132.8 | 0 | 0 | 2287130.3 | 2069418.26 | 5565988 | 4781010 | 3179400 | 1154181.63 | 3460358.4 | 607196.88 | 130857.6 | 110400 | 0 | 1787474.4 | 4335479.68 | 0 | 388856.16 | 137295 | 632863 | 379402.5 | 22332326.4 | 789120 | 12695433.6 | 343617.12 | 0 | 1389440 | 1464195.2 | 1046592 | 987300 | 2531545.38 | 4818500.4 | 1598280 | 2099596.8 | 1113156 | 2753407.8 | 576000 | 1008380.4 | 199708.2 | 4734272 | 186462 | 194365.44 | 21827481.6 | 41969624.4 | 9179856.97 | 10866510.6 | 31934760 | 14617817.5 | 0 | 0 |  | 95182692.3 | 0 | 6594793.92 | 12910838.4 | 16967308.8 | 62187148.8 | 0 | 0 | 5258870.4 | 6835038.72 | 6069570 | 1847820 | 656779.86 | 19791744 | 7405154.24 | 0 | 0 | 4451485.2 | 4249118.56 | 9405491.2 | 8741863 | 10287830.4 | 3983078.7 | 10556467.2 | 4690533.32 | 560208 | 212887.44 | 179808.696 | 0 | 0 | 1599429.6 | 2932930 | 3694260 | 3258084 | 0 | 0 | 13811068.72 | 0 | 10348089.6 | 0 | 0 | 0 |  | 511194501.55 | 334670393.076 | 845864894.626 | 74673244.236 | 95182692.3 | 29642261.41 | 446784827.69 | 1599429.6 | 0 | 175650112.99 | 22332326.4 | 0 | 0
Yesterday Day Peak | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 309 | 335 | 13 | 0 | 430 | 0 | 100 | 64 | 55 | 200 | 0 | 0 | 0 | 96 | 84 | 90 | 86 | 71 | 21 | 40 | 54 | 53 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 95 | 30 | 110 | 0 | 16 | 136 | 0 | 100 | 0 | 0 | 40 | 8 | 15 | 68 | 83 | 36 | 19 | 2 | 0 | 130 | 90 | 360 | 300 | 182 | 70 | 150 | 37 | 5 | 5 | 0 | 85 | 0 | 0 | 19 | 8 | 33 | 21 | 106 | 41 | 80 | 20 | 2.4 | 57 | 59 | 44 | 44 | 163 | 303 | 62 | 82 | 43 | 118 | 18 | 44 | 9 | 290 | 11 | 11 | 0 | 220 | 0 | 0 | 180 | 0 | 92 | 18 |  | 777 | 0 | 410 | 85 | 97 | 120 | 0 | 0 | 0 | 0 | 40 | 110 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 0 | 43 | 0 | 22 | 8 | 11 | 0 | 0 | 169 | 0 | 0 | 182 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 9625.4 | DayPeak
Yesterday Evening Peak | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 356 | 332 | 96 | 0 | 430 | 0 | 92 | 81 | 55 | 204 | 0 | 0 | 100 | 80 | 102 | 117 | 100 | 70 | 50 | 40 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 41 | 0 | 112 | 30 | 0 | 0 | 16 | 150 | 0 | 130 | 0 | 0 | 40 | 71 | 42 | 90 | 90 | 43 | 19 | 9 | 0 | 100 | 90 | 360 | 272 | 207 | 68 | 150 | 42 | 5 | 5 | 0 | 85 | 49 | 0 | 22 | 8 | 33 | 21 | 164 | 43 | 80 | 20 | 0 | 57 | 59 | 49 | 47 | 163 | 300 | 46 | 85 | 45 | 130 | 19 | 45 | 9 | 285 | 12 | 11 | 200 | 200 | 215 | 98 | 187 | 100 | 108 | 0 |  | 782 | 0 | 410 | 92 | 99 | 233 | 0 | 0 | 40 | 55 | 40 | 100 | 32 | 110 | 22 | 0 | 0 | 50 | 52 | 99 | 40 | 50 | 29 | 43 | 33 | 22 | 11 | 11 | 0 | 0 | 170 | 12 | 18 | 188 | 0 | 0 | 150 | 96 | 94 | 0 | 0 | 0 |  | 11534 | EvPeak
Forecast for Evening | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 412 | 350 | 105 | 0 | 450 | 305 | 100 | 81 | 55 | 216 | 0 | 0 | 100 | 100 | 102 | 115 | 100 | 71 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 113 | 30 | 130 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 70 | 45 | 90 | 92 | 45 | 19 | 10 | 0 | 100 | 100 | 360 | 360 | 217 | 68 | 150 | 40 | 5 | 5 | 0 | 85 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 44 | 89 | 20 | 0 | 58 | 60 | 47 | 47 | 163 | 330 | 66 | 86 | 45 | 130 | 19 | 47 | 9 | 341 | 12 | 11 | 200 | 273 | 300 | 100 | 185 | 100 | 92 |  |  | 788 | 48 | 410 | 100 | 115 | 225 | 0 | 0 | 42 | 85 | 40 | 120 | 33 | 110 | 26 | 0 | 0 | 50 | 48 | 102 | 40 | 50 | 38 | 52 | 35 | 22 | 10 | 11 | 0 | 0 | 170 | 17 | 18 | 214 | 0 | 0 | 180 | 95 | 94 | 0
Forecast for Day | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 350 | 350 | 105 | 0 | 450 | 0 | 100 | 81 | 55 | 216 | 0 | 0 | 100 | 100 | 102 | 115 | 100 | 71 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 41 | 0 | 113 | 30 | 130 | 0 | 16 | 151 | 0 | 135 | 0 | 0 | 40 | 70 | 45 | 90 | 92 | 45 | 19 | 10 | 0 | 100 | 100 | 360 | 360 | 217 | 68 | 150 | 40 | 5 | 5 | 0 | 85 | 0 | 20 | 22 | 8 | 33 | 21 | 125 | 44 | 89 | 20 | 2 | 58 | 60 | 47 | 47 | 163 | 330 | 66 | 86 | 45 | 130 | 19 | 47 | 9 | 341 | 12 | 11 | 130 | 200 | 200 | 100 | 180 | 100 | 92 |  |  | 788 | 0 | 410 | 100 | 115 | 225 | 0 | 0 | 0 | 0 | 40 | 120 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 170 |  | 0 | 214 | 0 | 0 | 180 | 95 | 94 | 0
Generation at 08:00(Today) | 74 | 0 | 0 | 120 | 365 | 12 | 0 | 60 | 353 | 0 | 0 | 450 | 0 | 50 | 49 | 15 | 208 | 0 | 0 | 0 | 50 | 32 | 16 | 50 | 8 | 10 | 6 | 18 | 37 | 55 | 0 | 25 | 24 | 33 | 33 | 16 | 0 | 112 | 30 | 130 | 0 | 16 | 41 | 0 | 135 | 0 | 0 | 40 | 8 | 17 | 90 | 84 | 44 | 19 | 9 | 0 | 100 | 100 | 360 | 300 | 173 | 68 | 154 | 30 | 5 | 5 | 0 | 51 | 0 | 0 | 22 | 8 | 25 | 21 | 118 | 44 | 48 | 17 | 1 | 52 | 60 | 47 | 41 | 163 | 300 | 60 | 50 | 45 | 130 | 19 | 44 | 9 | 280 | 8 | 11 | 0 | 155 | 0 | 0 | 98 | 0 | 90 | 9.2 | 0 | 427 | 0 | 417 | 10 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 100 | 18 | 100 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 52 | 0 | 22 | 10 | 8 | 0 | 0 | 169 | 0 | 0 | 182 | 0 | 0 | 180 | 92 | 0 | 0 | 0 | 0 | 0
[93 empty] | 7416250 | 69152500 | 61736250 | [65 empty] | 199
| Minimum Generation |  | 8655.4 | 7:00
| Highest Generation |  | 11534 | 19:00
| Day Peak Generation |  | 9625.4 | 12:00
| Evening Peak Generation |  | 11534 | 19:00
| HVDC Max Flow |  | 783 | 20:00
| HVDC EvPeak Flow |  | 782 | 19:00
| Load factor L.F |  | 86.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-09-18
Till now the maximum generation is : - |  |  | 11534 MW | 19:00 | Hrs on | 2018-09-17
The Summary of Yesterday's |  | 2018-09-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9625.4 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8753.2 | MW
Evening Peak Generation : |  | 11534 | MW Hour : | 19:00 | Available Max Generation : |  | 12759 | MW
E.P. Demand (at gen end) : |  | 11534 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11534 | MW Hour : | 19:00 | Reserve(Generation end) |  | 959 | MW
Total Gen. (MKWH) : |  | 238.8264 | System Load Factor : | 86.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -600 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-09-18
Actual : | 104.4 | Ft.(MSL) , | Rule curve : | 102.91 | Ft.( MSL )
Gas Consumed : | Total = | 1220.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104315505.646
|  | Coal : | 1599429.6 | Oil : | 622434940.68 | Total : | 728349875.926
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4141.7534 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1409.8305 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1263.4118 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1141.688 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1031.6779 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 832.5311 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 463.7022 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 214.3065 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 642.098 |  |  | 0 | 0%
Total | 0 |  | 11140.9994 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Siddhirgang 210 MW ST
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Kaptai #5
3) Ghorasal Unit-3,4
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-2
7) Baghabari-71 MW
8) Ashuganj Unit-3
9) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Kaptai Unit-4 was shut down from 09:12 to 11:29 for maintenance work .
b) Mymensingh-Jamalpur 132 kV Ckt-2 tripped at 12:35 from both ends showing dist C-phase Z1 ralay from both
end and was switched on at 12:44.
c) Haripur-Norshingdi 132 kV Ckt tripped at 12:44 from both ends showing general trip ,Z1 at Narsindi end & |  |  |  | About 79 MW Power interruption occurred under Norshingdi S/S
Z1, BC-phase at Haripur end and was switched on at 12:52. |  |  |  | area from 12:44 to 12:52.
d) After maintenance Haripur EGCB 412 MW ST was synchronized at 08:14 and tripped at 21:04 showing E/F
and again synchronized at 08:04(18/09/2018).
e) Sirajganj Unit-2 GT & ST were synchronized at 17:13 & 03:02(18/09/2018) respectively.
f) Raozan Unit-1 tripped at 18:59 due to tripping of boiler and was synchronized at 00:25(18/09/2018).
g) Khulshi 33 kV indoor bus tripped at 14:52 showing O/C Relay and was switched on at 15:22. |  |  |  | About 90 MW Power interruption occurred under Khulshi S/S
area from 14:52 to 15:22.
h) Naogaon-Bogura 132 kV Ckt-1 was switched on at 22:48 from Bogura end.
i) Barisal(S)-Patuakhali 132 kV Ckt tripped at 21:08 from Barisal(S) end showing O/C Relay and was |  |  |  | About 56 MW Power interruption occurred under Patuakhali S/S
switched on at 21:15. |  |  |  | area from 21:08 to 21:15.
j) Bagerhat 132/33 kV T1 & T3 transformers were shut down at 07:08(18/09/2018) due to 33 kV |  |  |  | About 35 MW Power interruption occurred under Bagerhat S/S
bus isolator clamp R-phase red hot and were switched on at 08:21 & 08:23 respectively. |  |  |  | area from 07:08 to 08:21(18/09/2018).
k) Madaripur 132/33 kV T1 transformer was shut down at 07:56(18/09/2018) due to oil leakage |  |  |  | About 10 MW Power interruption occurred under Madaripur S/S
of 33 kV B-phase bushing. |  |  |  | area from 07:56 (18/09/2018) to till now.
l) Tongi 132/33 kV T3 transformer was shut down at 07:40(18/09/2018) for D/W. |  |  |  | About 24 MW Power interruption occurred under Tongi S/S
area from 07:40(18/09/2018) to till now.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-09-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 74 | 1689000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2828700 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8141090
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 296386 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 356 | 6533220 | Gas shortage
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 96 | 1284100 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 332 | 7902000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 9326312 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 92 | 2111040 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 81 | 1881552 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1317612
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1957038
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 403236
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 1209600
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 80 | 2339520 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 204 | 4894820
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 50 | 643910
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1922544
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 931680 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1299960
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 117 | 2257440 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 1236346
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1253000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 70 | 1640640 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1159260 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 793800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 792800
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 41 | 908832 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 200 | 5780940 | Engine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 300 | 215 | 529709 | Low demand
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 98 | 637332
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 857350
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 108 | 2355840 | Engine problem
| Dhaka area Total |  |  |  | 5848 | 3936 | 79116609
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 2200000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 352080 | Engine problem
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 28MW | 0 | 0 | 104800
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 43 | 993600 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 142 | 3236876 | unit # 05 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 150 | 3464276 | Gas shortage
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2684376
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 891840 | Engine problem
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 71 | 1160104
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 42 | 831109
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1962120 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 449568
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 348480
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 90 | 2108160 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 842 | 20787389
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2513330 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 2274086 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 207 | 4542000
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8977400
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 272 | 6929000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 906264 | Gas shortage
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 152160 | Gas shortage
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 1672727 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Development work
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1881552
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 399952
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 150 | 3604540
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505008
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 183060 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 164 | 3264960
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 821900
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Line over load
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 505870
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 200 | 1259520
| Comilla Area Total |  |  |  | 2541 | 1881 | 40513329
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 43 | 1052160 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 446256
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 80 | 1381440 | Engine problem
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 15700
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 187 | 4466400 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 330 | 7361956
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 57 | 1336000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 59 | 1407880
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3245571
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 300 | 6883572 | FGMO.
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 49 | 1090200
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 1097000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 255744
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 46 | 1402000 | Frequency control.
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 85 | 1962240
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 1011960
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 130 | 2415270
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 450000
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 45 | 1084280
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 12 | 248616 | Engine problem
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 285 | 7397300 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 214740
| Sylhet Area Total |  |  |  | 1549 | 1362 | 31502373
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 782 | 18663273
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 92 | 1611840 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2046720 | Engine problem
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 467040
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 233 | 3867360
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 55 | 580224
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9842976
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 770250
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 94 | 597120 | Engine problem
| Khulna Area Total |  |  |  | 2214 | 1845 | 38446803
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2674560
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 22 | 219868
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 32 | 663414
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 100 | 2678000
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 1674000
| Barisal Area Total |  |  |  | 462 | 360 | 7909842
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 388776
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 52 | 396373
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 1010620 | Engine problem
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 1155936
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 29 | 373998
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 188 | 4791300 | FGMO
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 150 | 0
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 141 | 0 | 0 | On test
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*272+1*132 MW | 0 | 0 | 0 | On test
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 33 | 398516
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 509280
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 226476 | Engine problem
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237528
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 1064160 | Engine problem
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 99 | 1049720
| Rajshahi Area Total |  |  |  | 1264 | 778 | 11602683
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 170 | 414360 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 12 | 91000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 138000
| Rangpur Area Total |  |  |  | 484 | 200 | 643360
| Total |  |  |  | 16445 | 11534 | 237884344
| Eastern Grid Total |  |  |  | 12021 | 8351 | 179281656
| Western Grid Total |  |  |  | 4424 | 3183 | 58602688
| National Grid Total |  |  |  | 16445 | 11534 | 237884344
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-09-17 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7581 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3296 | MW
i) Dhaka area |  |  | 4143 | MW | i) Khulna area |  |  | 1339 | MW
ii) Chittagong area |  |  | 1129 | MW | ii) Rajshahi area |  |  | 1131 | MW
iii) Comilla area |  |  | 1033 | MW | iii) Barisal area |  |  | 272 | MW
iv) Mymensingh area |  |  | 794 | MW | iv) Rangpur area |  |  | 554 | MW
v) Sylhet area |  |  | 482 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10877 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 146 | 1600 | Netrokona | 85 | 2000 | Central s/s | 81 | 2200
Munsiganj | 110 | 1930 | Jamalpur | 123 | 2000 | Noapara | 96 | 1900
Sonargaon | 50 | 2000 | Sherpur | 82 | 1930 | Jessore | 154 | 2100
Shyampur | 173 | 1100 | Srimongal | 39 | 1930 | Jhenida | 95 | 2200
Bhulta | 180 | 100 | Shahjibazar | 113 | 2000 | Bottail | 132 | 1900
Madanganj | 52 | 1830 | Fenchuganj | 49 | 1900 | G.K Project | 57 | 2000
Shitalakhya | 105 | 1600 | Kulawara | 45 | 2200 | Faridpur | 160 | 2300
Rahim steel | 10 | 1100 | Sylhet | 143 | 1830 | Madaripur | 144 | 2100
Matuail | 92 | 100 | Chatak | 28 | 1830 | Gopalganj | 88 | 2200
Ghorasal | 80 | 2200 | Sunamganj | 37 | 1900 | Bagerhat | 83 | 1930
Narsingdi | 124 | 2000 | Biani Bazar | 43 | 1830 | Mongla | 38 | 1100
Haripur (SBU) | 109 | 1600 | Comilla (S) | 170 | 2000 | Satkhira | 101 | 1930
Ullon | 101 | 2300 | Comilla(N) | 129 | 1900 | Gallamari | 50 | 1300
Hasnabad | 220 | 2100 | Chandpur | 116 | 2100 | Magura | 52 | 1900
Magbazar | 145 | 1600 | Feni | 130 | 2200 | Chuadanga | 85 | 2000
Maniknagar | 108 | 1600 | Chowmuhani | 182 | 1830 | Barisal | 124 | 2000
Bangabhaban | 42 | 1600 | Ashuganj | 60 | 2200 | Patuakhali | 91 | 2000
Narinda | 88 | 1500 | Daudkandi | 111 | 2000 | Bhandaria | 50 | 1900
Dhanmondi | 160 | 1300 | B.Baria | 141 | 2000 | Ishurdi | 57 | 1830
Lalbag | 95 | 1600 | Ramganj | 38 | 1900 | Ruppur Paromanobik | 2 | 1700
Madartek | 56 | 2300 | Madunaghat | 56 | 1900 | Natore | 113 | 2000
Mirpur | 113 | 1800 | Hathazari | 91 | 2100 | Bogra | 245 | 1900
Kalyanpur | 129 | 1900 | Khulshi | 194 | 1200 | Noagaon | 96 | 1930
Gulshan | 158 | 1300 | Halishahar | 148 | 1500 | Rajshahi | 152 | 2000
Uttara | 100 | 1600 | Baraulia | 147 | 1000 | C.Nawabganj | 69 | 2100
Uttara(New) | 7 | 1200 | Sikalbaha | 36 | 2100 | Amnura | 39 | 1900
Kamrangirchar | 78 | 1900 | Dohazari | 86 | 1830 | Pabna | 120 | 1900
Savar | 130 | 1600 | Cox'sbazar | 75 | 1900 | Shahjadpur | 89 | 2000
Bhasantec | 175 | 1700 | Chandraghona | 31 | 2100 | Serajganj | 100 | 1930
Agargaon | 51 | 1700 | Kaptai | 5 | 1900 | Niyamatpur | 47 | 1900
Satmosjid | 113 | 1900 | A. Khaer Stl. | 12 | 1100 | Joypurhat | 39 | 1900
Tongi | 150 | 1800 | Bakulia | 115 | 1930 | Rangpur | 118 | 1930
Kabirpur | 215 | 1830 | Julda | 22 | 900 | Lalmonirhat | 86 | 1830
Basundhara | 130 | 1500 | TK chemical | 5 | 1000 | Saidpur | 109 | 1830
Manikganj | 100 | 2100 | Modern Steel | 15 | 100 | Purbasadipur | 77 | 1930
Joydevpur | 233 | 2200 | Shahmirpur | 30 | 600 | Thakurgaon | 60 | 100
New Tongi | 109 | 900 | Khagrachhari | 21 | 2100 | Palashbari | 97 | 100
Korda | 258 | 2100 | Matarbari | 26 | 1930 | Barapukuria | 50 | 1930
Dhamrai | 52 | 2100 | Baroiar Hat | 11 | 1830 | Panchagar | 36 | 1830
Tangail | 180 | 2100 | Abul Khair 230 | 180 | 100
Mymensing | 252 | 1830 | BSRM | 118 | 700
Kishorganj | 100 | 1900 | Goalpara | 40 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-09-17
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 392 | 6:00 | 380 | 19:00 | Kaliakoir | 374 | 7:00 | 356 | 18:30
Bheramara | 410 | 8:00 | 394 | 21:00 | Bhulta | 384 | 4:00 | 371 | 17:00
Ashuganj(N) | 390 | 8:00 | 381 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 220 | 5:00 | 210 | 10:00
Ishurdi | 235 | 9:00 | 223 | 18:30 | Megnaghat | 226 | 3:00 | 220 | 10:00
Ashuganj | 235 | 5:00 | 230 | 11:00 | Fenchuganj | 236 | 7:00 | 232 | 18:30
Serajganj | 223 | 18:00 | 213 | 1:00 | Siddhirganj | 224 | 4:00 | 217 | 12:00
Baghabari | 222 | 4:00 | 215 | 1:00 | Maniknagar | 223 | 5:00 | 215 | 15:00
Barapukuria | 230 | 7:00 | 217 | 18:30 | Old Airport | 224 | 3:00 | 214 | 12:00
Bogra | 218 | 9:00 | 203 | 21:00 | Barisal | 228 | 9:00 | 211 | 21:00
Khulna South | 235 | 9:00 | 223 | 19:30 | AKSML | 219 | 6:00 | 206 | 10:00
Rampura | 222 | 4:00 | 217 | 12:00 | BSRM | 222 | 6:00 | 210 | 10:00
Haripur | 222 | 1:00 | 218 | 12:00 | Bibiyana | 235 | 9:00 | 226 | 19:30
Hasnabad | 225 | 4:00 | 217 | 12:00 | Bhulta | 224 | 3:00 | 217 | 11:00
Aminbazar | 225 | 4:00 | 216 | 11:00 | Ashuganj (S) | 233 | 6:00 | 227 | 18:30
Tongi | 224 | 7:00 | 212 | 18:30 | Kaliakoir | 229 | 7:00 | 219 | 18:30
Comilla (N) | 231 | 6:00 | 225 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1930 | 130 | 1000 | Ramganj | 123 | 1100 | 113 | 1830
Munsiganj | 135 | 1800 | 131 | 1100 | Madanhat | 130 | 400 | 125 | 1000
Megnaghat | 133 | 100 | 128 | 1200 | Hathazari | 130 | 500 | 123 | 1000
Shyampur | 132 | 1830 | 124 | 1100 | Khulshi | 127 | 600 | 120 | 1000
Bhulta | 131 | 900 | 128 | 1100 | Halishahar | 131 | 600 | 122 | 1200
Madanganj | 138 | 100 | 132 | 900 | Baraulia | 127 | 300 | 121 | 1000
Shitalakhya | 139 | 300 | 132 | 1000 | Sikalbaha | 131 | 600 | 122 | 1000
Rahim steal | 134 | 100 | 130 | 1000 | Dohazari | 126 | 500 | 122 | 1100
Matuail | 133 | 100 | 128 | 1100 | Cox'sbazar | 121 | 500 | 111 | 1830
Ghorasal | 136 | 100 | 134 | 2000 | Chandraghona | 130 | 600 | 115 | 1000
Narsinghdi | 128 | 400 | 124 | 1000 | Kaptai | 130 | 700 | 127 | 1000
Haripur (SBU) | 134 | 1800 | 130 | 1000 | A. Khaer Stl. | 125 | 700 | 124 | 1000
Ullon | 133 | 800 | 126 | 1200 | Bakulia | 127 | 400 | 122 | 1000
Hasnabad | 135 | 500 | 130 | 1400 | Julda | 129 | 700 | 123 | 1100
Magbazar | 134 | 600 | 125 | 1200 | TK Chemical | 130 | 900 | 125 | 1000
Maniknagar | 131 | 600 | 127 | 1300 | Modern Steel | 128 | 600 | 121 | 1000
Bangabhaban | 131 | 600 | 127 | 1300 | Shahmirpur | 129 | 600 | 123 | 1100
Narinda | 131 | 600 | 127 | 1300 | Khagrachhari | 129 | 300 | 116 | 2100
Dhanmondi | 131 | 600 | 127 | 1300 | Matarbari | 123 | 900 | 115 | 1830
Lalbag | 133 | 500 | 125 | 1200 | Baroiar Hat | 126 | 800 | 120 | 2000
Madartek | 135 | 600 | 126 | 1200 | Goalpara | 138 | 1700 | 132 | 1830
Mirpur | 136 | 600 | 128 | 1500 | Central s/s | 138 | 1700 | 132 | 500
Kalyanpur | 136 | 600 | 129 | 1200 | Noapara | 136 | 1100 | 129 | 500
Gulshan | 135 | 500 | 126 | 1200 | Jessore | 130 | 1700 | 121 | 2100
Uttara | 132 | 600 | 124 | 1100 | Jhenida | 130 | 1800 | 118 | 1830
Uttara(New) | 132 | 600 | 124 | 1200 | Bottail | 135 | 700 | 127 | 1830
Kamrangirchar | 137 | 400 | 130 | 1200 | G.K.Project | 142 | 900 | 134 | 2000
Savar | 134 | 600 | 126 | 1200 | Faridpur | 132 | 900 | 122 | 100
Bhasantec | 136 | 600 | 127 | 1200 | Madaripur | 134 | 800 | 121 | 1830
Agargaon | 137 | 400 | 130 | 1200 | Gopalganj | 133 | 900 | 119 | 1830
Satmosjid | 137 | 600 | 128 | 1200 | Bagerhat | 136 | 1100 | 128 | 1830
Tongi | 134 | 800 | 125 | 1800 | Mongla | 132 | 1100 | 123 | 100
Kabirpur | 134 | 500 | 125 | 1830 | Satkhira | 136 | 900 | 128 | 1830
Basundhara | 131 | 2400 | 123 | 1830 | Gallamari | 138 | 900 | 132 | 500
Manikganj | 134 | 600 | 125 | 2100 | Magura | 130 | 1700 | 115 | 1900
Joydevpur | 141 | 300 | 133 | 1830 | Chuadanga | 125 | 1700 | 109 | 2000
New Tongi | 133 | 300 | 125 | 1830 | Barisal | 138 | 900 | 131 | 100
Kodda | 137 | 1830 | 132 | 700 | Patuakhali | 135 | 800 | 125 | 2100
Dhamrai | 133 | 800 | 124 | 1830 | Bhandaria | 136 | 1700 | 126 | 1830
Tangail | 134 | 700 | 120 | 1830 | Ishurdi | 140 | 1100 | 131 | 1830
Mymensing | 130 | 700 | 116 | 1930 | Ruppur Paromanobik | 141 | 900 | 133 | 1830
Kishorganj | 130 | 700 | 118 | 1830 | Natore | 136 | 900 | 124 | 1830
Netrokona | 130 | 700 | 110 | 1930 | Bogra | 129 | 900 | 117 | 2100
Jamalpur | 136 | 1200 | 122 | 2200 | Noagaon | 125 | 1800 | 107 | 2100
Sherpur | 135 | 1200 | 121 | 2200 | Rajshahi | 133 | 600 | 123 | 2100
Srimongal | 139 | 700 | 132 | 1830 | C.Nawabganj | 130 | 600 | 122 | 2100
Shahjibazar | 138 | 900 | 131 | 1830 | Amnura | 133 | 1700 | 122 | 1830
Fenchuganj | 136 | 600 | 132 | 2200 | Pabna | 132 | 900 | 124 | 1900
Khulawara | 136 | 700 | 131 | 2000 | Shahjadpur | 138 | 700 | 130 | 1830
Sylhet | 135 | 700 | 131 | 1830 | Serajganj | 130 | 600 | 122 | 1900
Chatak | 134 | 600 | 129 | 1930 | Niyamatpur | 123 | 1700 | 104 | 1830
Sunamganj | 133 | 600 | 127 | 2000 | Joypurhat | 125 | 1800 | 106 | 1830
Biani Bazar | 135 | 700 | 128 | 1830 | Rangpur | 119 | 1700 | 103 | 1830
Comilla(s) | 128 | 900 | 121 | 1700 | Lalmonirhat | 113 | 600 | 95 | 1830
Comilla(n) | 136 | 700 | 133 | 1400 | Saidpur | 119 | 700 | 101 | 1830
Chandpur | 128 | 700 | 123 | 1800 | Purbasadipur | 129 | 700 | 112 | 1830
Feni | 120 | 700 | 115 | 2000 | Thakurgaon | 120 | 500 | 104 | 100
Chowmuhani | 121 | 900 | 112 | 2200 | Palashbari | 120 | 900 | 105 | 1830
Ashuganj | 139 | 700 | 133 | 1930 | Barapukuria | 130 | 700 | 117 | 1830
Daudkandi | 134 | 2000 | 126 | 1200 | Panchagar | 117 | 600 | 95 | 1830
B.Baria | 137 | 600 | 129 | 1830

## L-Curve
Date | 2018-09-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 350 | 8000 | 3190 | 11190 |  |  |  | QF-LDC-12
0:30 | 435 | 7888 | 2999.5 | 10887.5 | Date: | 2018-09-17
1:00 | 520 | 7776 | 2809 | 10585
1:30 | 560 | 7709.5 | 2767.5 | 10477
2:00 | 600 | 7643 | 2726 | 10369
2:30 | 590 | 7606 | 2699.5 | 10305.5 | [5 empty] | Gen. at Eve. Peak | 11534 | 11534 MW (19:00 )
3:00 | 580 | 7569 | 2673 | 10242 | [6 empty] | 19:00
3:30 | 570 | 7476.5 | 2625.5 | 10102 | [5 empty] | Gen. at Day Peak | 9625.4 | 9625.4 MW (12:00 )
4:00 | 560 | 7384 | 2578 | 9962 | [6 empty] | 12:00
4:30 | 540 | 7344 | 2503.5 | 9847.5 | [5 empty] | Highest Generation | 11534
5:00 | 520 | 7304 | 2429 | 9733 | [6 empty] | 19:00
5:30 | 470 | 7071.5 | 2339 | 9410.5
6:00 | 420 | 6839 | 2249 | 9088
6:30 | 400 | 6650.2 | 2221.5 | 8871.7
7:00 | 380 | 6461.4 | 2194 | 8655.4
7:30 | 335 | 6485.25 | 2193.5 | 8678.75
8:00 | 290 | 6509.1 | 2193 | 8702.1
8:30 | 195 | 6595.85 | 2228.5 | 8824.35
9:00 | 100 | 6682.6 | 2264 | 8946.6
9:30 | 70 | 6837.4 | 2272 | 9109.4
10:00 | 40 | 6992.2 | 2280 | 9272.2
10:30 | 55 | 7067.8 | 2297 | 9364.8
11:00 | 70 | 7143.4 | 2314 | 9457.4
11:30 | 155 | 7207.4 | 2334 | 9541.4
12:00 | 240 | 7271.4 | 2354 | 9625.4
12:30 | 280 | 7250.8 | 2341.5 | 9592.3
13:00 | 320 | 7230.2 | 2329 | 9559.2
13:30 | 320 | 7330.3 | 2350 | 9680.3
14:00 | 320 | 7430.4 | 2371 | 9801.4
14:30 | 340 | 7532.1 | 2388 | 9920.1
15:00 | 360 | 7633.8 | 2405 | 10038.8
15:30 | 355 | 7662.45 | 2384.5 | 10046.95
16:00 | 350 | 7691.1 | 2364 | 10055.1
16:30 | 185 | 7502.95 | 2384 | 9886.95
17:00 | 20 | 7314.8 | 2404 | 9718.8
17:30 | 60 | 7159.4 | 2526.5 | 9685.9
18:00 | 100 | 7004 | 2649 | 9653
18:30 | 255 | 7677.5 | 2916 | 10593.5
19:00 | 410 | 8351 | 3183 | 11534
19:30 | 420 | 8274 | 3198 | 11472
20:00 | 420 | 8245 | 3238 | 11483 |  |  |  | Executive Engineer
20:30 | 410 | 8249.5 | 3220 | 11469.5 |  |  |  | Network Operation Division
21:00 | 400 | 8254 | 3202 | 11456
21:30 | 380 | 8213 | 3218 | 11431
22:00 | 360 | 8172 | 3234 | 11406 |  |  |  |  | Page 6 of 7
22:30 | 340 | 8185.5 | 3231 | 11416.5
23:00 | 320 | 8199 | 3228 | 11427
23:30 | 335 | 8099.5 | 3209 | 11308.5
24:00 | 350 | 8000 | 3190 | 11190
11534 MW (19:00 )
9625.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-09-17 |  | Energy | 238826436
[10 empty] | 2018-09-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4162 | 782 | 1815 | 2905 | 169 | 143 | 1060 | 0 | 154
0:30 | 4221.5 | 780 | 1800 | 2684.5 | 169.5 | 142 | 933 | 0 | 157 | Date: | 2018-09-17
1:00 | 4281 | 778 | 1785 | 2464 | 170 | 141 | 806 | 0 | 160
1:30 | 4288.5 | 778.5 | 1791.5 | 2401.5 | 170 | 141 | 746 | 0 | 160 | [7 empty] | Total Energy | 238.8264 | Total Energy Gen 238.826 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 238.826 MKWHr
2:00 | 4296 | 779 | 1798 | 2339 | 170 | 141 | 686 | 0 | 160 | [7 empty] | Energy not Served | 0
2:30 | 4296 | 778.5 | 1805 | 2299 | 169.5 | 141 | 658.5 | 0 | 158 | [7 empty] | Energy Requirement | 238.8264
3:00 | 4296 | 778 | 1812 | 2259 | 169 | 141 | 631 | 0 | 156
3:30 | 4279 | 778.5 | 1814 | 2194 | 169.5 | 141 | 571 | 0 | 155 | [6 empty] | Shortage
4:00 | 4262 | 779 | 1816 | 2129 | 170 | 141 | 511 | 0 | 154
4:30 | 4256.5 | 779 | 1822 | 2042 | 170 | 141 | 483 | 0 | 154
5:00 | 4251 | 779 | 1828 | 1955 | 170 | 141 | 455 | 0 | 154
5:30 | 4214.5 | 778.5 | 1733.5 | 1838.5 | 170.5 | 141.5 | 388.5 | 0 | 145
6:00 | 4178 | 778 | 1639 | 1722 | 171 | 142 | 322 | 0 | 136
6:30 | 4072 | 778.5 | 1653 | 1672.5 | 170.5 | 143 | 253 | 0 | 129 |  |  |  |  | Coal
7:00 | 3966 | 779 | 1667 | 1623 | 170 | 144 | 184 | 0 | 122
7:30 | 3991.5 | 778 | 1659.5 | 1629.5 | 170 | 143.5 | 184 | 0 | 122 |  |  |  | Oil |  |  |  | ,
8:00 | 4017 | 777 | 1652 | 1636 | 170 | 143 | 184 | 0 | 122
8:30 | 4007 | 777 | 1661 | 1734.5 | 170 | 143 | 224.5 | 0 | 106
9:00 | 3997 | 777 | 1670 | 1833 | 170 | 143 | 265 | 0 | 90
9:30 | 4096.5 | 777 | 1712 | 1884.5 | 169.5 | 128 | 245 | 0 | 95
10:00 | 4196 | 777 | 1754 | 1936 | 169 | 113 | 225 | 0 | 100
10:30 | 4224.5 | 777.5 | 1753 | 1996 | 169 | 104 | 225 | 0 | 106
11:00 | 4253 | 778 | 1752 | 2056 | 169 | 95 | 225 | 0 | 112
11:30 | 4281 | 777.5 | 1762.5 | 2084.5 | 169 | 110 | 229 | 0 | 109
12:00 | 4309 | 777 | 1773 | 2113 | 169 | 125 | 233 | 0 | 106
12:30 | 4254.5 | 777 | 1769.5 | 2111 | 169 | 125 | 262.5 | 0 | 104
13:00 | 4200 | 777 | 1766 | 2109 | 169 | 125 | 292 | 0 | 102
13:30 | 4200 | 777 | 1766 | 2109 | 169 | 125 | 292 | 0 | 102
14:00 | 4200 | 777 | 1766 | 2109 | 169 | 125 | 292 | 0 | 102
14:30 | 4192 | 777 | 1764.5 | 2330.5 | 169.5 | 128.5 | 320 | 0 | 104
15:00 | 4184 | 777 | 1763 | 2552 | 170 | 132 | 348 | 0 | 106
15:30 | 4157.5 | 777 | 1760.5 | 2567 | 170 | 134.5 | 367.5 | 0 | 106
16:00 | 4131 | 777 | 1758 | 2582 | 170 | 137 | 387 | 0 | 106
16:30 | 4132 | 777 | 1708 | 2438.5 | 170 | 137 | 398 | 0 | 121
17:00 | 4133 | 777 | 1658 | 2295 | 170 | 137 | 409 | 0 | 136
17:30 | 4041.5 | 777 | 1544.5 | 2295.5 | 170 | 140 | 572.5 | 0 | 143
18:00 | 3950 | 777 | 1431 | 2296 | 170 | 143 | 736 | 0 | 150
18:30 | 4106 | 779.5 | 1633 | 2701.5 | 170 | 142.5 | 904 | 0 | 157
19:00 | 4262 | 782 | 1835 | 3107 | 170 | 142 | 1072 | 0 | 164
19:30 | 4244 | 782 | 1798 | 3080 | 170 | 142 | 1088 | 0 | 168
20:00 | 4251 | 783 | 1780 | 3077 | 170 | 142 | 1110 | 0 | 170
20:30 | 4261 | 782.5 | 1785 | 3062.5 | 170 | 142.5 | 1099 | 0 | 167
21:00 | 4271 | 782 | 1790 | 3048 | 170 | 143 | 1088 | 0 | 164
21:30 | 4267.5 | 782 | 1813.5 | 2998.5 | 170 | 143 | 1092.5 | 0 | 164
22:00 | 4264 | 782 | 1837 | 2949 | 170 | 143 | 1097 | 0 | 164
22:30 | 4259.5 | 782 | 1851.5 | 2955.5 | 169.5 | 143 | 1091.5 | 0 | 164
23:00 | 4255 | 782 | 1866 | 2962 | 169 | 143 | 1086 | 0 | 164
23:30 | 4208.5 | 782 | 1840.5 | 2933.5 | 169 | 143 | 1073 | 0 | 159 | Max Temp. in Dhaka |  | 35.6° C
24:00 | 4162 | 782 | 1815 | 2905 | 169 | 143 | 1060 | 0 | 154
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 238.826 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 238.826 MKWHr
Note on W13: Author:

## Generation
2018-09-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 111 | 111 | 111 | 111 | 111 | 112 | 114 | 113 | 113 | 113 | 95 | 95 | 95 | 111 | 102 | 107 | 107 | 113 |  | 112 | 112 | 112 | 113 | 113 | 113 | 113 | 2582676
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 654200
3 | Chittagong ST-1 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 0 | 0 | [5 empty] | 2200000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 352080
| Teknaf Solartech 20MW | [9 empty] | 0 | 15 | 18 | 17 | 4.2 | 5.8 | 6.5 | 3.5 | 0 | [8 empty] | 104800
6 | Sikalbaha 225MW (Gas) | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 136 | 136 | 127 | 137 | 135 | 135 | 135 | 150 |  | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 3464276
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 130 | 135 | 135 | 135 | 135 | 135 | 135 | 2684376
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 45 | 45 | 45 | 45 | 45 | 31 | 16 | 16 | 15 | 15 | 15 | 15 | 24 | 39 | 40 | 40 | 40 | 41 |  | 42 | 42 | 42 | 42 | 42 | 44 | 44 | 831109
12 | Hathazari peaking | 72 | 72 | 72 | 72 | 72 | 72 | 8 | 8 | 8 | 8 | 8 | 8 | 31 | 30 | 31 | 70 | 65 | 65 |  | 71 | 71 | 71 | 71 | 71 | 71 | 63 | 1160104
| Daudkandi bangla trak | [13 empty] | 11 | 100 | 100 | 10 | 10 |  | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 1259520
14 | Daudkandi Peaking 52MW | 41 | 0 | [14 empty] | 0 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 399952
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 209 | 209 | 211 | 212 | 201 | 212 | 210 | 208 | 209 | 205 | 201 | 200 | 200 | 180 | 196 | 200 | 199 | 120 |  | 204 | 204 | 204 | 206 | 205 | 206 | 207 | 4894820
18 | Summit Gazipur | 265 | 265 | 265 | 270 | 270 | 270 | 270 | 271 | 270 | 225 | 223 | 220 | 203 | 190 | 190 | 190 | 170 | 173 |  | 200 | 200 | 255 | 270 | 270 | 270 | 263 | 5780940
19 | Ashuganj 195MW Modular | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 70 | 78 | 78 | 78 | 69 | 69 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1672727
20 | Ghorasal ST: Unit-1,2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1689000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2828700
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 340 | 340 | 340 | 340 | 300 | 377 | 365 | 310 | 310 | 310 | 310 | 310 | 250 |  | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 8141090
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 150 | 150 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2513330
30 | Ashuganj ST: Unit- 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 120 | 120 | 90 | 90 | 90 |  | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 2274086
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 34 | 34 | 34 | 32 | 37 | 40 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 906264
33 | Ashuganj CCPP 225 MW | 185 | 182 | 182 | 182 | 182 | 182 | 184 | 188 | 182 | 194 | 182 | 182 | 183 | 186 | 170 | 175 | 200 | 205 |  | 207 | 214 | 184 | 178 | 195 | 187 | 181 | 4542000
34 | Ashuganj CCPP(South) | 276 | 276 | 276 | 272 | 276 | 256 | 257 | 264 | 257 | 316 | 300 | 300 | 301 | 301 | 301 | 272 | 272 | 290 |  | 272 | 279 | 276 | 301 | 331 | 320 | 300 | 6929000
| Ashuganj CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8977400
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 152160
36 | Chandpur CCPP | 152 | 155 | 153 | 154 | 150 | 154 | 156 | 156 | 155 | 155 | 155 | 150 | 152 | 141 | 150 | 150 | 150 | 153 |  | 150 | 150 | 154 | 153 | 154 | 154 | 154 | 3604540
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 255 | 262 | 268 | 273 | 275 | 247 | 36 | 69 | 138 | 261 | 326 | 309 | 304 | 300 | 315 | 342 | 335 | 300 |  | 356 | 351 | 352 | 351 | 244 | 238 | 239 | 6533220
40 | Meghnaghat CCPP 450MW | 430 | 430 | 450 | 450 | 450 | 380 | 380 | 380 | 380 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 330 |  | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 9326312
41 | Haripur Power CCPP 360MW | 326 | 340 | 346 | 351 | 352 | 301 | 301 | 301 | 353 | 347 | 345 | 335 | 332 | 336 | 327 | 326 | 326 | 326 |  | 332 | 332 | 332 | 332 | 322 | 322 | 326 | 7902000
42 | Mymensingh RPCL 210MW | 47 | 47 | 47 | 47 | 47 | 48 | 46 | 44 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 43 | 42 |  | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 1052160
43 | Haripur NEPC 110MW | 96 | 96 | 24 | 13 | 0 | [5 empty] | 13 | 13 | 77 | 80 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1284100
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | 57 | 60 | 60 | 60 | 59 | 59 | 59 | 1336000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 59 | 59 |  | 59 | 59 | 59 | 59 | 59 | 60 | 60 | 1407880
46 | Shajibazar 330 MW | 300 | 307 | 301 | 302 | 304 | 311 | 304 | 310 | 302 | 312 | 300 | 303 | 305 | 305 | 302 | 301 | 300 | 308 |  | 300 | 301 | 309 | 301 | 313 | 312 | 302 | 6883572
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 61 | 63 | 56 | 56 | 65 | 63 | 63 | 36 | 63 | 59 | 62 | 40 | 63 | 52 | 52 | 40 | 63 |  | 46 | 55 | 64 | 59 | 64 | 65 | 55 | 1402000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 86 | 86 | 82 | 86 | 83 | 84 | 80 | 40 | 20 |  | 85 | 85 | 86 | 86 | 84 | 86 | 86 | 1962240
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 20 | 20 |  | 45 | 45 | 45 | 46 | 45 | 45 | 45 | 1011960
50 | Sylhet GT 150 MW | 107 | 107 | 107 | 107 | 107 | 77 | 79 | 79 | 79 | 100 | 98 | 118 | 99 | 128 | 78 | 78 | 78 | 80 |  | 130 | 90 | 87 | 97 | 117 | 130 | 100 | 2415270
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450000
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 47 | 45 | 45 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 |  | 45 | 46 | 46 | 46 | 47 | 46 | 46 | 1084280
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 214740
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255744
55 | Fenchugonj (Barakatullah) 51MW | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 42 | 44 | 44 | 47 | 47 | 47 | 47 | 47 | 23 |  | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 1090200
56 | Shahjahanulla 25 MW | 12 | 12 | 12 | 12 | 12 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 12 | 12 | 11 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 248616
57 | Summit Bibiana- 2 | 295 | 300 | 290 | 280 | 290 | 260 | 300 | 300 | 275 | 290 | 290 | 290 | 280 | 270 | 280 | 270 | 265 | 265 |  | 285 | 305 | 280 | 300 | 310 | 300 | 280 | 7397300
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1253000
59 | Sikalbaha (Energis) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 32 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 891840
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 449568
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 403236
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 446256
63 | Tripura | 160 | 160 | 156 | 154 | 154 | 136 | 122 | 122 | 90 | 100 | 112 | 106 | 102 | 108 | 106 | 106 | 136 | 150 |  | 164 | 168 | 170 | 164 | 164 | 164 | 154 | 3264960
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 31 | 31 | 30 | 21 | 8 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 6 | 5 |  | 9 | 15 | 19 | 25 | 28 | 32 | 31 | 348480
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505008
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183060
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821900
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 505870
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 25 | 25 | 25 | 559260
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792800
73 | Ghorashal (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 296386
76 | Siddhirganj (Desh) | 100 | 0 | [10 empty] | 5 | 50 | 80 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1209600
77 | Siddhirganj (Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 96 | 96 | 94 | 94 | 90 | 95 | 60 |  | 80 | 96 | 98 | 98 | 100 | 100 | 100 | 2339520
78 | Gazipur (RPCL) | 42 | 42 | 42 | 25 | 25 | 25 | 25 | 25 | 37 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 908832
79 | Kodda 149 MW | 133 | 133 | 125 | 40 | 16 | 16 | 16 | 16 | 98 | 82 | 82 | 90 | 117 | 117 | 117 | 117 | 117 | 117 |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 2257440
80 | Jamalpur 95MW | 88 | 88 | 88 | 72 | 72 | 8 | 8 | 8 | 8 | 8 | 56 | 80 | 0 | 8 | 24 | 48 | 48 | 83 |  | 80 | 80 | 80 | 87 | 88 | 88 | 87 | 1381440
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 75 | 50 | 64 | 64 | 80 | 80 | 80 | 80 | 80 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1881552
83 | Pagla (DPA ) | 21 | 10 | 0 |  |  | 0 | 10 | 11 | 11 | 21 | 21 | 21 | 21 | 50 | 50 | 50 | 11 | 11 |  | 50 | 51 | 51 | 50 | 51 | 51 | 51 | 643910
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 82 | 82 | 85 | 85 | 21 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1881552
85 | Keraniganj (Powerpac) 100MW | 100 | 88 | 88 | 86 | 86 | 10 | 10 | 10 | 50 | 73 | 86 | 86 | 100 | 100 | 100 | 100 | 100 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1957038
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 100 | 100 | 60 | 7 | 7 | 35 | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 65 |  | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 2111040
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 68 | 68 | 68 | 68 | 80 | 68 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1962120
92 | Fenchuganj (EPL) 44MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 47 | 25 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1097000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | 102 | 102 | 102 | 48 | 7 | 7 | 7 | 7 | 24 | 48 | 70 | 84 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1922544
95 | Patenga 50MW | 44 | 44 | 39 | 44 | 39 | 44 | 44 | 43 | 43 | 36 | 36 | 36 | 35 | 35 | 35 | 37 | 37 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 993600
96 | Chittagong ECPV 108 MW | 91 | 86 | 91 | 91 | 91 | 91 | 91 | 88 | 91 | 84 | 78 | 83 | 82 | 88 | 88 | 88 | 88 | 88 |  | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 2108160
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 34 | 28 | 40 |  | 40 | 40 | 40 | 35 | 32 | 40 | 39 | 931680
98 | Bosila 108MW | 70 | 70 | 70 | 71 | 71 | 71 | 70 | 71 | 71 | 71 | 71 | 71 | 65 | 61 | 60 | 69 | 60 | 65 |  | 70 | 70 | 70 | 70 | 71 | 71 | 71 | 1640640
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 55 | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1317612
100 | Northern 55 MW | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 29 | 49 | 51 | 54 | 53 | 53 | 55 | 56 | 55 | 55 | 55 |  | 56 | 56 | 55 | 55 | 56 | 56 | 56 | 1236346
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 163 | 130 | 130 | 100 | 100 |  | 163 | 100 | 100 | 100 | 130 | 163 | 130 | 3245571
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.4 | 1.1 | 1.6 | 2.2 | 2.4 | 2.4 | 2.2 | 1.2 | 1 | 0.6 | 0.3 | 0 | [8 empty] | 15700
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299960
104 | APR Energy , Keranigonj | [17 empty] | 12 |  | 215 | 158 | 104 | 51 | 51 | 51 | 0 | 529709
105 | Bramhangoan 100 MW (Aggreko) | [13 empty] | 10 | 94 | 98 | 10 | 10 |  | 98 | 97 | 97 | 96 | 52 | 52 | 52 | 637332
106 | United Mymensingh PPL | 187 | 190 | 192 | 190 | 190 | 190 | 189 | 190 | 190 | 185 | 187 | 180 | 180 | 189 | 185 | 185 | 185 | 187 |  | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 4466400
112 | Aggreko Aurahati 100MW | [13 empty] | 10 | 100 | 100 | 11 | 11 |  | 100 | 100 | 101 | 100 | 100 | 99 | 100 | 857350
114 | Summit Gazipur-1 150MW | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 106 | 2355840
115
116
117
118
120 | Eastern Zone Total | 7776 | 7643 | 7569 | 7384 | 7304 | 6839 | 6461.4 | 6509.1 | 6682.6 | 6992.2 | 7143.4 | 7271.4 | 7230.2 |  | 7633.8 | 7691.1 | 7314.8 | 7004 |  | 8351 | 8274 | 8245 | 8254 | 8172 | 8199 | 8000 | 179281656
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 90 | 90 | 90 | 51 | 10 | 10 | 10 | 10 | 51 | 69 | 82 | 85 | 85 | 84 | 84 | 82 | 82 | 85 |  | 92 | 92 | 86 | 87 | 85 | 85 | 87 | 1611840
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 49 | 16 | 16 | 16 | 60 | 65 | 98 | 97 | 97 | 97 | 78 | 82 | 95 | 98 |  | 99 | 105 | 105 | 108 | 109 | 115 | 115 | 2046720
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 44 | 44 | 44 | 44 | 44 | 23 | 0 | [10 empty] | 15 |  | 40 | 41 | 41 | 36 | 39 | 39 | 39 | 467040
129 | Khulna CCPP 225MW | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 | 160 | 160 | 175 |  | 233 | 240 | 240 | 241 | 240 | 241 | 241 | 3867360
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2674560
136 | Barisal GT: Unit-1, 2 | 22 | 22 | 22 | 12 | 0 | [14 empty] | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 219868
137 | Bhola Aggreko 95MW | 50 | 50 | 47 | 54 | 55 | 55 | 56 | 55 | 55 | 55 | 55 | 55 | 52 | 53 | 86 | 88 | 90 | 96 |  | 96 | 97 | 97 | 97 | 97 | 97 | 95 | 1674000
| Bhola CCPP 194MW | 118 | 120 | 118 | 100 | 100 | 100 | 100 | 120 | 100 | 120 | 104 | 110 | 100 | 120 | 100 | 100 | 100 | 120 |  | 100 | 101 | 120 | 105 | 118 | 120 | 102 | 2678000
140 | Bhola (Venture) 33MW | 37 | 31 | 32 | 33 | 33 | 28 | 26 | 25 | 25 | 25 | 24 | 25 | 25 | 26 | 23 | 24 | 25 | 23 |  | 32 | 30 | 32 | 15 | 32 | 33 | 33 | 663414
141 | Bangla Trak Noapara | [17 empty] | 10 |  | 94 | 94 | 94 | 91 | 91 | 91 | 91 | 597120
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 33 | 8 | 8 | 0 |  | 27 | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 770250
143 | Gopalganj Peaking | 40 | 40 | 35 | 30 | 10 | 10 | 0 | [9 empty] | 20 | 46 |  | 55 | 64 | 82 | 67 | 75 | 67 | 56 | 580224
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 778 | 779 | 778 | 779 | 779 | 778 | 779 | 777 | 777 | 777 | 778 | 777 | 777 | 777 | 777 | 777 | 777 | 777 |  | 782 | 782 | 783 | 782 | 782 | 782 | 782 | 18663273
147 | Bheramara 360 MW | 410 | 410 | 410 | 415 | 413 | 416 | 416 | 411 | 412 | 380 | 380 | 410 | 400 | 410 | 410 | 370 | 370 | 300 |  | 410 | 410 | 410 | 412 | 410 | 410 | 414 | 9842976
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 170 | 170 | 169 | 170 | 170 | 171 | 170 | 170 | 170 | 169 | 169 | 169 | 169 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 169 | 169 | 414360
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 0 | [15 empty] | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 388776
157 | Sirajgonj Unit-1 225MW (Gas) | 200 | 199 | 199 | 184 | 182 | 181 | 189 | 182 | 187 | 190 | 186 | 182 | 181 | 191 | 194 | 187 | 183 | 181 |  | 188 | 181 | 183 | 190 | 194 | 193 | 188 | 4791300
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | [17 empty] | 80 |  | 150 | 150 | 150 | 151 | 151 | 151 | 150 | 942092
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | 42 | 42 | 0 | [14 empty] | 26 |  | 52 | 51 | 51 | 51 | 50 | 50 | 50 | 396373
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509280
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 9 | 9 | 9 |  | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 226476
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 237528
165 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1010620
166 | Katakhali (Northern) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 43 | 43 | 43 | 1155936
167 | Katakhali Peaking | 35 | 35 | 35 | 35 | 35 | 0 | [11 empty] | 24 |  | 29 | 30 | 32 | 29 | 29 | 29 | 29 | 373998
168 | Santahar Peaking | 32 | 32 | 32 | 32 | 32 | 0 | [10 empty] | 7 | 31 |  | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 398516
169 | Rajlanka 52 MW | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 52 | 52 | 52 | 52 | 1064160
170 | Chapainawabganj-100 MW | 90 | 81 | 81 | 81 | 81 | 50 | 24 | 24 | 24 | 0 | [7 empty] | 10 |  | 99 | 102 | 102 | 102 | 102 | 96 | 90 | 1049720
171
172
173 | Rangpur GT | 8 | 8 | 8 | 0 | [13 empty] | 17 |  | 12 | 8 | 8 | 10 | 10 | 10 | 10 | 91000
175 | Saidpur GT | 12 | 12 | 12 | 0 | [15 empty] | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 138000
176
177
178
178 | Western Zone Total | 2809 | 2726 | 2673 | 2578 | 2429 | 2249 | 2194 | 2193 | 2264 | 2280 | 2314 | 2354 | 2329 | 2371 | 2405 | 2364 | 2404 | 2649 | 0 | 3183 | 3198 | 3238 | 3202 | 3234 | 3228 | 3190 | 59544780